## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-01 | Tuesday
|  |  | Date (day): | 2020-12-01 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13397.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14533 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-30 | 2020-12-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 100 | 100 | 100 |  | 70
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 71 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 101 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 360 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 293 | 250 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 340 | 400 | 400 |  |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 33 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 144 | 125 | 155 | 155 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 52 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 14 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 64 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 115 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 53 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 168 | 0 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2004 | 2412 | 3984 | 4324 | 498 | 1177
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 128 | 125 | 127 | 127 | 103 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 203 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 143 | 138 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 20 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 158 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 10 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 637 | 980 | 1688 | 1673 | 463 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 160 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 275 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 142 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 46 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 110 | 144 | 154
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 24 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 106 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 877 | 1095 | 1711 | 1972 | 467 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 101 | 100 | 130 | 130 | 72 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 17 | 59 | 17 | 17 |  | 78 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 65 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 49 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 254 | 294 | 530.6 | 479 | 72 | 83
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 265 | 265 | 260 | 260 |  | 70 | Machine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 33 | 36 | 36 | 36 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 90 | 150 | 150
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 8 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 325 | 325 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 435 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1549 | 1593 | 1682 | 1682 | 0 | 112
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 400 | 400 | 403 | 403
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 300 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 745 | 839 | 1158 | 1584 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 68 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 330 | 530 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 34 | 88 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 407 | 711 | 867 | 927 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 180 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 205 | 180 | 225 | 225 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 432 | 391 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 861 | 897 | 1506 | 1629 | 200 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 145 | 253 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7479 | 9074 | 13397.6 | 14533 | 1994 | 2136
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6969.6302 | 8456 | 12485.134 | 13543.2056
| A. |  | 2020-11-30 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9074 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5628 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9074 | MW
| 3 | Day peak Generation : |  |  | 7479 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8456 | MW
| 4 | Evening peak Generation : |  |  | 9074 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 173.8227 | MKWHr | By Solar | 0.43807 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 128.0443 | MKWHr |  | By Oil: | 18.4527 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.2177 | MKWHr |  | By Hydro: | 2.9883 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1994 | MW | Dhaka | 3185 | 3185 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2136 | MW | Chittagong | 952 | 952 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4130 | MW | Khulna | 1024 | 1024 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1042.94 | MMCFD |  |  | Rajshahi | 851 | 851 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 142677986.272 | ii) Oil : | Taka | 93904210.16 | Comilla | 707 | 707 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 57174783 | Total | Taka | 293756979.432 | Mymensingh | 625 | 625 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.8875 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -185 | MW (E to W) at | 19:00 | hrs | Barisal | 232 | 232 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -225 | MW at | 8:00 | hrs | Rangpur | 566 | 566 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 8456 | 8456 |  | 0
| B. |  | 2020-12-01 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 28.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14533 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 5333 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 176.2364 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5633 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.5658 | MKWHr. | ii) HVDC Flow at Peak Time |  | 400 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1158 | MKWHr. | iii) Maximum HVDC Flow : |  | 401 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.51 |  | (b) Today: | 100.27 |  | (c) Rule Curve: |  | 106.1
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-11-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 13 | 40 | 339 | 334 |  | 0 | 350 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 80 | 0 | 275 | 0 | 52 | 8 | 72 | 29 | 20 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 4 | 21 | 80 | 130 | 0 | 20 | 0 | 60 | 60 | 50 | 47 | 110 | 260 | 36 | 5 | 0 | 100 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 397 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 13 | 0 | 130 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 0 |  | 4406 | 1886 | 6292 | 3126 | 397 | 1756 | 330 | 480 | 123 | 0 | 80 | 0 | 0 | 100.56
2:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 340 | 327 |  | 0 | 310 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 25 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 80 | 0 | 275 | 0 | 56 | 8 | 72 | 29 | 20 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 129 | 0 | 0 | 0 | 60 | 60 | 11 | 25 | 110 | 257 | 36 | 5 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 400 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 13 | 0 | 130 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4256 | 1714 | 5970 | 3082 | 400 | 1571 | 330 | 390 | 123 | 0 | 74 | 0 | 0 | 100.55
3:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 338 | 283 |  | 0 | 300 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 22 | 25 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 80 | 0 | 260 | 0 | 112 | 8 | 72 | 29 | 20 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 129 | 0 | 0 | 0 | 60 | 60 | 11 | 10 | 110 | 253 | 20 | 5 | 0 | 100 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 400 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 151 | 0 | 13 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4117 | 1696 | 5813 | 3056 | 400 | 1468 | 303 | 389 | 123 | 0 | 74 | 0 | 0 | 100.54
4:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 292 | 283 |  | 0 | 300 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 25 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 80 | 0 | 265 | 0 | 221 | 8 | 72 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 72 | 130 | 0 | 0 | 0 | 40 | 60 | 11 | 10 | 110 | 253 | 20 | 5 | 0 | 72 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 400 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 136 | 0 | 13 | 0 | 130 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4080 | 1626 | 5706 | 3033 | 400 | 1388 | 303 | 389 | 121 | 0 | 72 | 0 | 0 | 100.53
5:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 280 | 283 |  | 0 | 300 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 25 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 80 | 0 | 250 | 0 | 181 | 8 | 72 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 72 | 131 | 0 | 0 | 0 | 40 | 60 | 11 | 10 | 110 | 258 | 20 | 5 | 0 | 70 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 400 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 37 | 0 | 0 |  | 4022 | 1606 | 5628 | 2969 | 400 | 1363 | 313 | 390 | 121 | 0 | 72 | 0 | 0 | 100.52
6:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 312 | 310 |  | 0 | 300 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 25 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 80 | 0 | 285 | 0 | 183 | 8 | 75 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 70 | 152 | 0 | 0 | 0 | 40 | 60 | 11 | 10 | 110 | 260 | 20 | 5 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 |  | 399 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4210 | 1627 | 5837 | 3115 | 399 | 1429 | 313 | 390 | 121 | 0 | 70 | 0 | 0 | 100.51
7:00 | 0 | 0 | 0 | 115 | 200 | 14 | 20 | 353 | 310 |  | 0 | 300 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 22 | 25 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 213 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 80 | 0 | 285 | 0 | 182 | 8 | 78 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 70 | 152 | 0 | 0 | 0 | 40 | 60 | 11 | 10 | 110 | 260 | 20 | 5 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 168 | 0 |  | 399 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 141 | 0 | 13 | 0 | 130 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4348 | 1811 | 6159 | 3326 | 399 | 1516 | 330 | 390 | 123 | 0 | 70 | 5 | 0 | 100.5
8:00 | 0 | 0 | 0 | 115 | 200 | 54 | 30 | 362 | 361 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 22 | 25 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 206 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 0 | 80 | 0 | 275 | 0 | 217 | 8 | 80 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 14 | 0 | 7 | 18 | 78 | 132 | 12 | 17 | 1 | 40 | 60 | 17 | 17 | 130 | 262 | 36 | 5 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 399 | 33 | 0 | 0 | 2 | 0 | 5 | 0 | 0 | 0 | 20 | 0 | 8 | 8 | 168 | 0 |  | 400 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4776 | 1843 | 6619 | 3495 | 400 | 1708 | 413 | 390 | 124 | 0 | 78 | 11 | 0 | 100.49
9:00 | 0 | 0 | 0 | 115 | 200 | 54 | 40 | 365 | 339 |  | 0 | 400 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 80 | 0 | 260 | 0 | 190 | 8 | 74 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 82 | 108 | 17 | 20 | 1 | 40 | 60 | 48 | 43 | 163 | 260 | 35 | 50 | 0 | 100 | 0 | 0 | 0 | 310 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 399 | 65 | 6 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 17 | 16 | 168 | 0 |  | 399 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 167 | 0 | 13 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 27 | 0 | 0 |  | 5045 | 1964 | 7009 | 3568 | 399 | 1944 | 467 | 390 | 125 | 0 | 82 | 34 | 0 | 100.48
10:00 | 0 | 0 | 0 | 115 | 200 | 86 | 40 | 340 | 323 |  | 0 | 340 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 265 | 0 | 158 | 8 | 76 | 5 | 5 | 0 | 24 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 84 | 108 | 17 | 20 | 2 | 40 | 60 | 45 | 47 | 110 | 262 | 20 | 50 | 0 | 100 | 0 | 0 | 0 | 290 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 399 | 65 | 34 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 41 | 40 | 168 | 13 |  | 400 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 157 | 0 | 12 | 0 | 180 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 250 | 15 | 0 | 0 |  | 5032 | 1917 | 6949 | 3513 | 400 | 1808 | 562 | 390 | 125 | 0 | 84 | 67 | 0 | 100.48
11:00 | 0 | 0 | 0 | 115 | 200 | 95 | 40 | 360 | 303 |  | 0 | 340 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 213 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 280 | 0 | 167 | 8 | 78 | 5 | 5 | 0 | 34 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 86 | 105 | 34 | 20 | 2 | 40 | 60 | 48 | 43 | 110 | 260 | 20 | 77 | 0 | 100 | 0 | 0 | 0 | 310 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 0 | 0 | 405 | 65 | 17 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 53 | 47 | 168 | 8 |  | 400 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 180 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 6 | 0 | 0 |  | 5149 | 1997 | 7146 | 3571 | 400 | 1895 | 571 | 420 | 127 | 0 | 86 | 76 | 0 | 100.46
12:00 | 0 | 0 | 0 | 115 | 200 | 98 | 50 | 365 | 293 |  | 0 | 340 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 216 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 300 | 0 | 186 | 8 | 80 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 90 | 101 | 17 | 20 | 2 | 60 | 60 | 47 | 43 | 130 | 265 | 33 | 77 | 0 | 100 | 0 | 0 | 0 | 310 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 405 | 65 | 17 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 53 | 49 | 168 | 10 |  | 400 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 193 | 0 | 23 | 0 | 205 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 330 | 34 | 0 | 0 |  | 5321 | 2158 | 7479 | 3729 | 400 | 1977 | 606 | 470 | 128 | 0 | 90 | 79 | 0 | 100.45
13:00 | 0 | 0 | 0 | 115 | 200 | 98 | 69 | 364 | 283 |  | 0 | 340 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 280 | 0 | 156 | 8 | 70 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 90 | 100 | 17 | 20 | 2 | 60 | 60 | 50 | 43 | 130 | 257 | 32 | 80 | 0 | 100 | 0 | 0 | 0 | 300 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 90 | 0 | 1 | 406 | 65 | 17 | 0 | 4 | 32 | 37 | 0 | 0 | 13 | 90 | 0 | 88 | 45 | 168 | 0 |  | 400 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 186 | 0 | 64 | 0 | 193 | 0 | 410 | 90 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 430 | 67 | 0 | 0 |  | 5417 | 2363 | 7780 | 3593 | 400 | 2036 | 892 | 570 | 126 | 0 | 90 | 73 | 7780 | 100.44
14:00 | 0 | 0 | 0 | 115 | 200 | 97 | 69 | 348 | 286 |  | 0 | 340 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 280 | 0 | 164 | 8 | 70 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 5 | 33 | 21 | 100 | 100 | 17 | 20 | 2 | 60 | 60 | 50 | 43 | 130 | 254 | 32 | 20 | 0 | 90 | 0 | 0 | 0 | 300 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 20 | 409 | 65 | 17 | 0 | 3 | 16 | 17 | 0 | 0 | 8 | 50 | 0 | 90 | 38 | 168 | 0 |  | 400 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 155 | 0 | 68 | 0 | 162 | 0 | 375 | 35 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 410 | 45 | 0 | 0 |  | 5240 | 2165 | 7405 | 3511 | 400 | 1931 | 742 | 550 | 124 | 0 | 100 | 47 | 0 | 100.43
15:00 | 0 | 0 | 0 | 115 | 200 | 94 | 67 | 346 | 285 |  | 0 | 340 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 80 | 0 | 295 | 0 | 163 | 8 | 70 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 5 | 33 | 21 | 96 | 98 | 17 | 20 | 1 | 60 | 60 | 50 | 43 | 130 | 253 | 32 | 81 | 0 | 90 | 0 | 0 | 0 | 300 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 10 | 363 | 65 | 17 | 0 | 2 | 16 | 17 | 0 | 0 | 8 | 50 | 0 | 75 | 26 | 168 | 0 |  | 401 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 155 | 0 | 58 | 0 | 161 | 0 | 406 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 410 | 37 | 0 | 0 |  | 5213 | 2157 | 7370 | 3472 | 401 | 1998 | 699 | 550 | 122 | 0 | 96 | 32 | 0 | 100.42
16:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 344 | 285 |  | 0 | 340 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 80 | 0 | 295 | 0 | 163 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 88 | 98 | 17 | 20 | 0 | 60 | 60 | 50 | 43 | 130 | 254 | 32 | 81 | 0 | 90 | 0 | 0 | 0 | 310 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 10 | 316 | 65 | 17 | 0 | 1 | 16 | 17 | 0 | 0 | 8 | 50 | 0 | 53 | 9 | 165 | 0 |  | 400 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 34 | 0 | 161 | 0 | 418 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 410 | 51 | 0 | 0 |  | 5093 | 2151 | 7244 | 3399 | 400 | 2012 | 660 | 550 | 123 | 0 | 88 | 12 | 0 | 100.41
17:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 344 | 270 |  | 0 | 340 | 142 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 4 | 0 | 80 | 0 | 305 | 0 | 160 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 2 | 21 | 5 | 33 | 21 | 94 | 100 | 50 | 20 | 0 | 60 | 60 | 50 | 43 | 130 | 260 | 32 | 81 | 0 | 90 | 0 | 0 | 0 | 300 | 8 | 5 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 12 | 316 | 65 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 8 | 50 | 0 | 53 | 0 | 144 | 0 |  | 399 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 34 | 0 | 161 | 0 | 423 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 410 | 56 | 0 | 0 |  | 5153 | 2225 | 7378 | 3404 | 399 | 1998 | 795 | 550 | 122 | 16 | 94 | 0 | 0 | 100.4
18:00 | 0 | 100 | 0 | 115 | 200 | 97 | 70 | 350 | 265 |  | 0 | 340 | 150 | 24 | 38 | 15 | 0 | 0 | 0 | 24 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 25 | 25 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 218 | 0 | 146 | 0 |  | 0 | 0 | 17 | 0 | 0 | 29 | 20 | 10 | 0 | 80 | 0 | 310 | 0 | 144 | 8 | 54 | 5 | 5 | 0 | 51 | 0 | 0 | 19 | 21 | 8 | 33 | 21 | 112 | 100 | 59 | 20 | 0 | 60 | 60 | 47 | 47 | 130 | 263 | 35 | 81 | 0 | 90 | 0 | 0 | 0 | 290 | 8 | 5 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 83 | 429 | 115 | 45 | 0 | 0 | 151 | 48 | 0 | 0 | 84 | 100 | 0 | 72 | 0 | 17 | 0 |  | 399 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 171 | 0 | 66 | 0 | 174 | 0 | 421 | 90 | 0 | 0 | 0 | 101 | 0 | 0 | 90 | 490 | 66 | 0 | 0 |  | 6168 | 2591 | 8759 | 3675 | 399 | 2040 | 1714 | 630 | 124 | 65 | 112 | 0 | 0 | 100.39
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 100 | 0 | 115 | 200 | 101 | 71 | 360 | 250 |  | 0 | 340 | 125 | 33 | 52 | 14 | 0 | 0 | 0 | 50 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 138 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 15 | 0 | 80 | 0 | 275 | 0 | 160 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 33 | 21 | 110 | 100 | 59 | 20 | 0 | 60 | 60 | 47 | 47 | 163 | 265 | 36 | 81 | 0 | 90 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 142 | 435 | 115 | 53 | 0 | 0 | 158 | 54 | 0 | 0 | 106 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 180 | 0 | 391 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 530 | 88 | 0 | 0 |  | 6374 | 2700 | 9074 | 3667 | 400 | 2063 | 1958 | 670 | 125 | 81 | 110 | 0 | 0 | 100.38
19:30 | 0 | 93 | 0 | 115 | 200 | 101 | 72 | 350 | 224 |  | 0 | 340 | 144 | 7 | 15 | 0 | 0 | 0 | 0 | 20 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 18 | 0 | 80 | 0 | 290 | 0 | 169 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 106 | 100 | 43 | 20 | 0 | 60 | 60 | 50 | 47 | 163 | 260 | 35 | 81 | 0 | 90 | 0 | 0 | 0 | 310 | 8 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 150 | 433 | 115 | 36 | 0 | 0 | 160 | 54 | 0 | 0 | 106 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 290 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 174 | 0 | 67 | 0 | 184 | 0 | 430 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 530 | 88 | 0 | 0 |  | 6139 | 2743 | 8882 | 3667 | 400 | 2103 | 1747 | 670 | 125 | 64 | 106 | 0 | 0 | 0
20:00 | 0 | 93 | 0 | 115 | 200 | 101 | 71 | 347 | 231 |  | 0 | 340 | 145 | 10 | 15 | 0 | 0 | 0 | 0 | 8 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 25 | 0 | 80 | 0 | 275 | 0 | 169 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 106 | 99 | 42 | 20 | 0 | 60 | 60 | 50 | 47 | 163 | 253 | 36 | 81 | 0 | 90 | 18 | 0 | 0 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 133 | 436 | 115 | 35 | 0 | 0 | 161 | 54 | 0 | 0 | 106 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 178 | 0 | 67 | 0 | 182 | 0 | 420 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 530 | 97 | 0 | 0 |  | 6080 | 2734 | 8814 | 3651 | 400 | 2095 | 1703 | 670 | 125 | 64 | 106 | 0 | 0 | 100.37
21:00 | 0 | 93 | 0 | 115 | 200 | 98 | 72 | 349 | 232 |  | 0 | 340 | 138 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 33 | 0 | 80 | 0 | 275 | 0 | 172 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 102 | 100 | 42 | 20 | 0 | 60 | 60 | 53 | 47 | 163 | 250 | 36 | 81 | 0 | 90 | 18 | 0 | 0 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 150 | 437 | 115 | 17 | 0 | 0 | 161 | 54 | 0 | 0 | 65 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 179 | 0 | 67 | 0 | 183 | 0 | 435 | 90 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 500 | 98 | 0 | 0 |  | 5997 | 2588 | 8585 | 3643 | 400 | 2131 | 1494 | 640 | 127 | 48 | 102 | 0 | 0 | 100.36
22:00 | 0 | 93 | 0 | 115 | 200 | 98 | 72 | 341 | 223 |  | 0 | 340 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 25 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 36 | 0 | 80 | 0 | 275 | 0 | 172 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 100 | 100 | 42 | 20 | 0 | 60 | 60 | 53 | 47 | 163 | 251 | 36 | 81 | 0 | 90 | 18 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 426 | 85 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 8 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 175 | 0 | 67 | 0 | 178 | 0 | 435 | 35 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 500 | 91 | 0 | 0 |  | 5529 | 2406 | 7935 | 3605 | 400 | 2109 | 929 | 640 | 127 | 25 | 100 | 0 | 0 | 100.35
23:00 | 0 | 93 | 0 | 115 | 200 | 98 | 72 | 344 | 223 |  | 0 | 340 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 216 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 290 | 0 | 174 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 90 | 112 | 17 | 20 | 0 | 60 | 60 | 53 | 47 | 163 | 258 | 36 | 78 | 0 | 85 | 18 | 0 | 0 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 426 | 55 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 0 | 0 |  | 400 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 175 | 0 | 13 | 0 | 178 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 99 | 0 | 0 |  | 5127 | 2167 | 7294 | 3642 | 400 | 2011 | 424 | 600 | 127 | 0 | 90 | 0 | 0 | 100.34
24:00 | 0 | 93 | 0 | 115 | 200 | 98 | 72 | 342 | 223 |  | 0 | 360 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 80 | 0 | 260 | 0 | 179 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 0 | 21 | 86 | 130 | 17 | 20 | 0 | 60 | 60 | 53 | 47 | 163 | 256 | 36 | 78 | 0 | 85 | 18 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 405 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 34 | 0 | 0 | 0 |  | 400 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 174 | 0 | 13 | 0 | 173 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 80 | 0 | 0 |  | 4977 | 2082 | 7059 | 3549 | 400 | 1976 | 321 | 600 | 127 | 0 | 86 | 0 | 0 | 100.33
KWH | 0 | 660100 | 0 | 2772000 | 4792700 | 1642409 | 1224608 | 8318970 | 6842000 |  | 0 | 7911000 | 3331404 | 75840 | 153648 | 34740 | 0 | 0 | 0 | 110400 | 294048 | 293760 | 0 | 0 | 0 | 0 | 806400 | 130415 | 0 | 268416 | 600000 | 702360 | 591400 | 629400 | 0 | 0 | 2144335 | 844000 | 0 | 0 | 0 | 4902661 | 0 | 2974150 | 0 |  | 0 | 0 | 32528 | 0 | 0 | 270240 | 337104 | 399360 | 0 | 1992525 | 0 | 7007900 | 0 | 3864000 | 217454 | 1516140 | 221832 | 189600 | 0 | 826292 | 0 | 0 | 59266 | 337860 | 103860 | 524000 | 516600 | 2115840 | 2646040 | 498240 | 316692 | 13100 | 1273000 | 1420680 | 940200 | 895896 | 3313881 | 5895000 | 717312 | 1215360 | 0 | 2180150 | 90000 | 0 | 0 | 7353500 | 222528 | 116000 | 0 | 260945 | 0 | 0 | 0 | 0 | 0 | 88695 | 890880 | 0 | 700872 | 9043000 | 1335600 | 355308 | 0 | 27960 | 843055 | 518785 | 0 | 0 | 480480 | 1086720 | 0 | 1114560 | 277250 | 2953440 | 33872 |  | 9565818 | 0 | 7172928 | 0 | 138240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494200 | 43008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336480 | 0 | 211806 | 0 | 0 | 3436000 | 0 | 0 | 0 | 0 | 4090545 | 0 | 829681 | 0 | 4178009 | 0 | 8978363 | 629760 | 0 | 0 | 0 | 481920 | 0 | 31061 | 494304 | 8781700 | 1226320 | 0 | 0 |  | 122702566 | 51120143 | 173822709 | 83207668 | 9565818 | 44836604 | 18126390 | 12217700 | 2988335 | 326288 | 2115840 | 438066 | 0
Fuel Cost | 0 | 976948 | 0 | 4074840 | 5319897 | 2167979.88 | 2081833.6 | 8402159.7 | 7047260 |  | 0 | 8622990 | 3697858.44 | 575625.6 | 1058634.72 | 293900.4 | 0 | 0 | 0 | 831312 | 2681717.76 | 2890598.4 | 0 | 0 | 0 | 0 | 5886720 | 1008107.95 | 0 | 201312 | 450000 | 0 | 0 | 0 | 0 | 0 | 578970.45 | 227880 | 0 | 0 | 0 | 5343900.49 | 0 | 5056055 | 0 |  | 0 | 0 | 315521.6 | 0 | 0 | 2140300.8 | 424751.04 | 1186099.2 | 0 | 2948937 | 0 | 5185846 | 0 | 3554880 | 280515.66 | 1743561 | 250670.16 | 265440 | 0 | 1412959.32 | 0 | 0 | 565990.3 | 429082.2 | 77895 | 917000 | 387450 | 15868800 | 2804802.4 | 4524019.2 | 402198.84 | 208814 | 2087720 | 2273088 | 1673556 | 1397597.76 | 3777824.34 | 6130800 | 1413104.64 | 2321337.6 | 0 | 3771659.5 | 197100 | 0 | 0 | 7427035 | 166896 | 88160 | 0 | 1972744.2 | 0 | 0 | 0 | 0 | 0 | 1036844.55 | 7260672 | 0 | 4941147.6 | 8409990 | 12180672 | 3357660.6 | 0 | 0 | 6373495.8 | 4518617.35 | 0 | 0 | 4117713.6 | 7237555.2 | 0 | 0 | 0 | 0 | 0 |  | 55099111.68 | 0 | 7531574.4 | 0 | 1086566.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766010 | 419758.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646041.6 | 0 | 160337.142 | 0 | 0 | 18623120 | 0 | 0 | 0 | 0 | 5399519.4 | 0 | 1244521.5 | 0 | 4888270.53 | 0 | 8888579.37 | 6574694.4 | 0 | 0 | 0 | 3739699.2 | 0 | 343224.05 | 3652906.56 | 38551663 | 0 | 0 | 0 |  | 209505026.85 | 157615597.312 | 367120624.162 | 91470405.442 | 55099111.68 | 51207580.83 | 90698090.16 | 57174783 | 806850.45 | 3206120 | 15868800 | 1588882.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 98 | 50 | 365 | 293 |  | 0 | 340 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 216 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 300 | 0 | 186 | 8 | 80 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 90 | 101 | 17 | 20 | 2 | 60 | 60 | 47 | 43 | 130 | 265 | 33 | 77 | 0 | 100 | 0 | 0 | 0 | 310 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 405 | 65 | 17 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 53 | 49 | 168 | 10 |  | 400 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 193 | 0 | 23 | 0 | 205 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 330 | 34 | 0 | 0 |  | 7479 | DayPeak
Yesterday Evening Peak | 0 | 100 | 0 | 115 | 200 | 101 | 71 | 360 | 250 | 0 | 0 | 340 | 125 | 33 | 52 | 14 | 0 | 0 | 0 | 50 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 138 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 15 | 0 | 80 | 0 | 275 | 0 | 160 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 33 | 21 | 110 | 100 | 59 | 20 | 0 | 60 | 60 | 47 | 47 | 163 | 265 | 36 | 81 | 0 | 90 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 142 | 435 | 115 | 53 | 0 | 0 | 158 | 54 | 0 | 0 | 106 | 100 | 0 | 90 | 0 | 0 | 0 |  | 400 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 180 | 0 | 391 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 530 | 88 | 0 | 0 |  | 9074 | EvPeak
Forecast for Evening | 0 | 100 | 0 | 115 | 200 | 100 | 78 | 412 | 360 | 0 | 0 | 400 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 80 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 154 | 130 | 17 | 17 | 0 | 60 | 60 | 51 | 44 | 163 | 260 | 36 | 86 | 0 | 150 | 20 | 0 | 0 | 325 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 403 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 100 | 0 | 115 | 200 | 100 | 78 | 412 | 360 | 0 | 0 | 400 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 80 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 130 | 17 | 17 | 1.6 | 60 | 60 | 51 | 44 | 163 | 260 | 36 | 86 | 0 | 150 | 20 | 0 | 0 | 325 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 403 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 93 | 0 | 115 | 200 | 98 | 50 | 297 | 287 | 0 | 0 | 380 | 155 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 22 | 20 |  | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 214 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 20 | 8 | 0 | 80 | 0 | 300 | 0 | 170 | 8 | 50 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 33 | 18 | 76 | 106 | 17 | 20 | 0 | 40 | 5 | 53 | 43 | 120 | 263 | 37 | 75 | 0 | 81 | 18 | 0 | 0 | 280 | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9 | 10 | 0 | 0 | 231 | 59 | 0 | 0 | 1 | 0 | 23 | 0 | 0 | 0 | 20 | 0 | 40 | 17 | 0 | 0 | 0 | 399 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 178 | 0 | 13 | 0 | 188 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 47 | 0 | 0 | 0
199
| Minimum Generation |  | 5628 | 5:00
| Highest Generation |  | 9074 | 19:00
| Day Peak Generation |  | 7479 | 12:00
| Evening Peak Generation |  | 9074 | 19:00
| HVDC Max Flow |  | 401 | 15:00
| HVDC EvPeak Flow |  | 400 | 19:00
| Load factor L.F |  | 79.82%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7479 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5633 | MW
Evening Peak Generation : |  | 9074 | MW Hour : | 19:00 | Available Max Generation : |  | 14533 | MW
E.P. Demand (at gen end) : |  | 9074 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9074 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5333 | MW
Total Gen. (MKWH) : |  | 173.8227 | System Load Factor : | 79.82% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -225 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-01
Actual : | 100.27 | Ft.(MSL) , | Rule curve : | 106.1 | Ft.( MSL )
Gas Consumed : | Total = | 1042.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142677986.272
: |  | Coal : | 57174783 | Oil : | 93904210.16 | Total : | 293756979.432
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3204.2796 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1084.2408 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 970.4831 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 876.5723 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 792.3338 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 639.3717 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 364.4433 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 164.8046 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 493.082 |  |  | 0 | 0%
Total | 0 |  | 8589.6112 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10)Ashuganj(S)-360 MW
2) Baghabari-71,100 MW
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-3,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Chandpur-163 MW STG
9) Sirajganj #1 CCPP STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymensing-Mymensing RPCL 132 Ckt-1 was under shut down from 08:36 to 17:22 for A/M.
b) Kaliakoir 400 KV Bus-1 was under shut down from 10:02 to 16:48 for C/M.
c) Madanganj 132/33 kV T-1 transformer was switched on at 10:23.
d) Cumilla(N)-Ashuganj 230 kV Ckt-1 tripped at 08:15 from both end showing Dist. T-phase, E/F relay
at Comilla(N) end & Dist. C-phase at Ashuganj end.
e) Joydevpur 132/33 kV T3 transformer tripped at 09:46 showing main protection operated at 132 kv end
and was switched on at 12:04.
f) Kaptai-Hathazari 132 Ckt-2 was under shut down from 08:46 to 16:32 for A/M.
g) Aminbazar 230/132 T02 transformer was under shut down from 08:53 to 17:27 for A/M.
h) Sreemongal 132/33 T-2 & T-3 transformers were under shut down from 08:36 to 15:10 for A/M.
i) Kulara-Fenchuganj 132 Ckt-1 was under shut down from 09:34 to 14:28 for A/M.
j) Tangail-Mymensing RPCL 132 kV Ckt-2 was under shut down 09:30 to 16:20 for A/M.
k) Netrokona 132/33 T-3 transformers was under shut down from 09:05 to 13:20 for A/M.
l) Sherpur-UMPL 132 kV Ckt-1 was under shut down 08:51 to 16:29 for A/M.
m) Bheramara HVDC 230 kV filter bank-4 was under shut down from 10:15 to 18:04 for A/M.
n) Bheramara HVDC 230 kV Bus-2 was under shut down from 10:44 to 15:29 for A/M.
o) Ashuganj Midland 50 Mw P/P tripped at 08:12 and was synchronized at 08:50.
p) Rangpur-Saidpur 132 kV Ckt-2 was under shut down 08:34 to 16:38 for A/M.
p) Madanganj 132/33 kV T-1 Transformer tripped at 4:40 showing Buchholz relay, backup protection
and was switched on at 10:23 (30/11/2020).
q) Manikganj- Kabirpur 132 kV Ckt-2 along with 132/33 kV GT-2 Transformer was under shut down at
07:34(30-11-2020) for A/M.
r) Baghabari-Ishurdi 230 kV Ckt-2 was under shut down from 08:30 to 22:14 for A/M.
s) After maint Meghnaghat 450 MW GT-1 was synchronized at 08:43.
t) Kaptai- Hathazari 132 kV Ckt-1 was under shut down 08:42 to 17:10 for A/M.
u) Sreemangal 132/33 kV T-2 Transformer was under shut down from 08:32 to 16:45 for A/M.
v) Bibiyana-Fenchuganj 230 kV Ckt-1 was under shut down from 08:58 to 12:59 for A/M.
w) Siddhirganj-Maniknagar 230 kV Ckt-1 was under shut down from 08:32 to 19:25 for A/M.
x) Netrokona 132/33 kV T-3 Transformer was under shut down from 09:10 to 13:20 for A/M.
y) Sherpur- UMPL 132 kV Ckt-1 was under shut down 09:05 to 16:47 for A/M.
z) Jamalpur- UMPL 132 kV Ckt-2 was under shut down 09:23 to 16:28 for A/M.
aa) Rangpur-Saidpur 132 kV Ckt-2 was under shut down 08:38 to 18:02 for A/M.
ab) Satmosjid 132/33 kV T-1 Transformer tripped at 10:05 showing differential B-phase,R -phase
and was switched on at 10:59.
ac) Faridpur 132/33 kV T-1 Transformer was under shut down from 10:03 to 14:14 for oil leakage maint.
ad) Jaldhaka 132/33 kV T-1 Transformer was under shut down from 11:18 to 11:57 for oil leakage maint.
ae) Faridpur 33 kV bus under 132/33 kV T-1 Transformer was under shut down from 12:08 to 12:21 due |  |  |  |  | About 26 MW power interruption occurred under Faridpur S/S
red hot maintenance at 33 kV isolator . |  |  |  |  | areas from 12:08 to 12:21.
af) Tongi 132/33 kV T-2 Transformer was under shut down from 08:58 to 13:37 for A/M.
ag) Savar-Manikganj 160 MW-Aminbazar 132 kV Ckt-1 was under shut down 09:23 to 16:20 for A/M.
ai) Chandpur Desh energy-Ramganj 132 kV Ckt-1 was under shut down 09:11 to 16:45 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 100 | 660100
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4792700 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 71 | 1224608
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 1642409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8318970 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 250 | 6842000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7911000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 33 | 75840 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 125 | 3331404 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 52 | 153648 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 14 | 34740 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 268416
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 110400 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 294048 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 806400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 293760 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 130415 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1302360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 591400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 629400 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 115 | 260945 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 53 | 355308 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1114560 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 2953440 | on test.
| Dhaka area Total |  |  |  | 5895 | 2412 | 46870271
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 88695
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 270240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 2988335 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4902661
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 138 | 2974150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 32528 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 890880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 337104
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 399360
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 158 | 843055 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 518785
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1086720
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 33872
| Chattogram area Total |  |  |  | 2266 | 980 | 15394345
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1992525 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 160 | 3864000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7007900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 221832 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 189600 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 826292
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 700872
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 46 | 1516140 | ST Under maint and Gas shortage
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 337860
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 103860 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2115840 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 524000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 24 | 59266 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 516600
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 106 | 480480
| Cumilla Area Total |  |  |  | 2980 | 1095 | 20674521
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2646040 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 316692
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 59 | 498240 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1335600 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 277250
| Mymensingh Area Total |  |  |  | 637 | 294 | 5086922
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1273000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1420680
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3313881
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 265 | 5895000 | Machin problem.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 940200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 895896
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 116000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 36 | 717312
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1215360
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 90 | 2180150
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 90000 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 222528 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7353500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 435 | 9043000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1593 | 34676507
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 400 | 9565818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 138240 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7172928 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 629760 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 839 | 17506746
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 43008 | Reserve.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 494200 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 68 | 829681
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 530 | 8781700
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 88 | 1226320
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 711 | 11374909
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4090545 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4178009 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 391 | 8978363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 336480
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211806
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 494304
| Rajshahi Area Total |  |  |  | 2183 | 897 | 18289507
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3436000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 481920
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31061
| Rangpur Area Total |  |  |  | 605 | 253 | 3948981
| Total |  |  |  | 19892 | 9074 | 173822709
| Eastern Grid Total |  |  |  | 13766 | 6374 | 122702566
| Western Grid Total |  |  |  | 6126 | 2700 | 51120143
| National Grid Total |  |  |  | 19892 | 9074 | 173822709
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-30
| (a) ENTIRE EASTERN GRID : |  | 5783 | MW | (b) ENTIRE WESTERN GRID : |  | 2673 | MW
| i) Dhaka area |  | 3185 | MW | i) Khulna area |  | 1024 | MW
| ii) Chittagong area |  | 952 | MW | ii) Rajshahi area |  | 851 | MW
| iii) Comilla area |  | 707 | MW | iii) Barisal area |  | 232 | MW
| iv) Mymensingh area |  | 625 | MW | iv) Rangpur area |  | 566 | MW
| v) Sylhet area |  | 314 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8456 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 106 | 10:00 | Jamalpur | 88 | 18:30 | Benapol | 34 | 18:00
| Munsiganj | 84 | 21:00 | Sherpur | 76 | 19:30 | Jhenida | 76 | 18:00
| Sonargaon | 60 | 19:00 | Srimongal | 24 | 18:00 | Bottail | 90 | 18:00
| Shyampur | 182 | 13:00 | Shahjibazar | 82 | 18:30 | G.K Project | 35 | 18:00
| Bhulta | 149 | 12:00 | Fenchuganj | 26 | 18:00 | Faridpur | 130 | 18:00
| Madanganj | 63 | 21:00 | Kulawara | 27 | 18:00 | Madaripur | 62 | 19:00
| Shitalakhya | 96 | 12:00 | Sylhet | 85 | 18:00 | Sariatpur | 40 | 19:30
| Rahim steel | 12 | 1:00 | Chatak | 19 | 18:00 | Gopalganj | 61 | 18:00
| Matuail | 20 | 11:00 | Sunamganj | 26 | 19:30 | Bagerhat | 77 | 19:30
| Ghorasal | 71 |  | Biani Bazar | 36 | 19:00 | Mongla | 34 | 8:00
| Narsingdi | 122 | 20:00 | Comilla (S) | 112 | 18:00 | Satkhira | 74 | 18:30
| Haripur (SBU) | 92 | 11:00 | Comilla(N) | 65 | 18:00 | Gallamari | 18 | 23:00
| Ullon | 46 | 18:00 | Chandpur | 60 | 19:30 | Magura | 38 | 18:30
| Hasnabad | 141 | 18:30 | Feni | 85 | 18:00 | Norail | 27 | 19:00
| Magbazar | 75 | 12:00 | Chowmuhani | 116 | 19:00 | Chuadanga | 60 | 18:00
| Maniknagar | 68 | 18:00 | Ashuganj | 40 | 18:30 | Barisal(N) | 28 | 20:00
| Bangabhaban | 24 | 11:00 | Daudkandi | 84 | 18:00 | Barisal (S) | 68 | 19:00
| Narinda | 76 | 18:00 | B.Baria | 97 | 20:00 | Patuakhali | 76 | 21:00
| Dhanmondi | 103 | 16:00 | Ramganj | 66 | 19:30 | Bhandaria | 40 | 19:00
| Lalbag | 65 | 17:00 | Chaddagram | 23 | 19:00 | Borhan Uddin | 26 | 22:00
| Madartek | 49 | 18:00 | PHP | 5 | 20:00 | Ishurdi | 44 | 19:00
| Dhaka University |  |  | Madunaghat | 44 | 18:00 | Ruppur Paromanobik | 2 | 2:00
| Aftabnagar | 7 | 0.77083 | Hathazari | 71 | 0.79167 | Natore | 79 | 0.75
| Fatullah | 32 | 17:00 | Khulshi | 169 | 21:00 | Bogra | 117 | 18:30
| Mirpur | 76 | 18:00 | Halishahar | 104 | 15:00 | Noagaon | 79 | 18:00
| Kalyanpur | 69 | 18:00 | Baraulia | 140 | 17:00 | Rajshahi | 94 | 19:30
| Gulshan | 88 | 13:00 | Sikalbaha | 23 | 18:30 | Rajshahi New | 8 | 18:00
| Uttara | 68 | 18:00 | Dohazari | 55 | 18:00 | C.Nawabganj | 49 | 13:00
| Uttara New | 20 | 18:00 | Cox'sbazar | 69 | 21:00 | Amnura | 30 | 18:00
| Kamrangirchar | 75 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 82 | 18:00
| Savar | 90 | 18:30 | Kaptai | 3.5 | 18:00 | Shahjadpur | 73 | 18:30
| Bhasantec | 107 | 18:00 | A. Khaer Stl. | 10 | 18:00 | Serajganj | 66 | 19:00
| Agargaon | 49 | 13:00 | Bakulia | 80 | 18:30 | Niyamatpur | 37 | 18:00
| Satmosjid | 60 | 0.75 | Julda | 21 | 0.75 | Joypurhat | 40 | 0.75
| Tongi | 84 | 10:00 | TK chemical | 19.7 | 18:30 | Sherpur(Bogura) | 36 | 19:30
| Kabirpur | 173 | 18:00 | Modern Steel | 18 | 19:30 | Mohastangor | 30 | 18:00
| Basundhara | 95 | 18:00 | Shahmirpur | 16 | 13:00 | Rangpur | 97 | 18:30
| Manikganj | 56 | 20:00 | Khagrachhari | 20 | 19:00 | Lalmonirhat | 42 | 18:00
| Joydevpur | 122 | 18:00 | Matarbari | 28 | 18:30 | Saidpur | 88 | 18:00
| New Tongi | 76 | 18:00 | Baroiar Hat | 18 | 18:30 | Purbasadipur | 81 | 19:30
| Kodda | 188 | 12:00 | Rangamati | 8 | 12:00 | Thakurgaon | 60 | 18:00
| Dhamrai | 68 | 18:30 | Abul Khair 230 | 17 | 13:00 | Palashbari | 87 | 18:00
| Rajendrapur | 76 | 19:00 | BSRM | 155 | 12:00 | Barapukuria | 34 | 18:00
| Valuka | 72 | 18:00 | GPH Ispat | 86 | 14:00 | Panchagar | 43 | 18:00
| Tangail | 133 | 18:00 | Goalpara | 16 | 19:00 | Joldhaka | 20 | 18:30
| Mymensing | 146 | 18:00 | Central s/s | 75 | 18:30 | Kurigram | 43 | 18:00
| Kishorganj | 80 | 19:30 | Noapara | 42 | 19:00
| Netrokona | 78 | 19:30 | Jessore | 81 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 4:00 | 403 | 12:00 | Kaliakoir | 389 | 0.125 | 370 | 0.5
| Bheramara | 412 | 5:00 | 398 | 10:00 | Bhulta | 388 | 0.16667 | 377 | 0.5
| Ashuganj(N) | 393 | 4:00 | 382 | 12:00 | Gopalganj | 420 | 0.16667 | 400 | 0.77083
| Payra | 420 | 6:00 | 410 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 8:00 | Comilla (N) | 238 | 5:00 | 230 | 12:00
| Ishurdi | 237 | 4:00 | 226 | 12:00 | Hathazari | 223 | 19:00 | 211 | 10:00
| Ashuganj | 239 | 2:00 | 231 | 12:00 | Megnaghat | 238 | 3:00 | 230 | 15:00
| Serajganj | 231 | 1:00 | 229 | 8:00 | Fenchuganj | 244 | 4:00 | 239 | 21:00
| Baghabari | 240 | 1:00 | 238 | 7:00 | Siddhirganj | 234 | 4:00 | 221 | 11:00
| Barapukuria | 235 | 21:00 | 225 | 8:00 | Maniknagar | 233 | 4:00 | 224 | 12:00
| Bogra | 232 | 2:00 | 224 | 8:00 | Agargaon | 235 | 4:00 | 225 | 12:00
| Rajshahi | 228 | 24:00 | 217 | 8:00 | Barisal | 250 | 6:00 | 244 | 11:00
| Khulna South | 232 | 4:00 | 215 | 8:00 | AKSML | 226 | 18:00 | 211 | 12:00
| Rampura | 232 | 1:00 | 226 | 11:00 | BSRM | 227 | 20:00 | 214 | 12:00
| Haripur | 231 | 1:00 | 224 | 12:00 | Bibiyana | 244 | 24:00 | 239 | 12:00
| Hasnabad | 232 | 1:00 | 225 | 12:00 | Bhulta | 235 | 19:00 | 227 | 17:00
| Shyampur | 232 | 6:00 | 220 | 11:00 | Ashuganj (S) | 334 | 21:00 | 230 | 15:00
| Aminbazar | 234 | 1:00 | 225 | 12:00 | Kaliakoir | 236 | 4:00 | 225 | 13:00
| Tongi | 230 | 4:00 | 219 | 11:00 | GPH | 223 | 4:00 | 212 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 2:00 | 133 | 11:00 | Madanhat | 136 | 0.77083 | 130 | 0.29167
| Munsiganj | 139 | 19:00 | 132 | 12:00 | Hathazari | 135 | 0.79167 | 128 | 0.5
| Sonargaon | 134 | 1:00 | 132 | 10:00 | Khulshi | 132 | 0.77083 | 125 | 0.41667
| Shyampur | 135 | 5:00 | 129 | 12:00 | Halishahar | 135 | 0.79167 | 126 | 0.45833
| Bhulta | 130 | 2:00 | 126 | 12:00 | Baraulia | 133 | 0.79167 | 126 | 0.5
| Madanganj | 137 | 19:00 | 130 | 11:00 | Sikalbaha | 134 | 0.77083 | 127 | 0.5
| Shitalakhya | 140 | 2:00 | 131 | 12:00 | Dohazari | 131 | 0.77083 | 126 | 0.41667
| Rahim steal | 138 | 1:00 | 134 | 11:00 | Cox'sbazar | 126 | 0.625 | 121 | 0.41667
| Matuail | 138 | 2:00 | 133 | 11:00 | Chandraghona | 134 | 0.75 | 129 | 0.5
| Ghorasal | 140 | 1:00 | 136 | 13:00 | Kaptai | 135 | 0.8125 | 129 | 0.41667
| Narsinghdi | 136 | 1:00 | 131 | 10:00 | A. Khaer Stl. | 133 | 0.83333 | 127 | 0.45833
| Haripur (SBU) | 138 | 3:00 | 134 | 11:00 | Bakulia | 133 | 0.79167 | 126 | 0.41667
| Ullon | 133 | 1:00 | 128 | 11:00 | Julda | 135 | 0.77083 | 127 | 0.41667
| Hasnabad | 140 | 3:00 | 132 | 12:00 | TK Chemical | 135 | 0.79167 | 127 | 0.45833
| Magbazar | 134 | 3:00 | 127 | 12:00 | Modern Steel | 133 | 0.79167 | 126 | 0.41667
| Maniknagar | 138 | 1:00 | 131 | 12:00 | Shahmirpur | 134 | 0.8125 | 127 | 0.33333
| Bangabhaban | 138 | 1:00 | 131 | 12:00 | Khagrachhari | 134 | 0.79167 | 128 | 0.5
| Narinda | 138 | 1:00 | 131 | 12:00 | Matarbari | 127 | 0.75 | 122 | 0.625
| Dhanmondi | 133 | 1:00 | 128 | 11:00 | Baroiar Hat | 138 | 0.79167 | 130 | 0.45833
| Lalbag | 132 | 3:00 | 124 | 18:00 | Rangamati | 134 | 19:00 | 128 | 12:00
| Madartek | 134 | 5:00 | 127 | 12:00 | Goalpara S/S | 137 | 3:00 | 128 | 12:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 136 | 17:00 | 127 | 0.5
| Aftabnagar | 134 | 3:00 | 128 | 11:00 | Noapara | 135 | 3:00 | 125 | 7:0
| Fatuiiah | 136 | 5:00 | 130 | 11:00 | Jessore | 132 | 1:00 | 125 | 0.5
| Mirpur | 132 | 5:00 | 126 | 12:00 | Benapol | 135 | 0.125 | 125 | 0.29167
| Kalyanpur | 133 | 5:00 | 126 | 12:00 | Jhenida | 134 | 4:00 | 125 | 0.5
| Gulshan | 133 | 5:00 | 127 | 12:00 | Bottail | 138 | 0.16667 | 128 | 0.75
| Uttara | 133 | 5:00 | 126 | 12:00 | G.K Project | 141 | 0.20833 | 135 | 0.75
| Uttara New | 133 | 5:00 | 125 | 12:00 | Faridpur | 138 | 0.16667 | 131 | 0.77083
| Kamrangirchar | 139 | 5:00 | 130 | 12:00 | Madaripur | 140 | 0.25 | 132 | 0.75
| Savar | 135 | 5:00 | 127 | 12:00 | Shariyatpur S/S | 141 | 4:00 | 134 | 0.77083
| Bhasantec | 138 | 5:00 | 129 | 16:00 | Gopalganj | 144 | 0.25 | 134 | 0.79167
| Agargaon | 138 | 5:00 | 130 | 16:00 | Bagerhat | 136 | 20:00 | 125 | 0.33333
| Satmosjid | 138 | 5:00 | 130 | 16:00 | Mongla | 134 | 20:00 | 122 | 0.33333
| Tongi | 139 | 4:00 | 132 | 15:00 | Satkhira | 136 | 3:00 | 125 | 8:00
| Kabirpur | 132 | 1:00 | 126 | 12:00 | Gallamari | 138 | 0.16667 | 127 | 0.33333
| Basundhara | 134 | 4:00 | 127 | 15:00 | Magura | 134 | 1:00 | 124 | 0.5
| Manikganj | 140 | 2:00 | 127 | 15:00 | Norail | 134 | 0.16667 | 122 | 0.33333
| Joydevpur | 140 | 19:00 | 134 | 15:00 | Chuadanga | 132 | 3:00 | 122 | 0.33333
| New Tongi | 137 | 1:00 | 130 | 15:00 | Barisal(N) | 142 | 4:00 | 137 | 18:00
| Kodda | 137 | 5:00 | 123 | 12:00 | Barisal (S) | 141 | 0.16667 | 135 | 0.77083
| Dhamrai | 132 | 4:00 | 125 | 12:00 | Patuakhali(S) | 140 | 0.125 | 132 | 0.77083
| Rajendrapur | 137 | 19:00 | 129 | 13:00 | Bhandaria | 140 | 0.29167 | 132 | 0.77083
| Valuka | 129 | 5:00 | 124 | 12:00 | Ishurdi | 138 | 2:00 | 133 | 8:00
| Tangail | 133 | 2:00 | 127 | 12:00 | Ruppur Paromanobik | 138 | 5:00 | 133 | 8:00
| Mymensing | 131 | 5:00 | 126 | 13:00 | Natore | 137 | 4:00 | 131 | 8:00
| Kishorganj | 131 | 5:00 | 127 | 13:00 | Bogra | 136 | 4:00 | 129 | 8:00
| Netrokona | 130 | 4:00 | 125 | 13:00 | Noagaon | 134 | 4:00 | 124 | 9:00
| Jamalpur | 136 | 19:00 | 125 | 1:00 | Rajshahi | 138 | 2:00 | 131 | 12:00
| Sherpur | 134 | 19:00 | 124 | 1:00 | Rajshahi New | 139 | 4:00 | 131 | 12:00
| Srimongal | 137 | 9:00 | 135 | 1:00 | C.Nawabganj | 138 | 3:00 | 129 | 13:00
| Shahjibazar | 134 | 1:00 | 133 | 7:00 | Amnura | 136 | 3:00 | 130 | 12:00
| Fenchuganj | 138 | 4:00 | 136 | 8:00 | Pabna | 138 | 4:00 | 132 | 12:00
| Khulawara | 137 | 1:00 | 135 | 11:00 | Shahjadpur | 140 | 2:00 | 136 | 8:00
| Sylhet | 135 | 1:00 | 133 | 12:00 | Serajganj | 136 | 3:00 | 130 | 8:00
| Chatak | 135 | 2:00 | 132 | 13:00 | Niyamatpur | 133 | 4:00 | 122 | 8:00
| Sunamganj | 135 | 2:00 | 132 | 17:00 | Joypurhat | 135 | 3:00 | 124 | 8:00
| Biani Bazar | 135 | 1:00 | 132 | 15:00 | Sherpur(Bogura) | 136 | 4:00 | 129 | 8:00
| Comilla(s) | 131 | 7:00 | 126 | 18:00 | Mohastangor | 135 | 3:00 | 127 | 13:00
| Comilla(n) | 141 | 18:30 | 136 | 11:00 | Rangpur | 129 | 5:00 | 120 | 8:00
| Chandpur | 139 | 18:30 | 135 | 9:00 | Lalmonirhat | 129 | 3:00 | 120 | 8:00
| Feni | 138 | 19:00 | 131 | 17:00 | Saidpur | 129 | 4:00 | 120 | 9:00
| Chowmuhani | 135 | 18:00 | 127 | 16:00 | Purbasadipur | 128 | 1:00 | 117 | 18:00
| Ashuganj | 136 | 6:00 | 134 | 15:00 | Thakurgaon | 128 | 3:00 | 115 | 18:00
| Daudkandi | 137 | 18:30 | 134 | 11:00 | Palashbari | 132 | 3:00 | 124 | 8:00
| B.Baria | 132 | 10:00 | 130 | 11:00 | Barapukuria | 135 | 4:00 | 125 | 8:00
| Ramganj | 131 | 16:00 | 128 | 18:00 | Panchagar | 127 | 5:00 | 108 | 18:00
| Chaddagram | 138 | 18:00 | 132 | 11:00 | Joldhaka | 130 | 4:00 | 117 | 18:00
| PHP | 136 | 18:30 | 130 | 11:00 | Kurigram | 127 | 0.125 | 117 | 0.33333

## L-Curve
Date | 2020-11-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 37 | 4977 | 2082 | 7059 |  |  |  | QF-LDC-11
0:30 | 41.5 | 4691.5 | 1984 | 6675.5 | Date: | 2020-11-30
1:00 | 46 | 4406 | 1886 | 6292
1:30 | 24 | 4331 | 1800 | 6131
2:00 | 2 | 4256 | 1714 | 5970
2:30 | 22 | 4186.5 | 1705 | 5891.5 | [5 empty] | Gen. at Eve. Peak | 9074 | 9074 MW (19:00 )
3:00 | 42 | 4117 | 1696 | 5813 | [6 empty] | 19:00
3:30 | 36 | 4098.5 | 1661 | 5759.5 | [5 empty] | Gen. at Day Peak | 7479 | 7479 MW (12:00 )
4:00 | 30 | 4080 | 1626 | 5706 | [6 empty] | 12:00
4:30 | 23.5 | 4051 | 1616 | 5667 | [5 empty] | Highest Generation | 9074
5:00 | 17 | 4022 | 1606 | 5628 | [6 empty] | 19:00
5:30 | 34 | 4116 | 1616.5 | 5732.5
6:00 | 51 | 4210 | 1627 | 5837
6:30 | 89.5 | 4279 | 1719 | 5998
7:00 | 128 | 4348 | 1811 | 6159
7:30 | 176.5 | 4562 | 1827 | 6389
8:00 | 225 | 4776 | 1843 | 6619
8:30 | 132 | 4910.5 | 1903.5 | 6814
9:00 | 39 | 5045 | 1964 | 7009
9:30 | 36.5 | 5038.5 | 1940.5 | 6979
10:00 | 34 | 5032 | 1917 | 6949
10:30 | 68.5 | 5090.5 | 1957 | 7047.5
11:00 | 103 | 5149 | 1997 | 7146
11:30 | 107 | 5235 | 2077.5 | 7312.5
12:00 | 111 | 5321 | 2158 | 7479
12:30 | 107 | 5369 | 2260.5 | 7629.5
13:00 | 103 | 5417 | 2363 | 7780
13:30 | 141.5 | 5328.5 | 2264 | 7592.5
14:00 | 180 | 5240 | 2165 | 7405
14:30 | 230 | 5226.5 | 2161 | 7387.5
15:00 | 280 | 5213 | 2157 | 7370
15:30 | 288.5 | 5153 | 2154 | 7307
16:00 | 297 | 5093 | 2151 | 7244
16:30 | 279 | 5123 | 2188 | 7311
17:00 | 261 | 5153 | 2225 | 7378
17:30 | 231.5 | 5660.5 | 2408 | 8068.5
18:00 | 202 | 6168 | 2591 | 8759
18:30 | 193.5 | 6271 | 2645.5 | 8916.5
19:00 | 185 | 6374 | 2700 | 9074
19:30 | 9 | 6139 | 2743 | 8882
20:00 | 3 | 6080 | 2734 | 8814 |  |  |  | Executive Engineer
20:30 | 45 | 6038.5 | 2661 | 8699.5 |  |  |  | Network Operation Division
21:00 | 87 | 5997 | 2588 | 8585
21:30 | 53 | 5763 | 2497 | 8260
22:00 | 19 | 5529 | 2406 | 7935 |  |  |  |  | Page 6 of 7
22:30 | 27.5 | 5328 | 2286.5 | 7614.5
23:00 | 36 | 5127 | 2167 | 7294
23:30 | 36.5 | 5052 | 2124.5 | 7176.5
24:00 | 37 | 4977 | 2082 | 7059
9074 MW (19:00 )
7479 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-30 |  | Energy | 173822709
[10 empty] | 2020-11-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3549 | 400 | 1976 | 424 | 600 | 127 | 0 | 0 | 86
0:30 | 3337.5 | 398.5 | 1866 | 377 | 540 | 125 | 0 | 0 | 83 | Date: | 2020-11-30
1:00 | 3126 | 397 | 1756 | 330 | 480 | 123 | 0 | 0 | 80
1:30 | 3104 | 398.5 | 1663.5 | 330 | 435 | 123 | 0 | 0 | 77 | [7 empty] | Total Energy | 173.8227 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3082 | 400 | 1571 | 330 | 390 | 123 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3069 | 400 | 1519.5 | 316.5 | 389.5 | 123 | 0 | 0 | 74 | [7 empty] | Energy Requirement | 173.8227
3:00 | 3056 | 400 | 1468 | 303 | 389 | 123 | 0 | 0 | 74
3:30 | 3044.5 | 400 | 1428 | 303 | 389 | 122 | 0 | 0 | 73 | [6 empty] | Shortage
4:00 | 3033 | 400 | 1388 | 303 | 389 | 121 | 0 | 0 | 72
4:30 | 3001 | 400 | 1375.5 | 308 | 389.5 | 121 | 0 | 0 | 72
5:00 | 2969 | 400 | 1363 | 313 | 390 | 121 | 0 | 0 | 72
5:30 | 3042 | 399.5 | 1396 | 313 | 390 | 121 | 0 | 0 | 71
6:00 | 3115 | 399 | 1429 | 313 | 390 | 121 | 0 | 0 | 70
6:30 | 3220.5 | 399 | 1472.5 | 321.5 | 390 | 122 | 0 | 0 | 70 |  |  |  |  | Coal
7:00 | 3326 | 399 | 1516 | 330 | 390 | 123 | 0 | 0 | 70
7:30 | 3410.5 | 399.5 | 1612 | 371.5 | 390 | 123.5 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3495 | 400 | 1708 | 413 | 390 | 124 | 0 | 0 | 78
8:30 | 3531.5 | 399.5 | 1826 | 440 | 390 | 124.5 | 0 | 0 | 80
9:00 | 3568 | 399 | 1944 | 467 | 390 | 125 | 0 | 0 | 82
9:30 | 3540.5 | 399.5 | 1876 | 514.5 | 390 | 125 | 0 | 0 | 83
10:00 | 3513 | 400 | 1808 | 562 | 390 | 125 | 0 | 0 | 84
10:30 | 3542 | 400 | 1851.5 | 566.5 | 405 | 126 | 0 | 0 | 85
11:00 | 3571 | 400 | 1895 | 571 | 420 | 127 | 0 | 0 | 86
11:30 | 3650 | 400 | 1936 | 588.5 | 445 | 127.5 | 0 | 0 | 88
12:00 | 3729 | 400 | 1977 | 606 | 470 | 128 | 0 | 0 | 90
12:30 | 3661 | 400 | 2006.5 | 749 | 520 | 127 | 0 | 0 | 90
13:00 | 3593 | 400 | 2036 | 892 | 570 | 126 | 0 | 0 | 90
13:30 | 3593 | 400 | 2036 | 892 | 570 | 126 | 0 | 0 | 90
14:00 | 3593 | 400 | 2036 | 892 | 570 | 126 | 0 | 0 | 90
14:30 | 3532.5 | 400.5 | 2017 | 795.5 | 560 | 124 | 0 | 0 | 93
15:00 | 3472 | 401 | 1998 | 699 | 550 | 122 | 0 | 0 | 96
15:30 | 3435.5 | 400.5 | 2005 | 679.5 | 550 | 122.5 | 0 | 0 | 92
16:00 | 3399 | 400 | 2012 | 660 | 550 | 123 | 0 | 0 | 88
16:30 | 3401.5 | 399.5 | 2005 | 727.5 | 550 | 122.5 | 8 | 0 | 91
17:00 | 3404 | 399 | 1998 | 795 | 550 | 122 | 16 | 0 | 94
17:30 | 3539.5 | 399 | 2019 | 1254.5 | 590 | 123 | 40.5 | 0 | 103
18:00 | 3675 | 399 | 2040 | 1714 | 630 | 124 | 65 | 0 | 112
18:30 | 3671 | 399.5 | 2051.5 | 1836 | 650 | 124.5 | 73 | 0 | 111
19:00 | 3667 | 400 | 2063 | 1958 | 670 | 125 | 81 | 0 | 110
19:30 | 3667 | 400 | 2103 | 1747 | 670 | 125 | 64 | 0 | 106
20:00 | 3651 | 400 | 2095 | 1703 | 670 | 125 | 64 | 0 | 106
20:30 | 3647 | 400 | 2113 | 1598.5 | 655 | 126 | 56 | 0 | 104
21:00 | 3643 | 400 | 2131 | 1494 | 640 | 127 | 48 | 0 | 102
21:30 | 3624 | 400 | 2120 | 1211.5 | 640 | 127 | 36.5 | 0 | 101
22:00 | 3605 | 400 | 2109 | 929 | 640 | 127 | 25 | 0 | 100
22:30 | 3623.5 | 400 | 2060 | 676.5 | 620 | 127 | 12.5 | 0 | 95
23:00 | 3642 | 400 | 2011 | 424 | 600 | 127 | 0 | 0 | 90
23:30 | 3595.5 | 400 | 1993.5 | 424 | 600 | 127 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 30.7° C
24:00 | 3549 | 400 | 1976 | 424 | 600 | 127 | 0 | 0 | 86
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 88 | 88 | 86 | 86 | 86 | 88 | 89 | 90 | 90 | 92 | 93 | 91 | 89 | 87 | 88 | 87 | 89 |  | 90 | 90 | 90 | 92 | 92 | 92 | 92 | 2144335
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 |  | 12 | 17 | 18 | 19 | 17 | [13 empty] | 88695
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 203 | 203 | 203 | 205 | 213 | 206 | 203 | 203 | 213 | 216 | 204 | 204 | 204 | 203 | 203 | 218 |  | 203 | 215 | 203 | 203 | 203 | 216 | 202 | 4902661
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 70 | 70 | 70 | 70 | 104 | 106 | 139 | 139 | 139 | 143 | 139 | 140 | 139 | 140 | 139 | 146 |  | 138 | 139 | 139 | 140 | 139 | 139 | 139 | 2974150
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 32528
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 6 | 91 |  | 115 | 15 | 15 |  |  |  | 0 | 260945
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | [17 empty] | 100 |  | 100 | 93 | 93 | 93 | 93 | 93 | 93 | 660100
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4792700
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1992525
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 221832
33 | Ashuganj 225 MW CCPP | 52 | 56 | 112 | 221 | 181 | 183 | 182 | 217 | 190 | 158 | 167 | 186 | 156 | 164 | 163 | 163 | 160 | 144 |  | 160 | 169 | 169 | 172 | 172 | 174 | 179 | 3864000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 260 | 265 | 250 | 285 | 285 | 275 | 260 | 265 | 280 | 300 | 280 | 280 | 295 | 295 | 305 | 310 |  | 275 | 290 | 275 | 275 | 275 | 290 | 260 | 7007900
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 189600
36 | Chandpur 150 MW CCPP | 72 | 72 | 72 | 72 | 72 | 75 | 78 | 80 | 74 | 76 | 78 | 80 | 70 | 70 | 70 | 46 | 46 | 54 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1516140
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 340 | 338 | 292 | 280 | 312 | 353 | 362 | 365 | 340 | 360 | 365 | 364 | 348 | 346 | 344 | 344 | 350 |  | 360 | 350 | 347 | 349 | 341 | 344 | 342 | 8318970
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 310 | 300 | 300 | 300 | 300 | 300 | 350 | 400 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 360 | 7911000
41 | Haripur 360MW CCPP(HPL) | 334 | 327 | 283 | 283 | 283 | 310 | 310 | 361 | 339 | 323 | 303 | 293 | 283 | 286 | 285 | 285 | 270 | 265 |  | 250 | 224 | 231 | 232 | 223 | 223 | 223 | 6842000
42 | RPCL 210MW CCPP | 130 | 129 | 129 | 130 | 131 | 152 | 152 | 132 | 108 | 108 | 105 | 101 | 100 | 100 | 98 | 98 | 100 | 100 |  | 100 | 100 | 99 | 100 | 100 | 112 | 130 | 2646040
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 8 | 16 | 40 | 47 | 49 | 45 | 38 | 26 | 9 | 0 | [9 empty] | 277250
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1273000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1420680
46 | Shajibazar 330 MW CCPP | 260 | 257 | 253 | 253 | 258 | 260 | 260 | 262 | 260 | 262 | 260 | 265 | 257 | 254 | 253 | 254 | 260 | 263 |  | 265 | 260 | 253 | 250 | 251 | 258 | 256 | 5895000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 20 | 20 | 20 | 20 | 20 | 36 | 35 | 20 | 20 | 33 | 32 | 32 | 32 | 32 | 32 | 35 |  | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 717312
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 77 | 77 | 80 | 20 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 1215360
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 100 | 72 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 85 | 85 | 2180150
51 | Sylhet 20 MW GTPP | [21 empty] | 18 | 18 | 18 | 18 | 18 | 90000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | [8 empty] | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 116000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 17 | 48 | 45 | 48 | 47 | 50 | 50 | 50 | 50 | 50 | 47 |  | 47 | 50 | 50 | 53 | 53 | 53 | 53 | 940200
56 | Shahjahanulla 25 MW PP | [8 empty] | 14 | 14 | 14 | 14 | 10 | 10 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 222528
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 300 | 295 | 285 | 280 | 300 | 310 | 310 | 310 | 290 | 310 | 310 | 300 | 300 | 300 | 310 | 300 | 290 |  | 290 | 310 | 290 | 300 | 290 | 275 | 290 | 7353500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 0 | [5 empty] | 16 | 17 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 337104
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 19 | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 268416
62 | Tangail 22 MW PP (Doreen) | 20 | 0 | [5 empty] | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 316692
63 | Impoprt (Tripura) | 80 | 74 | 74 | 72 | 72 | 70 | 70 | 78 | 82 | 84 | 86 | 90 | 90 | 100 | 96 | 88 | 94 | 112 |  | 110 | 106 | 106 | 102 | 100 | 90 | 86 | 2115840
64 | Malancha, Ctg. EPZ (United) | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 4 | 10 |  | 15 | 18 | 25 | 33 | 36 | 40 | 41 | 399360
65 | Feni 22MW PP (Doreen) | [7 empty] | 14 | 19 | 19 | 21 | 21 | 21 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 337860
66 | Feni 11 MW PP (Doreen) | [8 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 103860
67 | Jangalia 33MW PP (Summit) | 4 | 0 | [5 empty] | 7 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 524000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 516600
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 32 | 28 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 702360
71 | Maona 33 MW PP(Summit) | 25 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 591400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 629400
73 | Ghorashal 108MW PP (Regent) | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 54 | 54 | 86 | 95 | 98 | 98 | 97 | 94 | 94 | 94 | 97 |  | 101 | 101 | 101 | 98 | 98 | 98 | 98 | 1642409
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [12 empty] | 13 | 8 | 8 | 8 | 8 | 84 |  | 106 | 106 | 106 | 65 | 8 |  | 0 | 480480
| Manikgonj 162MW PP | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 165 | 144 | 17 | [7 empty] | 0 | 2953440
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 4 | 24 |  | 50 | 20 | 8 |  |  |  | 0 | 110400
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 16 | 48 |  | 64 | 64 | 64 | 48 | 25 |  | 0 | 293760
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 12 | 17 | 17 | 34 | 17 | 17 | 17 | 17 | 17 | 50 | 59 |  | 59 | 43 | 42 | 42 | 42 | 17 | 17 | 498240
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 19 |  | 24 | 8 | 8 |  |  |  |  | 59266
| Gazipur 100 MW PP | [8 empty] | 6 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 45 |  | 53 | 36 | 35 | 17 |  |  | 0 | 355308
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27960
| Jodiac Power | [7 empty] | 5 | 17 | 17 | 17 | 17 | 37 | 17 | 17 | 17 | 17 | 48 |  | 54 | 54 | 54 | 54 | 54 | 17 | 0 | 518785
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 38 |  | 52 | 15 | 15 | 15 |  |  | 0 | 153648
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 145 | 145 | 135 | 135 | 145 | 145 | 145 | 140 | 130 | 142 | 144 | 144 | 130 | 135 | 135 | 140 | 142 | 150 |  | 125 | 144 | 145 | 138 | 132 | 140 | 130 | 3331404
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 24 |  | 33 | 7 | 10 |  |  |  | 0 | 75840
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 8 | 17 | 41 | 53 | 53 | 88 | 90 | 75 | 53 | 53 | 72 |  | 90 | 90 | 90 | 90 | 90 | 50 | 34 | 1114560
88 | Ghorashal 78.5 MW PP(MAX) | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 50 | 69 | 69 | 67 | 68 | 68 | 70 |  | 71 | 72 | 71 | 72 | 72 | 72 | 72 | 1224608
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 47 | 25 | 10 | 10 | 10 | 10 | 10 | 17 | 43 | 47 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 895896
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 7 | 24 | 34 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 826292
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 16 | 64 |  | 64 | 64 | 64 | 64 | 8 |  |  | 294048
95 | Patenga 50MW PP (Baraka) | [16 empty] | 2 | 29 |  | 50 | 50 | 50 | 50 | 50 |  | 0 | 270240
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 15 |  | 14 | [5 empty] | 0 | 34740
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 35 | 17 | 17 |  |  | 0 | 130415
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 163 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3313881
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13100
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 0 |  |  |  | 17 | 17 | 17 | 35 | 35 | 35 | 54 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 806400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 0
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [25 empty] | 0 | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 90 | 50 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 890880
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [12 empty] | 1 | 20 | 10 | 10 | 12 | 83 |  | 142 | 150 | 133 | 150 | 50 |  | 0 | 700872
118 | Bibiyana-III 400 MW CCPP | 326 | 327 | 304 | 305 | 305 | 351 | 372 | 399 | 399 | 399 | 405 | 405 | 406 | 409 | 363 | 316 | 316 | 429 |  | 435 | 433 | 436 | 437 | 426 | 426 | 405 | 9043000
| Jamalpur 115 MW PP (United) | [7 empty] | 33 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 115 |  | 115 | 115 | 115 | 115 | 85 | 55 | 35 | 1335600
| Anwara 300 MW PP (United) | [12 empty] | 32 | 16 | 16 | 16 | 16 | 151 |  | 158 | 160 | 161 | 161 | 51 |  | 0 | 843055
| Juldah unit-2 (Acorn) | [7 empty] | 20 | 20 | 20 | 20 | 70 | 90 | 50 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 1086720
| Anlima Energy Ltd. | [9 empty] | 13 | 8 | 10 | [13 empty] | 0 | 33872
120 | Eastern Zone Total | 4406 | 4256 | 4117 | 4080 | 4022 | 4210 | 4348 | 4776 | 5045 | 5032 | 5149 | 5321 | 5417 | 5240 | 5213 | 5093 | 5153 | 6168 |  | 6374 | 6139 | 6080 | 5997 | 5529 | 5127 | 4977 | 122702566
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 16 |  | 49 | 49 | 49 | 16 |  |  | 0 | 138240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 90 | 35 | 17 | 17 | 17 | 90 |  | 90 | 90 | 90 | 90 | 35 |  | 0 | 629760
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 36 | 36 | 36 | 37 | 36 | 36 | 36 | 27 | 15 | 6 | 34 | 67 | 45 | 37 | 51 | 56 | 66 |  | 88 | 88 | 97 | 98 | 91 | 99 | 80 | 1226320
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [20 empty] | 16 | 16 | 16 |  |  | 0 | 43008
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 11 | 23 | 64 | 68 | 58 | 34 | 34 | 66 |  | 68 | 67 | 67 | 67 | 67 | 13 | 13 | 829681
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 24 | 23 | 22 | 20 | 19 | 19 | 17 | 16 | 15 | 19 | 18 | 20 | 22 | 20 | 18 | 18 | 19 | 24 |  | 25 | 26 | 26 | 26 | 27 | 25 | 24 | 494200
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 397 | 400 | 400 | 400 | 400 | 399 | 399 | 400 | 399 | 400 | 400 | 400 | 400 | 400 | 401 | 400 | 399 | 399 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9565818
147 | Bheramara 410 MW CCPP | 220 | 225 | 240 | 240 | 245 | 245 | 340 | 360 | 370 | 340 | 340 | 345 | 325 | 320 | 320 | 315 | 310 | 310 |  | 300 | 290 | 280 | 265 | 255 | 245 | 240 | 7172928
148 | Payra 1320 MW | 340 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 330 | 430 | 410 | 410 | 410 | 410 | 490 |  | 530 | 530 | 530 | 500 | 500 | 460 | 460 | 8781700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 139 | 139 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3436000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [25 empty] | 0 | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 154 | 154 | 151 | 136 | 130 | 130 | 141 | 150 | 167 | 157 | 164 | 193 | 186 | 155 | 155 | 154 | 154 | 171 |  | 180 | 174 | 178 | 179 | 175 | 175 | 174 | 4090545
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 154 | 180 | 180 | 205 | 193 | 162 | 161 | 161 | 161 | 174 |  | 180 | 184 | 182 | 183 | 178 | 178 | 173 | 4178009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 424 | 338 | 310 | 257 | 237 | 257 | 337 | 340 | 414 | 370 | 423 | 432 | 410 | 375 | 406 | 418 | 423 | 421 |  | 391 | 430 | 420 | 435 | 435 | 399 | 348 | 8978363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 336480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 211806
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 20 | 90 |  | 113 | 113 | 113 | 70 | 35 |  | 0 | 494304
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 101 |  | 113 | 113 | 113 | 70 | 35 |  | 0 | 481920
177 | Sympa Solar Power 8MW | [6 empty] | 0 |  | 2 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 31061
178
178