## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-02 | Wednesday
|  |  | Date (day): | 2020-12-02 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13071.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14425 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-01 | 2020-12-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 93 | 93 | 100 | 100 |  | 70
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 0 | 0 | 0 |  |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 74 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 343 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 260 | 235 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 250 | 350 | 350 |  |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 145 | 155 | 155 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 48 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 90 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 50 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 56 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 19 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 145 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 91 | 91 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 78 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 0 | 0 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1997 | 2458 | 3856 | 4196 | 498 | 1177
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 7 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 92 | 89 | 92 | 92 | 138 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 208 | 204 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 150 | 144 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 41 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 863 | 809 | 1503 | 1498 | 648 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 134 | 164 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 345 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 120 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 36 | 50 | 50 |  | 57 | Gas shortage,S T Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 104 | 144 | 154
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 56 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 864 | 1114 | 1671 | 1932 | 467 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 108 | 130 | 130 | 72 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 17 | 17 | 16 | 32 |  | 63 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 80 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 54 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 51 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 246 | 340 | 529.6 | 494 | 72 | 68
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 8 | 22 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 260 | 177 | 260 | 260 |  | 70 | Machine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 52 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 35 | 36 | 36 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 70 | 50 | 40 | 40 |  |  | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 16 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 325 | 325 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 304 | 283 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1416 | 1309 | 1572 | 1572 | 0 | 112
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 386 | 768 | 596 | 788
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 190 | 270 | 270 |  |  | Gas shortage
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 736 | 1048 | 1211 | 1829 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 26 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 62 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 570 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 96 | 97 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 529 | 755 | 867 | 927 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 161 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 160 | 225 | 225 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 432 | 422 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 812 | 889 | 1506 | 1629 | 271 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 85 | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 106 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 145 | 246 | 356 | 348 | 209 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7608 | 8968 | 13071.6 | 14425 | 2165 | 2121
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7156.678 | 8436 | 12296.1661 | 13569.2797
| A. |  | 2020-12-01 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 8968 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5633 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8968 | MW
| 3 | Day peak Generation : |  |  | 7608 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8436 | MW
| 4 | Evening peak Generation : |  |  | 8968 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 172.3982 | MKWHr | By Solar | 0.51543 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 121.037 | MKWHr |  | By Oil: | 21.6473 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6573 | MKWHr |  | By Hydro: | 2.0419 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2165 | MW | Dhaka | 3189 | 3189 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2121 | MW | Chittagong | 918 | 918 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4286 | MW | Khulna | 998 | 998 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 986.67 | MMCFD |  |  | Rajshahi | 839 | 839 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 134426190.206 | ii) Oil : | Taka | 140909144.59 | Comilla | 724 | 724 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 63639482.81 | Total | Taka | 338974817.606 | Mymensingh | 652 | 652 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.391 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 86 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -41 | MW at | 8:00 | hrs | Rangpur | 565 | 565 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 8436 | 8436 |  | 0
| B. |  | 2020-12-02 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 27.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14425 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7600 | MW
| 4 | Reserve(Generation end) |  |  |  | 5225 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 176.8581 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5635 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.4007 | MKWHr. | ii) HVDC Flow at Peak Time |  | 768 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0986 | MKWHr. | iii) Maximum HVDC Flow : |  | 768 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.27 |  | (b) Today: | 100.14 |  | (c) Rule Curve: |  | 105.91
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 93 | 0 | 115 | 200 | 13 | 40 | 338 | 252 |  | 0 | 360 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 260 | 0 | 186 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 130 | 17 | 0 | 0 | 60 | 60 | 53 | 47 | 163 | 258 | 20 | 20 | 0 | 85 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 151 | 0 | 13 | 0 | 159 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 52 | 0 | 0 |  | 4443 | 1954 | 6397 | 3348 | 400 | 1772 | 160 | 548 | 91 | 0 | 78 | 0 | 0 | 100.32
2:00 | 0 | 93 | 0 | 115 | 200 | 13 | 20 | 339 | 270 |  | 0 | 360 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 80 | 0 | 260 | 0 | 189 | 8 | 46 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 76 | 131 | 17 | 0 | 0 | 60 | 60 | 5 | 5 | 130 | 254 | 20 | 5 | 0 | 80 | 18 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 148 | 0 | 13 | 0 | 153 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 48 | 0 | 0 |  | 4137 | 1945 | 6082 | 3224 | 400 | 1589 | 152 | 550 | 91 | 0 | 76 | 0 | 0 | 100.31
3:00 | 0 | 93 | 0 | 115 | 200 | 13 | 20 | 338 | 278 |  | 0 | 360 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 80 | 0 | 260 | 0 | 187 | 8 | 46 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 76 | 132 | 17 | 0 | 0 | 60 | 60 | 5 | 5 | 110 | 260 | 20 | 5 | 0 | 80 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 43 | 0 | 0 |  | 4110 | 1818 | 5928 | 3198 | 400 | 1461 | 152 | 550 | 91 | 0 | 76 | 0 | 0 | 100.3
4:00 | 0 | 92 | 0 | 115 | 200 | 13 | 20 | 312 | 258 |  | 0 | 340 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 80 | 0 | 250 | 0 | 180 | 8 | 45 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 132 | 17 | 0 | 0 | 60 | 60 | 5 | 5 | 110 | 258 | 20 | 5 | 0 | 80 | 18 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 |  | 4002 | 1764 | 5766 | 3164 | 400 | 1410 | 142 | 490 | 88 | 0 | 72 | 0 | 0 | 100.29
5:00 | 0 | 93 | 0 | 115 | 200 | 13 | 20 | 275 | 257 |  | 0 | 340 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 80 | 0 | 250 | 0 | 180 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 132 | 0 | 0 | 0 | 40 | 60 | 5 | 5 | 110 | 261 | 20 | 5 | 0 | 80 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 399 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 46 | 0 | 0 |  | 3896 | 1737 | 5633 | 3047 | 399 | 1440 | 145 | 440 | 88 | 0 | 74 | 0 | 0 | 100.28
6:00 | 0 | 93 | 0 | 115 | 200 | 13 | 20 | 272 | 287 |  | 0 | 400 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 300 | 0 | 194 | 8 | 46 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 152 | 0 | 0 | 0 | 40 | 30 | 5 | 5 | 120 | 257 | 37 | 5 | 0 | 80 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 152 | 0 | 13 | 0 | 155 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 39 | 0 | 0 |  | 4063 | 1836 | 5899 | 3188 | 400 | 1576 | 133 | 440 | 88 | 0 | 74 | 0 | 0 | 100.27
7:00 | 0 | 94 | 0 | 115 | 200 | 82 | 20 | 273 | 287 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 209 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 300 | 0 | 179 | 8 | 46 | 5 | 5 | 0 | 8 | 0 | 0 | 0 | 13 | 0 | 16 | 21 | 70 | 149 | 0 | 20 | 0 | 40 | 10 | 5 | 10 | 120 | 255 | 37 | 40 | 0 | 80 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 231 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3 | 0 | 0 |  | 400 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 179 | 0 | 13 | 0 | 180 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 8 | 0 | 0 |  | 4278 | 1932 | 6210 | 3308 | 400 | 1718 | 179 | 440 | 89 | 0 | 70 | 6 | 0 | 100.27
8:00 | 0 | 93 | 0 | 115 | 200 | 98 | 50 | 297 | 287 |  | 0 | 380 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 22 | 20 | 8 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 214 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 20 | 8 | 0 | 80 | 0 | 300 | 0 | 170 | 8 | 50 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 33 | 18 | 76 | 106 | 17 | 20 | 0 | 40 | 5 | 53 | 43 | 120 | 263 | 37 | 75 | 0 | 81 | 18 | 0 | 0 | 280 | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9 | 10 | 0 | 0 | 231 | 59 | 0 | 0 | 1 | 0 | 23 | 0 | 0 | 0 | 20 | 0 | 40 | 17 | 0 | 0 |  | 399 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 178 | 0 | 13 | 0 | 188 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 47 | 0 | 0 |  | 4583 | 2008 | 6591 | 3320 | 399 | 1861 | 378 | 440 | 89 | 0 | 76 | 28 | 0 | 100.25
9:00 | 0 | 93 | 0 | 115 | 200 | 98 | 70 | 311 | 269 |  | 0 | 320 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 28 | 20 | 8 | 8 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 4 | 0 | 80 | 0 | 300 | 0 | 166 | 8 | 46 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 78 | 107 | 8 | 20 | 2 | 40 | 10 | 53 | 43 | 163 | 256 | 36 | 76 | 0 | 70 | 18 | 0 | 0 | 280 | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 14 | 40 | 0 | 8 | 231 | 75 | 1 | 0 | 3 | 33 | 35 | 0 | 0 | 26 | 60 | 0 | 53 | 34 | 0 | 0 |  | 399 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 179 | 0 | 13 | 0 | 178 | 0 | 350 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 310 | 37 | 0 | 0 |  | 4830 | 2009 | 6839 | 3295 | 399 | 1837 | 634 | 450 | 91 | 0 | 78 | 55 | 0 | 100.24
10:00 | 0 | 93 | 0 | 115 | 200 | 97 | 70 | 339 | 234 |  | 0 | 320 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 20 | 8 | 25 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 2 | 0 | 80 | 0 | 300 | 0 | 148 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 18 | 84 | 106 | 17 | 20 | 2 | 40 | 8 | 50 | 47 | 130 | 254 | 20 | 76 | 0 | 70 | 18 | 0 | 0 | 290 | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 17 | 40 | 0 | 10 | 251 | 45 | 60 | 0 | 3 | 33 | 35 | 0 | 0 | 46 | 60 | 0 | 53 | 41 | 0 | 19 |  | 400 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 160 | 0 | 380 | 35 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 310 | 37 | 0 | 0 |  | 4968 | 1984 | 6952 | 3253 | 400 | 1847 | 760 | 450 | 91 | 0 | 84 | 67 | 0 | 100.24
11:00 | 0 | 93 | 0 | 115 | 200 | 97 | 40 | 360 | 230 |  | 0 | 300 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 25 | 8 | 25 | 0 | 91 | 0 | 0 | 0 | 0 | 217 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 4 | 0 | 80 | 0 | 300 | 0 | 135 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 18 | 86 | 106 | 17 | 20 | 2 | 60 | 8 | 50 | 47 | 150 | 265 | 20 | 76 | 0 | 70 | 18 | 0 | 0 | 300 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 10 | 304 | 45 | 91 | 0 | 4 | 33 | 35 | 0 | 0 | 46 | 60 | 0 | 53 | 48 | 0 | 0 |  | 385 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 13 | 0 | 170 | 0 | 434 | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 390 | 96 | 0 | 0 |  | 5027 | 2173 | 7200 | 3377 | 385 | 1942 | 711 | 530 | 91 | 0 | 86 | 78 | 0 | 100.24
12:00 | 0 | 93 | 0 | 115 | 200 | 98 | 40 | 371 | 260 |  | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 28 | 17 | 19 | 25 | 0 | 92 | 0 | 0 | 0 | 0 | 208 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 2 | 0 | 80 | 0 | 300 | 0 | 134 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 19 | 92 | 102 | 17 | 20 | 2 | 60 | 8 | 52 | 46 | 163 | 260 | 34 | 76 | 0 | 70 | 18 | 0 | 0 | 310 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 90 | 0 | 10 | 304 | 54 | 91 | 0 | 4 | 150 | 41 | 0 | 0 | 56 | 90 | 0 | 78 | 51 | 0 | 0 |  | 386 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 173 | 0 | 13 | 0 | 177 | 0 | 432 | 70 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 96 | 0 | 0 |  | 5386 | 2222 | 7608 | 3426 | 386 | 1994 | 997 | 540 | 92 | 0 | 92 | 81 | 0 | 100.23
13:00 | 0 | 93 | 0 | 115 | 200 | 98 | 40 | 357 | 247 |  | 0 | 300 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 17 | 25 | 25 | 0 | 92 | 0 | 0 | 0 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 4 | 0 | 80 | 0 | 300 | 0 | 134 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 19 | 94 | 99 | 17 | 20 | 2 | 60 | 8 | 52 | 46 | 163 | 255 | 32 | 78 | 0 | 70 | 18 | 0 | 0 | 300 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 0 | 15 | 289 | 115 | 91 | 0 | 4 | 158 | 54 | 0 | 0 | 103 | 90 | 0 | 90 | 47 | 0 | 0 |  | 386 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 177 | 0 | 13 | 0 | 185 | 0 | 410 | 90 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 430 | 95 | 0 | 0 |  | 5452 | 2256 | 7708 | 3312 | 386 | 1952 | 1227 | 570 | 92 | 0 | 94 | 75 | 7708 | 100.22
14:00 | 0 | 94 | 0 | 115 | 200 | 98 | 40 | 345 | 235 |  | 0 | 280 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 30 | 25 | 25 | 25 | 0 | 89 | 0 | 0 | 0 | 0 | 206 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 0 | 80 | 0 | 260 | 0 | 143 | 8 | 42 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 0 | 0 | 94 | 44 | 17 | 20 | 2 | 60 | 8 | 52 | 46 | 110 | 254 | 32 | 40 | 0 | 70 | 18 | 0 | 0 | 290 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 100 | 0 | 86 | 232 | 85 | 91 | 0 | 3 | 125 | 54 | 0 | 0 | 75 | 90 | 0 | 90 | 39 | 0 | 0 |  | 386 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 13 | 0 | 155 | 0 | 346 | 90 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 430 | 90 | 0 | 0 |  | 5155 | 2100 | 7255 | 3043 | 386 | 1749 | 1260 | 570 | 89 | 0 | 94 | 64 | 0 | 100.22
15:00 | 0 | 93 | 0 | 115 | 200 | 98 | 40 | 355 | 235 |  | 0 | 280 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 25 | 25 | 25 | 0 | 87 | 0 | 0 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 270 | 0 | 154 | 8 | 42 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 92 | 55 | 17 | 20 | 1 | 60 | 0 | 53 | 46 | 110 | 199 | 32 | 40 | 0 | 70 | 18 | 0 | 0 | 310 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 0 | 70 | 232 | 85 | 91 | 0 | 2 | 125 | 54 | 0 | 0 | 26 | 90 | 0 | 90 | 27 | 0 | 0 |  | 386 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 177 | 0 | 425 | 90 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 430 | 88 | 0 | 0 |  | 5077 | 2178 | 7255 | 3079 | 386 | 1843 | 1154 | 570 | 87 | 0 | 92 | 44 | 0 | 100.21
16:00 | 0 | 93 | 0 | 115 | 200 | 94 | 40 | 357 | 235 |  | 0 | 280 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 25 | 25 | 25 | 0 | 86 | 0 | 0 | 0 | 0 | 227 | 0 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 270 | 0 | 165 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 88 | 68 | 17 | 20 | 0 | 60 | 0 | 17 | 15 | 110 | 197 | 32 | 10 | 0 | 70 | 18 | 0 | 0 | 305 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 0 | 70 | 232 | 85 | 91 | 0 | 1 | 71 | 54 | 0 | 0 | 26 | 90 | 0 | 90 | 10 | 0 | 0 |  | 386 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 180 | 0 | 419 | 53 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 430 | 91 | 0 | 0 |  | 4962 | 2125 | 7087 | 3121 | 386 | 1734 | 1083 | 570 | 86 | 0 | 88 | 19 | 0 | 100.21
17:00 | 0 | 94 | 0 | 115 | 200 | 101 | 40 | 372 | 247 |  | 0 | 280 | 135 | 6 | 0 | 2 | 0 | 0 | 0 | 12 | 40 | 10 | 0 | 0 | 0 | 0 | 35 | 35 | 13 | 19 | 25 | 30 | 25 | 25 | 25 | 0 | 90 | 0 | 0 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 5 | 0 | 80 | 0 | 280 | 0 | 184 | 8 | 37 | 5 | 5 | 0 | 51 | 0 | 0 | 7 | 21 | 8 | 33 | 21 | 94 | 72 | 25 | 20 | 0 | 60 | 0 | 25 | 15 | 163 | 197 | 32 | 75 | 0 | 70 | 18 | 0 | 0 | 315 | 15 | 2 | 0 | 9 | 0 | 0 | 15 | 0 | 2 | 0 | 100 | 0 | 70 | 0 | 115 | 91 | 0 | 0 | 70 | 41 | 0 | 0 | 26 | 100 | 0 | 90 | 0 | 0 | 0 |  | 496 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 162 | 0 | 55 | 0 | 178 | 0 | 400 | 53 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 430 | 89 | 0 | 0 |  | 4992 | 2324 | 7316 | 2898 | 496 | 1915 | 1243 | 570 | 90 | 10 | 94 | 0 | 0 | 100.2
18:00 | 0 | 93 | 0 | 115 | 200 | 101 | 40 | 369 | 244 |  | 0 | 280 | 145 | 65 | 18 | 15 | 0 | 0 | 0 | 65 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 25 | 25 | 38 | 0 | 89 | 0 | 0 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 34 | 0 | 26 | 50 | 20 | 10 | 0 | 80 | 0 | 345 | 0 | 186 | 8 | 31 | 5 | 5 | 0 | 51 | 0 | 0 | 36 | 21 | 8 | 33 | 21 | 106 | 84 | 25 | 20 | 0 | 60 | 0 | 53 | 39 | 163 | 176 | 34 | 80 | 0 | 70 | 18 | 0 | 0 | 315 | 16 | 2 | 0 | 121 | 0 | 0 | 67 | 0 | 16 | 0 | 100 | 0 | 93 | 285 | 115 | 91 | 0 | 0 | 142 | 54 | 0 | 48 | 54 | 100 | 0 | 90 | 0 | 0 | 0 |  | 495 | 0 | 195 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 426 | 90 | 0 | 11 | 0 | 101 | 0 | 0 | 100 | 550 | 97 | 0 | 0 |  | 6132 | 2738 | 8870 | 3205 | 495 | 2022 | 2181 | 690 | 89 | 82 | 106 | 0 | 0 | 100.2
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 93 | 0 | 115 | 200 | 74 | 0 | 343 | 235 |  | 0 | 250 | 145 | 100 | 48 | 0 | 0 | 0 | 0 | 90 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 25 | 52 | 0 | 89 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 14 | 0 | 80 | 0 | 345 | 0 | 164 | 8 | 36 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 104 | 108 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 177 | 35 | 80 | 0 | 50 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 145 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 0 | 120 | 283 | 115 | 91 | 0 | 0 | 144 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 422 | 90 | 0 | 0 | 0 | 106 | 0 | 0 | 113 | 570 | 97 | 0 | 0 |  | 6030 | 2938 | 8968 | 3129 | 768 | 1909 | 2177 | 710 | 89 | 82 | 104 | 0 | 0 | 100.19
19:30 | 0 | 93 | 0 | 115 | 200 | 74 | 0 | 340 | 235 |  | 0 | 250 | 135 | 100 | 48 | 0 | 0 | 0 | 0 | 100 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 25 | 52 | 0 | 90 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 18 | 0 | 80 | 0 | 345 | 0 | 156 | 8 | 36 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 106 | 111 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 180 | 35 | 80 | 0 | 50 | 19 | 0 | 0 | 285 | 16 | 11 | 0 | 145 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 0 | 120 | 283 | 115 | 91 | 0 | 0 | 144 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 401 | 90 | 0 | 0 | 0 | 106 | 0 | 0 | 113 | 570 | 96 | 0 | 0 |  | 6023 | 2916 | 8939 | 3130 | 768 | 1876 | 2177 | 710 | 90 | 82 | 106 | 0 | 0 | 0
20:00 | 0 | 93 | 0 | 115 | 200 | 74 | 0 | 339 | 235 |  | 0 | 250 | 130 | 100 | 48 | 0 | 0 | 0 | 0 | 100 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 25 | 16 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 24 | 0 | 0 | 50 | 20 | 27 | 0 | 80 | 0 | 345 | 0 | 157 | 8 | 33 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 104 | 110 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 213 | 35 | 80 | 0 | 50 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 115 | 0 | 0 | 40 | 0 | 0 | 0 | 100 | 0 | 120 | 284 | 115 | 91 | 0 | 0 | 144 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 385 | 90 | 0 | 0 | 0 | 106 | 0 | 0 | 113 | 570 | 90 | 0 | 0 |  | 5909 | 2895 | 8804 | 3160 | 768 | 1859 | 2040 | 710 | 91 | 72 | 104 | 0 | 0 | 100.19
21:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 339 | 212 |  | 0 | 250 | 130 | 85 | 30 | 0 | 0 | 0 | 0 | 100 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 25 | 0 | 80 | 0 | 345 | 0 | 173 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 100 | 110 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 233 | 36 | 80 | 0 | 50 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 114 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 70 | 283 | 115 | 45 | 0 | 0 | 143 | 54 | 0 | 0 | 45 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 390 | 90 | 0 | 0 | 0 | 108 | 0 | 0 | 113 | 570 | 86 | 0 | 0 |  | 5590 | 2888 | 8478 | 3188 | 768 | 1832 | 1741 | 710 | 91 | 48 | 100 | 0 | 0 | 100.18
22:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 341 | 212 |  | 0 | 250 | 135 | 70 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 29 | 0 | 80 | 0 | 345 | 0 | 169 | 8 | 33 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 98 | 110 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 233 | 36 | 79 | 0 | 40 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 10 | 283 | 115 | 35 | 0 | 0 | 143 | 54 | 0 | 0 | 0 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 52 | 0 | 160 | 0 | 393 | 57 | 0 | 0 | 0 | 50 | 0 | 0 | 113 | 570 | 88 | 0 | 0 |  | 5218 | 2787 | 8005 | 3169 | 768 | 1830 | 1291 | 710 | 91 | 48 | 98 | 0 | 0 | 100.18
23:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 347 | 212 |  | 0 | 250 | 150 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 33 | 0 | 80 | 0 | 345 | 0 | 161 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 92 | 107 | 0 | 20 | 0 | 60 | 22 | 50 | 47 | 163 | 234 | 36 | 79 | 0 | 50 | 19 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 283 | 85 | 0 | 0 | 0 | 142 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 579 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 70 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 52 | 0 | 160 | 0 | 435 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 98 | 0 | 0 |  | 4882 | 2480 | 7362 | 3189 | 579 | 1891 | 740 | 740 | 91 | 40 | 92 | 0 | 0 | 100.17
24:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 347 | 212 |  | 0 | 250 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 20 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 38 | 0 | 80 | 0 | 345 | 0 | 156 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 82 | 110 | 0 | 20 | 0 | 60 | 22 | 50 | 47 | 163 | 232 | 36 | 79 | 0 | 40 | 19 | 0 | 0 | 290 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 283 | 85 | 0 | 0 | 0 | 142 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 390 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 85 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 51 | 0 | 160 | 0 | 392 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 88 | 0 | 0 |  | 4764 | 2186 | 6950 | 3156 | 390 | 1841 | 679 | 695 | 91 | 16 | 82 | 0 | 0 | 100.17
KWH | 0 | 2412500 | 0 | 2772000 | 4795200 | 1652863 | 765184 | 8193030 | 5932000 |  | 0 | 6638300 | 3274531 | 494400 | 179544 | 24960 | 0 | 0 | 0 | 448320 | 587520 | 309120 | 0 | 0 | 0 | 0 | 870120 | 374355 | 187777 | 282312 | 600000 | 700200 | 565200 | 531900 | 351876 | 0 | 2041904 | 0 | 0 | 0 | 0 | 4873939 | 0 | 1635430 | 0 |  | 0 | 0 | 107029 | 0 | 60480 | 629280 | 470304 | 488640 | 0 | 1919630 | 0 | 7460600 | 0 | 4035000 | 200727 | 994110 | 142488 | 138720 | 0 | 954194 | 0 | 0 | 78216 | 346824 | 110700 | 564000 | 513050 | 2098560 | 2480720 | 336000 | 313668 | 12950 | 1307000 | 608640 | 915600 | 837722 | 3552872 | 5341000 | 728544 | 1258560 | 0 | 1666450 | 430000 | 0 | 0 | 7236500 | 257400 | 75096 | 0 | 629781 | 0 | 0 | 343200 | 0 | 61490 | 125820 | 1339200 | 0 | 896581 | 6405000 | 1554000 | 1095588 | 0 | 27000 | 1728262 | 810650 | 0 | 34200 | 942480 | 1249920 | 0 | 1374720 | 315840 | 0 | 15055 |  | 11400727 | 0 | 6127776 | 0 | 66240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500500 | 25340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21120 | 0 | 365760 | 0 | 213678 | 90327 | 0 | 3432700 | 0 | 0 | 0 | 0 | 4020755 | 0 | 642678 | 0 | 4246164 | 0 | 9109672 | 1019 | 0 | 21888 | 0 | 488640 | 0 | 33818 | 634368 | 10134300 | 1706181 | 0 | 0 |  | 119114546 | 53283651 | 172398197 | 78140308 | 11400727 | 42896673 | 21231121 | 13657327 | 2041904 | 416149 | 2098560 | 515428 | 0
Fuel Cost | 0 | 3570500 | 0 | 4074840 | 5322672 | 2181779.16 | 1300812.8 | 8274960.3 | 6109960 |  | 0 | 7235747 | 3634729.41 | 3752496 | 1237058.16 | 211161.6 | 0 | 0 | 0 | 3375849.6 | 5358182.4 | 3041740.8 | 0 | 0 | 0 | 0 | 6351876 | 2893764.15 | 1851481.22 | 211734 | 450000 | 0 | 0 | 0 | 3402640.92 | 0 | 551314.08 | 0 | 0 | 0 | 0 | 5312593.51 | 0 | 2780231 | 0 |  | 0 | 0 | 1038181.3 | 0 | 526176 | 4983897.6 | 592583.04 | 1451260.8 | 0 | 2841052.4 | 0 | 5520844 | 0 | 3712200 | 258937.83 | 1143226.5 | 161011.44 | 194208 | 0 | 1631671.74 | 0 | 0 | 746962.8 | 440466.48 | 83025 | 987000 | 384787.5 | 15739200 | 2629563.2 | 3050880 | 398358.36 | 206423 | 2143480 | 973824 | 1629768 | 1306846.32 | 4050274.08 | 5554640 | 1435231.68 | 2403849.6 | 0 | 2882958.5 | 941700 | 0 | 0 | 7308865 | 193050 | 57072.96 | 0 | 4761144.36 | 0 | 0 | 1784640 | 0 | 605061.6 | 1470835.8 | 10914480 | 0 | 6320896.05 | 5956650 | 14172480 | 10353306.6 | 0 | 0 | 13065660.72 | 7060761.5 | 0 | 341316 | 8077053.6 | 8324467.2 | 0 | 0 | 0 | 0 | 0 |  | 65668187.52 | 0 | 6434164.8 | 0 | 520646.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775775 | 247318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204652.8 | 0 | 702259.2 | 0 | 161754.246 | 544671.81 | 0 | 18605234 | 0 | 0 | 0 | 0 | 5307396.6 | 0 | 964017 | 0 | 4968011.88 | 0 | 9018575.28 | 10638.36 | 0 | 207717.12 | 0 | 3791846.4 | 0 | 373688.9 | 4687979.52 | 44489577 | 0 | 0 | 0 |  | 255300354.67 | 167684112.236 | 422984466.906 | 85901583.396 | 65668187.52 | 48524606.81 | 136829222.49 | 63639482.81 | 551314.08 | 4079922.1 | 15739200 | 2050947.7 | 0
Yesterday Day Peak | 0 | 93 | 0 | 115 | 200 | 98 | 40 | 371 | 260 |  | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 28 | 17 | 19 | 25 | 0 | 92 | 0 | 0 | 0 | 0 | 208 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 2 | 0 | 80 | 0 | 300 | 0 | 134 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 19 | 92 | 102 | 17 | 20 | 2 | 60 | 8 | 52 | 46 | 163 | 260 | 34 | 76 | 0 | 70 | 18 | 0 | 0 | 310 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 90 | 0 | 10 | 304 | 54 | 91 | 0 | 4 | 150 | 41 | 0 | 0 | 56 | 90 | 0 | 78 | 51 | 0 | 0 |  | 386 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 173 | 0 | 13 | 0 | 177 | 0 | 432 | 70 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 96 | 0 | 0 |  | 7608 | DayPeak
Yesterday Evening Peak | 0 | 93 | 0 | 115 | 200 | 74 | 0 | 343 | 235 | 0 | 0 | 250 | 145 | 100 | 48 | 0 | 0 | 0 | 0 | 90 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 25 | 52 | 0 | 89 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 14 | 0 | 80 | 0 | 345 | 0 | 164 | 8 | 36 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 104 | 108 | 17 | 20 | 0 | 60 | 22 | 53 | 47 | 163 | 177 | 35 | 80 | 0 | 50 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 145 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 0 | 120 | 283 | 115 | 91 | 0 | 0 | 144 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 0 | 0 |  | 768 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 62 | 0 | 160 | 0 | 422 | 90 | 0 | 0 | 0 | 106 | 0 | 0 | 113 | 570 | 97 | 0 | 0 |  | 8968 | EvPeak
Forecast for Evening | 0 | 100 | 0 | 115 | 200 | 100 | 0 | 412 | 360 | 0 | 0 | 350 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 80 | 0 | 360 | 0 | 225 | 8 | 50 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 154 | 130 | 32 | 17 | 0 | 60 | 60 | 51 | 44 | 163 | 260 | 36 | 86 | 0 | 40 | 20 | 0 | 0 | 325 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 788 | 16 | 270 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 85 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 100 | 0 | 115 | 200 | 100 | 0 | 412 | 360 | 0 | 0 | 350 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 |  | 80 | 0 | 360 | 0 | 225 | 8 | 50 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 130 | 16 | 17 | 1.6 | 60 | 60 | 51 | 44 | 163 | 260 | 36 | 86 | 0 | 40 | 20 | 0 | 0 | 325 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 596 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 85 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 93 | 0 | 115 | 200 | 52 | 0 | 392 | 293 | 0 | 0 | 330 | 150 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 17 |  | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 8 | 0 | 80 | 0 | 300 | 0 | 216 | 8 | 40 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 76 | 111 | 0 | 20 | 1 | 60 | 22 | 50 | 47 | 163 | 233 | 36 | 80 | 0 | 40 | 19 | 0 | 0 | 320 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 230 | 32 | 0 | 0 | 1 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 27 | 0 | 0 | 0 | 353 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 150 | 0 | 433 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 39 | 0 | 0 | 0
199
| Minimum Generation |  | 5633 | 5:00
| Highest Generation |  | 8968 | 19:00
| Day Peak Generation |  | 7608 | 12:00
| Evening Peak Generation |  | 8968 | 19:00
| HVDC Max Flow |  | 768 | 19:00
| HVDC EvPeak Flow |  | 768 | 19:00
| Load factor L.F |  | 80.1%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7608 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5635 | MW
Evening Peak Generation : |  | 8968 | MW Hour : | 19:00 | Available Max Generation : |  | 14425 | MW
E.P. Demand (at gen end) : |  | 8968 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 8968 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5225 | MW
Total Gen. (MKWH) : |  | 172.3982 | System Load Factor : | 80.1% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -41 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-02
Actual : | 100.14 | Ft.(MSL) , | Rule curve : | 105.91 | Ft.( MSL )
Gas Consumed : | Total = | 986.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 134426190.206
: |  | Coal : | 63639482.81 | Oil : | 140909144.59 | Total : | 338974817.606
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3233.1655 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1094.2731 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 979.509 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 884.7411 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 799.7086 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 645.3234 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 367.5017 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 166.3299 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 497.6736 |  |  | 0 | 0%
Total | 0 |  | 8668.2259 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10)Ashuganj(S)-360 MW
2) Baghabari-71,100 MW
3) Ghorasal Unit-1,2,4
4) Ashuganj unit-3,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Chandpur-163 MW STG
9) Sirajganj #1 CCPP STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Haripur-AES Haripur 360 MW, 230 kV Ckt-2 was under shut down from 08:58 to 10:45 for R/H maintenance
at S/S end.
b) Kaptai-Hathazari 132 kV Ckt-2 was under shut down from 08:45 to 16:58 for A/M.
c) Juldah 132/33 kV T-2 transformer was shut down at 08:25 t for A/M.
d) Manikganj-Kabirpur 132 kV Ckt-2 & 132/33 kV T-2 transformer were under shut down from 07:42 to 17:18 for A/M.
e) Tongi 132/33 kV T-3 transformer was under shut down from 09:15 to 14:45 for A/M.
f) Bhaluka 132 kV Bus-1 was shut down at 08:36 for A/M.
g) Aminbazar-Hasnabad 230 kV Ckt-2 was under shut down from 10:38 to 17:07 for A/M.
h) B.Baria-Shahjibazar 132 kV Ckt-1 was under shut down from 09:18 to 13:13 for A/M.
i) B.Baria 132/33 kV T-1 transformer was under shut down from 08:48 to 16:02 for A/M.
j) Comilla(N) 230/132 kV T-1 transformer was under shut down from 08:23 to 15:42 for A/M.
k) Chandpur Desh Energy-Ramganj 132 kV Ckt-2 was under shut down from 09:10 to 18:35 for A/M.
l) Haripur-Sonargaon 132 kV Ckt-2 was under shut down from 10:47 to 15:28 for A/M.
m) Netrokona 132/33 kV T-3 transformer was under shut down from 08:30 to 16:29 for A/M.
n) Jamalpur-UMPL 132 kV Ckt-1 was under shut down from 09:13 to 16:44 for A/M.
o) UMPL-Sherpur 132 kV Ckt-1 was under shut down from 09:07 to 16:56 for A/M.
p) Kaliakoir-Tangail 132 kV Ckt-2 was shut down at 11:19 for D/W.
q) Saidpur-Barapukuria 132 kV Ckt-1 was under shut down from 08:34 to 16:54 for A/M.
r)Rajshahi 132/33 kV T-1 Transformer was under shut down from 08:25 to 16:22 for A/M.
s) Naogaon-Bogura 132 kV Ckt-1 was under shut down from 08:20 to 17:54 for A/M.
t) Rajshahi 230/132 kV T-2 transformer was switched on at 09:51.
u) Rajshahi(N) 230/132 kV T-1 transformer was shut down at 10:27 for D/W.
v) Bheramara HVDC-Rajshahi(N) 230 kV Ckt-1 was under shut down from 10:08 to 19:00 for D/W.
w) Aminbazar 230/132 kV T-2 transformer under shut down from 09:23 to 14:29 for painting fire wall.
x) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 09:14 to 16:30 for A/M.
y) Kabirpur 132/33 kV T-3 transformer was under shut down from 11:09 to 14:06 for relay test.
z) Satmosjid 132/33 kV T-1 transformer was under shut down from 15:51 to 16:43 for protection testing.
aa) Mymensingh RPCL ST was synchronized at 16:58.
ab) Bheramara HVDC pole-2 was de-block at 17:50.
ac) Bibiyana-3 ST was shut down at 16:44 for water intake pump leakage.
ad) Sikalbaha 150 MW was shut down at 18:48 for gas shortage.
ae) Shyampur(old)-Shyampur(new) 132 kV Ckt-1 was shut down at 07:41(02/12/20200 for D/W.
af) Ashuganj-Bhulta 400 kV Ckt-2 was shut down at 07:20(02/12/2020) for A/M.
ag) Barapukuria unit-1 was synchronized at 22:17.
ah) Aminbazar-Hasnabad 230 kV Ckt-1 was shut down at 07:36(02/12/2020) for A/M.
ai) Bagerhat-Bhandaria 132 kV Ckt was shut down at 07:12(02/12/2020) for A/M.
ak) Aminbazar 230/132 kV T-2 transformer was shut at 07:30(02/12/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 93 | 2412500 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4795200 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 765184 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 74 | 1652863 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 8193030 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 235 | 5932000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6638300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 494400
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 145 | 3274531 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 179544 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 24960 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 282312
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 448320 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 587520 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 870120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 309120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 374355
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 187777
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1300200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 565200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 531900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 351876
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 629781 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 61490 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 91 | 1095588 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1374720 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 0 | Reserve.
| Dhaka area Total |  |  |  | 5895 | 2458 | 46104791
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 125820
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 629280
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 89 | 2041904 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4873939
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 1635430 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 107029 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1339200
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 470304
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 488640
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 60480 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 144 | 1728262 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 810650
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1249920
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 15055
| Chattogram area Total |  |  |  | 2266 | 809 | 15602913
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1919630 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 164 | 4035000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7460600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 142488 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138720 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 954194
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 896581 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 36 | 994110 | ST Under maint and Gas shortage
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 346824
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 110700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2098560 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 564000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 78216 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 513050
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 34200 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 942480
| Cumilla Area Total |  |  |  | 2980 | 1114 | 21430080
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 2480720 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 313668
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 17 | 336000 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12950
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 80 | 343200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1554000 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 315840
| Mymensingh Area Total |  |  |  | 637 | 340 | 5356378
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1307000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 608640 | #04 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3552872
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 177 | 5341000 | Gas shortage
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 915600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 837722
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 75096
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 728544
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1258560
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 50 | 1666450 | Gas shortage
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 430000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 257400 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7236500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 283 | 6405000 | ST Under maint and Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1309 | 30620384
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 768 | 11400727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 66240 | Reserve.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 190 | 6127776 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1019 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1048 | 17595762
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 25340 | Reserve.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 500500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 62 | 642678 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 10134300 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 97 | 1706181
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 755 | 13008999
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 161 | 4020755 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4246164 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 422 | 9109672 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 365760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 213678
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 21120 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 21888 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 634368
| Rajshahi Area Total |  |  |  | 2183 | 889 | 18633405
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 90327 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3432700 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 106 | 488640
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33818
| Rangpur Area Total |  |  |  | 605 | 246 | 4045485
| Total |  |  |  | 19892 | 8968 | 172398197
| Eastern Grid Total |  |  |  | 13766 | 6030 | 119114546
| Western Grid Total |  |  |  | 6126 | 2938 | 53283651
| National Grid Total |  |  |  | 19892 | 8968 | 172398197
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-01
| (a) ENTIRE EASTERN GRID : |  | 5797 | MW | (b) ENTIRE WESTERN GRID : |  | 2639 | MW
| i) Dhaka area |  | 3189 | MW | i) Khulna area |  | 998 | MW
| ii) Chittagong area |  | 918 | MW | ii) Rajshahi area |  | 839 | MW
| iii) Comilla area |  | 724 | MW | iii) Barisal area |  | 237 | MW
| iv) Mymensingh area |  | 652 | MW | iv) Rangpur area |  | 565 | MW
| v) Sylhet area |  | 314 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8436 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 110 | 15:00 | Jamalpur | 85 | 18:00 | Benapol | 34 | 18:00
| Munsiganj | 84 | 19:30 | Sherpur | 84 | 18:00 | Jhenida | 76 | 18:00
| Sonargaon | 55 | 20:00 | Srimongal | 30 | 19:30 | Bottail | 94 | 18:30
| Shyampur | 178 | 12:00 | Shahjibazar | 76 | 18:00 | G.K Project | 35 | 18:00
| Bhulta | 156 | 19:30 | Fenchuganj | 28 | 18:00 | Faridpur | 130 | 18:30
| Madanganj | 53 | 14:00 | Kulawara | 30 | 18:00 | Madaripur | 61 | 21:00
| Shitalakhya | 92 | 10:00 | Sylhet | 75 | 18:00 | Sariatpur | 40 | 20:00
| Rahim steel | 17 | 12:00 | Chatak | 18 | 18:00 | Gopalganj | 57 | 18:00
| Matuail | 64 | 10:00 | Sunamganj | 28 | 18:30 | Bagerhat | 78 | 18:00
| Ghorasal | 65 | 18:00 | Biani Bazar | 36 | 18:00 | Mongla | 32 | 1:00
| Narsingdi | 123 | 19:00 | Comilla (S) | 106 | 18:00 | Satkhira | 72 | 18:30
| Haripur (SBU) | 98 | 11:00 | Comilla(N) | 65 | 19:30 | Gallamari | 23 | 13:00
| Ullon | 46 | 18:00 | Chandpur | 62 | 19:30 | Magura | 40 | 18:00
| Hasnabad | 148 | 19:00 | Feni | 85 | 18:00 | Norail | 28 | 18:30
| Magbazar | 70 | 14:00 | Chowmuhani | 112 | 18:00 | Chuadanga | 61 | 18:00
| Maniknagar | 70 | 13:00 | Ashuganj | 40 | 19:30 | Barisal(N) | 27 | 19:00
| Bangabhaban | 24 | 10:00 | Daudkandi | 86 | 19:30 | Barisal (S) | 70 | 19:30
| Narinda | 78 | 13:00 | B.Baria | 97 | 18:00 | Patuakhali | 83 | 20:00
| Dhanmondi | 95 | 15:00 | Ramganj | 66 | 20:00 | Bhandaria | 40 | 19:00
| Lalbag | 72 | 17:00 | Chaddagram | 23 | 19:30 | Borhan Uddin | 26 | 21:00
| Madartek | 49 | 18:00 | PHP | 5 | 2:00 | Ishurdi | 43 | 18:00
| Dhaka University |  |  | Madunaghat | 43 | 18:30 | Ruppur Paromanobik | 2 | 18:00
| Aftabnagar | 7 | 0.75 | Hathazari | 78 | 0.75 | Natore | 77 | 0.77083
| Fatullah | 34 | 9:00 | Khulshi | 174 | 18:00 | Bogra | 126 | 18:30
| Mirpur | 77 | 18:00 | Halishahar | 110 | 18:30 | Noagaon | 80 | 19:00
| Kalyanpur | 66 | 18:00 | Baraulia | 132 | 11:00 | Rajshahi | 95 | 20:00
| Gulshan | 88 | 13:00 | Sikalbaha | 22 | 18:00 | Rajshahi New | 8 | 20:00
| Uttara | 69 | 18:00 | Dohazari | 56 | 19:00 | C.Nawabganj | 48 | 12:00
| Uttara New | 22 | 19:00 | Cox'sbazar | 77 | 19:30 | Amnura | 28 | 20:00
| Kamrangirchar | 77 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 80 | 18:00
| Savar | 96 | 12:00 | Kaptai | 3.8 | 18:00 | Shahjadpur | 74 | 19:00
| Bhasantec | 110 | 18:00 | A. Khaer Stl. | 9 | 16:00 | Serajganj | 62 | 20:00
| Agargaon | 50 | 14:00 | Bakulia | 82 | 18:00 | Niyamatpur | 40 | 18:00
| Satmosjid | 66 | 0.75 | Julda | 20 | 0.45833 | Joypurhat | 41 | 0.75
| Tongi | 67 | 18:00 | TK chemical | 19.9 | 18:30 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 176 | 15:00 | Modern Steel | 18 | 20:00 | Mohastangor | 30 | 18:00
| Basundhara | 112 | 18:00 | Shahmirpur | 17.1 | 18:00 | Rangpur | 108 | 18:00
| Manikganj | 52 | 18:30 | Khagrachhari | 20 | 18:30 | Lalmonirhat | 44 | 18:00
| Joydevpur | 124 | 19:00 | Matarbari | 50 | 0:00 | Saidpur | 89 | 18:00
| New Tongi | 80 | 12:00 | Baroiar Hat | 20 | 18:00 | Purbasadipur | 82 | 20:00
| Kodda | 179 | 12:00 | Rangamati | 10 | 18:00 | Thakurgaon | 62 | 18:00
| Dhamrai | 70 | 18:30 | Abul Khair 230 | 2 | 4:00 | Palashbari | 81 | 18:00
| Rajendrapur | 74 | 19:00 | BSRM | 151 | 6:00 | Barapukuria | 38 | 20:00
| Valuka | 70 | 18:00 | GPH Ispat | 81 | 17:00 | Panchagar | 43 | 18:30
| Tangail | 141 | 18:00 | Goalpara | 16 | 20:00 | Joldhaka | 20 | 18:00
| Mymensing | 136 | 18:30 | Central s/s | 78 | 18:00 | Kurigram | 40 | 18:30
| Kishorganj | 80 | 19:30 | Noapara | 42 | 18:00
| Netrokona | 83 | 18:00 | Jessore | 84 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 20:00 | 402 | 12:00 | Kaliakoir | 385 | 0.20833 | 368 | 0.5
| Bheramara | 409 | 6:00 | 402 | 10:00 | Bhulta | 390 | 0.83333 | 376 | 0.5
| Ashuganj(N) | 396 | 3:00 | 383 | 12:00 | Gopalganj | 420 | 0.25 | 395 | 0.8125
| Payra | 420 | 20:00 | 407 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 19:00 | 232 | 11:00 | Comilla (N) | 239 | 18:00 | 233 | 1:00
| Ishurdi | 238 | 4:00 | 229 | 8:00 | Hathazari | 218 | 24:00 | 210 | 4:00
| Ashuganj | 240 | 18:00 | 232 | 12:00 | Megnaghat | 236 | 19:30 | 230 | 11:00
| Serajganj | 232 | 22:00 | 227 | 11:00 | Fenchuganj | 245 | 18:00 | 240 | 12:00
| Baghabari | 241 | 4:00 | 236 | 11:00 | Siddhirganj | 233 | 19:30 | 226 | 11:00
| Barapukuria | 231 | 1:00 | 225 | 8:00 | Maniknagar | 232 | 5:00 | 224 | 11:00
| Bogra | 233 | 22:00 | 224 | 12:00 | Agargaon | 232 | 4:00 | 222 | 12:00
| Rajshahi | 229 | 4:00 | 218 | 8:00 | Barisal | 251 | 18:00 | 243 | 20:00
| Khulna South | 233 | 5:00 | 218 | 8:00 | AKSML | 224 | 18:30 | 214 | 2:00
| Rampura | 231 | 19:00 | 228 | 11:00 | BSRM | 228 | 23:00 | 218 | 2:00
| Haripur | 232 | 18:00 | 225 | 11:00 | Bibiyana | 243 | 6:00 | 239 | 17:00
| Hasnabad | 232 | 3:00 | 225 | 11:00 | Bhulta | 234 | 19:00 | 226 | 17:00
| Shyampur | 232 | 20:00 | 220 | 12:00 | Ashuganj (S) | 238 | 20:00 | 230 | 12:00
| Aminbazar | 233 | 21:00 | 223 | 12:00 | Kaliakoir | 231 | 3:00 | 222 | 12:00
| Tongi | 232 | 18:00 | 221 | 11:00 | GPH | 227 | 3:00 | 216 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 19:30 | 134 | 11:00 | Madanhat | 136 | 0.8125 | 132 | 0.041667
| Munsiganj | 140 | 18:00 | 133 | 11:00 | Hathazari | 136 | 0.75 | 130 | 0.041667
| Sonargaon | 139 | 18:00 | 132 | 5:00 | Khulshi | 133 | 0.77083 | 127 | 0.083333
| Shyampur | 135 | 19:30 | 128 | 12:00 | Halishahar | 135 | 0.8125 | 128 | 0.041667
| Bhulta | 132 | 17:00 | 127 | 12:00 | Baraulia | 133 | 0.77083 | 128 | 0.45833
| Madanganj | 134 | 4:00 | 131 | 15:00 | Sikalbaha | 135 | 0.75 | 129 | 0.083333
| Shitalakhya | 142 | 18:00 | 133 | 12:00 | Dohazari | 132 | 0.875 | 127 | 0.041667
| Rahim steal | 140 | 20:00 | 134 | 11:00 | Cox'sbazar | 127 | 0.33333 | 122 | 0.95833
| Matuail | 140 | 19:30 | 134 | 11:00 | Chandraghona | 135 | 0.77083 | 130 | 0.041667
| Ghorasal | 140 | 7:00 | 136 | 12:00 | Kaptai | 134 | 0.75 | 130 | 0.041667
| Narsinghdi | 136 | 18:00 | 131 | 11:00 | A. Khaer Stl. | 132 | 0.77083 | 129 | 0.41667
| Haripur (SBU) | 135 | 3:00 | 132 | 21:00 | Bakulia | 134 | 0.77083 | 127 | 0.041667
| Ullon | 132 | 4:00 | 126 | 16:00 | Julda | 135 | 0.77083 | 128 | 0.16667
| Hasnabad | 140 | 19:30 | 133 | 11:00 | TK Chemical | 135 | 0.77083 | 130 | 0.45833
| Magbazar | 132 | 2:00 | 126 | 12:00 | Modern Steel | 134 | 0.79167 | 128 | 0.45833
| Maniknagar | 137 | 5:00 | 133 | 12:00 | Shahmirpur | 135 | 0.77083 | 128 | 0.20833
| Bangabhaban | 137 | 5:00 | 133 | 12:00 | Khagrachhari | 134 | 0.77083 | 130 | 0.041667
| Narinda | 137 | 5:00 | 133 | 12:00 | Matarbari | 129 | 0.375 | 125 | 0.041667
| Dhanmondi | 132 | 4:00 | 126 | 16:00 | Baroiar Hat | 137 | 0.75 | 131 | 0.45833
| Lalbag | 128 | 3:00 | 117 | 12:00 | Rangamati | 135 | 20:00 | 130 | 4:00
| Madartek | 132 | 3:00 | 126 | 11:00 | Goalpara S/S | 139 | 15:00 | 128 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 15:00 | 131 | 0.33333
| Aftabnagar | 133 | 19:00 | 126 | 15:00 | Noapara | 137 | 15:00 | 129 | 0.29167
| Fatuiiah | 136 | 19:30 | 130 | 11:00 | Jessore | 135 | 15:00 | 124 | 0.33333
| Mirpur | 129 | 6:00 | 119 | 12:00 | Benapol | 136 | 0.625 | 127 | 0.79167
| Kalyanpur | 129 | 19:30 | 121 | 12:00 | Jhenida | 134 | 3:00 | 124 | 0.77083
| Gulshan | 132 | 6:00 | 126 | 12:00 | Bottail | 137 | 0.125 | 129 | 0.79167
| Uttara | 129 | 6:00 | 119 | 12:00 | G.K Project | 141 | 0.16667 | 136 | 0.5
| Uttara New | 127 | 6:00 | 118 | 12:00 | Faridpur | 138 | 0.16667 | 129 | 0.75
| Kamrangirchar | 138 | 19:30 | 130 | 12:00 | Madaripur | 141 | 0.25 | 132 | 0.77083
| Savar | 128 | 6:00 | 118 | 12:00 | Shariyatpur S/S | 142 | 4:00 | 133 | 0.79167
| Bhasantec | 135 | 6:00 | 128 | 12:00 | Gopalganj | 143 | 0.16667 | 133 | 0.75
| Agargaon | 136 | 6:00 | 129 | 12:00 | Bagerhat | 138 | 15:00 | 128 | 0.33333
| Satmosjid | 135 | 6:00 | 129 | 12:00 | Mongla | 135 | 15:00 | 127 | 0.33333
| Tongi | 141 | 19:00 | 135 | 15:00 | Satkhira | 137 | 6:00 | 126 | 8:00
| Kabirpur | 132 | 19:30 | 123 | 12:00 | Gallamari | 138 | 0.16667 | 132 | 0.79167
| Basundhara | 139 | 18:00 | 126 | 16:00 | Magura | 135 | 2:00 | 124 | 0.79167
| Manikganj | 140 | 4:00 | 128 | 8:00 | Norail | 133 | 0.125 | 123 | 0.79167
| Joydevpur | 140 | 20:00 | 134 | 15:00 | Chuadanga | 132 | 2:00 | 120 | 0.77083
| New Tongi | 139 | 23:00 | 133 | 8:00 | Barisal(N) | 142 | 3:00 | 136 | 19:00
| Kodda | 140 | 18:00 | 130 | 15:00 | Barisal (S) | 141 | 0.20833 | 134 | 0.83333
| Dhamrai | 131 | 3:00 | 123 | 15:00 | Patuakhali(S) | 139 | 0.25 | 132 | 0.79167
| Rajendrapur | 138 | 20:00 | 129 | 16:00 | Bhandaria | 140 | 0.16667 | 132 | 0.77083
| Valuka | 132 | 9:00 | 121 | 15:00 | Ishurdi | 139 | 6:00 | 134 | 12:00
| Tangail | 135 | 5:00 | 120 | 5:00 | Ruppur Paromanobik | 138 | 5:00 | 133 | 12:00
| Mymensing | 133 | 9:00 | 122 | 16:00 | Natore | 138 | 6:00 | 132 | 12:00
| Kishorganj | 133 | 10:00 | 126 | 15:00 | Bogra | 136 | 6:00 | 129 | 12:00
| Netrokona | 132 | 9:00 | 120 | 16:00 | Noagaon | 134 | 5:00 | 120 | 12:00
| Jamalpur | 138 | 17:00 | 124 | 16:00 | Rajshahi | 139 | 6:00 | 132 | 12:00
| Sherpur | 136 | 13:00 | 123 | 16:00 | Rajshahi New | 140 | 5:00 | 132 | 12:00
| Srimongal | 137 | 1:00 | 135 | 13:00 | C.Nawabganj | 138 | 5:00 | 130 | 12:00
| Shahjibazar | 136 | 10:00 | 132 | 16:00 | Amnura | 137 | 1:00 | 130 | 12:00
| Fenchuganj | 138 | 3:00 | 136 | 1:00 | Pabna | 138 | 6:00 | 132 | 12:00
| Khulawara | 137 | 1:00 | 134 | 16:00 | Shahjadpur | 141 | 6:00 | 135 | 12:00
| Sylhet | 135 | 1:00 | 133 | 14:00 | Serajganj | 135 | 6:00 | 130 | 12:00
| Chatak | 135 | 24:00 | 132 | 15:00 | Niyamatpur | 133 | 5:00 | 118 | 12:00
| Sunamganj | 135 | 5:00 | 132 | 13:00 | Joypurhat | 134 | 6:00 | 119 | 12:00
| Biani Bazar | 135 | 1:00 | 132 | 15:00 | Sherpur(Bogura) | 136 | 6:00 | 129 | 12:00
| Comilla(s) | 131 | 4:00 | 126 | 12:00 | Mohastangor | 135 | 4:00 | 126 | 8:00
| Comilla(n) | 143 | 18:00 | 136 | 11::00 | Rangpur | 128 | 6:00 | 118 | 12:00
| Chandpur | 138 | 7:00 | 137 | 9:00 | Lalmonirhat | 130 | 5:00 | 120 | 12:00
| Feni | 140 | 19:00 | 133 | 11:00 | Saidpur | 128 | 6:00 | 119 | 12:00
| Chowmuhani | 138 | 18:00 | 132 | 15:00 | Purbasadipur | 127 | 6:00 | 116 | 12:00
| Ashuganj | 136 | 3:00 | 135 | 1:00 | Thakurgaon | 128 | 5:00 | 115 | 12:00
| Daudkandi | 140 | 18:00 | 133 | 10:00 | Palashbari | 132 | 4:00 | 124 | 12:00
| B.Baria | 133 | 17:00 | 131 | 19:00 | Barapukuria | 131 | 6:00 | 125 | 11:00
| Ramganj | 134 | 18:00 | 129 | 17:00 | Panchagar | 126 | 6:00 | 113 | 12:00
| Chaddagram | 140 | 18:00 | 134 | 11:00 | Joldhaka | 127 | 6:00 | 116 | 12:00
| PHP | 138 | 18:30 | 131 | 11:00 | Kurigram | 128 | 0.25 | 118 | 0.5

## L-Curve
Date | 2020-12-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 161 | 4764 | 2186 | 6950 |  |  |  | QF-LDC-11
0:30 | 139.5 | 4603.5 | 2070 | 6673.5 | Date: | 2020-12-01
1:00 | 118 | 4443 | 1954 | 6397
1:30 | 164.5 | 4290 | 1949.5 | 6239.5
2:00 | 211 | 4137 | 1945 | 6082
2:30 | 196.5 | 4123.5 | 1881.5 | 6005 | [5 empty] | Gen. at Eve. Peak | 8968 | 9500 MW (19:30 )
3:00 | 182 | 4110 | 1818 | 5928 | [6 empty] | 19:00
3:30 | 171 | 4056 | 1791 | 5847 | [5 empty] | Gen. at Day Peak | 7608 | 7952.5 MW (12:00 )
4:00 | 160 | 4002 | 1764 | 5766 | [6 empty] | 12:00
4:30 | 157.5 | 3949 | 1750.5 | 5699.5 | [5 empty] | Highest Generation | 8968
5:00 | 155 | 3896 | 1737 | 5633 | [6 empty] | 19:00
5:30 | 163.5 | 3979.5 | 1786.5 | 5766
6:00 | 172 | 4063 | 1836 | 5899
6:30 | 95.5 | 4170.5 | 1884 | 6054.5
7:00 | 19 | 4278 | 1932 | 6210
7:30 | 30 | 4430.5 | 1970 | 6400.5
8:00 | 41 | 4583 | 2008 | 6591
8:30 | 20.5 | 4706.5 | 2008.5 | 6715
9:00 | 0 | 4830 | 2009 | 6839
9:30 | 43 | 4899 | 1996.5 | 6895.5
10:00 | 86 | 4968 | 1984 | 6952
10:30 | 133 | 4997.5 | 2078.5 | 7076
11:00 | 180 | 5027 | 2173 | 7200
11:30 | 155.5 | 5206.5 | 2197.5 | 7404
12:00 | 131 | 5386 | 2222 | 7608
12:30 | 78 | 5419 | 2239 | 7658
13:00 | 25 | 5452 | 2256 | 7708
13:30 | 26.5 | 5303.5 | 2178 | 7481.5
14:00 | 28 | 5155 | 2100 | 7255
14:30 | 178.5 | 5116 | 2139 | 7255
15:00 | 329 | 5077 | 2178 | 7255
15:30 | 309 | 5019.5 | 2151.5 | 7171
16:00 | 289 | 4962 | 2125 | 7087
16:30 | 282 | 4977 | 2224.5 | 7201.5
17:00 | 275 | 4992 | 2324 | 7316
17:30 | 137.5 | 5562 | 2531 | 8093
18:00 | 0 | 6132 | 2738 | 8870
18:30 | 43 | 6081 | 2838 | 8919
19:00 | 86 | 6030 | 2938 | 8968
19:30 | 43 | 6023 | 2916 | 8939
20:00 | 61 | 5909 | 2895 | 8804 |  |  |  | Executive Engineer
20:30 | 134 | 5749.5 | 2891.5 | 8641 |  |  |  | Network Operation Division
21:00 | 207 | 5590 | 2888 | 8478
21:30 | 288.5 | 5404 | 2837.5 | 8241.5
22:00 | 370 | 5218 | 2787 | 8005 |  |  |  |  | Page 6 of 7
22:30 | 335 | 5050 | 2633.5 | 7683.5
23:00 | 300 | 4882 | 2480 | 7362
23:30 | 230.5 | 4823 | 2333 | 7156
24:00 | 161 | 4764 | 2186 | 6950
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-01 |  | Energy | 172398197
[10 empty] | 2020-12-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3156 | 390 | 1841 | 740 | 695 | 91 | 16 | 0 | 82
0:30 | 3252 | 395 | 1806.5 | 450 | 621.5 | 91 | 8 | 0 | 80 | Date: | 2020-12-01
1:00 | 3348 | 400 | 1772 | 160 | 548 | 91 | 0 | 0 | 78
1:30 | 3286 | 400 | 1680.5 | 156 | 549 | 91 | 0 | 0 | 77 | [7 empty] | Total Energy | 172.3982 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3224 | 400 | 1589 | 152 | 550 | 91 | 0 | 0 | 76 | [7 empty] | Energy not Served | 0
2:30 | 3211 | 400 | 1525 | 152 | 550 | 91 | 0 | 0 | 76 | [7 empty] | Energy Requirement | 172.3982
3:00 | 3198 | 400 | 1461 | 152 | 550 | 91 | 0 | 0 | 76
3:30 | 3181 | 400 | 1435.5 | 147 | 520 | 89.5 | 0 | 0 | 74 | [6 empty] | Shortage
4:00 | 3164 | 400 | 1410 | 142 | 490 | 88 | 0 | 0 | 72
4:30 | 3105.5 | 399.5 | 1425 | 143.5 | 465 | 88 | 0 | 0 | 73
5:00 | 3047 | 399 | 1440 | 145 | 440 | 88 | 0 | 0 | 74
5:30 | 3117.5 | 399.5 | 1508 | 139 | 440 | 88 | 0 | 0 | 74
6:00 | 3188 | 400 | 1576 | 133 | 440 | 88 | 0 | 0 | 74
6:30 | 3248 | 400 | 1647 | 156 | 440 | 88.5 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3308 | 400 | 1718 | 179 | 440 | 89 | 0 | 0 | 70
7:30 | 3314 | 399.5 | 1789.5 | 278.5 | 440 | 89 | 0 | 0 | 73 |  |  |  | Oil |  |  |  | ,
8:00 | 3320 | 399 | 1861 | 378 | 440 | 89 | 0 | 0 | 76
8:30 | 3307.5 | 399 | 1849 | 506 | 445 | 90 | 0 | 0 | 77
9:00 | 3295 | 399 | 1837 | 634 | 450 | 91 | 0 | 0 | 78
9:30 | 3274 | 399.5 | 1842 | 697 | 450 | 91 | 0 | 0 | 81
10:00 | 3253 | 400 | 1847 | 760 | 450 | 91 | 0 | 0 | 84
10:30 | 3315 | 392.5 | 1894.5 | 735.5 | 490 | 91 | 0 | 0 | 85
11:00 | 3377 | 385 | 1942 | 711 | 530 | 91 | 0 | 0 | 86
11:30 | 3401.5 | 385.5 | 1968 | 854 | 535 | 91.5 | 0 | 0 | 89
12:00 | 3426 | 386 | 1994 | 997 | 540 | 92 | 0 | 0 | 92
12:30 | 3369 | 386 | 1973 | 1112 | 555 | 92 | 0 | 0 | 93
13:00 | 3312 | 386 | 1952 | 1227 | 570 | 92 | 0 | 0 | 94
13:30 | 3312 | 386 | 1952 | 1227 | 570 | 92 | 0 | 0 | 94
14:00 | 3312 | 386 | 1952 | 1227 | 570 | 92 | 0 | 0 | 94
14:30 | 3195.5 | 386 | 1897.5 | 1190.5 | 570 | 89.5 | 0 | 0 | 93
15:00 | 3079 | 386 | 1843 | 1154 | 570 | 87 | 0 | 0 | 92
15:30 | 3100 | 386 | 1788.5 | 1118.5 | 570 | 86.5 | 0 | 0 | 90
16:00 | 3121 | 386 | 1734 | 1083 | 570 | 86 | 0 | 0 | 88
16:30 | 3009.5 | 441 | 1824.5 | 1163 | 570 | 88 | 5 | 0 | 91
17:00 | 2898 | 496 | 1915 | 1243 | 570 | 90 | 10 | 0 | 94
17:30 | 3051.5 | 495.5 | 1968.5 | 1712 | 630 | 89.5 | 46 | 0 | 100
18:00 | 3205 | 495 | 2022 | 2181 | 690 | 89 | 82 | 0 | 106
18:30 | 3167 | 631.5 | 1965.5 | 2179 | 700 | 89 | 82 | 0 | 105
19:00 | 3129 | 768 | 1909 | 2177 | 710 | 89 | 82 | 0 | 104
19:30 | 3130 | 768 | 1876 | 2177 | 710 | 90 | 82 | 0 | 106
20:00 | 3160 | 768 | 1859 | 2040 | 710 | 91 | 72 | 0 | 104
20:30 | 3174 | 768 | 1845.5 | 1890.5 | 710 | 91 | 60 | 0 | 102
21:00 | 3188 | 768 | 1832 | 1741 | 710 | 91 | 48 | 0 | 100
21:30 | 3178.5 | 768 | 1831 | 1516 | 710 | 91 | 48 | 0 | 99
22:00 | 3169 | 768 | 1830 | 1291 | 710 | 91 | 48 | 0 | 98
22:30 | 3179 | 673.5 | 1860.5 | 1015.5 | 725 | 91 | 44 | 0 | 95
23:00 | 3189 | 579 | 1891 | 740 | 740 | 91 | 40 | 0 | 92
23:30 | 3172.5 | 484.5 | 1866 | 740 | 717.5 | 91 | 28 | 0 | 87 | Max Temp. in Dhaka |  | 30.2° C
24:00 | 3156 | 390 | 1841 | 740 | 695 | 91 | 16 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-12-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 91 | 91 | 91 | 88 | 88 | 88 | 89 | 89 | 91 | 91 | 91 | 92 | 92 | 89 | 87 | 86 | 90 | 89 |  | 89 | 90 | 91 | 91 | 91 | 91 | 91 | 2041904
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 9 | 14 | 17 | 19 | 19 | 17 | 15 | 11 | 6 | 0 | [9 empty] | 125820
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 202 | 209 | 214 | 203 | 203 | 217 | 208 | 205 | 206 | 204 | 227 | 204 | 204 |  | 204 | 203 | 203 | 203 | 203 | 210 | 203 | 4873939
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 70 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 140 | 70 | 70 | 70 | 71 | 70 | 70 | [8 empty] | 1635430
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 34 | 34 | 24 |  |  |  |  | 107029
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 9 | 121 |  | 145 | 145 | 115 | 114 | 15 |  |  | 629781
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 93 | 93 | 93 | 93 | 92 | 93 | 94 | 93 | 93 | 93 | 93 | 93 | 93 | 94 | 93 | 93 | 94 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2412500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4795200
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1919630
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142488
33 | Ashuganj 225 MW CCPP | 186 | 189 | 187 | 180 | 180 | 194 | 179 | 170 | 166 | 148 | 135 | 134 | 134 | 143 | 154 | 165 | 184 | 186 |  | 164 | 156 | 157 | 173 | 169 | 161 | 156 | 4035000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 250 | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 260 | 270 | 270 | 280 | 345 |  | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 7460600
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138720
36 | Chandpur 150 MW CCPP | 45 | 46 | 46 | 45 | 50 | 46 | 46 | 50 | 46 | 46 | 50 | 45 | 46 | 42 | 42 | 45 | 37 | 31 |  | 36 | 36 | 33 | 35 | 33 | 35 | 35 | 994110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 339 | 338 | 312 | 275 | 272 | 273 | 297 | 311 | 339 | 360 | 371 | 357 | 345 | 355 | 357 | 372 | 369 |  | 343 | 340 | 339 | 339 | 341 | 347 | 347 | 8193030
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 340 | 340 | 400 | 400 | 380 | 320 | 320 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6638300
41 | Haripur 360MW CCPP(HPL) | 252 | 270 | 278 | 258 | 257 | 287 | 287 | 287 | 269 | 234 | 230 | 260 | 247 | 235 | 235 | 235 | 247 | 244 |  | 235 | 235 | 235 | 212 | 212 | 212 | 212 | 5932000
42 | RPCL 210MW CCPP | 130 | 131 | 132 | 132 | 132 | 152 | 149 | 106 | 107 | 106 | 106 | 102 | 99 | 44 | 55 | 68 | 72 | 84 |  | 108 | 111 | 110 | 110 | 110 | 107 | 110 | 2480720
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 3 | 17 | 34 | 41 | 48 | 51 | 47 | 39 | 27 | 10 | 0 | [9 empty] | 315840
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1307000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 30 | 10 | 5 | 10 | 8 | 8 | 8 | 8 | 8 | 0 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 608640
46 | Shajibazar 330 MW CCPP | 258 | 254 | 260 | 258 | 261 | 257 | 255 | 263 | 256 | 254 | 265 | 260 | 255 | 254 | 199 | 197 | 197 | 176 |  | 177 | 180 | 213 | 233 | 233 | 234 | 232 | 5341000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 37 | 37 | 37 | 36 | 20 | 20 | 34 | 32 | 32 | 32 | 32 | 32 | 34 |  | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 728544
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 5 | 5 | 5 | 5 | 5 | 40 | 75 | 76 | 76 | 76 | 76 | 78 | 40 | 40 | 10 | 75 | 80 |  | 80 | 80 | 80 | 80 | 79 | 79 | 79 | 1258560
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 85 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 50 | 50 | 50 | 50 | 40 | 50 | 40 | 1666450
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 430000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 75096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 53 | 53 | 50 | 50 | 52 | 52 | 52 | 53 | 17 | 25 | 53 |  | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 915600
56 | Shahjahanulla 25 MW PP | [7 empty] | 12 | 12 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 257400
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 285 | 280 | 275 | 290 | 290 | 300 | 280 | 280 | 290 | 300 | 310 | 300 | 290 | 310 | 305 | 315 | 315 |  | 300 | 285 | 280 | 280 | 280 | 290 | 290 | 7236500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 13 | 55 |  | 55 | 55 | 55 | 17 |  |  |  | 187777
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 470304
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 282312
62 | Tangail 22 MW PP (Doreen) | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 313668
63 | Impoprt (Tripura) | 78 | 76 | 76 | 72 | 74 | 74 | 70 | 76 | 78 | 84 | 86 | 92 | 94 | 94 | 92 | 88 | 94 | 106 |  | 104 | 106 | 104 | 100 | 98 | 92 | 82 | 2098560
64 | Malancha, Ctg. EPZ (United) | 42 | 35 | 35 | 35 | 42 | 42 | 40 | 8 | 4 | 2 | 4 | 2 | 4 | 3 | 2 | 2 | 5 | 10 |  | 14 | 18 | 27 | 25 | 29 | 33 | 38 | 488640
65 | Feni 22MW PP (Doreen) | [6 empty] | 13 | 15 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 346824
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 110700
67 | Jangalia 33MW PP (Summit) | [6 empty] | 16 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 564000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 19 | 19 |  | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 513050
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 22 | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 18 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 700200
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 565200
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 19 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 531900
73 | Ghorashal 108MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 82 | 98 | 98 | 97 | 97 | 98 | 98 | 98 | 98 | 94 | 101 | 101 |  | 74 | 74 | 74 | 71 | 71 | 71 | 71 | 1652863
| Feni Lanka Power | [17 empty] | 48 | [8 empty] | 34200
| Chowmuhani 113 MW | [8 empty] | 26 | 46 | 46 | 56 | 103 | 75 | 26 | 26 | 26 | 54 |  | 113 | 113 | 113 | 45 |  |  |  | 942480
| Manikgonj 162MW PP | [26 empty] | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 12 | 65 |  | 90 | 100 | 100 | 100 | 50 |  |  | 448320
78 | Gazipur 52 MW PP | [8 empty] | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 |  | 52 | 52 | 16 |  |  |  |  | 351876
79 | Kodda 150MW PP | [16 empty] | 10 | 48 |  | 48 | 48 | 48 | 48 | 48 | 40 | 16 | 309120
80 | Jamalpur 95 MW PP(Powerpac) | 17 | 17 | 17 | 17 |  |  |  | 17 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 |  | 17 | 17 | 17 | 17 | 17 |  |  | 336000
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 7 | 36 | [8 empty] | 78216
| Gazipur 100 MW PP | [8 empty] | 1 | 60 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 45 | 35 |  |  | 1095588
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27000
| Jodiac Power | [7 empty] | 23 | 35 | 35 | 35 | 41 | 54 | 54 | 54 | 54 | 41 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 810650
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 18 |  | 48 | 48 | 48 | 30 |  |  |  | 179544
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 126 | 135 | 135 | 125 | 145 | 133 | 150 | 155 | 130 | 140 | 150 | 140 | 130 | 135 | 130 | 150 | 135 | 145 |  | 145 | 135 | 130 | 130 | 135 | 150 | 134 | 3274531
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 6 | 65 |  | 100 | 100 | 100 | 85 | 70 | 48 | 7 | 494400
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 40 | 53 | 53 | 53 | 78 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1374720
88 | Ghorashal 78.5 MW PP(MAX) | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 70 | 70 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | [8 empty] | 765184
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 47 | 5 | 5 | 5 | 5 | 5 | 10 | 43 | 43 | 47 | 47 | 46 | 46 | 46 | 46 | 15 | 15 | 39 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 837722
93 | Ashuganj 51 MW PP (Midland) | 51 | 7 | 7 | 7 | 7 | 7 | 8 |  | 10 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 954194
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 8 | 67 | 58 | 24 | 24 | 50 | 58 | 40 | 40 | 40 | 50 |  | 50 | 50 | 24 |  |  |  |  | 587520
95 | Patenga 50MW PP (Baraka) | [7 empty] | 4 | 12 | 12 | 12 | 7 | 25 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 629280
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 26 |  | 0 | [6 empty] | 60480
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 2 | 15 | [8 empty] | 24960
100 | Manikganj 55 MW PP (Northern) | [13 empty] | 35 | 17 | 17 | 35 | 55 |  | 55 | 55 | 55 | 55 | 17 |  |  | 374355
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 110 | 110 | 110 | 120 | 120 | 120 | 163 | 130 | 150 | 163 | 163 | 110 | 110 | 110 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3552872
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12950
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [5 empty] | 17 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 870120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 7 | 7 | 7 | [6 empty] | 15 | 67 |  | 80 | 80 | 40 | 16 | 16 |  |  | 343200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 1 | 30 | [6 empty] | 2 | 16 | [8 empty] | 61490
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 40 | 40 | 40 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 1339200
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [8 empty] | 8 | 10 | 10 | 10 | 15 | 86 | 70 | 70 | 70 | 93 |  | 120 | 120 | 120 | 70 | 10 |  |  | 896581
118 | Bibiyana-III 400 MW CCPP | 352 | 304 | 290 | 291 | 231 | 231 | 231 | 231 | 231 | 251 | 304 | 304 | 289 | 232 | 232 | 232 |  | 285 |  | 283 | 283 | 284 | 283 | 283 | 283 | 283 | 6405000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 59 | 75 | 45 | 45 | 54 | 115 | 85 | 85 | 85 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 1554000
| Anwara 300 MW PP (United) | [8 empty] | 33 | 33 | 33 | 150 | 158 | 125 | 125 | 71 | 70 | 142 |  | 144 | 144 | 144 | 143 | 143 | 142 | 142 | 1728262
| Juldah unit-2 (Acorn) | [6 empty] | 10 | 20 | 60 | 60 | 60 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 |  |  | 1249920
| Anlima Energy Ltd. | [9 empty] | 19 | [16 empty] | 15055
120 | Eastern Zone Total | 4443 | 4137 | 4110 | 4003 | 3895 | 4063 | 4278 | 4583 | 4830 | 4968 | 5027 | 5386 | 5452 | 5155 | 5077 | 4962 | 4992 | 6132 |  | 6030 | 6023 | 5909 | 5590 | 5218 | 4882 | 4764 | 119114546
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 48 | [8 empty] | 66240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 35 | 35 | 35 | 70 | 90 | 90 | 90 | 53 | 53 | 90 |  | 90 | 90 | 90 | 90 | 57 | 17 | 17 | 1019
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 52 | 48 | 43 | 36 | 46 | 39 | 8 | 47 | 37 | 37 | 96 | 96 | 95 | 90 | 88 | 91 | 89 | 97 |  | 97 | 96 | 90 | 86 | 88 | 98 | 88 | 1706181
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 | [8 empty] | 25340
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 55 | 62 |  | 62 | 62 | 62 | 62 | 52 | 52 | 51 | 642678
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 21 | 21 | 21 | 20 | 16 | 16 | 15 | 19 | 20 | 20 | 20 | 18 | 18 | 19 | 26 |  | 26 | 26 | 27 | 27 | 27 | 25 | 24 | 500500
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 400 | 400 | 400 | 400 | 399 | 400 | 400 | 399 | 399 | 400 | 385 | 386 | 386 | 386 | 386 | 386 | 496 | 495 |  | 768 | 768 | 768 | 768 | 768 | 579 | 390 | 11400727
147 | Bheramara 410 MW CCPP | 240 | 245 | 270 | 285 | 300 | 315 | 335 | 340 | 320 | 310 | 295 | 280 | 255 | 240 | 225 | 210 | 195 | 195 |  | 190 | 190 | 190 | 180 | 175 | 180 | 175 | 6127776
148 | Payra 1320 MW | 410 | 410 | 410 | 350 | 300 | 300 | 300 | 300 | 310 | 310 | 390 | 400 | 430 | 430 | 430 | 430 | 430 | 550 |  | 570 | 570 | 570 | 570 | 570 | 530 | 470 | 10134300
149
150 | Barapukuria TPP Unit-1 | [24 empty] | 70 | 85 | 90327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 138 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3432700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 151 | 148 | 130 | 130 | 130 | 152 | 179 | 178 | 179 | 150 | 161 | 173 | 177 | 154 | 153 | 153 | 162 | 161 |  | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 4020755
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 159 | 153 | 130 | 130 | 130 | 155 | 180 | 188 | 178 | 160 | 170 | 177 | 185 | 155 | 177 | 180 | 178 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4246164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 358 | 252 | 254 | 253 | 296 | 347 | 356 | 350 | 380 | 434 | 432 | 410 | 346 | 425 | 419 | 400 | 426 |  | 422 | 401 | 385 | 390 | 393 | 435 | 392 | 9109672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 365760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 213678
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 27 | [8 empty] | 21120
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 11 | [8 empty] | 21888
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 20 |  |  |  | 25 | 100 |  | 113 | 113 | 113 | 113 | 113 |  |  | 634368
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 101 |  | 106 | 106 | 106 | 108 | 50 |  |  | 488640
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 5 | 3 | 2 | 0 | [9 empty] | 33818
178
178