## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-03 | Thursday
|  |  | Date (day): | 2020-12-03 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12368.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13524 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-02 | 2020-12-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 113 | 113 | 115 | 115 |  | 55
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 54 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 364 | 347 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 221 | 263 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 260 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 96 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 150 | 155 | 155 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 84 | 76 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 82 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 150 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 75 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 53 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 0 | 40 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2074 | 2498 | 3811 | 4101 | 708 | 1162
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 87 | 90 | 92 | 92 | 138 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 212 | 205 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 0 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 60 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 121 | 158 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 627 | 797 | 1503 | 1498 | 648 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 129 | 129
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 50 | 100 | 34
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 191 | 192 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 270 | 0 | 0 |  | 360 | Under maint.
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 112 | 112 | 83 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 150 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 37 | 35 | 50 | 50 |  | 163 | Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 140 | 170 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 102 | 144 | 154
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 17 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 976 | 1241 | 1514 | 1825 | 214 | 883
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 108 | 120 | 120 | 82 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20 |  | 2 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 57 | 83 | 95
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 110 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 95 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 46 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 288 | 390 | 589.6 | 550 | 82 | 2
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 235 | 240 | 155 | 155 |  | 175 | GT-1 under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 32 | 35 | 36 | 36 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 40 | 40 | 0 | 0 |  | 231 | Under maint.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 325 | 325 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 230 | 80 | 230 | 230 | 170 |  | Gas shortage
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1212 | 1077 | 1257 | 1257 | 170 | 448
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 589 | 778 | 580 | 768
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 66 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  |  | Engine problem
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 100 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  |  | Engine problem
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 220 | 195 | 0 | 0 |  | 410 | Under maintenance
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 879 | 1169 | 1115 | 1539 | 0 | 425
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 54 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 280 | 590 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 66 | 81 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 366 | 750 | 867 | 927 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 167 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 175 | 225 | 225 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 411 | 285 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 78 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 20 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 741 | 828 | 1506 | 1629 | 271 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 88 | 89 | 85 | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 0 | 0 |  | 274 | Under maint.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 12 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 233 | 241 | 206 | 198 | 85 | 314
|  | Total |  |  |  |  | 20383 | 19892 | 7396 | 8991 | 12368.6 | 13524 | 2178 | 3526
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6933.6986 | 8429 | 11595.4765 | 12678.656
| A. |  | 2020-12-02 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 8991 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5635 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8991 | MW
| 3 | Day peak Generation : |  |  | 7396 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8429 | MW
| 4 | Evening peak Generation : |  |  | 8991 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 171.5029 | MKWHr | By Solar | 0.4627 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 114.3712 | MKWHr |  | By Oil: | 26.4519 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.1733 | MKWHr |  | By Hydro: | 2.1022 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2178 | MW | Dhaka | 3142 | 3142 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3526 | MW | Chittagong | 879 | 879 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5704 | MW | Khulna | 1041 | 1041 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 906.64 | MMCFD |  |  | Rajshahi | 851 | 851 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 125972738.756 | ii) Oil : | Taka | 186678042.57 | Comilla | 739 | 739 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 69117608.54 | Total | Taka | 381768389.866 | Mymensingh | 661 | 661 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.214 | MKWHr. | Sylhet | 319 | 319 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 64 | MW (E to W) at | 19:00 | hrs | Barisal | 235 | 235 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -140 | MW at | 8:00 | hrs | Rangpur | 562 | 562 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.8° C |  |  | Total | 8429 | 8429 |  | 0
| B. |  | 2020-12-03 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 28.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13524 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7600 | MW
| 4 | Reserve(Generation end) |  |  |  | 4324 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 175.4895 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5721 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8545 | MKWHr. | ii) HVDC Flow at Peak Time |  | 778 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.087 | MKWHr. | iii) Maximum HVDC Flow : |  | 779 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.14 |  | (b) Today: | 100.08 |  | (c) Rule Curve: |  | 105.91
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 338 | 242 |  | 0 | 250 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 20 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 37 | 0 | 80 | 0 | 345 | 0 | 156 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 74 | 110 | 0 | 20 | 0 | 60 | 22 | 50 | 47 | 163 | 231 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 8 | 0 | 0 | 0 | 33 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 389 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 51 | 0 | 160 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 96 | 0 | 0 |  | 4192 | 2157 | 6349 | 3098 | 389 | 1818 | 225 | 655 | 90 | 0 | 74 | 0 | 0 | 100.16
2:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 338 | 259 |  | 0 | 300 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 80 | 0 | 345 | 0 | 156 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 74 | 113 | 0 | 20 | 0 | 60 | 22 | 5 | 5 | 110 | 237 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 398 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 0 | 140 | 0 | 0 | 0 | 0 | 153 | 0 | 13 | 0 | 130 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 94 | 0 | 0 |  | 4063 | 2062 | 6125 | 3075 | 398 | 1673 | 159 | 656 | 90 | 0 | 74 | 0 | 0 | 100.16
3:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 338 | 303 |  | 0 | 330 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 80 | 0 | 345 | 0 | 156 | 8 | 35 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 72 | 113 | 0 | 20 | 0 | 60 | 22 | 5 | 5 | 110 | 234 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 398 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 44 | 0 | 0 |  | 4101 | 1817 | 5918 | 3064 | 398 | 1570 | 161 | 563 | 90 | 0 | 72 | 0 | 0 | 100.15
4:00 | 0 | 92 | 0 | 115 | 200 | 15 | 0 | 345 | 312 |  | 0 | 350 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 80 | 0 | 345 | 0 | 162 | 8 | 38 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 70 | 112 | 0 | 0 | 0 | 60 | 22 | 5 | 5 | 110 | 233 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 351 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 38 | 0 | 0 |  | 3956 | 1724 | 5680 | 3010 | 351 | 1532 | 161 | 472 | 84 | 0 | 70 | 0 | 0 | 100.15
5:00 | 0 | 93 | 0 | 115 | 200 | 15 | 0 | 353 | 312 |  | 0 | 350 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 80 | 0 | 290 | 0 | 185 | 8 | 38 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 68 | 111 | 0 | 0 | 0 | 60 | 22 | 5 | 5 | 110 | 237 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 350 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 39 | 0 | 0 |  | 3892 | 1743 | 5635 | 2977 | 350 | 1537 | 146 | 473 | 84 | 0 | 68 | 0 | 0 | 100.14
6:00 | 0 | 93 | 0 | 115 | 200 | 15 | 0 | 357 | 338 |  | 0 | 350 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 290 | 0 | 210 | 8 | 38 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 70 | 111 | 0 | 0 | 0 | 60 | 22 | 5 | 5 | 130 | 234 | 36 | 10 | 0 | 40 | 18 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 351 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 52 |  | 4010 | 1864 | 5874 | 3020 | 351 | 1676 | 200 | 473 | 84 | 0 | 70 | 0 | 0 | 100.14
7:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 366 | 328 |  | 0 | 350 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 80 | 0 | 300 | 0 | 218 | 8 | 45 | 5 | 5 | 0 | 37 | 0 | 0 | 0 | 18 | 0 | 23 | 20 | 68 | 111 | 0 | 20 | 0 | 60 | 22 | 19 | 18 | 130 | 237 | 36 | 10 | 0 | 40 | 19 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 |  | 350 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 84 | 0 | 140 | 0 | 0 | 0 | 0 | 146 | 0 | 13 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 |  | 4201 | 1925 | 6126 | 3189 | 350 | 1803 | 155 | 474 | 84 | 0 | 68 | 3 | 0 | 100.13
8:00 | 0 | 93 | 0 | 115 | 200 | 52 | 0 | 392 | 293 |  | 0 | 330 | 150 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 8 | 0 | 80 | 0 | 300 | 0 | 216 | 8 | 40 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 76 | 111 | 0 | 20 | 1 | 60 | 22 | 50 | 47 | 163 | 233 | 36 | 80 | 0 | 40 | 19 | 0 | 0 | 320 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 230 | 32 | 0 | 0 | 1 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 27 | 0 | 0 |  | 353 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 150 | 0 | 433 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 39 | 0 | 0 |  | 4549 | 1979 | 6528 | 3226 | 353 | 1932 | 321 | 495 | 87 | 0 | 76 | 38 | 0 | 100.13
9:00 | 0 | 110 | 0 | 115 | 200 | 52 | 0 | 379 | 287 |  | 0 | 300 | 140 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 2 | 0 | 89 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 4 | 0 | 80 | 0 | 300 | 0 | 190 | 8 | 36 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 76 | 107 | 0 | 20 | 1 | 40 | 22 | 28 | 47 | 163 | 234 | 35 | 77 | 0 | 40 | 18 | 0 | 0 | 320 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 10 | 73 | 0 | 230 | 80 | 0 | 0 | 3 | 83 | 54 | 0 | 0 | 0 | 0 | 0 | 69 | 27 | 0 | 0 |  | 352 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 150 | 0 | 435 | 70 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 300 | 56 | 0 | 0 |  | 4788 | 2062 | 6850 | 3146 | 352 | 1880 | 734 | 526 | 89 | 0 | 76 | 47 | 0 | 100.13
10:00 | 0 | 112 | 0 | 115 | 200 | 52 | 0 | 346 | 221 |  | 0 | 300 | 130 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 23 | 20 | 25 | 43 | 0 | 89 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 34 | 20 | 2 | 0 | 80 | 0 | 300 | 0 | 180 | 8 | 38 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 80 | 110 | 0 | 20 | 2 | 40 | 22 | 5 | 47 | 163 | 236 | 35 | 74 | 0 | 40 | 18 | 0 | 0 | 290 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 17 | 20 | 120 | 10 | 230 | 115 | 0 | 0 | 4 | 83 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 37 | 0 | 0 |  | 352 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 12 | 0 | 150 | 0 | 317 | 70 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 61 | 0 | 0 |  | 4943 | 1935 | 6878 | 3113 | 352 | 1642 | 1011 | 527 | 89 | 0 | 80 | 64 | 0 | 100.13
11:00 | 0 | 114 | 0 | 115 | 200 | 52 | 0 | 341 | 221 |  | 0 | 300 | 135 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 23 | 20 | 8 | 43 | 0 | 87 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 275 | 0 | 181 | 8 | 36 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 86 | 107 | 0 | 20 | 2 | 60 | 22 | 5 | 47 | 110 | 236 | 32 | 80 | 0 | 40 | 18 | 0 | 0 | 290 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 17 | 10 | 120 | 0 | 230 | 115 | 0 | 0 | 4 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 45 | 0 | 2 |  | 589 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 87 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 347 | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 66 | 0 | 0 |  | 4909 | 2139 | 7048 | 3090 | 589 | 1616 | 1000 | 507 | 87 | 0 | 86 | 73 | 0 | 100.13
12:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 364 | 221 |  | 0 | 300 | 140 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 31 | 20 | 8 | 43 | 0 | 87 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 285 | 0 | 191 | 8 | 37 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 90 | 105 | 0 | 20 | 2 | 60 | 22 | 11 | 46 | 110 | 235 | 32 | 76 | 0 | 40 | 18 | 0 | 0 | 310 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 60 | 140 | 5 | 230 | 115 | 0 | 0 | 4 | 121 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 46 | 0 | 0 |  | 589 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 411 | 70 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 66 | 0 | 0 |  | 5177 | 2219 | 7396 | 3116 | 589 | 1711 | 1202 | 508 | 87 | 17 | 90 | 76 | 0 | 100.13
13:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 352 | 264 |  | 0 | 280 | 130 | 100 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 31 | 20 | 8 | 43 | 0 | 87 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 6 | 0 | 80 | 0 | 275 | 0 | 181 | 8 | 36 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 88 | 83 | 0 | 20 | 2 | 60 | 22 | 17 | 46 | 163 | 230 | 32 | 76 | 0 | 40 | 18 | 0 | 0 | 300 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 18 | 100 | 170 | 35 | 200 | 115 | 0 | 0 | 4 | 124 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 41 | 0 | 0 |  | 589 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 412 | 90 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 62 | 0 | 0 |  | 5293 | 2258 | 7551 | 3042 | 589 | 1785 | 1344 | 508 | 87 | 38 | 88 | 70 | 7551 | 100.12
14:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 334 | 264 |  | 0 | 280 | 140 | 89 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 31 | 20 | 8 | 43 | 0 | 87 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 6 | 0 | 80 | 0 | 280 | 0 | 180 | 8 | 34 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 90 | 86 | 0 | 0 | 2 | 60 | 22 | 50 | 43 | 110 | 233 | 32 | 76 | 0 | 40 | 18 | 0 | 0 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 14 | 100 | 100 | 53 | 80 | 115 | 0 | 0 | 3 | 124 | 41 | 0 | 0 | 0 | 0 | 0 | 90 | 31 | 0 | 10 |  | 590 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 305 | 90 | 0 | 26 | 0 | 0 | 0 | 4 | 0 | 250 | 54 | 0 | 0 |  | 5039 | 2153 | 7192 | 2886 | 590 | 1635 | 1330 | 478 | 87 | 42 | 90 | 54 | 0 | 100.12
15:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 281 | 264 |  | 0 | 280 | 140 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 31 | 20 | 8 | 25 | 0 | 89 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 275 | 0 | 186 | 8 | 35 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 88 | 85 | 0 | 0 | 1 | 60 | 22 | 53 | 43 | 110 | 234 | 32 | 76 | 0 | 40 | 18 | 0 | 0 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 50 | 100 | 50 | 80 | 115 | 0 | 0 | 2 | 124 | 54 | 0 | 0 | 17 | 0 | 0 | 90 | 19 | 0 | 16 |  | 589 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 347 | 90 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 55 | 0 | 0 |  | 4957 | 2156 | 7113 | 2822 | 589 | 1680 | 1288 | 478 | 89 | 42 | 88 | 37 | 0 | 100.12
16:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 281 | 264 |  | 0 | 280 | 145 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 31 | 20 | 25 | 25 | 0 | 87 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 305 | 0 | 200 | 8 | 33 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 82 | 85 | 0 | 0 | 0 | 60 | 22 | 53 | 43 | 110 | 233 | 32 | 78 | 0 | 40 | 18 | 0 | 0 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 20 | 100 | 50 | 79 | 115 | 0 | 0 | 1 | 88 | 54 | 0 | 0 | 17 | 0 | 0 | 90 | 7 | 0 | 18 |  | 589 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 348 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 56 | 0 | 0 |  | 4949 | 2093 | 7042 | 2885 | 589 | 1698 | 1174 | 478 | 87 | 33 | 82 | 16 | 0 | 100.12
17:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 280 | 281 |  | 0 | 280 | 130 | 100 | 0 | 15 | 0 | 0 | 0 | 2 | 0 | 7 | 73 | 0 | 0 | 0 | 54 | 55 | 4 | 19 | 25 | 31 | 25 | 25 | 31 | 0 | 87 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 8 | 0 | 80 | 0 | 275 | 0 | 181 | 8 | 30 | 29 | 5 | 0 | 51 | 0 | 0 | 1 | 18 | 8 | 33 | 21 | 88 | 106 | 0 | 0 | 0 | 60 | 22 | 53 | 46 | 163 | 240 | 32 | 78 | 0 | 40 | 18 | 0 | 0 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 5 | 0 | 59 | 0 | 100 | 112 | 37 | 80 | 115 | 1 | 0 | 0 | 124 | 54 | 0 | 0 | 17 | 20 | 0 | 90 | 0 | 0 | 10 |  | 589 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 401 | 90 | 0 | 12 | 0 | 35 | 0 | 0 | 0 | 250 | 56 | 0 | 0 |  | 5142 | 2260 | 7402 | 2869 | 589 | 1845 | 1396 | 479 | 87 | 49 | 88 | 0 | 0 | 100.11
18:00 | 0 | 114 | 0 | 115 | 200 | 52 | 0 | 346 | 274 |  | 0 | 260 | 155 | 99 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 40 | 68 | 0 | 0 | 0 | 54 | 55 | 50 | 19 | 25 | 18 | 25 | 25 | 43 | 0 | 89 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 12 | 0 | 80 | 0 | 320 | 0 | 199 | 8 | 34 | 29 | 5 | 0 | 51 | 0 | 0 | 36 | 18 | 8 | 33 | 21 | 110 | 107 | 11 | 17 | 0 | 60 | 22 | 53 | 47 | 163 | 237 | 35 | 78 | 0 | 40 | 18 | 0 | 0 | 320 | 16 | 0 | 0 | 59 | 0 | 0 | 86 | 0 | 0 | 0 | 100 | 170 | 117 | 100 | 115 | 45 | 0 | 0 | 158 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 0 | 0 |  | 529 | 0 | 200 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 162 | 0 | 9 | 0 | 167 | 0 | 428 | 90 | 0 | 69 | 0 | 108 | 0 | 0 | 20 | 390 | 83 | 0 | 0 |  | 5862 | 2647 | 8509 | 3058 | 529 | 1891 | 2086 | 619 | 89 | 127 | 110 | 0 | 0 | 100.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 113 | 0 | 115 | 200 | 54 | 0 | 347 | 263 |  | 0 | 260 | 150 | 96 | 0 | 15 | 0 | 0 | 0 | 100 | 0 | 82 | 76 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 25 | 25 | 25 | 0 | 90 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 20 | 0 | 80 | 0 | 270 | 0 | 192 | 8 | 35 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 102 | 108 | 57 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 240 | 35 | 78 | 0 | 40 | 18 | 0 | 0 | 270 | 16 | 8 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 0 | 100 | 170 | 150 | 80 | 95 | 53 | 0 | 0 | 158 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 40 | 0 |  | 778 | 0 | 195 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 167 | 0 | 54 | 0 | 175 | 0 | 285 | 90 | 0 | 70 | 0 | 12 | 0 | 0 | 20 | 590 | 81 | 0 | 0 |  | 6003 | 2988 | 8991 | 3006 | 778 | 1686 | 2350 | 819 | 90 | 160 | 102 | 0 | 0 | 100.1
19:30 | 0 | 113 | 0 | 115 | 200 | 54 | 0 | 341 | 263 |  | 0 | 260 | 145 | 100 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 82 | 86 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 25 | 25 | 25 | 0 | 90 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 22 | 0 | 80 | 0 | 260 | 0 | 184 | 8 | 34 | 29 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 104 | 109 | 75 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 237 | 35 | 78 | 0 | 40 | 18 | 0 | 0 | 240 | 16 | 11 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 0 | 100 | 120 | 150 | 80 | 95 | 50 | 0 | 0 | 161 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 50 | 0 |  | 778 | 0 | 196 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 158 | 0 | 58 | 0 | 170 | 0 | 352 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 660 | 75 | 0 | 0 |  | 5834 | 3039 | 8873 | 2967 | 778 | 1724 | 2161 | 889 | 90 | 160 | 104 | 0 | 0 | 0
20:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 356 | 263 |  | 0 | 260 | 148 | 98 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 82 | 86 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 25 | 25 | 25 | 0 | 92 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 17 | 0 | 80 | 0 | 260 | 0 | 184 | 8 | 27 | 29 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 102 | 108 | 75 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 240 | 35 | 79 | 0 | 40 | 18 | 0 | 0 | 240 | 16 | 11 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 0 | 100 | 120 | 150 | 80 | 85 | 17 | 0 | 0 | 162 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 50 | 0 |  | 778 | 0 | 195 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 158 | 0 | 64 | 0 | 170 | 0 | 350 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 660 | 76 | 0 | 0 |  | 5796 | 3044 | 8840 | 2976 | 778 | 1723 | 2120 | 889 | 92 | 160 | 102 | 0 | 0 | 100.11
21:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 345 | 263 |  | 0 | 260 | 140 | 95 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 86 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 25 | 8 | 16 | 0 | 92 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 80 | 0 | 260 | 0 | 183 | 8 | 27 | 29 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 102 | 108 | 75 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 238 | 35 | 79 | 0 | 40 | 18 | 0 | 0 | 240 | 16 | 11 | 0 | 30 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 120 | 150 | 80 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 100 | 0 | 90 | 0 | 31 | 0 |  | 779 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 160 | 0 | 63 | 0 | 170 | 0 | 340 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 660 | 77 | 0 | 0 |  | 5435 | 2971 | 8406 | 2927 | 779 | 1720 | 1771 | 889 | 92 | 126 | 102 | 0 | 0 | 100.1
22:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 339 | 270 |  | 0 | 260 | 148 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 32 | 67 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 20 | 25 | 8 | 0 | 92 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 30 | 0 | 80 | 0 | 260 | 0 | 182 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 100 | 109 | 77 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 79 | 0 | 30 | 18 | 0 | 0 | 285 | 16 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 120 | 150 | 15 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 |  | 779 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 90 | 0 | 140 | 0 | 0 | 0 | 0 | 162 | 0 | 63 | 0 | 160 | 0 | 419 | 90 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 540 | 78 | 0 | 0 |  | 5051 | 2904 | 7955 | 2724 | 779 | 1858 | 1522 | 770 | 92 | 110 | 100 | 0 | 0 | 100.1
23:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 342 | 270 |  | 0 | 280 | 148 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 49 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 20 | 25 | 8 | 0 | 92 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 31 | 0 | 80 | 0 | 275 | 0 | 192 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 90 | 108 | 76 | 20 | 0 | 40 | 22 | 53 | 43 | 110 | 157 | 35 | 79 | 0 | 31 | 18 | 0 | 0 | 280 | 16 | 11 | 0 | 0 | 4 | 0 | 16 | 0 | 0 | 0 | 100 | 120 | 100 | 80 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 152 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 4994 | 1442 | 6436 | 2624 | 0 | 1674 | 1233 | 629 | 92 | 94 | 90 | 0 | 0 | 100.1
24:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 339 | 290 |  | 0 | 300 | 125 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 20 | 25 | 8 | 0 | 92 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 20 | 38 | 0 | 80 | 0 | 225 | 0 | 166 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 84 | 111 | 76 | 20 | 0 | 40 | 22 | 53 | 46 | 110 | 160 | 36 | 79 | 0 | 31 | 18 | 0 | 0 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 120 | 100 | 162 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 90 | 0 | 140 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 161 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 |  | 4964 | 1369 | 6333 | 2642 | 0 | 1640 | 1171 | 610 | 92 | 94 | 84 | 0 | 0 | 100.1
KWH | 0 | 2717500 | 0 | 2772000 | 4691755 | 1203318 | 0 | 8326140 | 6506000 |  | 0 | 6185000 | 3387607 | 1482240 | 0 | 156510 | 0 | 0 | 0 | 217920 | 0 | 327360 | 1168333 | 0 | 0 | 0 | 986400 | 623872 | 118465 | 278316 | 600000 | 694800 | 554600 | 505700 | 454872 | 0 | 2102182 | 0 | 0 | 0 | 0 | 4948504 | 0 | 0 | 0 |  | 0 | 0 | 25485 | 0 | 0 | 779520 | 453360 | 408000 | 0 | 1939420 | 0 | 7479700 | 0 | 4530000 | 200727 | 748070 | 378720 | 140160 | 0 | 1134428 | 0 | 0 | 123730 | 384732 | 128880 | 751200 | 523750 | 2087040 | 2454400 | 446400 | 306396 | 12800 | 1340000 | 532440 | 771000 | 885240 | 3274363 | 5129000 | 828288 | 1457280 | 0 | 942890 | 427000 | 0 | 0 | 7213500 | 239952 | 138048 | 0 | 499309 | 18336 | 0 | 520800 | 0 | 531360 | 123255 | 1140480 | 2098080 | 1237818 | 4160000 | 1731600 | 171384 | 0 | 25560 | 2097600 | 881832 | 0 | 0 | 272160 | 443520 | 0 | 1472640 | 268190 | 126720 | 57709 |  | 11854545 | 0 | 5213376 | 0 | 152640 | 0 | 0 | 0 | 0 | 0 | 37125 | 0 | 492100 | 0 | 0 | 0 | 0 | 0 | 0 | 716384 | 0 | 0 | 0 | 0 | 0 | 370800 | 0 | 222138 | 2047418 | 0 | 3435900 | 0 | 0 | 0 | 0 | 3897591 | 0 | 498640 | 0 | 4054509 | 0 | 8897236 | 1152480 | 0 | 470208 | 0 | 169920 | 0 | 32891 | 91872 | 8690000 | 1440218 | 0 | 61200 |  | 117503666 | 53999191 | 171502857 | 73293175 | 11854545 | 41078010 | 25382662 | 14173318 | 2102182 | 1069229 | 2087040 | 462696 | 0
Fuel Cost | 0 | 4021900 | 0 | 4074840 | 5207848.05 | 1588379.76 | 0 | 8409401.4 | 6701180 |  | 0 | 6741650 | 3760243.77 | 11250201.6 | 0 | 1324074.6 | 0 | 0 | 0 | 1640937.6 | 0 | 3221222.4 | 10772030.26 | 0 | 0 | 0 | 7200720 | 4822530.56 | 1168064.9 | 208737 | 450000 | 0 | 0 | 0 | 4398612.24 | 0 | 567589.14 | 0 | 0 | 0 | 0 | 5393869.36 | 0 | 0 | 0 |  | 0 | 0 | 247204.5 | 0 | 0 | 6173798.4 | 571233.6 | 1211760 | 0 | 2870341.6 | 0 | 5534978 | 0 | 4167600 | 258937.83 | 860280.5 | 427953.6 | 196224 | 0 | 1939871.88 | 0 | 0 | 1181621.5 | 488609.64 | 96660 | 1314600 | 392812.5 | 15652800 | 2601664 | 4053312 | 389122.92 | 204032 | 2197600 | 851904 | 1372380 | 1380974.4 | 3732773.82 | 5334160 | 1631727.36 | 2783404.8 | 0 | 1631199.7 | 935130 | 0 | 0 | 7285635 | 179964 | 104916.48 | 0 | 3774776.04 | 311345.28 | 0 | 2708160 | 0 | 5228582.4 | 1440850.95 | 9294912 | 22764168 | 8726616.9 | 3868800 | 15792192 | 1619578.8 | 0 | 0 | 15857856 | 7680756.72 | 0 | 0 | 2332411.2 | 2953843.2 | 0 | 0 | 0 | 0 | 0 |  | 68282179.2 | 0 | 5474044.8 | 0 | 1199750.4 | 0 | 0 | 0 | 0 | 0 | 386842.5 | 0 | 762755 | 0 | 0 | 0 | 0 | 0 | 0 | 6339998.4 | 0 | 0 | 0 | 0 | 0 | 711936 | 0 | 168158.466 | 12345930.54 | 0 | 18622578 | 0 | 0 | 0 | 0 | 5144820.12 | 0 | 747960 | 0 | 4743775.53 | 0 | 8808263.64 | 12031891.2 | 0 | 4462273.92 | 0 | 1318579.2 | 0 | 363445.55 | 678934.08 | 38149100 | 0 | 0 | 0 |  | 277536070.16 | 190743216.546 | 468279286.706 | 79748652.626 | 68282179.2 | 46224086.13 | 176869617.27 | 69117608.54 | 567589.14 | 9808425.3 | 15652800 | 2008328.5 | 0
Yesterday Day Peak | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 364 | 221 |  | 0 | 300 | 140 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 31 | 20 | 8 | 43 | 0 | 87 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 2 | 0 | 80 | 0 | 285 | 0 | 191 | 8 | 37 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 90 | 105 | 0 | 20 | 2 | 60 | 22 | 11 | 46 | 110 | 235 | 32 | 76 | 0 | 40 | 18 | 0 | 0 | 310 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 60 | 140 | 5 | 230 | 115 | 0 | 0 | 4 | 121 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 46 | 0 | 0 |  | 589 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 411 | 70 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 66 | 0 | 0 |  | 7396 | DayPeak
Yesterday Evening Peak | 0 | 113 | 0 | 115 | 200 | 54 | 0 | 347 | 263 | 0 | 0 | 260 | 150 | 96 | 0 | 15 | 0 | 0 | 0 | 100 | 0 | 82 | 76 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 25 | 25 | 25 | 0 | 90 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 20 | 0 | 80 | 0 | 270 | 0 | 192 | 8 | 35 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 102 | 108 | 57 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 240 | 35 | 78 | 0 | 40 | 18 | 0 | 0 | 270 | 16 | 8 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 0 | 100 | 170 | 150 | 80 | 95 | 53 | 0 | 0 | 158 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 40 | 0 |  | 778 | 0 | 195 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 167 | 0 | 54 | 0 | 175 | 0 | 285 | 90 | 0 | 70 | 0 | 12 | 0 | 0 | 20 | 590 | 81 | 0 | 0 |  | 8991 | EvPeak
Forecast for Evening | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 300 | 0 | 0 | 300 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 129 | 100 | 0 | 0 | 225 | 112 | 50 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 154 | 120 | 95 | 20 | 0 | 60 | 60 | 51 | 44 | 163 | 155 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 325 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 230 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 768 | 16 | 0 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 300 | 0 | 0 | 300 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 |  | 129 | 50 | 0 | 0 | 225 | 112 | 50 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 120 | 83 | 20 | 1.6 | 60 | 60 | 51 | 44 | 163 | 155 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 325 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 230 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 580 | 0 | 0 | 0 | 115 | 100 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 114 | 0 | 115 | 200 | 51 | 0 | 361 | 300 | 0 | 0 | 350 | 145 |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 31 | 25 |  | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 140 | 0 | 0 | 0 | 184 | 112 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 70 | 113 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 36 | 77 | 0 | 0 | 19 | 0 | 0 | 300 | 13 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 8 | 100 | 100 | 25 | 237 | 101 | 0 | 0 | 1 | 230 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 208 | 0 | 426 | 70 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5635 | 5:00
| Highest Generation |  | 8991 | 19:00
| Day Peak Generation |  | 7396 | 12:00
| Evening Peak Generation |  | 8991 | 19:00
| HVDC Max Flow |  | 779 | 21:00
| HVDC EvPeak Flow |  | 778 | 19:00
| Load factor L.F |  | 79.48%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7396 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5721 | MW
Evening Peak Generation : |  | 8991 | MW Hour : | 19:00 | Available Max Generation : |  | 13524 | MW
E.P. Demand (at gen end) : |  | 8991 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 8991 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4324 | MW
Total Gen. (MKWH) : |  | 171.5029 | System Load Factor : | 79.48% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -140 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-03
Actual : | 100.08 | Ft.(MSL) , | Rule curve : | 105.91 | Ft.( MSL )
Gas Consumed : | Total = | 906.64 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125972738.756
: |  | Coal : | 69117608.54 | Oil : | 186678042.57 | Total : | 381768389.866
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3222.6928 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1090.6358 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 976.2366 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 881.7795 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 797.0348 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 643.1656 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 366.3929 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.7769 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 496.0089 |  |  | 0 | 0%
Total | 0 |  | 8639.7237 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10)Ashuganj(S)-360 MW
2) Baghabari-71,100 MW
3) Ghorasal Unit-1,2,4
4) Ashuganj unit-3
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Chandpur-163 MW
9) Sirajganj #1 CCPP STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Comilla(N) 230/132 kV T-1 transformer was under shut down from 08:16 to 15:01 for A/M.
b) Ishurdi-Bheramara 132 kv Ckt-1 was under shut down from 08:23 to 17:21 for A/M.
c) Ishurdi 132 kV Bus-2 was under shut down from 08:24 to 17:18 for A/M.
d) Kaptai-Hathazari 132 kV Ckt-2 was under shut down from 08:54 to 17:11 for a/M.
e) Manikganj-Kabirpur 132 kV Ckt-2 was under shut down from 08:11 to 16:42 for A/M.
f) RPCL-Mymensingh 132 kV Ckt-2 was under shut down from 08:40 to 17:25 for A/M.
f) Jamalpur-UMPL 132 kV Ckt-1 was under shut down from 09:14 to 17:07 for A/M.
g) UMPL-Sherpur 132 kV Ckt-1 was under shut down from 09:06 to 16:36 for A/M.
h) Saidpur-B.Pukuria 132 kV Ckt-1 was under shut down from 08:42 to 16:45 for A/M.
i) Rajshahi 132/33 kV T-2 transformer was under shut down from 08:02 to 16:45 for A/M.
j) Khulna(C)-Khulna(s) 132 kV Ckt-1 was under shut down from 08:27 to 15:55 for A/M.
i) Naogaon-Bogura 132 kV Ckt-1 was under shut down from 09:18 to 16:40 for A/M.
k)Khulna(S) 132 kV Capacitor bank was under shut down from 09:10 to 14:25 for A/M.
l) Magura 132/33 kV T-1 transformer was under shut down from 08:30 to 15:52 for A/M.
m) Savar-Manikganj power 132 kV Ckt-2 was under shut down from 09:27 to 16:05 for A/M.
n) Srimangal-Shahjibazar 132 kV Ckt-2 was under shut down from 10:12 to 13:34 for protection test.
o)Kaliakoir-Kodda 300 MW 132 kV Ckt was under shut down from 10:11 to 16:37 for A/M.
p) Aminbazar-Hasnabad 230 kV Ckt-2 was under shut down from 11:49 to 17:18 for A/M.
q) Bhaluka 132 kV Bus-2 was under shut down from 08:37 to 14:17 for A/M.
r) Srimongal-Shahjibazar 132 kV Ckt-1 was under shut down from 13:35 to 16:58 for protection test.
s) Srimongal-Fenchuganj 132 kV Ckt-2 was under shut down from 09:07 to 13:22 for A/M.
t) Bheramara HVDC 400 kV filter 10CF26 was switched on at 13:10.
u) Kallyanpur GT-2 33 kV was under shut down from 10:46 to 11:25 for SF6 gas filling of HT CB.
v) Bheramara HVDC pole-2 tripped at 17:31 due to tripping of all 400 kV filter and was De-blocked at 18:25.
w) Kodda-Summit Kodda 149 MW 132 kV Ckt was under shut down from 17:07 to 20:28 for R/H maint. At
B-phase,CT connector at S/S end.
x) Shahjibazar 330 MWCCPP GT-1 was shut down at 21:30 for gas shortage.
y) Bibiyana unit-3 ST synchronized at 23:23.
z) All 132 kV and 230 kV Ckts of Ishurdi S/S tripped at 22:52 from far ends due to Ishurdi-Natore 132 kV Ckt-1 |  |  |  |  | And the following S/S were black out :
CB problem at Ishurdi end. |  |  |  |  | Khulna(C)=60 MW,Goalpara=13 Mw,Bagerhat=56 MW,Mongla=22 MW,
At the same time following plants with load tripped : |  |  |  |  | Benapole=22 MW, Jhenaidah=42 MW,Magura=24 MW,Norail=20 MW,
HVDC Bheramara=582 MW,Bheramara 360 MW=195 MW,Orion Rupsha=90 MW,Bhola Aggreko=63 MW |  |  |  |  | Bheramara GK=26 MW,Pabna=50 MW,Ruppur=2 MW,Satkhira=48 MW,
Total=930 MW. |  |  |  |  | Noapara=35 MW,Jessore=62 MW,Goalmara=20 MW,Chuadanga=45 MW,
Bottail=66 MW, Total=613 MW.
aa) Baghabari-Ishurdi 230 kV Ckt-2, Ckt-1,Ghorashal-Ishurdi 230 kV Ckt-1,Ishurdi-HVDC 230 kV Ckt-4, 3,
HVDC-Khulna(S) 230 kV Ckt-2,1,HVDC-Rajshahi 230 kV CKt-2, HVDC-Bheramara 230 kV Ckt-1,2, Ishurdi
230/132 kV auto transformer To1, To3,,T02 were switched on at 23:41,23:42,00:09(03/12/2020),23:54,
00:13(03/12/2020),00:15(03/12/2020),00:17(03/12/2020),02:56(03/12/2020),00:24(03/12/2020),00:32(03/12/2020),
23:50,00:03(03/12/2020),07:03 respectively.
ab) All the 132 kV Ckts from Ishurdi were closed but due to CT problem re-opened from Ishurdi end at 0
0:42(03/12/2020).
ac) Barapukuria unit-3 was shut down at 07:04(03/12/2020) due to maintenance work.
ad) Ishurdi-Bheramara 132 kV Ckt-1,2, Ishurdi-Pabna 132 kV Ckt,Ishurdi-Baghabari 132 kV,Ishurdi 132/33 kV T-2,
T-1 transformer were switched on at 07:16(03/12/2020),0:17,07:26,07:33,07:29,01:15 respectively.
ae) HVDC Bheramara pole-1 was De-block at 00:23(03/12/2020).
af) ashuganj-Bhulta 400 kV Ckt-2 was shut down at 07:17(03/12/2020) for A/MN.
ag) Hasnabad-B.Gaon 132 kV Ckt was shut down at 07:36(03/12/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 113 | 2717500 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4691755 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 54 | 1203318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8326140 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 263 | 6506000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 6185000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 96 | 1482240 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3387607 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 156510 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 76 | 1168333 | Machin problem.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 278316
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 217920
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 986400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 327360 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 623872
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 118465 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1294800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 554600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 505700 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 454872 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 150 | 499309 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 18336 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 531360 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 53 | 171384 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1472640 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 40 | 126720 | On test
| Dhaka area Total |  |  |  | 5895 | 2498 | 46778457
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123255
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 779520
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 90 | 2102182 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4948504
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 25485 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1140480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 453360
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 408000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25560
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 158 | 2097600 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 881832
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 443520
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 57709
| Chattogram area Total |  |  |  | 2266 | 797 | 13487007
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1939420 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 192 | 4530000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7479700 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 378720 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 140160 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1134428
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1237818
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 748070 | ST Under maint & DP High
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 170 | 2098080 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 384732
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 128880
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2087040
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 751200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 123730
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 523750
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 272160 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1241 | 24158615
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 2454400 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 306396
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 57 | 446400 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 110 | 520800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 1731600 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 268190
| Mymensingh Area Total |  |  |  | 637 | 390 | 5740586
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1340000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 532440 | #04 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3274363 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 240 | 5129000 | Gas shortage
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 771000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 885240
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 138048 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 828288
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1457280
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 40 | 942890 | Gas shortage
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 427000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 239952 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7213500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 80 | 4160000 | Under ST synchronized process
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1077 | 27339001
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 778 | 11854545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 152640 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 195 | 5213376 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 37125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1152480 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1169 | 18410166
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 492100 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 54 | 498640 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 590 | 8690000 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 81 | 1440218
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 61200 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 750 | 11182158
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 167 | 3897591 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4054509 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 285 | 8897236 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 370800
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 222138
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 78 | 716384 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 470208 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 20 | 91872 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 828 | 18720738
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 89 | 2047418
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3435900 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 12 | 169920 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32891
| Rangpur Area Total |  |  |  | 605 | 241 | 5686129
| Total |  |  |  | 19892 | 8991 | 171502857
| Eastern Grid Total |  |  |  | 13766 | 6003 | 117503666
| Western Grid Total |  |  |  | 6126 | 2988 | 53999191
| National Grid Total |  |  |  | 19892 | 8991 | 171502857
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-02
| (a) ENTIRE EASTERN GRID : |  | 5740 | MW | (b) ENTIRE WESTERN GRID : |  | 2689 | MW
| i) Dhaka area |  | 3142 | MW | i) Khulna area |  | 1041 | MW
| ii) Chittagong area |  | 879 | MW | ii) Rajshahi area |  | 851 | MW
| iii) Comilla area |  | 739 | MW | iii) Barisal area |  | 235 | MW
| iv) Mymensingh area |  | 661 | MW | iv) Rangpur area |  | 562 | MW
| v) Sylhet area |  | 319 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8429 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 108 | 16:00 | Jamalpur | 100 | 18:00 | Benapol | 34 | 18:00
| Munsiganj | 82 | 20:00 | Sherpur | 82 | 18:00 | Jhenida | 76 | 18:30
| Sonargaon | 57 | 9:00 | Srimongal | 34 | 8:00 | Bottail | 90 | 13:00
| Shyampur | 142 | 4:00 | Shahjibazar | 89 | 18:00 | G.K Project | 34 | 18:00
| Bhulta | 156 | 18:30 | Fenchuganj | 25 | 18:00 | Faridpur | 132 | 18:30
| Madanganj | 58 | 21:00 | Kulawara | 30 | 18:00 | Madaripur | 63 | 19:00
| Shitalakhya | 87 | 12:00 | Sylhet | 80 | 18:00 | Sariatpur | 40 | 19:30
| Rahim steel | 14 | 10:00 | Chatak | 20 | 18:00 | Gopalganj | 59 | 20:00
| Matuail | 60 | 15:00 | Sunamganj | 29 | 20:00 | Bagerhat | 78 | 18:30
| Ghorasal | 68 | 19:30 | Biani Bazar | 38 | 18:00 | Mongla | 37 | 12:00
| Narsingdi | 124 | 20:00 | Comilla (S) | 110 | 18:00 | Satkhira | 74 | 18:30
| Haripur (SBU) | 96 | 17:00 | Comilla(N) | 63 | 18:30 | Gallamari | 22 | 20:00
| Ullon | 46 | 18:30 | Chandpur | 63 | 20:00 | Magura | 38 | 18:00
| Hasnabad | 146 | 18:00 | Feni | 80 | 18:00 | Norail | 28 | 18:30
| Magbazar | 75 | 15:00 | Chowmuhani | 118 | 18:30 | Chuadanga | 60 | 18:30
| Maniknagar | 70 | 17:00 | Ashuganj | 41 | 18:30 | Barisal(N) | 28 | 18:30
| Bangabhaban | 24 | 11:00 | Daudkandi | 90 | 20:00 | Barisal (S) | 72 | 18:00
| Narinda | 72 | 12:00 | B.Baria | 98 | 19:30 | Patuakhali | 82 | 21:00
| Dhanmondi | 112 | 13:00 | Ramganj | 64 | 18:30 | Bhandaria | 40 | 19:00
| Lalbag | 73 | 18:00 | Chaddagram | 23 | 18:30 | Borhan Uddin | 25 | 19:30
| Madartek | 48 | 18:00 | PHP | 5 | 7:00 | Ishurdi | 44 | 18:00
| Dhaka University |  |  | Madunaghat | 43 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.41667 | Hathazari | 72 | 0.75 | Natore | 79 | 0.75
| Fatullah | 32 | 17:00 | Khulshi | 173 | 12:00 | Bogra | 122 | 18:30
| Mirpur | 78 | 18:00 | Halishahar | 103 | 14:00 | Noagaon | 82 | 18:30
| Kalyanpur | 63 | 18:00 | Baraulia | 133 | 1:00 | Rajshahi | 96 | 20:00
| Gulshan | 86 | 13:00 | Sikalbaha | 21 | 18:30 | Rajshahi New | 8 | 18:00
| Uttara | 67 | 18:00 | Dohazari | 58 | 19:30 | C.Nawabganj | 52 | 18:00
| Uttara New | 22 | 12:00 | Cox'sbazar | 76 | 18:00 | Amnura | 30 | 18:00
| Kamrangirchar | 76 | 18:00 | Chandraghona | 20 | 18:30 | Pabna | 78 | 19:00
| Savar | 104 | 12:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 73 | 18:30
| Bhasantec | 110 | 18:00 | A. Khaer Stl. | 9 | 16:00 | Serajganj | 66 | 18:30
| Agargaon | 51 | 13:00 | Bakulia | 80 | 13:00 | Niyamatpur | 39 | 18:00
| Satmosjid | 69 | 0.54167 | Julda | 20 | 0.58333 | Joypurhat | 42 | 0.75
| Tongi | 85 | 11:00 | TK chemical | 20.5 | 18:00 | Sherpur(Bogura) | 40 | 18:00
| Kabirpur | 179 | 18:00 | Modern Steel | 17 | 8:00 | Mohastangor | 32 | 18:00
| Basundhara | 91 | 18:00 | Shahmirpur | 15.7 | 11:00 | Rangpur | 106 | 18:30
| Manikganj | 54 | 18:00 | Khagrachhari | 18 | 19:00 | Lalmonirhat | 42 | 18:30
| Joydevpur | 123 | 18:00 | Matarbari | 26.5 | 19:00 | Saidpur | 90 | 18:00
| New Tongi | 94 | 11:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 82 | 18:00
| Kodda | 164 | 19:00 | Rangamati | 9 | 18:00 | Thakurgaon | 63 | 18:00
| Dhamrai | 70 | 19:00 | Abul Khair 230 | 2 | 8:00 | Palashbari | 80 | 18:00
| Rajendrapur | 76 | 19:00 | BSRM | 144 | 9:00 | Barapukuria | 38 | 19:00
| Valuka | 70 | 18:30 | GPH Ispat | 85 | 7:00 | Panchagar | 44 | 18:00
| Tangail | 116 | 19:30 | Goalpara | 17 | 13:00 | Joldhaka | 19 | 18:30
| Mymensing | 149 | 18:00 | Central s/s | 78 | 18:00 | Kurigram | 36 | 18:30
| Kishorganj | 80 | 18:30 | Noapara | 42 | 18:00
| Netrokona | 80 | 19:30 | Jessore | 77 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 23:00 | 404 | 11:00 | Kaliakoir | 387 | 0.16667 | 376 | 0.5
| Bheramara | 413 | 3:00 | 0 | 23:00 | Bhulta | 388 | 0.77083 | 376 | 0.20833
| Ashuganj(N) | 395 | 24:00 | 387 | 11:00 | Gopalganj | 421 | 0.16667 | 390 | 0.8125
| Payra | 421 | 24:00 | 404 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 232 | 12:00 | Comilla (N) | 240 | 13:00 | 233 | 11:00
| Ishurdi | 240 | 5:00 | 230 | 8:00 | Hathazari | 222 | 17:00 | 210 | 10:00
| Ashuganj | 240 | 18:00 | 235 | 9:00 | Megnaghat | 238 | 24:00 | 230 | 1:00
| Serajganj | 233 | 5:00 | 230 | 8:00 | Fenchuganj | 246 | 23:00 | 241 | 7:00
| Baghabari | 243 | 24:00 | 236 | 19:30 | Siddhirganj | 234 | 23:00 | 228 | 11:00
| Barapukuria | 231 | 1:00 | 225 | 8:00 | Maniknagar | 232 | 24:00 | 226 | 11:00
| Bogra | 233 | 3:00 | 225 | 13:00 | Agargaon | 233 | 6:00 | 226 | 11:00
| Rajshahi | 231 | 4:00 | 208 | 24:00 | Barisal | 251 | 21:00 | 232 | 23:00
| Khulna South | 234 | 3:00 | 216 | 8:00 | AKSML | 224 | 24:00 | 209 | 4:00
| Rampura | 231 | 1:00 | 228 | 10:00 | BSRM | 228 | 23:00 | 215 | 3:00
| Haripur | 232 | 23:00 | 226 | 12:00 | Bibiyana | 243 | 23:00 | 240 | 3:00
| Hasnabad | 235 | 23:00 | 228 | 12:00 | Bhulta | 234 | 19:00 | 228 | 17:00
| Shyampur | 232 | 24:00 | 220 | 12:00 | Ashuganj (S) | 238 | 18:30 | 232 | 5:00
| Aminbazar | 234 | 24:00 | 227 | 12:00 | Kaliakoir | 234 | 18:30 | 227 | 12:00
| Tongi | 232 | 18:00 | 223 | 11:00 | GPH | 224 | 18:30 | 210 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 0:00 | 135 | 11:00 | Madanhat | 136 | 0 | 128 | 0.45833
| Munsiganj | 139 | 23:00 | 135 | 3:00 | Hathazari | 136 | 0.79167 | 128 | 0.45833
| Sonargaon | 140 | 0:00 | 133 | 7:00 | Khulshi | 132 | 0.77083 | 126 | 0.29167
| Shyampur | 136 | 0:00 | 132 | 8:00 | Halishahar | 134 | 0.79167 | 125 | 0.125
| Bhulta | 132 | 22:00 | 129 | 11:00 | Baraulia | 133 | 0 | 125 | 0.16667
| Madanganj | 137 | 0:00 | 129 | 6:00 | Sikalbaha | 134 | 0.79167 | 125 | 0.25
| Shitalakhya | 140 | 18:00 | 135 | 11:00 | Dohazari | 130 | 0.79167 | 124 | 0.25
| Rahim steal | 139 | 18:00 | 136 | 10:00 | Cox'sbazar | 127 | 0 | 118 | 0.125
| Matuail | 140 | 0:00 | 135 | 11:00 | Chandraghona | 135 | 0.83333 | 129 | 0.16667
| Ghorasal | 140 | 1:00 | 136 | 12:00 | Kaptai | 135 | 0.041667 | 132 | 0.16667
| Narsinghdi | 137 | 0:00 | 134 | 7:00 | A. Khaer Stl. | 132 | 0.875 | 125 | 0.45833
| Haripur (SBU) | 137 | 10:00 | 131 | 5:00 | Bakulia | 133 | 0.79167 | 125 | 0.45833
| Ullon | 133 | 24:00 | 127 | 10:00 | Julda | 134 | 0.79167 | 124 | 0.125
| Hasnabad | 139 | 5:00 | 135 | 15:00 | TK Chemical | 133 | 0.041667 | 126 | 0.66667
| Magbazar | 133 | 24:00 | 126 | 12:00 | Modern Steel | 133 | 0.77083 | 126 | 0.45833
| Maniknagar | 139 | 24:00 | 135 | 10:00 | Shahmirpur | 134 | 0.8125 | 125 | 0.25
| Bangabhaban | 139 | 24:00 | 135 | 10:00 | Khagrachhari | 134 | 0.79167 | 126 | 0.45833
| Narinda | 139 | 24:00 | 135 | 10:00 | Matarbari | 127 | 0.95833 | 121 | 0.16667
| Dhanmondi | 133 | 24:00 | 127 | 10:00 | Baroiar Hat | 136 | 0 | 130 | 0.25
| Lalbag | 128 | 24:00 | 120 | 11:00 | Rangamati | 134 | 0:00 | 127 | 3:00
| Madartek | 133 | 24:00 | 127 | 11:00 | Goalpara S/S | 139 | 4:00 | 128 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 4:00 | 131 | 0.45833
| Aftabnagar | 133 | 2:00 | 127 | 10:00 | Noapara | 136 | 5:00 | 128 | 0.29167
| Fatuiiah | 137 | 24:00 | 132 | 12:00 | Jessore | 134 | 7:00 | 125 | 0.75
| Mirpur | 129 | 21:00 | 122 | 11:00 | Benapol | 135 | 0.16667 | 125 | 0.33333
| Kalyanpur | 130 | 21:00 | 124 | 9:00 | Jhenida | 134 | 5:00 | 124 | 0.79167
| Gulshan | 132 | 23:00 | 126 | 11:00 | Bottail | 137 | 0.20833 | 130 | 0.33333
| Uttara | 128 | 3:00 | 121 | 11:00 | G.K Project | 141 | 0.25 | 137 | 0.8125
| Uttara New | 129 | 23:00 | 121 | 10:00 | Faridpur | 139 | 0.125 | 128 | 0.8125
| Kamrangirchar | 138 | 18:30 | 132 | 12:00 | Madaripur | 142 | 0.16667 | 130 | 0.875
| Savar | 132 | 21:00 | 121 | 11:00 | Shariyatpur S/S | 141 | 4:00 | 132 | 0.8125
| Bhasantec | 135 | 1:00 | 130 | 12:00 | Gopalganj | 144 | 0.25 | 130 | 0.8125
| Agargaon | 136 | 3:00 | 131 | 12:00 | Bagerhat | 139 | 22:00 | 124 | 0.33333
| Satmosjid | 135 | 2:00 | 131 | 11:00 | Mongla | 136 | 22:00 | 125 | 0.33333
| Tongi | 139 | 23:00 | 135 | 8:00 | Satkhira | 137 | 5:00 | 128 | 8:00
| Kabirpur | 134 | 24:00 | 127 | 16:00 | Gallamari | 138 | 0.16667 | 129 | 0.33333
| Basundhara | 133 | 23:00 | 126 | 13:00 | Magura | 135 | 2:00 | 125 | 0.33333
| Manikganj | 143 | 18:30 | 130 | 16:00 | Norail | 133 | 0.125 | 125 | 0.8125
| Joydevpur | 142 | 18:30 | 134 | 15:00 | Chuadanga | 132 | 5:00 | 121 | 0.8125
| New Tongi | 139 | 18:30 | 133 | 9:00 | Barisal(N) | 142 | 10:00 | 132 | 23:00
| Kodda | 139 | 18:00 | 127 | 8:00 | Barisal (S) | 140 | 0.29167 | 132 | 0.83333
| Dhamrai | 133 | 24:00 | 126 | 12:00 | Patuakhali(S) | 141 | 0.25 | 130 | 0.83333
| Rajendrapur | 138 | 18:30 | 130 | 13:00 | Bhandaria | 140 | 0.16667 | 128 | 0.95833
| Valuka | 130 | 22:00 | 121 | 7:00 | Ishurdi | 140 | 3:00 | 133 | 19:30
| Tangail | 130 | 1:00 | 125 | 16:00 | Ruppur Paromanobik | 138 | 2:00 | 134 | 11:00
| Mymensing | 131 | 23:00 | 122 | 7:00 | Natore | 137 | 1:00 | 132 | 12:00
| Kishorganj | 131 | 4:00 | 128 | 12:00 | Bogra | 137 | 3:00 | 130 | 12:00
| Netrokona | 130 | 22:00 | 122 | 7:00 | Noagaon | 133 | 4:00 | 121 | 13:00
| Jamalpur | 139 | 20:00 | 119 | 7:00 | Rajshahi | 139 | 1:00 | 132 | 12:00
| Sherpur | 138 | 20:00 | 119 | 1:00 | Rajshahi New | 141 | 4:00 | 132 | 12:00
| Srimongal | 140 | 24:00 | 135 | 15:00 | C.Nawabganj | 138 | 3:00 | 130 | 12:00
| Shahjibazar | 137 | 24:00 | 133 | 1:00 | Amnura | 138 | 2:0 | 131 | 12:00
| Fenchuganj | 137 | 1:00 | 136 | 2:00 | Pabna | 138 | 2:0 | 133 | 8:00
| Khulawara | 137 | 24:00 | 135 | 12:00 | Shahjadpur | 140 | 1:00 | 136 | 8:00
| Sylhet | 135 | 1:00 | 134 | 13:00 | Serajganj | 135 | 1:00 | 131 | 13:00
| Chatak | 135 | 1:00 | 132 | 18:30 | Niyamatpur | 133 | 4:00 | 119 | 12:00
| Sunamganj | 134 | 1:00 | 132 | 12:00 | Joypurhat | 135 | 3:00 | 120 | 12:00
| Biani Bazar | 135 | 1:00 | 132 | 15:00 | Sherpur(Bogura) | 137 | 3:00 | 130 | 12:00
| Comilla(s) | 131 | 1:00 | 127 | 10:00 | Mohastangor | 135 | 3:00 | 128 | 8:00
| Comilla(n) | 143 | 23:00 | 137 | 12:00 | Rangpur | 129 | 4:00 | 120 | 12:00
| Chandpur | 145 | 23:00 | 138 | 11:00 | Lalmonirhat | 130 | 2:00 | 120 | 19:00
| Feni | 138 | 18:00 | 134 | 7:00 | Saidpur | 127 | 4:00 | 118 | 9:00
| Chowmuhani | 135 | 18:00 | 131 | 7:00 | Purbasadipur | 126 | 1:00 | 116 | 8:00
| Ashuganj | 136 | 20:00 | 134 | 13:00 | Thakurgaon | 128 | 3:00 | 116 | 9:00
| Daudkandi | 140 | 23:00 | 136 | 11:00 | Palashbari | 131 | 3:00 | 124 | 11:00
| B.Baria | 133 | 23:00 | 131 | 12:00 | Barapukuria | 131 | 1:00 | 125 | 8:00
| Ramganj | 138 | 19:00 | 131 | 22:00 | Panchagar | 127 | 4:00 | 113 | 9:00
| Chaddagram | 139 | 20:00 | 135 | 12:00 | Joldhaka | 128 | 2:00 | 117 | 9:00
| PHP | 137 | 19:00 | 131 | 8:00 | Kurigram | 127 | 0.125 | 119 | 0.375

## L-Curve
Date | 2020-12-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 60 | 4964 | 1369 | 6333 |  |  |  | QF-LDC-11
0:30 | 82 | 4578 | 1763 | 6341 | Date: | 2020-12-02
1:00 | 104 | 4192 | 2157 | 6349
1:30 | 83 | 4127.5 | 2109.5 | 6237
2:00 | 62 | 4063 | 2062 | 6125
2:30 | 51 | 4082 | 1939.5 | 6021.5 | [5 empty] | Gen. at Eve. Peak | 8991 | 9500 MW (19:30 )
3:00 | 40 | 4101 | 1817 | 5918 | [6 empty] | 19:00
3:30 | 41 | 4028.5 | 1770.5 | 5799 | [5 empty] | Gen. at Day Peak | 7396 | 7952.5 MW (12:00 )
4:00 | 42 | 3956 | 1724 | 5680 | [6 empty] | 12:00
4:30 | 41 | 3924 | 1733.5 | 5657.5 | [5 empty] | Highest Generation | 8991
5:00 | 40 | 3892 | 1743 | 5635 | [6 empty] | 19:00
5:30 | 46.5 | 3951 | 1803.5 | 5754.5
6:00 | 53 | 4010 | 1864 | 5874
6:30 | 43 | 4105.5 | 1894.5 | 6000
7:00 | 33 | 4201 | 1925 | 6126
7:30 | 86.5 | 4375 | 1952 | 6327
8:00 | 140 | 4549 | 1979 | 6528
8:30 | 95 | 4668.5 | 2020.5 | 6689
9:00 | 50 | 4788 | 2062 | 6850
9:30 | 68 | 4865.5 | 1998.5 | 6864
10:00 | 86 | 4943 | 1935 | 6878
10:30 | 153 | 4926 | 2037 | 6963
11:00 | 220 | 4909 | 2139 | 7048
11:30 | 178.5 | 5043 | 2179 | 7222
12:00 | 137 | 5177 | 2219 | 7396
12:30 | 111 | 5235 | 2238.5 | 7473.5
13:00 | 85 | 5293 | 2258 | 7551
13:30 | 149 | 5166 | 2205.5 | 7371.5
14:00 | 213 | 5039 | 2153 | 7192
14:30 | 267.5 | 4998 | 2154.5 | 7152.5
15:00 | 322 | 4957 | 2156 | 7113
15:30 | 307.5 | 4953 | 2124.5 | 7077.5
16:00 | 293 | 4949 | 2093 | 7042
16:30 | 282 | 5045.5 | 2176.5 | 7222
17:00 | 271 | 5142 | 2260 | 7402
17:30 | 144.5 | 5502 | 2453.5 | 7955.5
18:00 | 18 | 5862 | 2647 | 8509
18:30 | 41 | 5932.5 | 2817.5 | 8750
19:00 | 64 | 6003 | 2988 | 8991
19:30 | 162 | 5834 | 3039 | 8873
20:00 | 188 | 5796 | 3044 | 8840 |  |  |  | Executive Engineer
20:30 | 209 | 5615.5 | 3007.5 | 8623 |  |  |  | Network Operation Division
21:00 | 230 | 5435 | 2971 | 8406
21:30 | 323 | 5243 | 2937.5 | 8180.5
22:00 | 416 | 5051 | 2904 | 7955 |  |  |  |  | Page 6 of 7
22:30 | 303 | 5022.5 | 2173 | 7195.5
23:00 | 190 | 4994 | 1442 | 6436
23:30 | 125 | 4979 | 1405.5 | 6384.5
24:00 | 60 | 4964 | 1369 | 6333
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-02 |  | Energy | 171502857
[10 empty] | 2020-12-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2642 | 0 | 1640 | 1233 | 610 | 92 | 94 | 0 | 84
0:30 | 2870 | 194.5 | 1729 | 729 | 632.5 | 91 | 47 | 0 | 79 | Date: | 2020-12-02
1:00 | 3098 | 389 | 1818 | 225 | 655 | 90 | 0 | 0 | 74
1:30 | 3086.5 | 393.5 | 1745.5 | 192 | 655.5 | 90 | 0 | 0 | 74 | [7 empty] | Total Energy | 171.5029 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3075 | 398 | 1673 | 159 | 656 | 90 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3069.5 | 398 | 1621.5 | 160 | 609.5 | 90 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 171.5029
3:00 | 3064 | 398 | 1570 | 161 | 563 | 90 | 0 | 0 | 72
3:30 | 3037 | 374.5 | 1551 | 161 | 517.5 | 87 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3010 | 351 | 1532 | 161 | 472 | 84 | 0 | 0 | 70
4:30 | 2993.5 | 350.5 | 1534.5 | 153.5 | 472.5 | 84 | 0 | 0 | 69
5:00 | 2977 | 350 | 1537 | 146 | 473 | 84 | 0 | 0 | 68
5:30 | 2998.5 | 350.5 | 1606.5 | 173 | 473 | 84 | 0 | 0 | 69
6:00 | 3020 | 351 | 1676 | 200 | 473 | 84 | 0 | 0 | 70
6:30 | 3104.5 | 350.5 | 1739.5 | 177.5 | 473.5 | 84 | 0 | 0 | 69 |  |  |  |  | Coal
7:00 | 3189 | 350 | 1803 | 155 | 474 | 84 | 0 | 0 | 68
7:30 | 3207.5 | 351.5 | 1867.5 | 238 | 484.5 | 85.5 | 0 | 0 | 72 |  |  |  | Oil |  |  |  | ,
8:00 | 3226 | 353 | 1932 | 321 | 495 | 87 | 0 | 0 | 76
8:30 | 3186 | 352.5 | 1906 | 527.5 | 510.5 | 88 | 0 | 0 | 76
9:00 | 3146 | 352 | 1880 | 734 | 526 | 89 | 0 | 0 | 76
9:30 | 3129.5 | 352 | 1761 | 872.5 | 526.5 | 89 | 0 | 0 | 78
10:00 | 3113 | 352 | 1642 | 1011 | 527 | 89 | 0 | 0 | 80
10:30 | 3101.5 | 470.5 | 1629 | 1005.5 | 517 | 88 | 0 | 0 | 83
11:00 | 3090 | 589 | 1616 | 1000 | 507 | 87 | 0 | 0 | 86
11:30 | 3103 | 589 | 1663.5 | 1101 | 507.5 | 87 | 8.5 | 0 | 88
12:00 | 3116 | 589 | 1711 | 1202 | 508 | 87 | 17 | 0 | 90
12:30 | 3079 | 589 | 1748 | 1273 | 508 | 87 | 27.5 | 0 | 89
13:00 | 3042 | 589 | 1785 | 1344 | 508 | 87 | 38 | 0 | 88
13:30 | 3042 | 589 | 1785 | 1344 | 508 | 87 | 38 | 0 | 88
14:00 | 3042 | 589 | 1785 | 1344 | 508 | 87 | 38 | 0 | 88
14:30 | 2932 | 589 | 1732.5 | 1316 | 493 | 88 | 40 | 0 | 88
15:00 | 2822 | 589 | 1680 | 1288 | 478 | 89 | 42 | 0 | 88
15:30 | 2853.5 | 589 | 1689 | 1231 | 478 | 88 | 37.5 | 0 | 85
16:00 | 2885 | 589 | 1698 | 1174 | 478 | 87 | 33 | 0 | 82
16:30 | 2877 | 589 | 1771.5 | 1285 | 478.5 | 87 | 41 | 0 | 85
17:00 | 2869 | 589 | 1845 | 1396 | 479 | 87 | 49 | 0 | 88
17:30 | 2963.5 | 559 | 1868 | 1741 | 549 | 88 | 88 | 0 | 99
18:00 | 3058 | 529 | 1891 | 2086 | 619 | 89 | 127 | 0 | 110
18:30 | 3032 | 653.5 | 1788.5 | 2218 | 719 | 89.5 | 143.5 | 0 | 106
19:00 | 3006 | 778 | 1686 | 2350 | 819 | 90 | 160 | 0 | 102
19:30 | 2967 | 778 | 1724 | 2161 | 889 | 90 | 160 | 0 | 104
20:00 | 2976 | 778 | 1723 | 2120 | 889 | 92 | 160 | 0 | 102
20:30 | 2951.5 | 778.5 | 1721.5 | 1945.5 | 889 | 92 | 143 | 0 | 102
21:00 | 2927 | 779 | 1720 | 1771 | 889 | 92 | 126 | 0 | 102
21:30 | 2825.5 | 779 | 1789 | 1646.5 | 829.5 | 92 | 118 | 0 | 101
22:00 | 2724 | 779 | 1858 | 1522 | 770 | 92 | 110 | 0 | 100
22:30 | 2674 | 389.5 | 1766 | 1377.5 | 699.5 | 92 | 102 | 0 | 95
23:00 | 2624 | 0 | 1674 | 1233 | 629 | 92 | 94 | 0 | 90
23:30 | 2633 | 0 | 1657 | 1233 | 619.5 | 92 | 94 | 0 | 87 | Max Temp. in Dhaka |  | 29.8° C
24:00 | 2642 | 0 | 1640 | 1233 | 610 | 92 | 94 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-12-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 90 | 84 | 84 | 84 | 84 | 87 | 89 | 89 | 87 | 87 | 87 | 87 | 89 | 87 | 87 | 89 |  | 90 | 90 | 92 | 92 | 92 | 92 | 92 | 2102182
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 | 13 | 17 | 17 | 19 | 18 | 14 | 12 | 6 | 0 | [9 empty] | 123255
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 203 | 203 | 209 | 220 | 216 | 204 | 203 | 204 | 212 | 204 | 204 | 205 | 217 | 203 | 217 |  | 205 | 203 | 203 | 203 | 203 | 205 | 202 | 4948504
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [11 empty] | 17 | 17 | [12 empty] | 0 | 25485
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 0 | 59 |  | 150 | 150 | 150 | 30 | 15 |  |  | 499309
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 93 | 93 | 93 | 93 | 92 | 93 | 93 | 93 | 110 | 112 | 114 | 113 | 113 | 113 | 113 | 113 | 113 | 114 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2717500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4691755
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1939420
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 29 | 26 | 26 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 378720
33 | Ashuganj 225 MW CCPP | 156 | 156 | 156 | 162 | 185 | 210 | 218 | 216 | 190 | 180 | 181 | 191 | 181 | 180 | 186 | 200 | 181 | 199 |  | 192 | 184 | 184 | 183 | 182 | 192 | 166 | 4530000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 345 | 345 | 345 | 345 | 290 | 290 | 300 | 300 | 300 | 300 | 275 | 285 | 275 | 280 | 275 | 305 | 275 | 320 |  | 270 | 260 | 260 | 260 | 260 | 275 | 225 | 7479700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 140160
36 | Chandpur 150 MW CCPP | 35 | 35 | 35 | 38 | 38 | 38 | 45 | 40 | 36 | 38 | 36 | 37 | 36 | 34 | 35 | 33 | 30 | 34 |  | 35 | 34 | 27 | 27 |  |  |  | 748070
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 338 | 338 | 345 | 353 | 357 | 366 | 392 | 379 | 346 | 341 | 364 | 352 | 334 | 281 | 281 | 280 | 346 |  | 347 | 341 | 356 | 345 | 339 | 342 | 339 | 8326140
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 300 | 330 | 350 | 350 | 350 | 350 | 330 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 260 |  | 260 | 260 | 260 | 260 | 260 | 280 | 300 | 6185000
41 | Haripur 360MW CCPP(HPL) | 242 | 259 | 303 | 312 | 312 | 338 | 328 | 293 | 287 | 221 | 221 | 221 | 264 | 264 | 264 | 264 | 281 | 274 |  | 263 | 263 | 263 | 263 | 270 | 270 | 290 | 6506000
42 | RPCL 210MW CCPP | 110 | 113 | 113 | 112 | 111 | 111 | 111 | 111 | 107 | 110 | 107 | 105 | 83 | 86 | 85 | 85 | 106 | 107 |  | 108 | 109 | 108 | 108 | 109 | 108 | 111 | 2454400
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 27 | 27 | 37 | 45 | 46 | 41 | 31 | 19 | 7 | 0 | [9 empty] | 268190
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 40 | 40 | 40 | 1340000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 532440
46 | Shajibazar 330 MW CCPP | 231 | 237 | 234 | 233 | 237 | 234 | 237 | 233 | 234 | 236 | 236 | 235 | 230 | 233 | 234 | 233 | 240 | 237 |  | 240 | 237 | 240 | 238 | 158 | 157 | 160 | 5129000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 35 |  | 35 | 35 | 35 | 35 | 36 | 35 | 36 | 828288
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 80 | 77 | 74 | 80 | 76 | 76 | 76 | 76 | 78 | 78 | 78 |  | 78 | 78 | 79 | 79 | 79 | 79 | 79 | 1457280
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 30 | 31 | 31 | 942890
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 427000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 5 | [8 empty] | 0 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 138048
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 5 | 5 | 5 | 5 | 5 | 19 | 50 | 28 | 5 | 5 | 11 | 17 | 50 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 771000
56 | Shahjahanulla 25 MW PP | [7 empty] | 16 | 14 | 14 | 14 | 14 | 14 | 16 | 8 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 239952
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 285 | 300 | 300 | 305 | 310 | 320 | 320 | 290 | 290 | 310 | 300 | 290 | 295 | 310 | 320 | 320 |  | 270 | 240 | 240 | 240 | 285 | 280 | 260 | 7213500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 4 | 50 |  | 35 | 17 | 17 | 17 |  |  |  | 118465
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 |  |  | 20 | 20 | 453360
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 278316
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 306396
63 | Impoprt (Tripura) | 74 | 74 | 72 | 70 | 68 | 70 | 68 | 76 | 76 | 80 | 86 | 90 | 88 | 90 | 88 | 82 | 88 | 110 |  | 102 | 104 | 102 | 102 | 100 | 90 | 84 | 2087040
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 4 | 4 | 5 | 40 | 32 | 8 | 4 | 2 | 2 | 2 | 6 | 6 | 2 | 2 | 8 | 12 |  | 20 | 22 | 17 | 24 | 30 | 31 | 38 | 408000
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 384732
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 128880
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 8 | 8 | 23 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 751200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 12 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 523750
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 23 | 23 | 31 | 31 | 31 | 31 | 31 | 31 | 18 |  | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 694800
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 |  | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 554600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 |  | 25 | 25 | 25 | 8 | 25 | 25 | 25 | 505700
73 | Ghorashal 108MW PP (Regent) | 71 | 71 | 71 | 15 | 15 | 15 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 |  | 54 | 54 | 51 | 51 | 51 | 51 | 52 | 1203318
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [14 empty] | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 272160
| Manikgonj 162MW PP | [19 empty] | 40 | 50 | 50 | 31 |  |  |  | 126720
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 35 |  | 100 | 50 | 50 |  |  |  | 0 | 217920
78 | Gazipur 52 MW PP | [8 empty] | 2 | 43 | 43 | 43 | 43 | 43 | 25 | 25 | 31 | 43 |  | 25 | 25 | 25 | 16 | 8 | 8 | 8 | 454872
79 | Kodda 150MW PP | [16 empty] | 7 | 40 |  | 82 | 82 | 82 | 48 | 32 | 16 | 16 | 327360
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 11 |  | 57 | 75 | 75 | 75 | 77 | 76 | 76 | 446400
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 36 |  | 52 | 16 | 16 | 16 |  |  |  | 123730
| Gazipur 100 MW PP | [16 empty] | 1 | 45 |  | 53 | 50 | 17 |  |  |  | 0 | 171384
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25560
| Jodiac Power | 17 | [6 empty] | 22 | 54 | 54 | 35 | 35 | 35 | 41 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 881832
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 11 | 34 | 64 | 86 | 84 | 73 | 73 | 73 | 73 | 73 | 68 |  | 76 | 86 | 86 | 86 | 67 | 49 | 48 | 1168333
86 | Meghnaghat CCPP(Summit) | 140 | 134 | 136 | 144 | 146 | 148 | 155 | 150 | 140 | 130 | 135 | 140 | 130 | 140 | 140 | 145 | 130 | 155 |  | 150 | 145 | 148 | 140 | 148 | 148 | 125 | 3387607
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 1 | 48 | 65 | 65 | 85 | 100 | 89 | 100 | 100 | 100 | 99 |  | 96 | 100 | 98 | 95 | 100 | 100 | 100 | 1482240
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 18 | 69 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1472640
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 47 | 5 | 5 | 5 | 5 | 5 | 18 | 47 | 47 | 47 | 47 | 46 | 46 | 43 | 43 | 43 | 46 | 47 |  | 47 | 47 | 47 | 47 | 47 | 43 | 46 | 885240
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 5 | 5 | 5 | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1134428
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | 10 | [6 empty] | 2 | 17 | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 32 | 779520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 9 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 |  | 0 | 156510
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 623872
101 | Kushiara 163 MW CCPP (KP) | 163 | 110 | 110 | 110 | 110 | 130 | 130 | 163 | 163 | 163 | 110 | 110 | 163 | 110 | 110 | 110 | 163 | 163 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3274363
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12800
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 |  |  |  | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 986400
104 | Keranigonj 300 MW PP (APR) | [24 empty] | 4 |  | 18336
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 5 | 86 |  | 110 | 110 | 110 | 70 | 50 | 16 | 0 | 520800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 42 | 73 | 75 | 71 | 62 | 70 | 70 | 59 | [8 empty] | 0 | 531360
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 10 | 20 | 10 | 60 | 100 | 100 | 50 | 20 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1140480
116 | Chandpur 200MW (Desh energy) | [7 empty] | 17 | 73 | 120 | 120 | 140 | 170 | 100 | 100 | 100 | 112 | 170 |  | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 2098080
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 10 |  | 5 | 35 | 53 | 50 | 50 | 37 | 117 |  | 150 | 150 | 150 | 150 | 150 | 100 | 100 | 1237818
118 | Bibiyana-III 400 MW CCPP | 282 | 282 | 282 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 200 | 80 | 80 | 79 | 80 | 100 |  | 80 | 80 | 80 | 80 | 15 | 80 | 162 | 4160000
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 |  |  |  |  | 32 | 80 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 95 | 95 | 85 | 85 | 85 | 85 | 85 | 1731600
| Anwara 300 MW PP (United) | 33 | [6 empty] | 16 | 83 | 83 | 70 | 121 | 124 | 124 | 124 | 88 | 124 | 158 |  | 158 | 161 | 162 | 162 | 162 | 162 | 162 | 2097600
| Juldah unit-2 (Acorn) | [16 empty] | 20 | 100 |  | 100 | 100 | 100 | 100 | 20 |  | 0 | 443520
| Anlima Energy Ltd. | [10 empty] | 2 |  |  | 10 | 16 | 18 | 10 | [8 empty] | 0 | 57709
120 | Eastern Zone Total | 4192 | 4063 | 4101 | 3957 | 3891 | 4010 | 4201 | 4549 | 4788 | 4943 | 4909 | 5177 | 5293 | 5039 | 4957 | 4949 | 5142 | 5862 |  | 6003 | 5834 | 5796 | 5435 | 5051 | 4994 | 4964 | 117503666
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 17 |  | 66 | 66 | 66 |  |  |  | 0 | 152640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 17 | 70 | 70 | 35 | 70 | 90 | 90 | 90 | 35 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 0 |  | 1152480
130
131
132 | United Payra Power Ltd. | [5 empty] | 52 | [19 empty] | 0 | 61200
133 | Bhola Nutan Biddut BD LTD (GAS) | 96 | 94 | 44 | 38 | 39 | 40 | 40 | 39 | 56 | 61 | 66 | 66 | 62 | 54 | 55 | 56 | 56 | 83 |  | 81 | 75 | 76 | 77 | 78 |  |  | 1440218
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 51 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | [7 empty] | 9 |  | 54 | 58 | 64 | 63 | 63 |  | 0 | 498640
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 19 | 21 | 21 | 20 | 18 | 12 | 12 | 14 | 20 | 21 | 19 | 17 | 17 | 21 | 26 |  | 25 | 26 | 27 | 27 | 27 | 18 | 18 | 492100
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | [6 empty] | 37125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 389 | 398 | 398 | 351 | 350 | 351 | 350 | 353 | 352 | 352 | 589 | 589 | 589 | 590 | 589 | 589 | 589 | 529 |  | 778 | 778 | 778 | 779 | 779 | 0 |  | 11854545
147 | Bheramara 410 MW CCPP | 180 | 190 | 205 | 230 | 245 | 260 | 295 | 280 | 265 | 250 | 250 | 220 | 220 | 215 | 205 | 205 | 205 | 200 |  | 195 | 196 | 195 | 195 | 195 | 0 |  | 5213376
148 | Payra 1320 MW | 430 | 430 | 340 | 250 | 250 | 250 | 250 | 270 | 300 | 300 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 390 |  | 590 | 660 | 660 | 660 | 540 | 400 | 380 | 8690000
149
150 | Barapukuria TPP Unit-1 | 85 | 86 | 83 | 82 | 83 | 83 | 84 | 85 | 86 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 89 | 89 |  | 89 | 89 | 89 | 89 | 90 | 89 | 90 | 2047418
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3435900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 161 | 153 | 130 | 130 | 130 | 130 | 146 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 162 |  | 167 | 158 | 158 | 160 | 162 | 159 | 164 | 3897591
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 130 | 130 | 130 | 130 | 130 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 167 |  | 175 | 170 | 170 | 170 | 160 | 152 | 161 | 4054509
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 412 | 398 | 305 | 333 | 334 | 386 | 414 | 433 | 435 | 317 | 347 | 411 | 412 | 305 | 347 | 348 | 401 | 428 |  | 285 | 352 | 350 | 340 | 419 | 395 | 308 | 8897236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | [5 empty] | 18 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 22 | 370800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 222138
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 21 | 42 | 42 | 33 | 42 | 87 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 716384
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [13 empty] | 26 |  |  | 12 | 69 |  | 70 | 70 | 70 | 70 | 50 |  | 0 | 470208
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 20 |  | 20 | [5 empty] | 0 | 91872
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 108 |  | 12 | [5 empty] | 0 | 169920
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 32891
178
178