## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-04 | Friday
|  |  | Date (day): | 2020-12-04 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12306.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13397 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-03 | 2020-12-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 93 | 94 | 115 | 115 |  | 55
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 51 | 52 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 342 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 325 | 325 | 325 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 340 | 400 | 400 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 145 | 126 | 155 | 155 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 1 | 48 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 28 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 46 | 86 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 10 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 3 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 10 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 98 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 58 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 17 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2188 | 2826 | 3774 | 4064 | 708 | 1162
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 89 | 86 | 92 | 92 | 138 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 215 | 204 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 9 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 198 | 179 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 45 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 80 | 50 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 2 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 765 | 778 | 1503 | 1498 | 648 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 140 | 80 | 100 | 100
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 80 | 80 | 54
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 160 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 35 | 5 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 128 | 68 | 68 | 68 | 127 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 150 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 50 | 50
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 118 | 100 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 120 | 141 | 150
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 26 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1011 | 877 | 1468 | 1728 | 278 | 720
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 110 | 164 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20 |  | 2 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 60 | 83 | 95
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 60 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 35 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 265 | 365 | 633.6 | 580 | 52 | 2
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 152 | 157 | 155 | 155 |  | 175 | GT-1 under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 32 | 36 | 36 | 36 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 325 | 325 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 238 | 238 | 235 | 235 | 170 |  | Gas shortage
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1114 | 1112 | 1224 | 1224 | 170 | 448
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 448 | 760 | 580 | 768
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 66 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  |  | Engine problem
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 100 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maintenance
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 538 | 956 | 1115 | 1539 | 0 | 425
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 26 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 43 | 86 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 500 | 660 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 10 | 8 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 568 | 780 | 867 | 927 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 109 | 175 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 188 | 225 | 225 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 426 | 301 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 104 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 20 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 831 | 1026 | 1506 | 1629 | 271 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 92 | 95 | 95 | 95
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 114 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 211 | 208 | 216 | 208 | 85 | 314
|  | Total |  |  |  |  | 20383 | 19892 | 7491 | 8928 | 12306.6 | 13397 | 2212 | 3363
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7128.5323 | 8496 | 11711.1194 | 12748.7581
| A. |  | 2020-12-03 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 8928 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5721 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8928 | MW
| 3 | Day peak Generation : |  |  | 7491 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8496 | MW
| 4 | Evening peak Generation : |  |  | 8928 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 171.9337 | MKWHr | By Solar | 0.40173 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 104.7623 | MKWHr |  | By Oil: | 39.2421 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.8098 | MKWHr |  | By Hydro: | 2.0801 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2212 | MW | Dhaka | 3200 | 3200 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3363 | MW | Chittagong | 943 | 943 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5575 | MW | Khulna | 1018 | 1018 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 874.33 | MMCFD |  |  | Rajshahi | 839 | 839 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 120437748.682 | ii) Oil : | Taka | 288444946.6 | Comilla | 716 | 716 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 59790100.62 | Total | Taka | 468672795.902 | Mymensingh | 651 | 651 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.417 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -17 | MW (E to W) at | 19:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -316 | MW at | 8:00 | hrs | Rangpur | 577 | 577 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.2° C |  |  | Total | 8496 | 8496 |  | 0
| B. |  | 2020-12-04 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 27.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 7800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13397 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6400 | MW
| 4 | Reserve(Generation end) |  |  |  | 5597 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 150.2109 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5707 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.6764 | MKWHr. | ii) HVDC Flow at Peak Time |  | 760 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9613 | MKWHr. | iii) Maximum HVDC Flow : |  | 761 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.08 |  | (b) Today: | 99.98 |  | (c) Rule Curve: |  | 105.73
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 354 | 300 |  | 0 | 300 | 135 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 20 | 25 | 8 | 0 | 93 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 0 | 80 | 0 | 0 | 0 | 160 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 82 | 111 | 17 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 79 | 0 | 0 | 18 | 0 | 0 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 100 | 237 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 89 | 0 | 140 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 14 | 155 | 0 | 295 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 |  | 4669 | 1628 | 6297 | 2429 | 286 | 1623 | 1117 | 589 | 93 | 78 | 82 | 0 | 0 | 100.09
2:00 | 0 | 113 | 0 | 115 | 200 | 53 | 0 | 339 | 300 |  | 0 | 320 | 140 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 20 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 80 | 0 | 0 | 0 | 159 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 80 | 111 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 79 | 0 | 0 | 18 | 0 | 0 | 280 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 102 | 40 | 237 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 162 | 0 | 305 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 |  | 4512 | 1513 | 6025 | 2414 | 255 | 1695 | 915 | 497 | 91 | 78 | 80 | 0 | 0 | 100.09
3:00 | 0 | 113 | 0 | 115 | 200 | 52 | 0 | 339 | 300 |  | 0 | 350 | 140 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 80 | 0 | 0 | 0 | 159 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 80 | 110 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 80 | 0 | 0 | 18 | 0 | 0 | 290 | 13 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 237 | 65 | 0 | 0 | 0 | 125 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 157 | 0 | 333 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 |  | 4345 | 1590 | 5935 | 2403 | 398 | 1753 | 724 | 488 | 89 | 0 | 80 | 0 | 0 | 100.09
4:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 338 | 300 |  | 0 | 350 | 135 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 0 | 0 | 162 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 78 | 110 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 160 | 36 | 80 | 0 | 0 | 18 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 237 | 65 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 156 | 0 | 307 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 |  | 4267 | 1510 | 5777 | 2402 | 346 | 1716 | 661 | 488 | 86 | 0 | 78 | 0 | 0 | 100.08
5:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 338 | 300 |  | 0 | 350 | 130 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 0 | 0 | 161 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 78 | 110 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 36 | 80 | 0 | 0 | 18 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 237 | 65 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 156 | 0 | 305 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 |  | 4213 | 1508 | 5721 | 2398 | 346 | 1714 | 612 | 488 | 85 | 0 | 78 | 0 | 0 | 100.08
6:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 363 | 300 |  | 0 | 370 | 145 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 0 | 0 | 189 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 74 | 110 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 36 | 80 | 0 | 0 | 18 | 0 | 0 | 310 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 237 | 71 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 123 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 169 | 0 | 335 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 |  | 4348 | 1575 | 5923 | 2468 | 346 | 1803 | 635 | 511 | 86 | 0 | 74 | 0 | 0 | 100.08
7:00 | 0 | 113 | 0 | 115 | 200 | 51 | 0 | 370 | 300 |  | 0 | 350 | 148 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 100 | 0 | 0 | 0 | 202 | 13 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 70 | 110 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 35 | 80 | 0 | 0 | 19 | 0 | 0 | 310 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 15 | 102 | 0 | 236 | 85 | 0 | 0 | 0 | 138 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 2 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 88 | 0 | 46 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 175 | 0 | 372 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 |  | 4548 | 1562 | 6110 | 2518 | 346 | 1822 | 809 | 454 | 88 | 0 | 70 | 3 | 0 | 100.07
8:00 | 0 | 114 | 0 | 115 | 200 | 51 | 0 | 361 | 300 |  | 0 | 350 | 145 | 96 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 140 | 0 | 0 | 0 | 184 | 112 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 70 | 113 | 0 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 36 | 77 | 0 | 0 | 19 | 0 | 0 | 300 | 13 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 8 | 100 | 100 | 25 | 237 | 101 | 0 | 0 | 1 | 230 | 35 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 208 | 0 | 426 | 70 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 4920 | 1769 | 6689 | 2594 | 346 | 1926 | 1157 | 488 | 89 | 0 | 70 | 19 | 0 | 100.07
9:00 | 0 | 108 | 0 | 115 | 200 | 51 | 0 | 354 | 315 |  | 0 | 350 | 140 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 140 | 0 | 0 | 0 | 180 | 112 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 70 | 110 | 0 | 20 | 1 | 40 | 22 | 50 | 47 | 140 | 145 | 36 | 77 | 0 | 0 | 19 | 0 | 0 | 300 | 14 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 15 | 13 | 100 | 100 | 102 | 237 | 115 | 0 | 0 | 3 | 233 | 35 | 0 | 0 | 0 | 20 | 0 | 90 | 21 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 199 | 0 | 400 | 90 | 0 | 45 | 0 | 50 | 0 | 3 | 0 | 470 | 0 | 0 | 0 |  | 5122 | 1926 | 7048 | 2563 | 346 | 1941 | 1440 | 558 | 89 | 0 | 70 | 41 | 0 | 100.07
10:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 340 | 314 |  | 0 | 330 | 140 | 100 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 35 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0 | 140 | 0 | 0 | 0 | 194 | 112 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 6 | 18 | 0 | 33 | 18 | 64 | 109 | 0 | 20 | 2 | 40 | 22 | 50 | 44 | 110 | 148 | 35 | 77 | 0 | 0 | 19 | 0 | 0 | 280 | 14 | 5 | 0 | 81 | 0 | 0 | 0 | 0 | 16 | 16 | 100 | 90 | 137 | 238 | 95 | 0 | 0 | 4 | 198 | 35 | 0 | 0 | 0 | 30 | 0 | 90 | 28 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 25 | 0 | 178 | 0 | 400 | 70 | 0 | 70 | 0 | 90 | 0 | 4 | 0 | 440 | 10 | 0 | 0 |  | 5055 | 1895 | 6950 | 2479 | 346 | 1894 | 1494 | 528 | 91 | 0 | 64 | 54 | 0 | 100.06
11:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 368 | 314 |  | 0 | 330 | 142 | 100 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0 | 140 | 0 | 0 | 0 | 185 | 112 | 0 | 26 | 15 | 0 | 51 | 0 | 0 | 8 | 18 | 0 | 33 | 18 | 66 | 105 | 0 | 20 | 2 | 40 | 22 | 50 | 43 | 110 | 152 | 35 | 76 | 0 | 0 | 19 | 0 | 0 | 310 | 14 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 18 | 100 | 70 | 142 | 239 | 95 | 0 | 0 | 4 | 198 | 35 | 0 | 0 | 15 | 30 | 0 | 90 | 35 | 0 | 0 |  | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 25 | 0 | 172 | 0 | 423 | 70 | 0 | 70 | 0 | 102 | 0 | 5 | 0 | 460 | 10 | 0 | 0 |  | 5170 | 2111 | 7281 | 2532 | 496 | 1956 | 1528 | 548 | 91 | 0 | 66 | 64 | 0 | 100.06
12:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 370 | 312 |  | 0 | 300 | 145 | 100 | 1 | 28 | 0 | 0 | 0 | 10 | 3 | 0 | 46 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 140 | 0 | 0 | 0 | 198 | 128 | 0 | 26 | 35 | 0 | 51 | 0 | 0 | 8 | 18 | 0 | 33 | 20 | 68 | 105 | 0 | 17 | 2 | 40 | 22 | 53 | 43 | 110 | 152 | 32 | 76 | 0 | 0 | 19 | 0 | 0 | 310 | 14 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 19 | 100 | 118 | 142 | 238 | 106 | 0 | 0 | 4 | 198 | 35 | 0 | 0 | 26 | 80 | 0 | 90 | 35 | 0 | 2 |  | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 43 | 0 | 179 | 0 | 426 | 90 | 0 | 70 | 0 | 114 | 0 | 5 | 20 | 500 | 10 | 0 | 0 |  | 5343 | 2148 | 7491 | 2492 | 448 | 1984 | 1753 | 592 | 89 | 0 | 68 | 65 | 0 | 100.06
13:00 | 0 | 94 | 0 | 115 | 200 | 51 | 0 | 364 | 314 |  | 0 | 300 | 140 | 100 | 23 | 48 | 0 | 0 | 0 | 30 | 7 | 0 | 60 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 6 | 0 | 140 | 0 | 0 | 0 | 182 | 128 | 0 | 26 | 35 | 0 | 51 | 0 | 0 | 25 | 18 | 0 | 33 | 21 | 66 | 104 | 9 | 17 | 1 | 40 | 22 | 50 | 43 | 110 | 158 | 32 | 78 | 0 | 0 | 19 | 0 | 0 | 305 | 14 | 5 | 0 | 174 | 0 | 0 | 8 | 0 | 32 | 17 | 100 | 120 | 142 | 238 | 115 | 0 | 0 | 3 | 198 | 35 | 0 | 0 | 26 | 90 | 0 | 90 | 32 | 0 | 0 |  | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 201 | 0 | 424 | 90 | 0 | 113 | 0 | 113 | 0 | 5 | 35 | 520 | 9 | 0 | 0 |  | 5563 | 2162 | 7725 | 2424 | 392 | 1990 | 2064 | 612 | 89 | 30 | 66 | 58 | 7725 | 100.05
14:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 340 | 284 |  | 0 | 320 | 132 | 100 | 30 | 55 | 0 | 0 | 0 | 30 | 7 | 0 | 69 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 3 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 110 | 0 | 0 | 0 | 182 | 128 | 0 | 26 | 49 | 0 | 51 | 0 | 0 | 25 | 18 | 0 | 33 | 21 | 66 | 88 | 24 | 20 | 1 | 40 | 22 | 53 | 43 | 110 | 157 | 20 | 79 | 0 | 0 | 19 | 0 | 0 | 275 | 15 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 32 | 15 | 100 | 90 | 142 | 238 | 115 | 0 | 0 | 3 | 198 | 35 | 0 | 0 | 26 | 90 | 0 | 90 | 25 | 0 | 0 |  | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9 | 93 | 0 | 0 | 7 | 0 | 0 | 0 | 72 | 0 | 42 | 0 | 171 | 0 | 339 | 90 | 0 | 113 | 0 | 96 | 0 | 4 | 35 | 520 | 7 | 0 | 0 |  | 5447 | 2066 | 7513 | 2335 | 392 | 1874 | 2053 | 613 | 89 | 43 | 66 | 48 | 0 | 100.05
15:00 | 0 | 94 | 0 | 115 | 200 | 51 | 0 | 344 | 264 |  | 0 | 320 | 130 | 100 | 15 | 15 | 0 | 0 | 0 | 7 | 7 | 0 | 72 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 10 | 25 | 25 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 110 | 0 | 0 | 0 | 182 | 128 | 0 | 26 | 51 | 0 | 51 | 0 | 0 | 25 | 21 | 0 | 33 | 21 | 66 | 88 | 24 | 20 | 1 | 40 | 22 | 53 | 43 | 110 | 160 | 20 | 78 | 0 | 0 | 19 | 0 | 0 | 275 | 16 | 5 | 0 | 145 | 0 | 0 | 8 | 0 | 30 | 10 | 100 | 85 | 100 | 238 | 115 | 0 | 0 | 2 | 198 | 35 | 0 | 0 | 26 | 38 | 0 | 90 | 16 | 0 | 0 |  | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9 | 94 | 0 | 0 | 10 | 0 | 0 | 0 | 138 | 0 | 43 | 0 | 153 | 0 | 332 | 90 | 0 | 113 | 0 | 38 | 0 | 3 | 35 | 480 | 11 | 0 | 0 |  | 5185 | 2016 | 7201 | 2402 | 393 | 1851 | 1750 | 574 | 87 | 46 | 66 | 32 | 0 | 100.05
16:00 | 0 | 95 | 0 | 115 | 200 | 51 | 0 | 362 | 264 |  | 0 | 320 | 145 | 100 | 15 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 83 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 10 | 25 | 25 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 110 | 0 | 0 | 0 | 195 | 128 | 0 | 26 | 53 | 0 | 51 | 0 | 0 | 8 | 21 | 0 | 33 | 18 | 74 | 105 | 24 | 20 | 0 | 40 | 22 | 53 | 43 | 110 | 159 | 35 | 78 | 0 | 0 | 19 | 0 | 0 | 285 | 16 | 5 | 0 | 95 | 0 | 0 | 8 | 0 | 30 | 4 | 100 | 90 | 105 | 239 | 115 | 0 | 0 | 1 | 180 | 35 | 0 | 0 | 26 | 50 | 0 | 90 | 5 | 0 | 8 |  | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 43 | 0 | 173 | 0 | 381 | 90 | 0 | 95 | 0 | 0 | 0 | 2 | 0 | 460 | 17 | 0 | 0 |  | 5215 | 2005 | 7220 | 2523 | 393 | 1919 | 1623 | 553 | 87 | 36 | 74 | 12 | 0 | 100.04
17:00 | 0 | 94 | 0 | 115 | 200 | 54 | 0 | 350 | 263 |  | 0 | 320 | 123 | 100 | 16 | 15 | 0 | 0 | 0 | 12 | 24 | 48 | 87 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 10 | 25 | 25 | 18 | 0 | 86 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 21 | 0 | 20 | 3 | 0 | 110 | 0 | 0 | 0 | 154 | 78 | 0 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 21 | 0 | 33 | 18 | 96 | 107 | 24 | 20 | 0 | 40 | 22 | 53 | 43 | 110 | 157 | 35 | 78 | 0 | 0 | 19 | 0 | 0 | 290 | 16 | 5 | 0 | 130 | 0 | 0 | 8 | 0 | 32 | 0 | 100 | 123 | 135 | 238 | 115 | 20 | 0 | 0 | 161 | 35 | 0 | 0 | 26 | 50 | 0 | 90 | 0 | 0 | 21 |  | 393 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 44 | 0 | 168 | 0 | 341 | 90 | 0 | 95 | 0 | 72 | 0 | 0 | 35 | 380 | 35 | 0 | 0 |  | 5406 | 2065 | 7471 | 2438 | 393 | 1855 | 1926 | 474 | 86 | 203 | 96 | 0 | 0 | 100.04
18:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 346 | 323 |  | 0 | 340 | 146 | 100 | 28 | 15 | 0 | 0 | 0 | 80 | 40 | 98 | 86 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 32 | 25 | 25 | 33 | 0 | 85 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 31 | 0 | 20 | 6 | 0 | 80 | 0 | 0 | 0 | 175 | 68 | 0 | 26 | 54 | 0 | 51 | 0 | 0 | 40 | 21 | 0 | 33 | 21 | 102 | 108 | 54 | 20 | 0 | 40 | 22 | 53 | 44 | 110 | 158 | 20 | 78 | 0 | 0 | 19 | 0 | 0 | 295 | 16 | 5 | 0 | 290 | 0 | 0 | 29 | 0 | 125 | 0 | 100 | 135 | 150 | 238 | 115 | 35 | 0 | 0 | 179 | 35 | 0 | 17 | 48 | 50 | 0 | 90 | 0 | 0 | 0 |  | 760 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 81 | 0 | 183 | 0 | 340 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 17 | 0 | 0 |  | 6137 | 2740 | 8877 | 2483 | 760 | 1952 | 2654 | 554 | 85 | 287 | 102 | 0 | 0 | 100.04
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 94 | 0 | 115 | 200 | 52 | 0 | 342 | 325 |  | 0 | 340 | 126 | 100 | 48 | 15 | 0 | 0 | 0 | 100 | 0 | 98 | 86 | 0 | 0 | 10 | 54 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 9 | 0 | 80 | 0 | 0 | 0 | 160 | 68 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 0 | 33 | 21 | 120 | 110 | 60 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 157 | 36 | 78 | 0 | 0 | 19 | 0 | 0 | 285 | 16 | 11 | 0 | 300 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 100 | 150 | 238 | 115 | 0 | 0 | 0 | 179 | 45 | 0 | 0 | 26 | 50 | 0 | 90 | 0 | 0 | 0 |  | 760 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 86 | 0 | 188 | 0 | 301 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 660 | 8 | 0 | 0 |  | 5958 | 2970 | 8928 | 2486 | 760 | 1865 | 2569 | 755 | 86 | 287 | 120 | 0 | 0 | 100.02
19:30 | 0 | 94 | 0 | 115 | 200 | 52 | 0 | 338 | 325 |  | 0 | 340 | 140 | 100 | 49 | 15 | 0 | 0 | 0 | 100 | 0 | 98 | 86 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 12 | 0 | 80 | 26 | 0 | 0 | 202 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 120 | 110 | 60 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 35 | 78 | 0 | 0 | 19 | 0 | 0 | 295 | 16 | 11 | 0 | 300 | 0 | 0 | 60 | 0 | 117 | 0 | 100 | 68 | 150 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 26 | 50 | 0 | 90 | 0 | 0 | 0 |  | 761 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 85 | 0 | 185 | 0 | 392 | 90 | 0 | 113 | 0 | 45 | 0 | 0 | 113 | 660 | 8 | 0 | 0 |  | 5947 | 2913 | 8860 | 2546 | 761 | 1945 | 2361 | 754 | 86 | 287 | 120 | 0 | 0 | 0
20:00 | 0 | 94 | 0 | 115 | 200 | 52 | 0 | 338 | 324 |  | 0 | 340 | 133 | 100 | 48 | 15 | 0 | 0 | 0 | 100 | 0 | 98 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 15 | 0 | 80 | 50 | 0 | 0 | 184 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 118 | 110 | 60 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 78 | 0 | 0 | 19 | 0 | 0 | 275 | 16 | 11 | 0 | 300 | 0 | 0 | 40 | 0 | 114 | 0 | 100 | 68 | 150 | 239 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 26 | 50 | 0 | 90 | 0 | 0 | 0 |  | 761 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 88 | 0 | 187 | 0 | 365 | 90 | 0 | 113 | 0 | 35 | 0 | 0 | 70 | 660 | 8 | 0 | 0 |  | 5902 | 2840 | 8742 | 2555 | 761 | 1904 | 2276 | 754 | 87 | 287 | 118 | 0 | 0 | 100.03
21:00 | 0 | 94 | 0 | 115 | 200 | 52 | 0 | 339 | 320 |  | 0 | 340 | 140 | 100 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 82 | 86 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 19 | 0 | 80 | 60 | 0 | 0 | 220 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 110 | 109 | 54 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 158 | 36 | 78 | 0 | 0 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 69 | 0 | 100 | 68 | 150 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 |  | 760 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 87 | 0 | 187 | 0 | 393 | 90 | 0 | 113 | 0 | 34 | 0 | 0 | 0 | 570 | 35 | 0 | 0 |  | 5636 | 2734 | 8370 | 2601 | 760 | 1964 | 1912 | 664 | 88 | 271 | 110 | 0 | 0 | 100.02
22:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 339 | 320 |  | 0 | 340 | 130 | 100 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 64 | 85 | 0 | 0 | 0 | 0 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 1 | 20 | 21 | 0 | 80 | 60 | 0 | 0 | 223 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 102 | 110 | 60 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 159 | 36 | 78 | 0 | 0 | 19 | 0 | 0 | 275 | 16 | 11 | 0 | 145 | 0 | 0 | 24 | 0 | 39 | 0 | 100 | 68 | 150 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 |  | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 89 | 0 | 186 | 0 | 344 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 570 | 23 | 0 | 0 |  | 5442 | 2561 | 8003 | 2603 | 760 | 1898 | 1650 | 664 | 90 | 236 | 102 | 0 | 0 | 100.02
23:00 | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 348 | 320 |  | 0 | 360 | 145 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 0 | 0 | 0 | 0 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 20 | 15 | 0 | 80 | 60 | 0 | 0 | 221 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 96 | 110 | 60 | 20 | 0 | 60 | 22 | 53 | 47 | 110 | 159 | 20 | 79 | 0 | 0 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 100 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 |  | 574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 57 | 0 | 172 | 0 | 426 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 | 0 |  | 5148 | 2213 | 7361 | 2592 | 574 | 1982 | 1361 | 594 | 92 | 70 | 96 | 0 | 0 | 100.01
24:00 | 0 | 94 | 0 | 115 | 200 | 51 | 0 | 346 | 290 |  | 0 | 360 | 135 | 100 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 15 | 0 | 80 | 70 | 0 | 0 | 222 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 94 | 110 | 0 | 20 | 0 | 60 | 22 | 53 | 47 | 130 | 156 | 20 | 79 | 0 | 0 | 18 | 0 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 50 | 237 | 50 | 0 | 0 | 0 | 179 | 35 | 0 | 0 | 0 | 20 | 0 | 90 | 0 | 0 | 0 |  | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 56 | 0 | 163 | 0 | 434 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 | 0 |  | 4864 | 2021 | 6885 | 2576 | 445 | 1978 | 1061 | 595 | 93 | 43 | 94 | 0 | 0 | 100.01
KWH | 0 | 2593800 | 0 | 2803500 | 4878073 | 1226318 | 0 | 8566488 | 7268000 |  | 0 | 7264500 | 3351476 | 2152320 | 325848 | 327588 | 0 | 0 | 0 | 554880 | 0 | 504960 | 1491101 | 0 | 0 | 26544 | 1099800 | 895519 | 78059 | 394272 | 600000 | 539820 | 569700 | 627900 | 62808 | 0 | 2080080 | 0 | 0 | 0 | 0 | 4909434 | 0 | 0 | 0 |  | 0 | 0 | 450810 | 0 | 73920 | 107520 | 483984 | 419040 | 0 | 2434170 | 270486 | 87500 | 0 | 4517000 | 1605818 | 0 | 621072 | 506880 | 0 | 1240097 | 0 | 0 | 218693 | 462276 | 0 | 819600 | 49360 | 1961280 | 2517760 | 529920 | 415152 | 10000 | 976000 | 523800 | 1266000 | 1083960 | 2929990 | 3620000 | 763872 | 1878720 | 0 | 6790 | 433000 | 0 | 0 | 7224500 | 352032 | 157090 | 0 | 2576835 | 0 | 0 | 261600 | 0 | 756860 | 119610 | 1902720 | 2370720 | 2350181 | 5701000 | 2464800 | 67272 | 0 | 26641 | 4074764 | 991053 | 0 | 28500 | 347760 | 783360 | 0 | 2169600 | 214380 | 0 | 25091 |  | 10676364 | 0 | 0 | 0 | 148800 | 0 | 0 | 0 | 0 | 0 | 153375 | 0 | 473900 | 29184 | 0 | 0 | 0 | 0 | 0 | 1002992 | 0 | 0 | 0 | 8160 | 0 | 499680 | 0 | 217026 | 2167854 | 0 | 0 | 14000 | 0 | 0 | 0 | 3671273 | 0 | 855098 | 53760 | 4447564 | 0 | 8731218 | 1518240 | 0 | 1454016 | 0 | 933120 | 0 | 31103 | 503616 | 10641900 | 257810 | 0 | 0 |  | 123443627 | 48490053 | 171933680 | 60030794 | 10676364 | 44731529 | 37269383 | 12809754 | 2080080 | 1972762 | 1961280 | 401734 | 0
Fuel Cost | 0 | 3838824 | 0 | 4121145 | 5414661.03 | 1618739.76 | 0 | 8652152.88 | 7486040 |  | 0 | 7918305 | 3720138.36 | 16336108.8 | 2245092.72 | 2771394.48 | 0 | 0 | 0 | 4178246.4 | 0 | 4968806.4 | 13747951.22 | 0 | 0 | 241284.96 | 8028540 | 6922361.87 | 769661.74 | 295704 | 450000 | 0 | 0 | 0 | 607353.36 | 0 | 561621.6 | 0 | 0 | 0 | 0 | 5351283.06 | 0 | 0 | 0 |  | 0 | 0 | 4372857 | 0 | 643104 | 851558.4 | 609819.84 | 1244548.8 | 0 | 3602571.6 | 397614.42 | 64750 | 0 | 4155640 | 2071505.22 | 0 | 701811.36 | 709632 | 0 | 2120565.87 | 0 | 0 | 2088518.15 | 587090.52 | 0 | 1434300 | 37020 | 14709600 | 2668825.6 | 4811673.6 | 527243.04 | 159400 | 1600640 | 838080 | 2253480 | 1690977.6 | 3340188.6 | 3764800 | 1504827.84 | 3588355.2 | 0 | 11746.7 | 948270 | 0 | 0 | 7296745 | 264024 | 119388.4 | 0 | 19480872.6 | 0 | 0 | 1360320 | 0 | 7447502.4 | 1398240.9 | 15507168 | 25722312 | 16568776.05 | 5301930 | 22478976 | 635720.4 | 0 | 0 | 30805215.84 | 8632071.63 | 0 | 284430 | 2980303.2 | 5217177.6 | 0 | 0 | 0 | 0 | 0 |  | 61495856.64 | 0 | 0 | 0 | 1169568 | 0 | 0 | 0 | 0 | 0 | 1598167.5 | 0 | 734545 | 284835.84 | 0 | 0 | 0 | 0 | 0 | 8876479.2 | 0 | 0 | 0 | 79070.4 | 0 | 959385.6 | 0 | 164288.682 | 13072159.62 | 0 | 0 | 485100 | 0 | 0 | 0 | 4846080.36 | 0 | 1282647 | 914457.6 | 5203649.88 | 0 | 8643905.82 | 15850425.6 | 0 | 13798611.84 | 0 | 7241011.2 | 0 | 343688.15 | 3721722.24 | 46717941 | 0 | 0 | 0 |  | 349857606.02 | 197483597.172 | 547341203.192 | 67478182.212 | 61495856.64 | 52959566.47 | 269741704 | 59790100.62 | 561621.6 | 18703242.6 | 14709600 | 1901329.05 | 0
Yesterday Day Peak | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 370 | 312 |  | 0 | 300 | 145 | 100 | 1 | 28 | 0 | 0 | 0 | 10 | 3 | 0 | 46 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 140 | 0 | 0 | 0 | 198 | 128 | 0 | 26 | 35 | 0 | 51 | 0 | 0 | 8 | 18 | 0 | 33 | 20 | 68 | 105 | 0 | 17 | 2 | 40 | 22 | 53 | 43 | 110 | 152 | 32 | 76 | 0 | 0 | 19 | 0 | 0 | 310 | 14 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 19 | 100 | 118 | 142 | 238 | 106 | 0 | 0 | 4 | 198 | 35 | 0 | 0 | 26 | 80 | 0 | 90 | 35 | 0 | 2 |  | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 43 | 0 | 179 | 0 | 426 | 90 | 0 | 70 | 0 | 114 | 0 | 5 | 20 | 500 | 10 | 0 | 0 |  | 7491 | DayPeak
Yesterday Evening Peak | 0 | 94 | 0 | 115 | 200 | 52 | 0 | 342 | 325 | 0 | 0 | 340 | 126 | 100 | 48 | 15 | 0 | 0 | 0 | 100 | 0 | 98 | 86 | 0 | 0 | 10 | 54 | 55 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 9 | 0 | 80 | 0 | 0 | 0 | 160 | 68 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 0 | 33 | 21 | 120 | 110 | 60 | 20 | 0 | 40 | 22 | 53 | 47 | 110 | 157 | 36 | 78 | 0 | 0 | 19 | 0 | 0 | 285 | 16 | 11 | 0 | 300 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 100 | 150 | 238 | 115 | 0 | 0 | 0 | 179 | 45 | 0 | 0 | 26 | 50 | 0 | 90 | 0 | 0 | 0 |  | 760 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 86 | 0 | 188 | 0 | 301 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 660 | 8 | 0 | 0 |  | 8928 | EvPeak
Forecast for Evening | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 325 | 0 | 0 | 400 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 100 | 80 | 0 | 0 | 225 | 68 | 50 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 150 | 150 | 95 | 20 | 0 | 60 | 22 | 51 | 44 | 163 | 155 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 325 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 0 |  |  | 768 | 16 | 0 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 325 | 0 | 0 | 400 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 92 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 |  | 100 | 80 | 0 | 0 | 225 | 68 | 50 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 141 | 164 | 83 | 20 | 1.6 | 60 | 22 | 51 | 44 | 163 | 155 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 325 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 235 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 0 |  |  | 580 | 0 | 0 | 0 | 115 | 100 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 93 | 0 | 115 | 200 | 51 | 0 | 400 | 320 | 0 | 0 | 400 | 130 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 |  | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 80 | 80 | 0 | 0 | 194 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 70 | 164 | 0 | 20 | 0 | 60 | 22 | 50 | 47 | 110 | 158 | 20 | 80 | 0 | 0 | 19 | 0 | 0 | 305 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 20 | 0 | 237 | 32 | 0 | 0 | 1 | 103 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 193 | 0 | 340 | 35 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 8 | 0 | 0 | 0
199
| Minimum Generation |  | 5721 | 5:00
| Highest Generation |  | 8928 | 19:00
| Day Peak Generation |  | 7491 | 12:00
| Evening Peak Generation |  | 8928 | 19:00
| HVDC Max Flow |  | 761 | 19:30
| HVDC EvPeak Flow |  | 760 | 19:00
| Load factor L.F |  | 80.24%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7491 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5707 | MW
Evening Peak Generation : |  | 8928 | MW Hour : | 19:00 | Available Max Generation : |  | 13397 | MW
E.P. Demand (at gen end) : |  | 8928 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7800 | MW
Maximum Generation : |  | 8928 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5597 | MW
Total Gen. (MKWH) : |  | 171.9337 | System Load Factor : | 80.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -316 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-04
Actual : | 99.98 | Ft.(MSL) , | Rule curve : | 105.73 | Ft.( MSL )
Gas Consumed : | Total = | 874.33 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120437748.682
: |  | Coal : | 59790100.62 | Oil : | 288444946.6 | Total : | 468672795.902
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2779.6505 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 936.7648 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 837.801 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 756.488 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 683.9227 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 551.8801 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 319.484 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 142.3827 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 425.5852 |  |  | 0 | 0%
Total | 0 |  | 7433.959 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10)Ashuganj(S)-360 MW
2) Baghabari-71,100 MW
3) Ghorasal Unit-1,2,4
4) Ashuganj unit-3
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Chandpur-163 MW
9) Sirajganj #1 CCPP STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Rajshahi 132/33 kV T-2 transformer was under shut down from 08:20 to 16:35 for A/M.
b) Baroaulia-Hathazari 132 kv Ckt-1 was under shut down from 08:16 to 15:26 for A/M.
c) Aminbazar 230/132kV T03 transformer was under shut down from 08:16 to 17:11 for A/M.
d) Saver-Manikganj P/P 132 kV Ckt-2 was under shut down from 08:55 to 15:53 for A/M.
e) Jamalpur--UMPL 132 kV Ckt-2 was under shut down from 08:11 to 16:42 for A/M.
f) Sherpur-UMPL 132 kV Ckt-1 was under shut down from 09:01 to 16:49 for A/M.
g) Agargaon 230/132 kV T01 transformer was under shut down from 07:51 to 18:08 for A/M.
h) Tongi(old)-Tongi(New) 132 kV Ckt-2 was under shut down from 10:22 to 14:09 for A/M.
i) Cumilla(N) 230/132 kV T-2 transformer was under shut down from 08:24 to 16:54 for A/M.
j) Mymensing RPCL-Mymensing S/S 132 kV Ckt-2 was under shut down from 08:32 to 17:02 for A/M.
k) Bhandaria-Bagerhat 132 kV Ckt was under shut down from 07:58 to 16:41 for A/M.
l) Naogaon-Bogura 132 kV Ckt-1 was under shut down from 09:12 to 16:22 for A/M.
m) Saidpur-Barapukuria 132 kV Ckt-2 was under shut down from 08:40 to 16:56 for A/M.
n) Magura 132/33 kV T-2 transformer was under shut down from 08:21 to 16:12 for A/M.
o) Sylhet-Fenchuganj 132 kV Ckt-2 tripped at 10:04 showing Dist. Relay at Sylhet end and was switched
on at 12:57.
p) Sirajganj 225 MW unit-2 STG was synchronized at 13:21.
q) Ashuganj unit-5 was synchronized at 19:01.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 94 | 2593800 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2803500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4878073 | Machine problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 52 | 1226318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8566488 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 325 | 7268000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7264500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2152320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 126 | 3351476 | FGMO and GT-2 under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 325848 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 327588 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 86 | 1491101 | Machin problem.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 394272
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 554880
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 10 | 26544 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1099800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 504960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 895519
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 78059 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1139820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 569700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 627900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 62808 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 2576835
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 756860
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 67272 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2169600 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 5895 | 2826 | 53773841
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 119610
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 107520 | 33 kV line fault
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2080080 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4909434
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 450810 | Engine problem
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1902720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 483984
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 419040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 73920 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 179 | 4074764 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 45 | 991053 | Engine problem
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 783360 | Engine problem
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 25091
| Chattogram area Total |  |  |  | 2266 | 778 | 16448027
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2434170 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 270486 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 160 | 4517000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 87500 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 621072 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 506880 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1605818 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1240097
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 2350181
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 2370720 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 462276
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 1961280
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 218693 | High Voltage.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 49360
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 28500 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 347760 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 877 | 19891393
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 110 | 2517760 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 415152
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 60 | 529920 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10000
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 60 | 261600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2464800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 214380
| Mymensingh Area Total |  |  |  | 637 | 365 | 6413612
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 976000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 523800 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2929990 | Gas shortage
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3620000 | Gas shortage
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1266000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1083960
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 157090 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 36 | 763872
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1878720 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 6790 | Gas shortage
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 433000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 352032 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7224500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 238 | 5701000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1112 | 26916754
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 760 | 10676364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 148800 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 153375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 53760 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1518240 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 956 | 12550539
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 29184 | Reserve.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 473900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 86 | 855098 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 660 | 10641900
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 8 | 257810
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 780 | 12257892
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 175 | 3671273 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4447564 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 301 | 8731218 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 499680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217026
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 8160 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 104 | 1002992
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1454016
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 503616
| Rajshahi Area Total |  |  |  | 2183 | 1026 | 20535545
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 95 | 2167854
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 14000 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 933120
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31103
| Rangpur Area Total |  |  |  | 605 | 208 | 3146077
| Total |  |  |  | 19892 | 8928 | 171933680
| Eastern Grid Total |  |  |  | 13766 | 5958 | 123443627
| Western Grid Total |  |  |  | 6126 | 2970 | 48490053
| National Grid Total |  |  |  | 19892 | 8928 | 171933680
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-03
| (a) ENTIRE EASTERN GRID : |  | 5826 | MW | (b) ENTIRE WESTERN GRID : |  | 2670 | MW
| i) Dhaka area |  | 3200 | MW | i) Khulna area |  | 1018 | MW
| ii) Chittagong area |  | 943 | MW | ii) Rajshahi area |  | 839 | MW
| iii) Comilla area |  | 716 | MW | iii) Barisal area |  | 236 | MW
| iv) Mymensingh area |  | 651 | MW | iv) Rangpur area |  | 577 | MW
| v) Sylhet area |  | 316 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8496 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 108 | 17:00 | Jamalpur | 99 | 18:00 | Benapol | 34 | 18:00
| Munsiganj | 84 | 19:30 | Sherpur | 84 | 18:00 | Jhenida | 78 | 18:00
| Sonargaon | 64 | 19:00 | Srimongal | 26 | 18:00 | Bottail | 92 | 18:30
| Shyampur | 97 | 10:00 | Shahjibazar | 82 | 18:00 | G.K Project | 35 | 18:00
| Bhulta | 150 | 19:30 | Fenchuganj | 27 | 18:00 | Faridpur | 130 | 18:00
| Madanganj | 53 | 21:00 | Kulawara | 30 | 18:00 | Madaripur | 57 | 20:00
| Shitalakhya | 90 | 11:00 | Sylhet | 75 | 18:00 | Sariatpur | 40 | 20:00
| Rahim steel | 12 | 12:00 | Chatak | 20 | 18:00 | Gopalganj | 60 | 18:00
| Matuail | 72 | 10:00 | Sunamganj | 27 | 19:00 | Bagerhat | 79 | 18:30
| Ghorasal | 66 | 19:00 | Biani Bazar | 38 | 18:30 | Mongla | 31 | 11:00
| Narsingdi | 124 | 20:00 | Comilla (S) | 120 | 19:00 | Satkhira | 72 | 19:00
| Haripur (SBU) | 98 | 12:00 | Comilla(N) | 57 | 20:00 | Gallamari | 22 | 13:00
| Ullon | 46 | 18:00 | Chandpur | 62 | 19:00 | Magura | 36 | 18:00
| Hasnabad | 143 | 18:00 | Feni | 68 | 18:00 | Norail | 28 | 18:00
| Magbazar | 76 | 15:00 | Chowmuhani | 112 | 18:00 | Chuadanga | 61 | 18:00
| Maniknagar | 70 | 12:00 | Ashuganj | 43 | 18:30 | Barisal(N) | 29 | 20:00
| Bangabhaban | 22 | 11:00 | Daudkandi | 92 | 19:30 | Barisal (S) | 68 | 18:00
| Narinda | 76 | 18:00 | B.Baria | 97 | 19:30 | Patuakhali | 80 | 19:00
| Dhanmondi | 110 | 13:00 | Ramganj | 64 | 18:30 | Bhandaria | 40 | 20:00
| Lalbag | 74 | 17:00 | Chaddagram | 34 | 17:00 | Borhan Uddin | 26 | 22:00
| Madartek | 48 | 18:00 | PHP | 6 | 14:00 | Ishurdi | 41 | 20:00
| Dhaka University |  |  | Madunaghat | 41 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.70833 | Hathazari | 68 | 0.79167 | Natore | 83 | 0.75
| Fatullah | 35 | 12:00 | Khulshi | 182 | 12:00 | Bogra | 114 | 18:00
| Mirpur | 76 | 18:00 | Halishahar | 109 | 18:00 | Noagaon | 78 | 19:00
| Kalyanpur | 63 | 18:00 | Baraulia | 130 | 12:00 | Rajshahi | 94 | 20:00
| Gulshan | 82 | 18:00 | Sikalbaha | 21 | 19:00 | Rajshahi New | 8 | 20:00
| Uttara | 71 | 18:00 | Dohazari | 56 | 19:00 | C.Nawabganj | 50 | 19:00
| Uttara New | 22 | 18:00 | Cox'sbazar | 73 | 19:00 | Amnura | 30 | 18:00
| Kamrangirchar | 74 | 18:00 | Chandraghona | 20 | 18:30 | Pabna | 76 | 18:30
| Savar | 98 | 16:00 | Kaptai | 3.6 | 18:00 | Shahjadpur | 73 | 18:30
| Bhasantec | 116 | 13:00 | A. Khaer Stl. | 9 | 4:00 | Serajganj | 57 | 19:00
| Agargaon | 49 | 13:00 | Bakulia | 78 | 12:00 | Niyamatpur | 38 | 18:30
| Satmosjid | 67 | 0.75 | Julda | 22 | 0.33333 | Joypurhat | 42 | 0.77083
| Tongi | 76 | 18:00 | TK chemical | 21 | 18:00 | Sherpur(Bogura) | 39 | 18:00
| Kabirpur | 176 | 12:00 | Modern Steel | 16 | 4:00 | Mohastangor | 32 | 18:00
| Basundhara | 95 | 18:00 | Shahmirpur | 17 | 8:00 | Rangpur | 105 | 18:30
| Manikganj | 52 | 19:00 | Khagrachhari | 20 | 1:00 | Lalmonirhat | 42 | 19:00
| Joydevpur | 117 | 18:30 | Matarbari | 28 | 18:00 | Saidpur | 88 | 18:00
| New Tongi | 77 | 18:00 | Baroiar Hat | 34 | 18:00 | Purbasadipur | 83 | 18:00
| Kodda | 182 | 18:00 | Rangamati | 8 | 12:00 | Thakurgaon | 64 | 18:00
| Dhamrai | 66 | 11:00 | Abul Khair 230 | 122 | 12:00 | Palashbari | 80 | 18:30
| Rajendrapur | 72 | 21:00 | BSRM | 148 | 15:00 | Barapukuria | 40 | 19:00
| Valuka | 82 | 18:30 | GPH Ispat | 79 | 6:00 | Panchagar | 42 | 18:30
| Tangail | 118 | 19:30 | Goalpara | 17 | 13:00 | Joldhaka | 20 | 18:30
| Mymensing | 139 | 18:00 | Central s/s | 78 | 18:00 | Kurigram | 40 | 18:30
| Kishorganj | 76 | 19:30 | Noapara | 43 | 18:30
| Netrokona | 80 | 18:30 | Jessore | 81 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 20:00 | 405 | 24:00 | Kaliakoir | 391 | 0.125 | 380 | 0.45833
| Bheramara | 412 | 4:00 | 399 | 18:00 | Bhulta | 385 | 0.041667 | 375 | 0.5
| Ashuganj(N) | 386 | 4:00 | 381 | 12:00 | Gopalganj | 417 | 0.083333 | 387 | 0.79167
| Payra | 422 | 1:00 | 404 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 7:00 | Comilla (N) | 240 | 1:00 | 235 | 12:00
| Ishurdi | 237 | 1:00 | 225 | 7:00 | Hathazari | 222 | 4:00 | 212 | 15:00
| Ashuganj | 240 | 9:00 | 235 | 4:00 | Megnaghat | 238 | 14:00 | 232 | 11:00
| Serajganj | 232 | 1:00 | 228 | 7:00 | Fenchuganj | 245 | 1:00 | 240 | 11:00
| Baghabari | 243 | 1:00 | 236 | 11:00 | Siddhirganj | 234 | 3:00 | 229 | 11:00
| Barapukuria | 231 | 14:00 | 223 | 7:00 | Maniknagar | 233 | 1:00 | 227 | 11:00
| Bogra | 233 | 14:00 | 222 | 8:00 | Agargaon | 233 | 17:00 | 227 | 11:00
| Rajshahi | 229 | 17:00 | 211 | 1:00 | Barisal | 248 | 1:00 | 234 | 8:00
| Khulna South | 234 | 1:00 | 219 | 7:00 | AKSML | 226 | 18:30 | 217 | 11:00
| Rampura | 231 | 1:00 | 228 | 11:00 | BSRM | 229 | 18:30 | 220 | 11:00
| Haripur | 232 | 7:00 | 228 | 10:00 | Bibiyana | 245 | 4:00 | 239 | 20:00
| Hasnabad | 235 | 1:00 | 228 | 9:00 | Bhulta | 235 | 19:00 | 229 | 17:00
| Shyampur | 232 | 1:00 | 220 | 11:00 | Ashuganj (S) | 237 | 18:00 | 234 | 11:00
| Aminbazar | 234 | 1:00 | 228 | 11:00 | Kaliakoir | 236 | 4:00 | 229 | 3:00
| Tongi | 234 | 18:00 | 223 | 13:00 | GPH | 225 | 4:00 | 216 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 1:00 | 136 | 11:00 | Madanhat | 136 | 0.77083 | 130 | 0.45833
| Munsiganj | 140 | 14:00 | 135 | 1:00 | Hathazari | 135 | 0.041667 | 130 | 0.45833
| Sonargaon | 139 | 1:00 | 135 | 12:00 | Khulshi | 132 | 0.77083 | 127 | 0.45833
| Shyampur | 136 | 5:00 | 131 | 11:00 | Halishahar | 134 | 0.91667 | 128 | 0.45833
| Bhulta | 133 | 4:00 | 130 | 10:00 | Baraulia | 135 | 0.91667 | 127 | 0.5
| Madanganj | 141 | 19:00 | 133 | 16:00 | Sikalbaha | 135 | 0.91667 | 128 | 0.5
| Shitalakhya | 141 | 1:00 | 135 | 11:00 | Dohazari | 132 | 0.75 | 127 | 0.45833
| Rahim steal | 140 | 20:00 | 137 | 10:00 | Cox'sbazar | 127 | 0.375 | 116 | 0.75
| Matuail | 140 | 1:00 | 136 | 11:00 | Chandraghona | 134 | 0.041667 | 129 | 0.45833
| Ghorasal | 140 | 1:00 | 138 | 9:00 | Kaptai | 135 | 0.041667 | 132 | 0.29167
| Narsinghdi | 138 | 7:00 | 134 | 10:00 | A. Khaer Stl. | 132 | 0.91667 | 127 | 0.5
| Haripur (SBU) | 139 | 21:00 | 134 | 1:00 | Bakulia | 132 | 0.33333 | 127 | 0.5
| Ullon | 133 | 6:00 | 129 | 11:00 | Julda | 133 | 0.041667 | 129 | 0.5
| Hasnabad | 140 | 13:00 | 136 | 12:00 | TK Chemical | 134 | 0.375 | 130 | 0.45833
| Magbazar | 133 | 3:00 | 129 | 11:00 | Modern Steel | 132 | 0.041667 | 127 | 0.45833
| Maniknagar | 138 | 1:00 | 135 | 11:00 | Shahmirpur | 134 | 0.375 | 128 | 0.66667
| Bangabhaban | 138 | 1:00 | 135 | 11:00 | Khagrachhari | 134 | 0.041667 | 128 | 0.5
| Narinda | 138 | 1:00 | 135 | 11:00 | Matarbari | 130 | 0.375 | 122 | 0.45833
| Dhanmondi | 133 | 6:00 | 129 | 11:00 | Baroiar Hat | 135 | 0.041667 | 132 | 0.41667
| Lalbag | 128 | 1:00 | 121 | 11:00 | Rangamati | 134 | 18:30 | 128 | 12:00
| Madartek | 133 | 1:00 | 128 | 11:00 | Goalpara S/S | 138 | 1:00 | 129 | 20:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 1:00 | 129 | 0.29167
| Aftabnagar | 133 | 1:00 | 129 | 10:00 | Noapara | 137 | 1:00 | 127 | 0.29167
| Fatuiiah | 137 | 1:00 | 133 | 11:00 | Jessore | 134 | 3:00 | 125 | 0.29167
| Mirpur | 131 | 4:00 | 123 | 11:00 | Benapol | 136 | 0.91667 | 125 | 0.29167
| Kalyanpur | 129 | 4:00 | 124 | 11:00 | Jhenida | 132 | 1:00 | 121 | 0.83333
| Gulshan | 132 | 4:00 | 128 | 11:00 | Bottail | 136 | 0.041667 | 126 | 0.8125
| Uttara | 128 | 4:00 | 122 | 12:00 | G.K Project | 138 | 0.041667 | 130 | 0.83333
| Uttara New | 129 | 4:00 | 122 | 11:00 | Faridpur | 136 | 0.16667 | 126 | 0.8125
| Kamrangirchar | 139 | 4:00 | 133 | 11:00 | Madaripur | 138 | 0.20833 | 130 | 0.8125
| Savar | 130 | 1:00 | 122 | 12:00 | Shariyatpur S/S | 139 | 3:00 | 130 | 0.79167
| Bhasantec | 136 | 4:00 | 128 | 12:00 | Gopalganj | 141 | 0.20833 | 130 | 0.79167
| Agargaon | 137 | 4:00 | 129 | 12:00 | Bagerhat | 140 | 22:00 | 129 | 0.29167
| Satmosjid | 136 | 4:00 | 129 | 12:00 | Mongla | 137 | 9:00 | 128 | 0.83333
| Tongi | 142 | 18:00 | 135 | 15:00 | Satkhira | 138 | 1:00 | 127 | 7:00
| Kabirpur | 134 | 1:00 | 128 | 12:00 | Gallamari | 138 | 0.58333 | 130 | 0.83333
| Basundhara | 133 | 1:00 | 128 | 12:00 | Magura | 131 | 1:00 | 121 | 0.77083
| Manikganj | 140 | 18:00 | 130 | 10:00 | Norail | 131 | 0.041667 | 120 | 0.83333
| Joydevpur | 141 | 19:30 | 134 | 11:00 | Chuadanga | 131 | 3:00 | 118 | 0.83333
| New Tongi | 140 | 18:00 | 134 | 16:00 | Barisal(N) | 140 | 17:00 | 133 | 9:00
| Kodda | 140 | 18:00 | 128 | 13:00 | Barisal (S) | 139 | 0.041667 | 133 | 0.29167
| Dhamrai | 134 | 18:00 | 128 | 16:00 | Patuakhali(S) | 138 | 0.70833 | 130 | 0.79167
| Rajendrapur | 138 | 22:00 | 133 | 13:00 | Bhandaria | 137 | 0.70833 | 130 | 0.8125
| Valuka | 131 | 1:00 | 125 | 24:00 | Ishurdi | 136 | 17:00 | 130 | 20:00
| Tangail | 133 | 1:00 | 130 | 7:00 | Ruppur Paromanobik | 139 | 1:00 | 130 | 20:00
| Mymensing | 132 | 4:00 | 127 | 24:00 | Natore | 137 | 17:00 | 130 | 7:00
| Kishorganj | 133 | 14:00 | 128 | 24:00 | Bogra | 135 | 5:00 | 129 | 8:00
| Netrokona | 131 | 4:00 | 127 | 24:00 | Noagaon | 134 | 5:00 | 124 | 8:00
| Jamalpur | 139 | 18:30 | 126 | 24:00 | Rajshahi | 138 | 14:00 | 130 | 7:00
| Sherpur | 138 | 18:30 | 125 | 24:00 | Rajshahi New | 139 | 17:00 | 130 | 1:00
| Srimongal | 140 | 1:00 | 137 | 13:00 | C.Nawabganj | 138 | 17:00 | 128 | 12:00
| Shahjibazar | 138 | 4:00 | 135 | 12:00 | Amnura | 140 | 18:00 | 128 | 8:00
| Fenchuganj | 138 | 6:00 | 135 | 11:00 | Pabna | 137 | 2:00 | 130 | 20:00
| Khulawara | 138 | 1:00 | 135 | 11:00 | Shahjadpur | 140 | 1:00 | 136 | 13:00
| Sylhet | 135 | 1:00 | 131 | 12:00 | Serajganj | 135 | 1:00 | 131 | 12:00
| Chatak | 135 | 4:00 | 130 | 12:00 | Niyamatpur | 133 | 5:00 | 122 | 8:00
| Sunamganj | 135 | 3:00 | 130 | 12:00 | Joypurhat | 135 | 4:00 | 124 | 8:00
| Biani Bazar | 135 | 3:00 | 131 | 18:00 | Sherpur(Bogura) | 137 | 15:00 | 129 | 8:00
| Comilla(s) | 130 | 5:00 | 124 | 19:00 | Mohastangor | 136 | 14:00 | 127 | 8:00
| Comilla(n) | 142 | 9:18 | 138 | 13:00 | Rangpur | 129 | 14:00 | 118 | 8:00
| Chandpur | 145 | 18:00 | 138 | 21:00 | Lalmonirhat | 130 | 5:00 | 118 | 8:00
| Feni | 139 | 18:00 | 135 | 11:00 | Saidpur | 128 | 3:00 | 118 | 8:00
| Chowmuhani | 139 | 18:30 | 134 | 8:00 | Purbasadipur | 127 | 3:00 | 114 | 9:00
| Ashuganj | 138 | 14:00 | 136 | 11:00 | Thakurgaon | 126 | 2:00 | 118 | 18:00
| Daudkandi | 140 | 7:00 | 136 | 10:00 | Palashbari | 132 | 4:00 | 127 | 7:00
| B.Baria | 134 | 7:00 | 133 | 10:00 | Barapukuria | 131 | 14:00 | 123 | 7:00
| Ramganj | 138 | 18:30 | 130 | 9:00 | Panchagar | 126 | 5:00 | 113 | 9:00
| Chaddagram | 141 | 18:00 | 136 | 12:00 | Joldhaka | 127 | 3:00 | 116 | 8:00
| PHP | 138 | 18:30 | 133 | 11:00 | Kurigram | 128 | 0.041667 | 117 | 0.33333

## L-Curve
Date | 2020-12-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 15 | 4864 | 2021 | 6885 |  |  |  | QF-LDC-11
0:30 | 60.5 | 4766.5 | 1824.5 | 6591 | Date: | 2020-12-03
1:00 | 106 | 4669 | 1628 | 6297
1:30 | 118 | 4590.5 | 1570.5 | 6161
2:00 | 130 | 4512 | 1513 | 6025
2:30 | 120 | 4428.5 | 1551.5 | 5980 | [5 empty] | Gen. at Eve. Peak | 8928 | 8928 MW (19:00 )
3:00 | 110 | 4345 | 1590 | 5935 | [6 empty] | 19:00
3:30 | 107.5 | 4306 | 1550 | 5856 | [5 empty] | Gen. at Day Peak | 7491 | 7491 MW (12:00 )
4:00 | 105 | 4267 | 1510 | 5777 | [6 empty] | 12:00
4:30 | 110.5 | 4240 | 1509 | 5749 | [5 empty] | Highest Generation | 8928
5:00 | 116 | 4213 | 1508 | 5721 | [6 empty] | 19:00
5:30 | 125 | 4280.5 | 1541.5 | 5822
6:00 | 134 | 4348 | 1575 | 5923
6:30 | 204 | 4448 | 1568.5 | 6016.5
7:00 | 274 | 4548 | 1562 | 6110
7:30 | 295 | 4734 | 1665.5 | 6399.5
8:00 | 316 | 4920 | 1769 | 6689
8:30 | 173 | 5021 | 1847.5 | 6868.5
9:00 | 30 | 5122 | 1926 | 7048
9:30 | 17 | 5088.5 | 1910.5 | 6999
10:00 | 4 | 5055 | 1895 | 6950
10:30 | 80.5 | 5112.5 | 2003 | 7115.5
11:00 | 157 | 5170 | 2111 | 7281
11:30 | 100.5 | 5256.5 | 2129.5 | 7386
12:00 | 44 | 5343 | 2148 | 7491
12:30 | 57 | 5453 | 2155 | 7608
13:00 | 70 | 5563 | 2162 | 7725
13:30 | 43.5 | 5505 | 2114 | 7619
14:00 | 17 | 5447 | 2066 | 7513
14:30 | 81.5 | 5316 | 2041 | 7357
15:00 | 146 | 5185 | 2016 | 7201
15:30 | 141.5 | 5200 | 2010.5 | 7210.5
16:00 | 137 | 5215 | 2005 | 7220
16:30 | 87.5 | 5310.5 | 2035 | 7345.5
17:00 | 38 | 5406 | 2065 | 7471
17:30 | 60 | 5771.5 | 2402.5 | 8174
18:00 | 82 | 6137 | 2740 | 8877
18:30 | 49.5 | 6047.5 | 2855 | 8902.5
19:00 | 17 | 5958 | 2970 | 8928
19:30 | 70 | 5947 | 2913 | 8860
20:00 | 28 | 5902 | 2840 | 8742 |  |  |  | Executive Engineer
20:30 | 41.5 | 5769 | 2787 | 8556 |  |  |  | Network Operation Division
21:00 | 55 | 5636 | 2734 | 8370
21:30 | 73.5 | 5539 | 2647.5 | 8186.5
22:00 | 92 | 5442 | 2561 | 8003 |  |  |  |  | Page 6 of 7
22:30 | 48.5 | 5295 | 2387 | 7682
23:00 | 5 | 5148 | 2213 | 7361
23:30 | 10 | 5006 | 2117 | 7123
24:00 | 15 | 4864 | 2021 | 6885
8928 MW (19:00 )
7491 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-03 |  | Energy | 171933680
[10 empty] | 2020-12-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2576 | 445 | 1978 | 1361 | 595 | 93 | 43 | 0 | 94
0:30 | 2502.5 | 365.5 | 1800.5 | 1239 | 592 | 93 | 60.5 | 0 | 88 | Date: | 2020-12-03
1:00 | 2429 | 286 | 1623 | 1117 | 589 | 93 | 78 | 0 | 82
1:30 | 2421.5 | 270.5 | 1659 | 1016 | 543 | 92 | 78 | 0 | 81 | [7 empty] | Total Energy | 171.9337 | Total Energy Gen 171.934 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.934 MKWHr
2:00 | 2414 | 255 | 1695 | 915 | 497 | 91 | 78 | 0 | 80 | [7 empty] | Energy not Served | 0
2:30 | 2408.5 | 326.5 | 1724 | 819.5 | 492.5 | 90 | 39 | 0 | 80 | [7 empty] | Energy Requirement | 171.9337
3:00 | 2403 | 398 | 1753 | 724 | 488 | 89 | 0 | 0 | 80
3:30 | 2402.5 | 372 | 1734.5 | 692.5 | 488 | 87.5 | 0 | 0 | 79 | [6 empty] | Shortage
4:00 | 2402 | 346 | 1716 | 661 | 488 | 86 | 0 | 0 | 78
4:30 | 2400 | 346 | 1715 | 636.5 | 488 | 85.5 | 0 | 0 | 78
5:00 | 2398 | 346 | 1714 | 612 | 488 | 85 | 0 | 0 | 78
5:30 | 2433 | 346 | 1758.5 | 623.5 | 499.5 | 85.5 | 0 | 0 | 76
6:00 | 2468 | 346 | 1803 | 635 | 511 | 86 | 0 | 0 | 74
6:30 | 2493 | 346 | 1812.5 | 722 | 482.5 | 87 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 2518 | 346 | 1822 | 809 | 454 | 88 | 0 | 0 | 70
7:30 | 2556 | 346 | 1874 | 983 | 471 | 88.5 | 0 | 0 | 70 |  |  |  | Oil |  |  |  | ,
8:00 | 2594 | 346 | 1926 | 1157 | 488 | 89 | 0 | 0 | 70
8:30 | 2578.5 | 346 | 1933.5 | 1298.5 | 523 | 89 | 0 | 0 | 70
9:00 | 2563 | 346 | 1941 | 1440 | 558 | 89 | 0 | 0 | 70
9:30 | 2521 | 346 | 1917.5 | 1467 | 543 | 90 | 0 | 0 | 67
10:00 | 2479 | 346 | 1894 | 1494 | 528 | 91 | 0 | 0 | 64
10:30 | 2505.5 | 421 | 1925 | 1511 | 538 | 91 | 0 | 0 | 65
11:00 | 2532 | 496 | 1956 | 1528 | 548 | 91 | 0 | 0 | 66
11:30 | 2512 | 472 | 1970 | 1640.5 | 570 | 90 | 0 | 0 | 67
12:00 | 2492 | 448 | 1984 | 1753 | 592 | 89 | 0 | 0 | 68
12:30 | 2458 | 420 | 1987 | 1908.5 | 602 | 89 | 15 | 0 | 67
13:00 | 2424 | 392 | 1990 | 2064 | 612 | 89 | 30 | 0 | 66
13:30 | 2424 | 392 | 1990 | 2064 | 612 | 89 | 30 | 0 | 66
14:00 | 2424 | 392 | 1990 | 2064 | 612 | 89 | 30 | 0 | 66
14:30 | 2413 | 392.5 | 1920.5 | 1907 | 593 | 88 | 38 | 0 | 66
15:00 | 2402 | 393 | 1851 | 1750 | 574 | 87 | 46 | 0 | 66
15:30 | 2462.5 | 393 | 1885 | 1686.5 | 563.5 | 87 | 41 | 0 | 70
16:00 | 2523 | 393 | 1919 | 1623 | 553 | 87 | 36 | 0 | 74
16:30 | 2480.5 | 393 | 1887 | 1774.5 | 513.5 | 86.5 | 119.5 | 0 | 85
17:00 | 2438 | 393 | 1855 | 1926 | 474 | 86 | 203 | 0 | 96
17:30 | 2460.5 | 576.5 | 1903.5 | 2290 | 514 | 85.5 | 245 | 0 | 99
18:00 | 2483 | 760 | 1952 | 2654 | 554 | 85 | 287 | 0 | 102
18:30 | 2484.5 | 760 | 1908.5 | 2611.5 | 654.5 | 85.5 | 287 | 0 | 111
19:00 | 2486 | 760 | 1865 | 2569 | 755 | 86 | 287 | 0 | 120
19:30 | 2546 | 761 | 1945 | 2361 | 754 | 86 | 287 | 0 | 120
20:00 | 2555 | 761 | 1904 | 2276 | 754 | 87 | 287 | 0 | 118
20:30 | 2578 | 760.5 | 1934 | 2094 | 709 | 87.5 | 279 | 0 | 114
21:00 | 2601 | 760 | 1964 | 1912 | 664 | 88 | 271 | 0 | 110
21:30 | 2602 | 760 | 1931 | 1781 | 664 | 89 | 253.5 | 0 | 106
22:00 | 2603 | 760 | 1898 | 1650 | 664 | 90 | 236 | 0 | 102
22:30 | 2597.5 | 667 | 1940 | 1505.5 | 629 | 91 | 153 | 0 | 99
23:00 | 2592 | 574 | 1982 | 1361 | 594 | 92 | 70 | 0 | 96
23:30 | 2584 | 509.5 | 1980 | 1361 | 594.5 | 92.5 | 56.5 | 0 | 95 | Max Temp. in Dhaka |  | 29.2° C
24:00 | 2576 | 445 | 1978 | 1361 | 595 | 93 | 43 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 171.934 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.934 MKWHr
Note on W13: Author:

## Generation
g | 2020-12-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 93 | 91 | 89 | 86 | 85 | 86 | 88 | 89 | 89 | 91 | 91 | 89 | 89 | 89 | 87 | 87 | 86 | 85 |  | 86 | 86 | 87 | 88 | 90 | 92 | 93 | 2080080
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 | 13 | 16 | 18 | 19 | 17 | 15 | 10 | 4 | 0 | [9 empty] | 119610
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 201 | 201 | 205 | 216 | 202 | 202 | 210 | 234 | 215 | 206 | 204 | 204 | 208 | 204 | 215 |  | 204 | 204 | 203 | 203 | 203 | 203 | 203 | 4909434
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 51 | 85 |  | 85 | 85 | 85 | 85 | 68 |  |  | 450810
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 15 | 45 | 81 | 95 | 95 | 174 | 195 | 145 | 95 | 130 | 290 |  | 300 | 300 | 300 | 195 | 145 | 45 |  | 2576835
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 13 | 112 | 112 | 112 | 112 | 128 | 128 | 128 | 128 | 128 | 78 | 68 |  | 68 | 45 | 45 | 45 | 45 | 45 | 45 | 1605818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 114 | 108 | 93 | 93 | 93 | 94 | 93 | 94 | 95 | 94 | 93 |  | 94 | 94 | 94 | 94 | 93 | 93 | 94 | 2593800
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2803500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4878073
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 140 | 140 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2434170
30 | Ashuganj TPP Unit- 5 | [19 empty] | 0 | 26 | 50 | 60 | 60 | 60 | 70 | 270486
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 621072
33 | Ashuganj 225 MW CCPP | 160 | 159 | 159 | 162 | 161 | 189 | 202 | 184 | 180 | 194 | 185 | 198 | 182 | 182 | 182 | 195 | 154 | 175 |  | 160 | 202 | 184 | 220 | 223 | 221 | 222 | 4517000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | [26 empty] | 87500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 35 | 35 | 49 | 51 | 53 | 54 | 54 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 506880
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 354 | 339 | 339 | 338 | 338 | 363 | 370 | 361 | 354 | 340 | 368 | 370 | 364 | 340 | 344 | 362 | 350 | 346 |  | 342 | 338 | 338 | 339 | 339 | 348 | 346 | 8566488
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 320 | 350 | 350 | 350 | 370 | 350 | 350 | 350 | 330 | 330 | 300 | 300 | 320 | 320 | 320 | 320 | 340 |  | 340 | 340 | 340 | 340 | 340 | 360 | 360 | 7264500
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 315 | 314 | 314 | 312 | 314 | 284 | 264 | 264 | 263 | 323 |  | 325 | 325 | 324 | 320 | 320 | 320 | 290 | 7268000
42 | RPCL 210MW CCPP | 111 | 111 | 110 | 110 | 110 | 110 | 110 | 113 | 110 | 109 | 105 | 105 | 104 | 88 | 88 | 105 | 107 | 108 |  | 110 | 110 | 110 | 109 | 110 | 110 | 110 | 2517760
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 10 | 21 | 28 | 35 | 35 | 32 | 25 | 16 | 5 | 0 | [9 empty] | 214380
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 976000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 523800
46 | Shajibazar 330 MW CCPP | 158 | 158 | 158 | 160 | 159 | 159 | 158 | 159 | 145 | 148 | 152 | 152 | 158 | 157 | 160 | 159 | 157 | 158 |  | 157 | 159 | 158 | 158 | 159 | 159 | 156 | 3620000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 35 | 35 | 32 | 32 | 20 | 20 | 35 | 35 | 20 |  | 36 | 35 | 36 | 36 | 36 | 20 | 20 | 763872
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 77 | 77 | 77 | 76 | 76 | 78 | 79 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 79 | 79 | 1878720
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [26 empty] | 6790
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 433000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 5 | 5 | 5 |  | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 157090
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 53 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1266000
56 | Shahjahanulla 25 MW PP | 16 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 15 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 352032
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 280 | 290 | 280 | 280 | 310 | 310 | 300 | 300 | 280 | 310 | 310 | 305 | 275 | 275 | 285 | 290 | 295 |  | 285 | 295 | 275 | 280 | 275 | 280 | 280 | 7224500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 |  |  | 17 | 17 | [8 empty] | 78059
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 483984
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 394272
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 415152
63 | Impoprt (Tripura) | 82 | 80 | 80 | 78 | 78 | 74 | 70 | 70 | 70 | 64 | 66 | 68 | 66 | 66 | 66 | 74 | 96 | 102 |  | 120 | 120 | 118 | 110 | 102 | 96 | 94 | 1961280
64 | Malancha, Ctg. EPZ (United) | 25 | 39 | 39 | 40 | 40 | 40 | 38 | 4 | 4 | 2 | 2 | 3 | 6 | 3 | 3 | 3 | 3 | 6 |  | 9 | 12 | 15 | 19 | 21 | 15 | 15 | 419040
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 462276
66 | Feni 11 MW PP (Doreen) | [26 empty] | 0
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 20 | 21 | 21 | 21 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 49360
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 31 | 31 | 9 | 9 | 9 | 9 | 3 | 10 | 10 | 10 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 539820
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 569700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 627900
73 | Ghorashal 108MW PP (Regent) | 51 | 53 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 54 | 51 |  | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 1226318
| Feni Lanka Power | [17 empty] | 17 | [8 empty] | 28500
| Chowmuhani 113 MW | [10 empty] | 15 | 26 | 26 | 26 | 26 | 26 | 26 | 48 |  | 26 | 26 | 26 |  |  |  |  | 347760
Manikgonj 162MW PP
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 0 | 7 | 7 | 10 | 30 | 30 | 7 | 7 | 12 | 80 |  | 100 | 100 | 100 | 60 | 45 |  |  | 554880
78 | Gazipur 52 MW PP | 8 | [15 empty] | 18 | 33 | [8 empty] | 62808
79 | Kodda 150MW PP | [16 empty] | 48 | 98 |  | 98 | 98 | 98 | 82 | 64 | 10 |  | 504960
80 | Jamalpur 95 MW PP(Powerpac) | 17 | [11 empty] | 9 | 24 | 24 | 24 | 24 | 54 |  | 60 | 60 | 60 | 54 | 60 | 60 |  | 529920
81 | Jangalia 52 MW PP (Lakdanavi) | [9 empty] | 6 | 8 | 8 | 25 | 25 | 25 | 8 | 8 | 40 |  | 16 | [6 empty] | 218693
| Gazipur 100 MW PP | [16 empty] | 20 | 35 | [8 empty] | 67272
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 3 | 2 | 1 | [10 empty] | 26641
| Jodiac Power | 54 | 54 | 38 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 45 | 54 | 54 | 54 | 54 | 54 | 35 | 991053
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [11 empty] | 1 | 23 | 30 | 15 | 15 | 16 | 28 |  | 48 | 49 | 48 |  |  | 7 | 15 | 325848
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 49 | 36 | 36 | 36 | 36 | 36 | 32 | 36 | 36 | 35 | 40 | 46 | 60 | 69 | 72 | 83 | 87 | 86 |  | 86 | 86 | 85 | 86 | 85 | 92 | 100 | 1491101
86 | Meghnaghat CCPP(Summit) | 135 | 140 | 140 | 135 | 130 | 145 | 148 | 145 | 140 | 140 | 142 | 145 | 140 | 132 | 130 | 145 | 123 | 146 |  | 126 | 140 | 133 | 140 | 130 | 145 | 135 | 3351476
87 | Meghnaghat 100 MW(IEL) | 100 | 78 | 60 | 60 | 34 | 18 | 50 | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2152320
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2169600
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1083960
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1240097
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 3 | 7 | 7 | 7 |  | 24 | 40
95 | Patenga 50MW PP (Baraka) | [12 empty] | 15 | [10 empty] | 1 | 31 | 50 | 107520
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 21 | 31 |  | 0 | [6 empty] | 73920
97 | katpotti 52 MW | [19 empty] | 10 | [6 empty] | 26544
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 3 | 15 | 15 | 15 | 28 | 48 | 55 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 |  |  |  |  | 327588
100 | Manikganj 55 MW PP (Northern) | 17 | [5 empty] | 17 | 35 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 895519
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 140 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 2929990
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 10000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 35 | 35 | 35 | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 |  |  | 17 | 1099800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 29 |  | 60 | 60 | 40 | 24 | 24 |  |  | 261600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 8 | 15 | 15 | 16 | 15 | 17 | 32 | 32 | 30 | 30 | 32 | 125 |  | 149 | 117 | 114 | 69 | 39 |  |  | 756860
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 60 |  |  |  |  | 15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1902720
116 | Chandpur 200MW (Desh energy) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 100 | 100 | 90 | 70 | 118 | 120 | 90 | 85 | 90 | 123 | 135 |  | 100 | 68 | 68 | 68 | 68 | 68 | 68 | 2370720
117 | Ashuganj 150MW PP (Midland) | 100 | 40 | [5 empty] | 25 | 102 | 137 | 142 | 142 | 142 | 142 | 100 | 105 | 135 | 150 |  | 150 | 150 | 150 | 150 | 150 | 100 | 50 | 2350181
118 | Bibiyana-III 400 MW CCPP | 237 | 237 | 237 | 237 | 237 | 237 | 236 | 237 | 237 | 238 | 239 | 238 | 238 | 238 | 238 | 239 | 238 | 238 |  | 238 | 238 | 239 | 238 | 238 | 238 | 237 | 5701000
| Jamalpur 115 MW PP (United) | 85 | 85 | 65 | 65 | 65 | 71 | 85 | 101 | 115 | 95 | 95 | 106 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 50 | 2464800
| Anwara 300 MW PP (United) | 162 | 162 | 125 | 70 | 70 | 70 | 138 | 230 | 233 | 198 | 198 | 198 | 198 | 198 | 198 | 180 | 161 | 179 |  | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 4074764
| Juldah unit-2 (Acorn) | [8 empty] | 20 | 30 | 30 | 80 | 90 | 90 | 38 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 783360
| Anlima Energy Ltd. | [11 empty] | 2 |  |  |  | 8 | 21 | [9 empty] | 25091
120 | Eastern Zone Total | 4669 | 4512 | 4345 | 4267 | 4213 | 4348 | 4548 | 4920 | 5122 | 5055 | 5170 | 5343 | 5563 | 5447 | 5185 | 5215 | 5406 | 6137 |  | 5958 | 5947 | 5902 | 5636 | 5442 | 5148 | 4864 | 123443627
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 14 | 32 |  | 66 | 32 | 16 | 16 |  |  |  | 148800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 6 | 17 | 17 | 17 | 17 | 17 | 35 | 70 | 90 | 70 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 35 | 35 | 1518240
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | [9 empty] | 10 | 10 | 10 | 9 | 7 | 11 | 17 | 35 | 17 |  | 8 | 8 | 8 | 35 | 23 | 36 | 36 | 257810
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [21 empty] | 16 | 16 |  |  |  | 29184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [9 empty] | 25 | 25 | 43 | 47 | 42 | 43 | 43 | 44 | 81 |  | 86 | 85 | 88 | 87 | 89 | 57 | 56 | 855098
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 17 | 23 | 21 | 20 | 20 | 21 | 20 | 18 | 17 | 15 | 16 | 15 | 18 | 19 | 17 | 18 | 17 | 20 |  | 26 | 26 | 27 | 27 | 24 | 25 | 24 | 473900
141 | Noapara 100 MW PP (Bangla Trac) | 14 | [25 empty] | 53760
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 16 | 16 | 16 | [11 empty] | 16 |  | 40 | [6 empty] | 153375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 286 | 255 | 398 | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 496 | 448 | 392 | 392 | 393 | 393 | 393 | 760 |  | 760 | 761 | 761 | 760 | 760 | 574 | 445 | 10676364
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 360 | 270 | 260 | 260 | 260 | 300 | 320 | 400 | 470 | 440 | 460 | 500 | 520 | 520 | 480 | 460 | 380 | 460 |  | 660 | 660 | 660 | 570 | 570 | 500 | 500 | 10641900
149
150 | Barapukuria TPP Unit-1 | 89 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 92 | 92 | 93 | 94 | 93 | 94 | 94 |  | 95 | 94 | 94 | 94 | 94 | 94 | 95 | 2167854
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 140 | 140 | 140 | 123 | 46
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 134 | 130 | 130 | 130 | 130 | 130 | 133 | 176 | 188 | 133 | 148 | 109 | 43 | 72 | 138 | 174 | 153 | 172 |  | 175 | 173 | 174 | 175 | 174 | 166 | 163 | 3671273
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 155 | 162 | 157 | 156 | 156 | 169 | 175 | 208 | 199 | 178 | 172 | 179 | 201 | 171 | 153 | 173 | 168 | 183 |  | 188 | 185 | 187 | 187 | 186 | 172 | 163 | 4447564
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 295 | 305 | 333 | 307 | 305 | 335 | 372 | 426 | 400 | 400 | 423 | 426 | 424 | 339 | 332 | 381 | 341 | 340 |  | 301 | 392 | 365 | 393 | 344 | 426 | 434 | 8731218
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 499680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 217026
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | 8 | [25 empty] | 8160
170 | Chapainawabganj 100 MW Peaking PP | 78 | 78 | [10 empty] | 30 | 36 | 36 | 36 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 60 | 43 | 1002992
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 7 | 45 | 70 | 70 | 70 | 113 | 113 | 113 | 95 | 95 | 113 |  | 113 | 113 | 113 | 113 | 70 | 35 |  | 1454016
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 20 | 35 | 35 | 35 |  | 35 | 113 |  | 113 | 113 | 70 |  |  |  |  | 503616
173 | Rangpur 20 MW GTPP | [13 empty] | 7 | 10 | [11 empty] | 14000
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 50 | 90 | 102 | 114 | 113 | 96 | 38 |  | 72 | 113 |  | 113 | 45 | 35 | 34 |  |  |  | 933120
177 | Sympa Solar Power 8MW | [6 empty] | 0 |  | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 31103
178
178