## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-06 | Sunday
|  |  | Date (day): | 2020-12-06 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12154.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13453 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-05 | 2020-12-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 93 | 94 | 115 | 115 |  | 55
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 71 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 391 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 325 | 345 | 325 | 345
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 140 | 155 | 155 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 45 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 57 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 21 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 115 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 92 | 76 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 41 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2003 | 2667 | 3824 | 4134 | 498 | 1162
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 87 | 74 | 86 | 86 | 144 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 211 | 203 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 0 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 124 | 160 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 14 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 664 | 773 | 1497 | 1492 | 654 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 100 | 130 | 130
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 194 | 183 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 20 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 15 | 15 | 15 | 40 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 150 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 50 | 50
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 55 | 154 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 84 | 139 | 148
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 16 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 17 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 685 | 976 | 1461 | 1721 | 313 | 720
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 141 | 108 | 140 | 120 | 82 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20 |  | 2 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 24 | 95 | 95
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 92 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 68 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 22 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 260 | 359 | 621.6 | 550 | 82 | 2
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 153 | 158 | 158 |  | 172 | GT-1 under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 35 | 36 | 36 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 78 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 19 | 19 | 19 |  | 6 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 320 | 0 | 250
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 412 | 398 | 400 | 400 | 170
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1321 | 1379 | 1078 | 1328 | 170 | 442
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 455 | 693 | 549 | 693
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  |  | Engine problem
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 100 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maintenance
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 545 | 815 | 1084 | 1464 | 0 | 425
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 26 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 35 | 90 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 340 | 550 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 10 | 24 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 400 | 706 | 867 | 927 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 70 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 154 | 196 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 209 | 225 | 225 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 364 | 425 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 70 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 789 | 1225 | 1506 | 1629 | 271 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 93 | 93 | 95 | 95
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 105 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 97 | 198 | 216 | 208 | 85 | 314
|  | Total |  |  |  |  | 20383 | 19892 | 6764 | 9098 | 12154.6 | 13453 | 2073 | 3357
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6355.0969 | 8548 | 11419.8198 | 12639.7279
| A. |  | 2020-12-05 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9098 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5281 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9098 | MW
| 3 | Day peak Generation : |  |  | 6764 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8548 | MW
| 4 | Evening peak Generation : |  |  | 9098 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 165.2378 | MKWHr | By Solar | 0.22906 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 114.9658 | MKWHr |  | By Oil: | 24.6279 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.0778 | MKWHr |  | By Hydro: | 1.8709 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2073 | MW | Dhaka | 3109 | 3109 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3357 | MW | Chittagong | 1003 | 1003 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5430 | MW | Khulna | 1051 | 1051 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 937.62 | MMCFD |  |  | Rajshahi | 845 | 845 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 131654424.944 | ii) Oil : | Taka | 173426945.3 | Comilla | 719 | 719 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 52302080.27 | Total | Taka | 357383450.514 | Mymensingh | 674 | 674 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.54 | MKWHr. | Sylhet | 317 | 317 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -32 | MW (E to W) at | 19:00 | hrs | Barisal | 243 | 243 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -355 | MW at | 7:00 | hrs | Rangpur | 587 | 587 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.7° C |  |  | Total | 8548 | 8548 |  | 0
| B. |  | 2020-12-06 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 27.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13453 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4253 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 167.0903 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5622 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.7258 | MKWHr. | ii) HVDC Flow at Peak Time |  | 693 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7405 | MKWHr. | iii) Maximum HVDC Flow : |  | 693 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.86 |  | (b) Today: | 99.7 |  | (c) Rule Curve: |  | 105.64
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 339 | 320 |  | 0 | 400 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 22 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 70 | 164 | 0 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 159 | 36 | 80 | 0 | 0 | 18 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 14 | 0 | 170 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 30 | 0 | 0 |  | 4367 | 1608 | 5975 | 2828 | 409 | 1987 | 196 | 395 | 90 | 0 | 70 | 0 | 0 | 99.88
2:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 341 | 320 |  | 0 | 400 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 80 | 80 | 0 | 0 | 194 | 26 | 0 | 26 | 55 | 0 | 5 | 0 | 0 | 0 | 18 | 0 | 28 | 18 | 68 | 164 | 0 | 20 | 0 | 60 | 30 | 5 | 5 | 163 | 157 | 20 | 5 | 0 | 0 | 18 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 161 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4023 | 1515 | 5538 | 2736 | 408 | 1747 | 145 | 344 | 90 | 0 | 68 | 0 | 0 | 99.88
3:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 357 | 320 |  | 0 | 400 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 80 | 80 | 0 | 0 | 184 | 26 | 0 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 66 | 165 | 0 | 0 | 0 | 60 | 30 | 5 | 5 | 163 | 158 | 20 | 5 | 0 | 0 | 19 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 170 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 3906 | 1531 | 5437 | 2686 | 408 | 1709 | 135 | 345 | 88 | 0 | 66 | 0 | 0 | 99.87
4:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 354 | 300 |  | 0 | 400 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 80 | 80 | 0 | 0 | 196 | 26 | 0 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 66 | 165 | 0 | 0 | 0 | 60 | 30 | 5 | 5 | 163 | 158 | 20 | 5 | 0 | 0 | 19 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 169 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 3914 | 1432 | 5346 | 2708 | 311 | 1689 | 140 | 345 | 87 | 0 | 66 | 0 | 0 | 99.87
5:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 346 | 300 |  | 0 | 340 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 0 | 80 | 80 | 0 | 0 | 190 | 26 | 0 | 23 | 5 | 0 | 5 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 64 | 158 | 0 | 0 | 0 | 60 | 30 | 5 | 5 | 163 | 158 | 20 | 5 | 0 | 0 | 19 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 165 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 3856 | 1425 | 5281 | 2711 | 313 | 1622 | 140 | 345 | 86 | 0 | 64 | 0 | 0 | 99.86
6:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 359 | 300 |  | 0 | 340 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 23 | 0 | 80 | 80 | 0 | 0 | 195 | 26 | 0 | 23 | 5 | 0 | 30 | 0 | 0 | 0 | 18 | 5 | 25 | 15 | 66 | 160 | 0 | 20 | 0 | 60 | 30 | 50 | 29 | 130 | 160 | 36 | 40 | 0 | 0 | 19 | 0 | 0 | 310 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 |  | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 172 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4144 | 1458 | 5602 | 2825 | 312 | 1770 | 199 | 345 | 85 | 0 | 66 | 0 | 0 | 99.86
7:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 346 | 300 |  | 0 | 340 | 150 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 80 | 80 | 0 | 0 | 204 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 66 | 165 | 0 | 20 | 0 | 60 | 30 | 50 | 49 | 130 | 158 | 36 | 81 | 0 | 0 | 18 | 0 | 0 | 300 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 62 | 0 | 410 | 0 | 0 | 0 | 0 | 16 | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 2 | 0 | 0 |  | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 164 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 | 0 |  | 4408 | 1456 | 5864 | 2855 | 312 | 1854 | 347 | 344 | 83 | 0 | 66 | 3 | 0 | 99.85
8:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 355 | 320 |  | 0 | 340 | 135 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 54 | 12 | 0 | 0 | 25 | 28 | 25 | 25 | 7 | 0 | 85 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 70 | 164 | 0 | 20 | 0 | 60 | 30 | 50 | 47 | 130 | 159 | 36 | 78 | 0 | 0 | 18 | 0 | 0 | 280 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 20 | 68 | 5 | 410 | 0 | 0 | 0 | 1 | 66 | 54 | 0 | 0 | 0 | 0 | 0 | 78 | 8 | 0 | 0 |  | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 35 | 0 | 168 | 0 | 390 | 70 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 340 | 36 | 0 | 0 |  | 4609 | 1718 | 6327 | 2845 | 312 | 1894 | 669 | 435 | 85 | 0 | 70 | 17 | 0 | 99.85
9:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 338 | 324 |  | 0 | 340 | 130 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 18 | 25 | 17 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 60 | 165 | 0 | 20 | 0 | 60 | 30 | 50 | 50 | 130 | 159 | 36 | 78 | 0 | 0 | 18 | 0 | 0 | 280 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 50 | 68 | 10 | 410 | 0 | 0 | 0 | 2 | 107 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 35 | 0 | 164 | 0 | 400 | 70 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 340 | 35 | 0 | 0 |  | 4803 | 1744 | 6547 | 2844 | 313 | 1910 | 874 | 437 | 86 | 0 | 60 | 23 | 0 | 99.84
10:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 338 | 324 |  | 0 | 340 | 130 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 12 | 25 | 17 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 19 | 58 | 162 | 0 | 20 | 1 | 60 | 30 | 50 | 50 | 130 | 157 | 35 | 77 | 0 | 0 | 18 | 0 | 0 | 260 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 100 | 50 | 10 | 410 | 35 | 0 | 0 | 3 | 124 | 54 | 0 | 0 | 0 | 0 | 0 | 70 | 26 | 0 | 0 |  | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 34 | 0 | 161 | 0 | 341 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 340 | 37 | 0 | 0 |  | 4762 | 1624 | 6386 | 2805 | 312 | 1829 | 828 | 435 | 86 | 0 | 58 | 33 | 0 | 99.84
11:00 | 0 | 94 | 0 | 115 | 200 | 73 | 0 | 345 | 324 |  | 0 | 340 | 140 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 12 | 25 | 8 | 16 | 0 | 81 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 196 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 64 | 161 | 0 | 20 | 1 | 60 | 30 | 50 | 50 | 130 | 159 | 35 | 77 | 0 | 0 | 18 | 0 | 0 | 290 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 100 | 50 | 10 | 412 | 35 | 0 | 0 | 4 | 125 | 54 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 15 |  | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 35 | 0 | 167 | 0 | 363 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 340 | 10 | 0 | 0 |  | 4789 | 1752 | 6541 | 2849 | 456 | 1863 | 763 | 435 | 81 | 0 | 64 | 30 | 0 | 99.83
12:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 352 | 325 |  | 0 | 340 | 140 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 45 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 12 | 25 | 8 | 16 | 0 | 87 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 194 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 70 | 141 | 0 | 20 | 2 | 60 | 30 | 50 | 47 | 130 | 159 | 34 | 77 | 0 | 0 | 18 | 0 | 0 | 290 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 92 | 0 | 100 | 55 | 10 | 412 | 68 | 0 | 0 | 4 | 124 | 54 | 0 | 0 | 0 | 20 | 0 | 41 | 22 | 0 | 14 |  | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 35 | 0 | 171 | 0 | 364 | 90 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 340 | 10 | 0 | 0 |  | 4933 | 1831 | 6764 | 2820 | 455 | 1860 | 1007 | 433 | 87 | 0 | 70 | 32 | 0 | 99.83
13:00 | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 352 | 324 |  | 0 | 400 | 100 | 7 | 0 | 14 | 0 | 0 | 0 | 0 | 7 | 0 | 58 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 12 | 25 | 17 | 16 | 0 | 78 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 35 | 17 | 5 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 76 | 102 | 0 | 17 | 1 | 60 | 30 | 50 | 47 | 163 | 152 | 35 | 76 | 0 | 0 | 18 | 0 | 0 | 275 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 121 | 0 | 70 | 68 | 0 | 389 | 85 | 0 | 0 | 3 | 124 | 54 | 0 | 0 | 14 | 50 | 0 | 90 | 26 | 0 | 2 |  | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 33 | 0 | 201 | 0 | 330 | 90 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 340 | 36 | 0 | 0 |  | 5076 | 1876 | 6952 | 2791 | 456 | 1929 | 1137 | 434 | 78 | 17 | 76 | 34 | 6952 | 99.82
14:00 | 0 | 93 | 0 | 115 | 200 | 73 | 0 | 340 | 313 |  | 0 | 360 | 140 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 70 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 12 | 25 | 17 | 16 | 0 | 78 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 37 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 183 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 76 | 103 | 0 | 20 | 1 | 60 | 30 | 50 | 50 | 140 | 154 | 34 | 76 | 0 | 0 | 18 | 0 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 120 | 0 | 70 | 50 | 0 | 389 | 55 | 0 | 0 | 3 | 124 | 54 | 0 | 0 | 17 | 20 | 0 | 90 | 17 | 0 | 0 |  | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 34 | 0 | 166 | 0 | 350 | 90 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 340 | 10 | 0 | 0 |  | 4964 | 1822 | 6786 | 2739 | 456 | 1850 | 1114 | 433 | 78 | 17 | 76 | 23 | 0 | 99.82
15:00 | 0 | 94 | 0 | 115 | 200 | 73 | 0 | 340 | 319 |  | 0 | 360 | 140 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 12 | 25 | 17 | 16 | 0 | 89 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 38 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 76 | 103 | 0 | 20 | 1 | 60 | 30 | 50 | 47 | 140 | 153 | 34 | 76 | 0 | 0 | 18 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 115 | 0 | 70 | 50 | 0 | 351 | 55 | 0 | 0 | 2 | 125 | 54 | 0 | 0 | 17 | 20 | 0 | 90 | 15 | 0 | 0 |  | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 34 | 0 | 161 | 0 | 356 | 53 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 340 | 7 | 0 | 0 |  | 4945 | 1762 | 6707 | 2676 | 457 | 1875 | 1067 | 431 | 89 | 17 | 76 | 19 | 0 | 99.81
16:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 348 | 319 |  | 0 | 360 | 150 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 12 | 25 | 17 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 44 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 219 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 74 | 105 | 0 | 17 | 0 | 60 | 30 | 50 | 49 | 140 | 151 | 34 | 76 | 0 | 0 | 18 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 106 | 0 | 70 | 16 | 0 | 351 | 32 | 0 | 0 | 1 | 125 | 54 | 0 | 0 | 17 | 10 | 0 | 57 | 5 | 0 | 8 |  | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 34 | 0 | 166 | 0 | 406 | 53 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 340 | 10 | 0 | 0 |  | 4805 | 1826 | 6631 | 2730 | 456 | 1927 | 907 | 434 | 79 | 17 | 74 | 7 | 0 | 99.81
17:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 380 | 333 |  | 0 | 400 | 140 | 16 | 2 | 15 | 0 | 0 | 0 | 2 | 0 | 10 | 50 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 12 | 25 | 17 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 45 | 20 | 10 | 0 | 80 | 80 | 0 | 0 | 182 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 80 | 105 | 0 | 20 | 0 | 60 | 30 | 50 | 49 | 163 | 152 | 34 | 76 | 0 | 0 | 18 | 0 | 0 | 320 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 95 | 0 | 90 | 32 | 16 | 351 | 48 | 0 | 0 | 0 | 140 | 54 | 0 | 0 | 17 | 44 | 0 | 53 | 0 | 0 | 10 |  | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 52 | 0 | 194 | 0 | 406 | 53 | 0 | 27 | 0 | 82 | 0 | 0 | 0 | 380 | 36 | 0 | 0 |  | 5079 | 2074 | 7153 | 2774 | 456 | 2092 | 1177 | 473 | 67 | 34 | 80 | 0 | 0 | 99.8
18:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 378 | 333 |  | 0 | 420 | 150 | 81 | 15 | 30 | 0 | 0 | 0 | 16 | 0 | 48 | 90 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 12 | 25 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 45 | 20 | 16 | 0 | 100 | 80 | 0 | 0 | 216 | 26 | 0 | 23 | 15 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 92 | 107 | 11 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 152 | 35 | 78 | 0 | 0 | 18 | 0 | 0 | 310 | 19 | 0 | 0 | 60 | 0 | 0 | 10 | 0 | 56 | 0 | 100 | 118 | 137 | 399 | 115 | 0 | 0 | 0 | 156 | 54 | 0 | 0 | 17 | 100 | 0 | 86 | 0 | 0 | 0 |  | 692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 79 | 0 | 205 | 0 | 427 | 90 | 0 | 102 | 0 | 96 | 0 | 0 | 0 | 550 | 13 | 0 | 0 |  | 5866 | 2744 | 8610 | 2930 | 692 | 2150 | 1893 | 643 | 75 | 135 | 92 | 0 | 0 | 99.79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 391 | 345 |  | 0 | 420 | 140 | 100 | 15 | 30 | 0 | 0 | 0 | 57 | 0 | 64 | 100 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 25 | 21 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 0 | 15 | 0 | 100 | 80 | 0 | 0 | 183 | 26 | 0 | 20 | 15 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 84 | 108 | 24 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 153 | 35 | 78 | 0 | 0 | 18 | 0 | 0 | 320 | 19 | 5 | 0 | 115 | 0 | 0 | 92 | 0 | 76 | 0 | 100 | 154 | 150 | 398 | 115 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 90 | 0 | 209 | 0 | 425 | 90 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 550 | 24 | 0 | 0 |  | 6154 | 2944 | 9098 | 2916 | 693 | 2191 | 2346 | 643 | 74 | 151 | 84 | 0 | 0 | 99.76
19:30 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 339 | 345 |  | 0 | 420 | 130 | 100 | 0 | 55 | 0 | 0 | 0 | 40 | 0 | 64 | 100 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 25 | 24 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 24 | 0 | 100 | 80 | 0 | 0 | 182 | 26 | 0 | 20 | 15 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 88 | 108 | 25 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 153 | 36 | 78 | 0 | 0 | 18 | 0 | 0 | 285 | 19 | 5 | 0 | 145 | 0 | 0 | 80 | 0 | 76 | 0 | 100 | 150 | 150 | 398 | 95 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 92 | 0 | 187 | 0 | 416 | 90 | 0 | 113 | 0 | 86 | 0 | 0 | 109 | 550 | 24 | 0 | 0 |  | 6065 | 2871 | 8936 | 2838 | 693 | 2159 | 2289 | 644 | 74 | 151 | 88 | 0 | 0 | 0
20:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 342 | 324 |  | 0 | 420 | 145 | 100 | 0 | 55 | 0 | 0 | 0 | 45 | 0 | 64 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 28 | 25 | 24 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 27 | 0 | 100 | 80 | 0 | 0 | 190 | 26 | 0 | 20 | 15 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 88 | 108 | 25 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 152 | 35 | 78 | 0 | 0 | 18 | 0 | 0 | 290 | 19 | 5 | 0 | 145 | 0 | 0 | 80 | 0 | 91 | 0 | 100 | 120 | 150 | 398 | 95 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 0 | 0 |  | 692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 92 | 0 | 191 | 0 | 435 | 90 | 0 | 113 | 0 | 60 | 0 | 0 | 50 | 550 | 27 | 0 | 0 |  | 6051 | 2770 | 8821 | 2858 | 692 | 2168 | 2145 | 644 | 75 | 151 | 88 | 0 | 0 | 99.77
21:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 344 | 324 |  | 0 | 420 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 30 | 0 | 48 | 88 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 27 | 0 | 100 | 80 | 0 | 0 | 196 | 26 | 0 | 20 | 15 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 84 | 107 | 16 | 20 | 0 | 60 | 30 | 47 | 50 | 163 | 151 | 35 | 78 | 0 | 0 | 18 | 0 | 0 | 295 | 19 | 5 | 0 | 80 | 0 | 0 | 24 | 0 | 22 | 0 | 100 | 120 | 150 | 399 | 95 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 100 | 0 | 90 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 92 | 0 | 193 | 0 | 434 | 90 | 0 | 113 | 0 | 56 | 0 | 0 | 0 | 550 | 37 | 0 | 0 |  | 5777 | 2734 | 8511 | 2883 | 693 | 2171 | 1843 | 644 | 75 | 118 | 84 | 0 | 0 | 99.76
22:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 339 | 324 |  | 0 | 420 | 138 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 86 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 27 | 0 | 100 | 80 | 0 | 0 | 182 | 26 | 0 | 20 | 15 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 80 | 108 | 17 | 20 | 0 | 60 | 30 | 53 | 50 | 163 | 152 | 36 | 79 | 0 | 0 | 18 | 0 | 0 | 285 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 120 | 80 | 399 | 95 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 60 | 0 | 90 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 92 | 0 | 189 | 0 | 405 | 90 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 550 | 37 | 0 | 0 |  | 5355 | 2543 | 7898 | 2836 | 693 | 2138 | 1362 | 644 | 77 | 68 | 80 | 0 | 0 | 99.75
23:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 339 | 324 |  | 0 | 420 | 145 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 16 | 0 | 100 | 80 | 0 | 0 | 184 | 26 | 0 | 23 | 15 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 72 | 128 | 8 | 20 | 0 | 60 | 30 | 53 | 50 | 163 | 152 | 35 | 79 | 0 | 0 | 18 | 0 | 0 | 280 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 120 | 80 | 399 | 65 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 10 | 0 | 90 | 0 | 0 | 0 |  | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 92 | 0 | 186 | 0 | 430 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 5246 | 2125 | 7371 | 2873 | 409 | 2146 | 1215 | 542 | 78 | 36 | 72 | 0 | 0 | 99.74
24:00 | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 349 | 324 |  | 0 | 420 | 142 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 33 | 20 | 25 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 17 | 30 | 0 | 100 | 80 | 0 | 0 | 194 | 26 | 0 | 20 | 15 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 68 | 129 | 0 | 20 | 0 | 60 | 30 | 53 | 50 | 120 | 152 | 35 | 79 | 0 | 0 | 18 | 0 | 0 | 290 | 19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 120 | 10 | 399 | 25 | 0 | 0 | 0 | 126 | 54 | 0 | 0 | 0 | 10 | 0 | 90 | 0 | 0 | 0 |  | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 58 | 0 | 186 | 0 | 400 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 38 | 0 | 0 |  | 4942 | 1947 | 6889 | 2858 | 411 | 2063 | 908 | 502 | 79 | 0 | 68 | 0 | 0 | 99.73
KWH | 0 | 2416300 | 0 | 2803500 | 4775391 | 1700954 | 0 | 8556550 | 7690000 |  | 0 | 9016500 | 3347462 | 984960 | 43320 | 291922 | 0 | 0 | 0 | 172800 | 26496 | 285120 | 1209062 | 0 | 0 | 0 | 877680 | 616443 | 54806 | 271548 | 600000 | 547020 | 599800 | 519600 | 125496 | 0 | 1870915 | 0 | 0 | 0 | 0 | 4916690 | 0 | 0 | 0 |  | 0 | 0 | 137863 | 0 | 0 | 595680 | 417840 | 269760 | 0 | 2097740 | 1933474 | 0 | 0 | 4624000 | 669090 | 0 | 507312 | 341760 | 0 | 1050728 | 0 | 0 | 170678 | 390456 | 123480 | 682500 | 515750 | 1740480 | 3185040 | 109440 | 376200 | 7500 | 1434000 | 716760 | 1051800 | 1029960 | 3735409 | 3544000 | 781536 | 1537920 | 0 | 0 | 434000 | 0 | 0 | 7287700 | 390240 | 75500 | 0 | 491782 | 0 | 0 | 297600 | 0 | 1156320 | 12285 | 1403520 | 1533600 | 955127 | 9326000 | 1092000 | 0 | 0 | 23521 | 2263200 | 1038554 | 0 | 0 | 359520 | 669120 | 0 | 1366080 | 162200 | 0 | 53945 |  | 10725818 | 0 | 0 | 0 | 42240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421400 | 36480 | 0 | 0 | 1545000 | 0 | 0 | 376560 | 0 | 0 | 0 | 0 | 0 | 417760 | 0 | 202572 | 2238109 | 0 | 0 | 0 | 0 | 0 | 0 | 4162091 | 0 | 985286 | 0 | 4489164 | 0 | 9101727 | 1226880 | 0 | 618240 | 0 | 389760 | 0 | 23552 | 208128 | 8839700 | 696990 | 0 | 0 |  | 118490305 | 46747457 | 165237762 | 67961054 | 10725818 | 47004744 | 23828341 | 11077809 | 1870915 | 799543 | 1740480 | 229058 | 0
Fuel Cost | 0 | 3576124 | 0 | 4121145 | 5300684.01 | 2245259.28 | 0 | 8642115.5 | 7920700 |  | 0 | 9827985 | 3715682.82 | 7475846.4 | 298474.8 | 2469660.12 | 0 | 0 | 0 | 1301184 | 241643.52 | 2805580.8 | 11147551.64 | 0 | 0 | 0 | 6407064 | 4765104.39 | 540387.16 | 203661 | 450000 | 0 | 0 | 0 | 1213546.32 | 0 | 505147.05 | 0 | 0 | 0 | 0 | 5359192.1 | 0 | 0 | 0 |  | 0 | 0 | 1337271.1 | 0 | 0 | 4717785.6 | 526478.4 | 801187.2 | 0 | 3104655.2 | 2842206.78 | 0 | 0 | 4254080 | 863126.1 | 0 | 573262.56 | 478464 | 0 | 1796744.88 | 0 | 0 | 1629974.9 | 495879.12 | 92610 | 1194375 | 386812.5 | 13053600 | 3376142.4 | 993715.2 | 477774 | 119550 | 2351760 | 1146816 | 1872204 | 1606737.6 | 4258366.26 | 3685760 | 1539625.92 | 2937427.2 | 0 | 0 | 950460 | 0 | 0 | 7360577 | 292680 | 57380 | 0 | 3717871.92 | 0 | 0 | 1547520 | 0 | 11378188.8 | 143611.65 | 11438688 | 16639560 | 6733645.35 | 8673180 | 9959040 | 0 | 0 | 0 | 17109792 | 9045805.34 | 0 | 0 | 3081086.4 | 4456339.2 | 0 | 0 | 0 | 0 | 0 |  | 61780711.68 | 0 | 0 | 0 | 332006.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653170 | 356044.8 | 0 | 0 | 3167250 | 0 | 0 | 3332556 | 0 | 0 | 0 | 0 | 0 | 802099.2 | 0 | 153347.004 | 13495797.27 | 0 | 0 | 0 | 0 | 0 | 0 | 5493960.12 | 0 | 1477929 | 0 | 5252321.88 | 0 | 9010709.73 | 12808627.2 | 0 | 5867097.6 | 0 | 3024537.6 | 0 | 260249.6 | 1538065.92 | 38806283 | 0 | 0 | 0 |  | 265633556.49 | 167612764.004 | 433246320.494 | 77741738.494 | 61780711.68 | 53912686.45 | 165951537.4 | 52302080.27 | 505147.05 | 7475407.9 | 13053600 | 523411.25 | 0
Yesterday Day Peak | 0 | 93 | 0 | 115 | 200 | 71 | 0 | 352 | 325 |  | 0 | 340 | 140 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 45 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 12 | 25 | 8 | 16 | 0 | 87 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 17 | 2 | 0 | 80 | 80 | 0 | 0 | 194 | 26 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 19 | 70 | 141 | 0 | 20 | 2 | 60 | 30 | 50 | 47 | 130 | 159 | 34 | 77 | 0 | 0 | 18 | 0 | 0 | 290 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 92 | 0 | 100 | 55 | 10 | 412 | 68 | 0 | 0 | 4 | 124 | 54 | 0 | 0 | 0 | 20 | 0 | 41 | 22 | 0 | 14 |  | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 35 | 0 | 171 | 0 | 364 | 90 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 340 | 10 | 0 | 0 |  | 6764 | DayPeak
Yesterday Evening Peak | 0 | 94 | 0 | 115 | 200 | 71 | 0 | 391 | 345 | 0 | 0 | 420 | 140 | 100 | 15 | 30 | 0 | 0 | 0 | 57 | 0 | 64 | 100 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 25 | 21 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 50 | 0 | 15 | 0 | 100 | 80 | 0 | 0 | 183 | 26 | 0 | 20 | 15 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 84 | 108 | 24 | 20 | 0 | 60 | 30 | 50 | 50 | 163 | 153 | 35 | 78 | 0 | 0 | 18 | 0 | 0 | 320 | 19 | 5 | 0 | 115 | 0 | 0 | 92 | 0 | 76 | 0 | 100 | 154 | 150 | 398 | 115 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 17 | 100 | 0 | 90 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 90 | 0 | 209 | 0 | 425 | 90 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 550 | 24 | 0 | 0 |  | 9098 | EvPeak
Forecast for Evening | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 345 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 86 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 |  | 130 | 80 | 0 | 0 | 225 | 26 | 50 | 30 | 15 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 148 | 120 | 95 | 20 | 0 | 60 | 30 | 51 | 44 | 163 | 158 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 250 | 19 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 0 |  |  | 693 | 16 | 0 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 115 | 0 | 115 | 200 | 100 | 0 | 412 | 325 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 25 | 52 | 0 | 86 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 |  | 130 | 80 | 0 | 0 | 225 | 26 | 50 | 30 | 15 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 139 | 140 | 95 | 20 | 1.6 | 60 | 30 | 51 | 44 | 163 | 158 | 36 | 86 | 0 | 0 | 20 | 0 | 0 | 0 | 19 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 0 |  |  | 549 | 0 | 0 | 0 | 115 | 100 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 92 | 0 | 115 | 200 | 71 | 0 | 369 | 320 | 0 | 0 | 450 | 135 |  | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 66 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 28 | 17 |  | 16 | 0 | 73 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 5 | 0 | 140 | 80 | 0 | 0 | 181 | 26 | 0 | 20 | 15 | 0 | 51 | 0 | 0 | 1 | 18 | 5 | 33 | 18 | 64 | 143 | 0 | 20 | 0 | 60 | 30 | 50 | 47 | 163 | 152 | 36 | 76 | 0 | 0 | 18 | 0 | 0 | 0 | 17 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 11 | 7 | 100 | 54 | 21 | 397 | 48 | 0 | 0 | 1 | 151 | 54 | 0 | 0 | 0 | 50 | 0 | 21 | 5 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 23 | 0 | 196 | 0 | 367 | 72 | 0 | 16 | 0 | 0 | 0 | 1 | 109 | 450 | 11 | 0 | 0 | 0
199
| Minimum Generation |  | 5281 | 5:00
| Highest Generation |  | 9098 | 19:00
| Day Peak Generation |  | 6764 | 12:00
| Evening Peak Generation |  | 9098 | 19:00
| HVDC Max Flow |  | 693 | 19:00
| HVDC EvPeak Flow |  | 693 | 19:00
| Load factor L.F |  | 75.67%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6764 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5622 | MW
Evening Peak Generation : |  | 9098 | MW Hour : | 19:00 | Available Max Generation : |  | 13453 | MW
E.P. Demand (at gen end) : |  | 9098 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9098 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4253 | MW
Total Gen. (MKWH) : |  | 165.2378 | System Load Factor : | 75.67% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -355 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-06
Actual : | 99.7 | Ft.(MSL) , | Rule curve : | 105.64 | Ft.( MSL )
Gas Consumed : | Total = | 937.62 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 131654424.944
: |  | Coal : | 52302080.27 | Oil : | 173426945.3 | Total : | 357383450.514
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3229.4471 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1092.9816 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 978.3471 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 883.6896 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 798.7592 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 644.5573 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 367.108 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 166.1336 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 497.0825 |  |  | 0 | 0%
Total | 0 |  | 8658.1061 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71,100 MW
3) Ghorasal Unit-1,2,4
4) Ashuganj unit-3
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Sirajganj #1 CCPP STG
9)Ashuganj(S)-360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi 230/132 kV T01 transformer was under shut down from 08:12 to 13:56 for A/M.
b) Saver-Manikganj 132 kV Ckt-2 was under shut down from 09:05 to 17:14 for A/M.
c) Cumilla(N) 230/132 kV T02 transformer was under shut down from 08:48 to 16:53 for A/M.
d) Kabirpur-Tongi 132 kV Ckt-2 was under shut down from 08:18 to 16:19 for A/M.
e) Jamalpur-Mymensing 132 kV Ckt-1 was under shut down from 09:22 to 17:18 for A/M.
f) Norsingdi-Ghorasal 132 kV Ckt was under shut down from 09:02 to 17:12 for A/M.
g) BSRM-GPH Ispat 230 kV Ckt was under shut down from 09:00 to 15:31 for C/M.
h) Dohazari-Cox's Bazar 132 kV Ckt-2 was under shut down from 10:22 to 17:00 for D/W.
i) Saidpur-Barapukuria 132 kV Ckt-2 was under shut down from 08:36 to 15:27 for A/M.
j) Rajshahi 132/33 kV T3 transformer was under shut down from 07:56 to 17:22 for A/M.
k) Naogaon-Bogura 132 kV Ckt-2 was under shut down from 08:24 to 17:50 for A/M.
l) Barisal-Bhola 230 kV Ckt-2 was under shut down from 09:00 to 15:31 for C/M.
m) Khulna(S)-Khulna© 132 kV Ckt-2 was under shut down from 08:33 to 16:31 for A/M.
n) Rangpur 33 kV Bus-1 & 2 along with 132/33 kV T1 transformer were under shut down from 08:10 to 17:10
for C/M.
o) Shahjibazar 132/33 kV T3 transformer was under shut down from 08:10 to 17:47 for C/M.
p) Sonargaon 132/33 kV T2 transformer was under shut down from 12:11 to for C/M.
q) Ishurdi-Natore 132 kV Ckt-2 was switched on at 19:36.
r) Rajshahi(N)-HVDC Bheramara 230 kV Ckt-2 was switched on at 20:25 from Rajshahi end.
s) Bottail 132/33 kV T2 transformer was under shut down from 15:13 to 15:50 due to cable connection
at 33 kV end.
t) Sylhet-Fenchuganj P/P 132 kV Ckt was under shut down from 00:14 to 10:44(06-12-2020) due to
tripping of MCB at Sylhet.
u) Bheramara HVDC Pole-2 tripped at 04:24(06-12-2020) showing external protection trip and was switched
on at 10:54(06-12-2020).
v) Mymensing-Bhaluka 132 kV Ckt-1 tripped at 06:07(06-12-20200 showing Dist. Z1,R-phase,SOTF at both
end.
w) Kaliakoir-Bibiyana 400 kV Ckt-2 tripped at 07:07(06-12-20200 showing Dist. Z1,at Kaliakoir end and was
switched on at 07:75(06-12-2020).
x) Shympur(old)-Shympur(new) 132 kV Ckt-2 was shut down at 07:40 for D/W.
y) Summit Bibiyana-2 341 MW P/P tripped at 07:07 due to unit transformer of South Bibiyana-2 GT
got tripped showing line overload.
z) Cox'sbazar 132/33 kv T1 transformer was shut down at 07:13(06-12-2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 94 | 2416300 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2803500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4775391 | Machine problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1700954 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 8556550 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7690000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9016500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 984960
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3347462 | FGMO and GT-2 under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 43320 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 291922 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1209062
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 271548
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 57 | 172800 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 26496 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 877680 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 285120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 616443
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 54806 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1147020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 599800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 519600 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 125496 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 115 | 491782 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 76 | 1156320 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1366080 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 5895 | 2667 | 50546912
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 12285
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 595680
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 74 | 1870915 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4916690
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 137863 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1403520
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 417840 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 269760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23521
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 2263200 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1038554
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 669120
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 53945
| Chattogram area Total |  |  |  | 2266 | 773 | 13672893
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2097740 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4624000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 507312 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 15 | 341760 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 669090 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1050728
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 955127
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 154 | 1533600 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 390456 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 123480 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 84 | 1740480 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 682500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 170678 | High Voltage.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 515750
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 359520 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 976 | 17695695
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 3185040 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 376200
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 109440 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 92 | 297600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1092000 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 162200
| Mymensingh Area Total |  |  |  | 637 | 359 | 5229980
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1434000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 716760 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3735409
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 153 | 3544000 | Gas shortage
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1051800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1029960
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 75500
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 781536
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1537920 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 434000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 19 | 390240 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7287700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 398 | 9326000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1379 | 31344825
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 693 | 10725818 | Low demand
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 42240 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1226880 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 815 | 11994938
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 36480 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 421400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 90 | 985286
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 550 | 8839700 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 24 | 696990
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 706 | 10979856
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1545000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4162091 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 209 | 4489164 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 425 | 9101727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 417760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 202572
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 70 | 376560 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 618240
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 208128
| Rajshahi Area Total |  |  |  | 2183 | 1225 | 21121242
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 93 | 2238109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 389760
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23552
| Rangpur Area Total |  |  |  | 605 | 198 | 2651421
| Total |  |  |  | 19892 | 9098 | 165237762
| Eastern Grid Total |  |  |  | 13766 | 6154 | 118490305
| Western Grid Total |  |  |  | 6126 | 2944 | 46747457
| National Grid Total |  |  |  | 19892 | 9098 | 165237762
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-05
| (a) ENTIRE EASTERN GRID : |  | 5822 | MW | (b) ENTIRE WESTERN GRID : |  | 2726 | MW
| i) Dhaka area |  | 3109 | MW | i) Khulna area |  | 1051 | MW
| ii) Chittagong area |  | 1003 | MW | ii) Rajshahi area |  | 845 | MW
| iii) Comilla area |  | 719 | MW | iii) Barisal area |  | 243 | MW
| iv) Mymensingh area |  | 674 | MW | iv) Rangpur area |  | 587 | MW
| v) Sylhet area |  | 317 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8548 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 102 | 12:00 | Jamalpur | 87 | 19:00 | Benapol | 34 | 18:00
| Munsiganj | 82 | 19:00 | Sherpur | 84 | 18:30 | Jhenida | 77 | 18:00
| Sonargaon | 59 | 18:30 | Srimongal | 39 | 18:00 | Bottail | 96 | 18:30
| Shyampur | 162 | 12:00 | Shahjibazar | 78 | 18:30 | G.K Project | 34 | 18:00
| Bhulta | 145 | 18:30 | Fenchuganj | 24 | 18:00 | Faridpur | 130 | 18:30
| Madanganj | 53 | 18:30 | Kulawara | 30 | 18:00 | Madaripur | 61 | 20:00
| Shitalakhya | 104 | 12:00 | Sylhet | 71 | 18:00 | Sariatpur | 40 | 19:30
| Rahim steel | 7 | 10:00 | Chatak | 19 | 18:30 | Gopalganj | 59 | 18:00
| Matuail | 70 | 10:00 | Sunamganj | 28 | 18:00 | Bagerhat | 78 | 18:30
| Ghorasal | 60 | 19:00 | Biani Bazar | 38 | 18:30 | Mongla | 29 | 12:00
| Narsingdi | 119 | 20:00 | Comilla (S) | 92 | 18:00 | Satkhira | 78 | 18:30
| Haripur (SBU) | 95 | 9:00 | Comilla(N) | 83 | 19:30 | Gallamari | 21 | 13:00
| Ullon | 42 | 18:00 | Chandpur | 66 | 19:00 | Magura | 38 | 18:00
| Hasnabad | 138 | 20:00 | Feni | 70 | 22:00 | Norail | 28 | 18:30
| Magbazar | 67 | 14:00 | Chowmuhani | 116 | 19:00 | Chuadanga | 61 | 18:30
| Maniknagar | 64 | 18:00 | Ashuganj | 40 | 20:00 | Barisal(N) | 30 | 20:00
| Bangabhaban | 14 | 11:00 | Daudkandi | 90 | 20:00 | Barisal (S) | 68 | 18:30
| Narinda | 72 | 12:00 | B.Baria | 96 | 20:00 | Patuakhali | 83 | 20:00
| Dhanmondi | 93 | 12:00 | Ramganj | 66 | 19:00 | Bhandaria | 40 | 19:00
| Lalbag | 70 | 19:00 | Chaddagram | 26 | 18:00 | Borhan Uddin | 26 | 19:00
| Madartek | 48 | 18:30 | PHP | 5 | 19:00 | Ishurdi | 48 | 18:30
| Dhaka University |  |  | Madunaghat | 44 | 12:00 | Ruppur Paromanobik | 2 | 2:00
| Aftabnagar | 6 | 0.5 | Hathazari | 75 | 0.75 | Natore | 83 | 0.75
| Fatullah | 32 | 9:00 | Khulshi | 163 | 18:00 | Bogra | 118 | 18:00
| Mirpur | 76 | 18:00 | Halishahar | 131 | 12:00 | Noagaon | 81 | 19:30
| Kalyanpur | 63 | 19:00 | Baraulia | 160 | 12:00 | Rajshahi | 96 | 20:00
| Gulshan | 72 | 18:00 | Sikalbaha | 21 | 19:00 | Rajshahi New | 9 | 18:00
| Uttara | 65 | 18:00 | Dohazari | 52 | 18:00 | C.Nawabganj | 49 | 18:30
| Uttara New | 23 | 18:00 | Cox'sbazar | 79 | 18:00 | Amnura | 30 | 18:30
| Kamrangirchar | 72 | 13:00 | Chandraghona | 20 | 18:00 | Pabna | 78 | 19:30
| Savar | 103 | 18:00 | Kaptai | 3.2 | 18:00 | Shahjadpur | 71 | 18:00
| Bhasantec | 101 | 18:00 | A. Khaer Stl. | 9 | 11:00 | Serajganj | 58 | 18:00
| Agargaon | 45 | 18:30 | Bakulia | 72 | 18:00 | Niyamatpur | 38 | 19:00
| Satmosjid | 65 | 0.75 | Julda | 14 | 0.041667 | Joypurhat | 40 | 0.75
| Tongi | 93 | 11:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 42 | 18:00
| Kabirpur | 192 | 18:30 | Modern Steel | 15 | 10:00 | Mohastangor | 30 | 18:00
| Basundhara | 92 | 18:00 | Shahmirpur | 18 | 8:00 | Rangpur | 122 | 18:30
| Manikganj | 44 | 18:30 | Khagrachhari | 18 | 8:00 | Lalmonirhat | 44 | 18:00
| Joydevpur | 114 | 18:00 | Matarbari | 26 | 18:00 | Saidpur | 93 | 18:00
| New Tongi | 79 | 12:00 | Baroiar Hat | 24 | 18:30 | Purbasadipur | 80 | 18:00
| Kodda | 171 | 16:00 | Rangamati | 8 | 13:00 | Thakurgaon | 64 | 18:30
| Dhamrai | 58 | 18:00 | Abul Khair 230 | 141 | 11:00 | Palashbari | 76 | 19:30
| Rajendrapur | 74 | 18:00 | BSRM | 102 | 0:00 | Barapukuria | 40 | 19:00
| Valuka | 84 | 18:00 | GPH Ispat | 85 | 6:00 | Panchagar | 41 | 19:00
| Tangail | 136 | 18:00 | Goalpara | 16 | 20:00 | Joldhaka | 13 | 18:00
| Mymensing | 142 | 18:00 | Central s/s | 78 | 18:30 | Kurigram | 38 | 19:00
| Kishorganj | 80 | 19:00 | Noapara | 46 | 18:30
| Netrokona | 71 | 18:00 | Jessore | 76 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 19:00 | 406 | 10:00 | Kaliakoir | 388 | 0.25 | 377 | 0.45833
| Bheramara | 407 | 6:00 | 398 | 10:00 | Bhulta | 383 | 0.8125 | 373 | 0.45833
| Ashuganj(N) | 386 | 4:00 | 376 | 11:00 | Gopalganj | 423 | 0.25 | 396 | 0.75
| Payra | 423 | 8:00 | 408 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 234 | 10:00 | Comilla (N) | 238 | 13:00 | 234 | 1:00
| Ishurdi | 237 | 4:00 | 225 | 7:00 | Hathazari | 223 | 4:00 | 213 | 11:00
| Ashuganj | 237 | 18:30 | 234 | 15:00 | Megnaghat | 237 | 8:00 | 230 | 10:00
| Serajganj | 233 | 4:00 | 228 | 18:00 | Fenchuganj | 245 | 8:00 | 241 | 11:00
| Baghabari | 241 | 6:00 | 236 | 18:00 | Siddhirganj | 234 | 6:00 | 226 | 11:00
| Barapukuria | 232 | 17:00 | 222 | 18:00 | Maniknagar | 232 | 5:00 | 225 | 11:00
| Bogra | 232 | 5:00 | 222 | 8:00 | Agargaon | 233 | 8:00 | 225 | 11:00
| Rajshahi | 229 | 19:00 | 218 | 7:00 | Barisal | 250 | 13:00 | 241 | 20:00
| Khulna South | 233 | 4:00 | 213 | 18:00 | AKSML | 225 | 13:00 | 215 | 5:00
| Rampura | 231 | 23:00 | 226 | 11:00 | BSRM | 229 | 23:00 | 218 | 4:00
| Haripur | 231 | 1:00 | 225 | 12:00 | Bibiyana | 244 | 1:00 | 239 | 12:00
| Hasnabad | 235 | 1:00 | 230 | 11:00 | Bhulta | 233 | 19:00 | 227 | 17:00
| Shyampur | 231 | 8:00 | 220 | 10:00 | Ashuganj (S) | 236 | 19:00 | 231 | 11:00
| Aminbazar | 233 | 1:00 | 227 | 15:00 | Kaliakoir | 235 | 6:00 | 226 | 11:00
| Tongi | 230 | 1:00 | 225 | 11:00 | GPH | 225 | 6:00 | 214 | 5:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 8:00 | 128 | 24:00 | Madanhat | 136 | 0.875 | 131 | 0.083333
| Munsiganj | 139 | 19:00 | 133 | 10:00 | Hathazari | 135 | 0.16667 | 131 | 0.45833
| Sonargaon | 138 | 19:00 | 132 | 11:00 | Khulshi | 132 | 0.79167 | 125 | 0.25
| Shyampur | 135 | 8:00 | 130 | 11:00 | Halishahar | 134 | 0.91667 | 125 | 0.083333
| Bhulta | 133 | 24:00 | 128 | 10:00 | Baraulia | 135 | 0.95833 | 128 | 0.20833
| Madanganj | 139 | 8:00 | 133 | 11:00 | Sikalbaha | 135 | 0.54167 | 130 | 0.125
| Shitalakhya | 140 | 5:00 | 132 | 11:00 | Dohazari | 133 | 0.70833 | 125 | 0.20833
| Rahim steal | 139 | 7:00 | 135 | 10:00 | Cox'sbazar | 128 | 0.33333 | 118 | 0.75
| Matuail | 139 | 8:00 | 128 | 24:00 | Chandraghona | 135 | 0.8125 | 128 | 0.125
| Ghorasal | 140 | 1:00 | 137 | 15:00 | Kaptai | 135 | 0.29167 | 132 | 0.041667
| Narsinghdi | 137 | 7:00 | 132 | 11:00 | A. Khaer Stl. | 134 | 0.95833 | 129 | 0.041667
| Haripur (SBU) | 139 | 7:00 | 135 | 11:00 | Bakulia | 133 | 0.91667 | 128 | 0.20833
| Ullon | 133 | 8:00 | 127 | 11:00 | Julda | 134 | 0.54167 | 127 | 0.083333
| Hasnabad | 139 | 1:00 | 133 | 11:00 | TK Chemical | 134 | 0.91667 | 130 | 0.29167
| Magbazar | 133 | 4:00 | 127 | 11:00 | Modern Steel | 133 | 0.83333 | 128 | 0.125
| Maniknagar | 138 | 1:00 | 135 | 11:00 | Shahmirpur | 133 | 0.58333 | 126 | 0.25
| Bangabhaban | 138 | 1:00 | 135 | 11:00 | Khagrachhari | 134 | 0.33333 | 128 | 0.125
| Narinda | 138 | 1:00 | 135 | 11:00 | Matarbari | 131 | 0.70833 | 121 | 0.75
| Dhanmondi | 133 | 8:00 | 127 | 11:00 | Baroiar Hat | 136 | 0.041667 | 133 | 0.41667
| Lalbag | 140 | 18:30 | 132 | 11:00 | Rangamati | 134 | 21:00 | 128 | 4:00
| Madartek | 132 | 1:00 | 126 | 11:00 | Goalpara S/S | 138 | 19:00 | 128 | 18:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 19:30 | 129 | 0.29167
| Aftabnagar | 132 | 1:00 | 127 | 10:00 | Noapara | 136 | 4:00 | 123 | 0.75
| Fatuiiah | 136 | 8:00 | 131 | 11:00 | Jessore | 134 | 22:00 | 121 | 0.75
| Mirpur | 130 | 6:00 | 124 | 12:00 | Benapol | 134 | 0.125 | 122 | 0.75
| Kalyanpur | 131 | 6:00 | 125 | 12:00 | Jhenida | 1434 | 4:00 | 118 | 0.75
| Gulshan | 132 | 6:00 | 127 | 12:00 | Bottail | 136 | 0.16667 | 124 | 0.75
| Uttara | 129 | 6:00 | 123 | 12:00 | G.K Project | 140 | 0.16667 | 130 | 0.75
| Uttara New | 130 | 3:00 | 123 | 12:00 | Faridpur | 138 | 0.041667 | 129 | 0.75
| Kamrangirchar | 138 | 6:00 | 131 | 12:00 | Madaripur | 141 | 0.041667 | 133 | 0.75
| Savar | 132 | 6:00 | 124 | 12:00 | Shariyatpur S/S | 141 | 1:00 | 131 | 0.75
| Bhasantec | 132 | 6:00 | 131 | 11:00 | Gopalganj | 144 | 0.25 | 132 | 0.75
| Agargaon | 136 | 5:00 | 132 | 12:00 | Bagerhat | 139 | 21:00 | 128 | 0.75
| Satmosjid | 137 | 6:00 | 131 | 11:00 | Mongla | 137 | 22:00 | 127 | 0.45833
| Tongi | 141 | 21:00 | 136 | 22:00 | Satkhira | 137 | 5:00 | 125 | 18:00
| Kabirpur | 133 | 1:00 | 128 | 18:00 | Gallamari | 139 | 0.79167 | 129 | 0.75
| Basundhara | 138 | 13:00 | 126 | 12:00 | Magura | 135 | 2:00 | 119 | 0.75
| Manikganj | 141 | 14:00 | 133 | 21:00 | Norail | 132 | 0.041667 | 118 | 0.75
| Joydevpur | 142 | 20:00 | 135 | 11:00 | Chuadanga | 132 | 3:00 | 114 | 0.75
| New Tongi | 139 | 19:00 | 133 | 11:00 | Barisal(N) | 142 | 8:00 | 133 | 18:30
| Kodda | 140 | 13:00 | 132 | 21:00 | Barisal (S) | 140 | 0.29167 | 132 | 0.75
| Dhamrai | 133 | 5:00 | 128 | 18:00 | Patuakhali(S) | 139 | 0.375 | 130 | 0.75
| Rajendrapur | 138 | 21:00 | 130 | 17:00 | Bhandaria | 140 | 0.375 | 130 | 0.83333
| Valuka | 128 | 13:00 | 119 | 9:00 | Ishurdi | 138 | 5:00 | 130 | 18:00
| Tangail | 134 | 6:00 | 126 | 18:00 | Ruppur Paromanobik | 137 | 4:00 | 133 | 12:00
| Mymensing | 132 | 13:00 | 125 | 8:00 | Natore | 137 | 3:00 | 129 | 18:00
| Kishorganj | 132 | 13:00 | 128 | 8:00 | Bogra | 136 | 19:00 | 129 | 8:00
| Netrokona | 131 | 13:00 | 124 | 9:00 | Noagaon | 133 | 3:00 | 122 | 13:00
| Jamalpur | 139 | 18:30 | 128 | 4:00 | Rajshahi | 139 | 2:00 | 132 | 18:00
| Sherpur | 140 | 19:00 | 119 | 8:00 | Rajshahi New | 140 | 19:00 | 133 | 7:00
| Srimongal | 139 | 15:00 | 136 | 16:00 | C.Nawabganj | 140 | 19:30 | 132 | 10:00
| Shahjibazar | 136 | 13:00 | 134 | 20:00 | Amnura | 138 | 4:00 | 133 | 12:00
| Fenchuganj | 138 | 1:00 | 135 | 15:00 | Pabna | 138 | 4:00 | 130 | 18:00
| Khulawara | 138 | 1:00 | 135 | 19:30 | Shahjadpur | 140 | 3:00 | 134 | 18:00
| Sylhet | 136 | 1:00 | 133 | 11:00 | Serajganj | 135 | 4:00 | 132 | 18:00
| Chatak | 134 | 1:00 | 130 | 18:00 | Niyamatpur | 132 | 3:00 | 121 | 11:00
| Sunamganj | 135 | 7:00 | 131 | 17:00 | Joypurhat | 134 | 3:00 | 121 | 13:00
| Biani Bazar | 135 | 01:0 | 130 | 18:00 | Sherpur(Bogura) | 137 | 19:00 | 129 | 8:00
| Comilla(s) | 129 | 1:00 | 126 | 13:00 | Mohastangor | 135 | 4:00 | 126 | 8:00
| Comilla(n) | 142 | 23:00 | 139 | 15:00 | Rangpur | 128 | 4:00 | 118 | 18:00
| Chandpur | 145 | 19:00 | 138 | 7:00 | Lalmonirhat | 130 | 17:00 | 117 | 18:00
| Feni | 139 | 13:00 | 135 | 16:00 | Saidpur | 130 | 6:00 | 116 | 18:00
| Chowmuhani | 135 | 9:00 | 130 | 8:00 | Purbasadipur | 128 | 17:00 | 113 | 18:00
| Ashuganj | 137 | 23:00 | 135 | 19:30 | Thakurgaon | 127 | 4:00 | 116 | 8:00
| Daudkandi | 140 | 8:00 | 136 | 16:00 | Palashbari | 132 | 15:00 | 125 | 8:00
| B.Baria | 134 | 7:00 | 132 | 22:00 | Barapukuria | 132 | 17:00 | 122 | 18:00
| Ramganj | 138 | 0:00 | 128 | 20:00 | Panchagar | 125 | 5:00 | 111 | 18:00
| Chaddagram | 139 | 19:30 | 135 | 16:00 | Joldhaka | 128 | 3:00 | 114 | 18:00
| PHP | 138 | 13:00 | 130 | 19:00 | Kurigram | 126 | 0.66667 | 116 | 0.77083

## L-Curve
Date | 2020-12-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 41 | 4942 | 1947 | 6889 |  |  |  | QF-LDC-11
0:30 | 92.5 | 4654.5 | 1777.5 | 6432 | Date: | 2020-12-05
1:00 | 144 | 4367 | 1608 | 5975
1:30 | 119.5 | 4195 | 1561.5 | 5756.5
2:00 | 95 | 4023 | 1515 | 5538
2:30 | 93 | 3964.5 | 1523 | 5487.5 | [5 empty] | Gen. at Eve. Peak | 9098 | 9500 MW (19:30 )
3:00 | 91 | 3906 | 1531 | 5437 | [6 empty] | 19:00
3:30 | 92 | 3910 | 1481.5 | 5391.5 | [5 empty] | Gen. at Day Peak | 6764 | 7952.5 MW (12:00 )
4:00 | 93 | 3914 | 1432 | 5346 | [6 empty] | 12:00
4:30 | 101.5 | 3885 | 1428.5 | 5313.5 | [5 empty] | Highest Generation | 9098
5:00 | 110 | 3856 | 1425 | 5281 | [6 empty] | 19:00
5:30 | 147.5 | 4000 | 1441.5 | 5441.5
6:00 | 185 | 4144 | 1458 | 5602
6:30 | 270 | 4276 | 1457 | 5733
7:00 | 355 | 4408 | 1456 | 5864
7:30 | 283.5 | 4508.5 | 1587 | 6095.5
8:00 | 212 | 4609 | 1718 | 6327
8:30 | 148 | 4706 | 1731 | 6437
9:00 | 84 | 4803 | 1744 | 6547
9:30 | 67 | 4782.5 | 1684 | 6466.5
10:00 | 50 | 4762 | 1624 | 6386
10:30 | 42 | 4775.5 | 1688 | 6463.5
11:00 | 34 | 4789 | 1752 | 6541
11:30 | 33 | 4861 | 1791.5 | 6652.5
12:00 | 32 | 4933 | 1831 | 6764
12:30 | 60.5 | 5004.5 | 1853.5 | 6858
13:00 | 89 | 5076 | 1876 | 6952
13:30 | 49 | 5020 | 1849 | 6869
14:00 | 9 | 4964 | 1822 | 6786
14:30 | 40 | 4954.5 | 1792 | 6746.5
15:00 | 71 | 4945 | 1762 | 6707
15:30 | 92.5 | 4875 | 1794 | 6669
16:00 | 114 | 4805 | 1826 | 6631
16:30 | 91 | 4942 | 1950 | 6892
17:00 | 68 | 5079 | 2074 | 7153
17:30 | 49.5 | 5472.5 | 2409 | 7881.5
18:00 | 31 | 5866 | 2744 | 8610
18:30 | 31.5 | 6010 | 2844 | 8854
19:00 | 32 | 6154 | 2944 | 9098
19:30 | 40 | 6065 | 2871 | 8936
20:00 | 52 | 6051 | 2770 | 8821 |  |  |  | Executive Engineer
20:30 | 51.5 | 5914 | 2752 | 8666 |  |  |  | Network Operation Division
21:00 | 51 | 5777 | 2734 | 8511
21:30 | 64.5 | 5566 | 2638.5 | 8204.5
22:00 | 78 | 5355 | 2543 | 7898 |  |  |  |  | Page 6 of 7
22:30 | 64 | 5300.5 | 2334 | 7634.5
23:00 | 50 | 5246 | 2125 | 7371
23:30 | 45.5 | 5094 | 2036 | 7130
24:00 | 41 | 4942 | 1947 | 6889
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-05 |  | Energy | 165237762
[10 empty] | 2020-12-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2858 | 411 | 2063 | 1215 | 502 | 79 | 0 | 0 | 68
0:30 | 2843 | 410 | 2025 | 705.5 | 448.5 | 84.5 | 0 | 0 | 69 | Date: | 2020-12-05
1:00 | 2828 | 409 | 1987 | 196 | 395 | 90 | 0 | 0 | 70
1:30 | 2782 | 408.5 | 1867 | 170.5 | 369.5 | 90 | 0 | 0 | 69 | [7 empty] | Total Energy | 165.2378 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2736 | 408 | 1747 | 145 | 344 | 90 | 0 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 2711 | 408 | 1728 | 140 | 344.5 | 89 | 0 | 0 | 67 | [7 empty] | Energy Requirement | 165.2378
3:00 | 2686 | 408 | 1709 | 135 | 345 | 88 | 0 | 0 | 66
3:30 | 2697 | 359.5 | 1699 | 137.5 | 345 | 87.5 | 0 | 0 | 66 | [6 empty] | Shortage
4:00 | 2708 | 311 | 1689 | 140 | 345 | 87 | 0 | 0 | 66
4:30 | 2709.5 | 312 | 1655.5 | 140 | 345 | 86.5 | 0 | 0 | 65
5:00 | 2711 | 313 | 1622 | 140 | 345 | 86 | 0 | 0 | 64
5:30 | 2768 | 312.5 | 1696 | 169.5 | 345 | 85.5 | 0 | 0 | 65
6:00 | 2825 | 312 | 1770 | 199 | 345 | 85 | 0 | 0 | 66
6:30 | 2840 | 312 | 1812 | 273 | 344.5 | 84 | 0 | 0 | 66 |  |  |  |  | Coal
7:00 | 2855 | 312 | 1854 | 347 | 344 | 83 | 0 | 0 | 66
7:30 | 2850 | 312 | 1874 | 508 | 389.5 | 84 | 0 | 0 | 68 |  |  |  | Oil |  |  |  | ,
8:00 | 2845 | 312 | 1894 | 669 | 435 | 85 | 0 | 0 | 70
8:30 | 2844.5 | 312.5 | 1902 | 771.5 | 436 | 85.5 | 0 | 0 | 65
9:00 | 2844 | 313 | 1910 | 874 | 437 | 86 | 0 | 0 | 60
9:30 | 2824.5 | 312.5 | 1869.5 | 851 | 436 | 86 | 0 | 0 | 59
10:00 | 2805 | 312 | 1829 | 828 | 435 | 86 | 0 | 0 | 58
10:30 | 2827 | 384 | 1846 | 795.5 | 435 | 83.5 | 0 | 0 | 61
11:00 | 2849 | 456 | 1863 | 763 | 435 | 81 | 0 | 0 | 64
11:30 | 2834.5 | 455.5 | 1861.5 | 885 | 434 | 84 | 0 | 0 | 67
12:00 | 2820 | 455 | 1860 | 1007 | 433 | 87 | 0 | 0 | 70
12:30 | 2805.5 | 455.5 | 1894.5 | 1072 | 433.5 | 82.5 | 8.5 | 0 | 73
13:00 | 2791 | 456 | 1929 | 1137 | 434 | 78 | 17 | 0 | 76
13:30 | 2791 | 456 | 1929 | 1137 | 434 | 78 | 17 | 0 | 76
14:00 | 2791 | 456 | 1929 | 1137 | 434 | 78 | 17 | 0 | 76
14:30 | 2733.5 | 456.5 | 1902 | 1102 | 432.5 | 83.5 | 17 | 0 | 76
15:00 | 2676 | 457 | 1875 | 1067 | 431 | 89 | 17 | 0 | 76
15:30 | 2703 | 456.5 | 1901 | 987 | 432.5 | 84 | 17 | 0 | 75
16:00 | 2730 | 456 | 1927 | 907 | 434 | 79 | 17 | 0 | 74
16:30 | 2752 | 456 | 2009.5 | 1042 | 453.5 | 73 | 25.5 | 0 | 77
17:00 | 2774 | 456 | 2092 | 1177 | 473 | 67 | 34 | 0 | 80
17:30 | 2852 | 574 | 2121 | 1535 | 558 | 71 | 84.5 | 0 | 86
18:00 | 2930 | 692 | 2150 | 1893 | 643 | 75 | 135 | 0 | 92
18:30 | 2923 | 692.5 | 2170.5 | 2119.5 | 643 | 74.5 | 143 | 0 | 88
19:00 | 2916 | 693 | 2191 | 2346 | 643 | 74 | 151 | 0 | 84
19:30 | 2838 | 693 | 2159 | 2289 | 644 | 74 | 151 | 0 | 88
20:00 | 2858 | 692 | 2168 | 2145 | 644 | 75 | 151 | 0 | 88
20:30 | 2870.5 | 692.5 | 2169.5 | 1994 | 644 | 75 | 134.5 | 0 | 86
21:00 | 2883 | 693 | 2171 | 1843 | 644 | 75 | 118 | 0 | 84
21:30 | 2859.5 | 693 | 2154.5 | 1602.5 | 644 | 76 | 93 | 0 | 82
22:00 | 2836 | 693 | 2138 | 1362 | 644 | 77 | 68 | 0 | 80
22:30 | 2854.5 | 551 | 2142 | 1288.5 | 593 | 77.5 | 52 | 0 | 76
23:00 | 2873 | 409 | 2146 | 1215 | 542 | 78 | 36 | 0 | 72
23:30 | 2865.5 | 410 | 2104.5 | 1215 | 522 | 78.5 | 18 | 0 | 70 | Max Temp. in Dhaka |  | 27.7° C
24:00 | 2858 | 411 | 2063 | 1215 | 502 | 79 | 0 | 0 | 68
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-12-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 88 | 87 | 86 | 85 | 83 | 85 | 86 | 86 | 81 | 87 | 78 | 78 | 89 | 79 | 67 | 75 |  | 74 | 74 | 75 | 75 | 77 | 78 | 79 | 1870915
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | [18 empty] | 12285
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 205 | 203 | 216 | 241 | 205 | 215 | 202 | 202 | 202 | 231 | 211 | 203 | 204 | 203 | 205 | 203 | 218 |  | 203 | 203 | 203 | 208 | 203 | 203 | 203 | 4916690
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 137863
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 4 | 60 |  | 115 | 145 | 145 | 80 |  |  |  | 491782
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 94 | 93 | 93 | 94 | 94 | 94 | 94 | 93 | 93 | 93 | 94 | 93 | 93 | 93 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2416300
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2803500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4775391
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2097740
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 20 | 20 | 20 | 20 | 20 | 23 | 20 | 507312
33 | Ashuganj 225 MW CCPP | 182 | 194 | 184 | 196 | 190 | 195 | 204 | 182 | 182 | 182 | 196 | 194 | 182 | 183 | 182 | 219 | 182 | 216 |  | 183 | 182 | 190 | 196 | 182 | 184 | 194 | 4624000
34 | Ashuganj 450 MW CCPP(South)
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 341760
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 341 | 357 | 354 | 346 | 359 | 346 | 355 | 338 | 338 | 345 | 352 | 352 | 340 | 340 | 348 | 380 | 378 |  | 391 | 339 | 342 | 344 | 339 | 339 | 349 | 8556550
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 400 | 360 | 360 | 360 | 400 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 9016500
41 | Haripur 360MW CCPP(HPL) | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 320 | 324 | 324 | 324 | 325 | 324 | 313 | 319 | 319 | 333 | 333 |  | 345 | 345 | 324 | 324 | 324 | 324 | 324 | 7690000
42 | RPCL 210MW CCPP | 164 | 164 | 165 | 165 | 158 | 160 | 165 | 164 | 165 | 162 | 161 | 141 | 102 | 103 | 103 | 105 | 105 | 107 |  | 108 | 108 | 108 | 107 | 108 | 128 | 129 | 3185040
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 8 | 19 | 26 | 21 | 22 | 26 | 17 | 15 | 5 | 0 | [9 empty] | 162200
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1434000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716760
46 | Shajibazar 330 MW CCPP | 159 | 157 | 158 | 158 | 158 | 160 | 158 | 159 | 159 | 157 | 159 | 159 | 152 | 154 | 153 | 151 | 152 | 152 |  | 153 | 153 | 152 | 151 | 152 | 152 | 152 | 3544000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 20 | 20 | 20 | 20 | 36 | 36 | 36 | 36 | 35 | 35 | 34 | 35 | 34 | 34 | 34 | 34 | 35 |  | 35 | 36 | 35 | 35 | 36 | 35 | 35 | 781536
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 5 | 5 | 5 | 5 | 40 | 81 | 78 | 78 | 77 | 77 | 77 | 76 | 76 | 76 | 76 | 76 | 78 |  | 78 | 78 | 78 | 78 | 79 | 79 | 79 | 1537920
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 434000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 |  |  | 0 | 3 | 5 | 5 | 5 | [10 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 75500
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 5 | 5 | 5 | 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 47 | 53 | 53 | 53 | 1051800
56 | Shahjahanulla 25 MW PP | 16 | 0 |  |  |  | 8 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 390240
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 300 | 300 | 295 | 310 | 300 | 280 | 280 | 260 | 290 | 290 | 275 | 270 | 290 | 290 | 320 | 310 |  | 320 | 285 | 290 | 295 | 285 | 280 | 290 | 7287700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 54806
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 |  |  | 20 | 20 | 20 | 20 | 20 | 17 | 417840
61 | Narshingdi 22 MW PP (Doreen) | 19 | 0 |  |  |  |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 |  | 19 | 0 | 271548
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 0 |  | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 376200
63 | Impoprt (Tripura) | 70 | 68 | 66 | 66 | 64 | 66 | 66 | 70 | 60 | 58 | 64 | 70 | 76 | 76 | 76 | 74 | 80 | 92 |  | 84 | 88 | 88 | 84 | 80 | 72 | 68 | 1740480
64 | Malancha, Ctg. EPZ (United) | 22 | 10 | 7 | 7 | 6 | 23 | 20 | 2 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 10 | 16 |  | 15 | 24 | 27 | 27 | 27 | 16 | 30 | 269760
65 | Feni 22MW PP (Doreen) | 18 | 18 | 0 | 0 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 390456
66 | Feni 11 MW PP (Doreen) | 8 | 0 |  |  | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 123480
67 | Jangalia 33MW PP (Summit) | 33 | 28 | 0 |  | 0 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 682500
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 18 | 18 | 15 | 15 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 515750
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 18 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 28 | 28 | 28 | 32 | 33 | 33 | 33 | 547020
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 599800
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 |  | 21 | 24 | 24 | 25 | 25 | 25 | 25 | 519600
73 | Ghorashal 108MW PP (Regent) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 73 | 71 | 71 | 73 | 73 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1700954
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [12 empty] | 14 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 359520
Manikgonj 162MW PP
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 16 |  | 57 | 40 | 45 | 30 |  |  | 0 | 172800
78 | Gazipur 52 MW PP | [7 empty] | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [11 empty] | 125496
79 | Kodda 150MW PP | [16 empty] | 10 | 48 |  | 64 | 64 | 64 | 48 | 32 |  | 0 | 285120
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 11 |  | 24 | 25 | 25 | 16 | 17 | 8 | 0 | 109440
81 | Jangalia 52 MW PP (Lakdanavi) | [9 empty] | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | [6 empty] | 170678
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 1 | [10 empty] | 23521
| Jodiac Power | 54 | 0 |  |  | 0 | 11 | 41 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1038554
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 2 | 15 |  | 15 | [5 empty] | 0 | 43320
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) |  |  |  |  | 0 | 7 | 10 | 36 | 40 | 40 | 40 | 45 | 58 | 70 | 70 | 30 | 50 | 90 |  | 100 | 100 | 100 | 88 | 86 | 88 | 88 | 1209062
86 | Meghnaghat CCPP(Summit) | 135 | 145 | 135 | 140 | 140 | 145 | 150 | 135 | 130 | 130 | 140 | 140 | 100 | 140 | 140 | 150 | 140 | 150 |  | 140 | 130 | 145 | 140 | 138 | 145 | 142 | 3347462
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 10 | 42 | 96 | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 81 |  | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 984960
| Meghnaghat 104 MW PP (OPCL) |  |  |  |  | 0 | 7 | 41 | 78 | 90 | 70 | 21 | 41 | 90 | 90 | 90 | 57 | 53 | 86 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1366080
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 5 | 5 | 5 | 5 | 29 | 49 | 47 | 50 | 50 | 50 | 47 | 47 | 50 | 47 | 49 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1029960
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 1050728
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 7 | 7 | 7 | [11 empty] | 0 | 26496
95 | Patenga 50MW PP (Baraka) | 7 | 0 | [8 empty] | 11 | 31 | 35 | 37 | 38 | 44 | 45 | 45 |  | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 595680
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 14 | 15 | 15 | 15 | 15 | 30 |  | 30 | 55 | 55 | 55 |  |  | 0 | 291922
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 12 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 |  | 0 | 616443
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 140 | 140 | 140 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 3735409
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 7500
103 | Kamalaghat 54 MW PP(Banco Energy) |  |  |  |  | 0 | 17 | 17 | 54 | 54 | 17 | 17 | 35 | 54 | 54 | 54 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 877680
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 7 | 7 | 7 | 7 | 7 |  | 10 |  | 92 | 80 | 80 | 24 |  |  | 0 | 297600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 22 | 72 | 72 | 72 | 92 | 121 | 120 | 115 | 106 | 95 | 56 |  | 76 | 76 | 91 | 22 |  |  | 0 | 1156320
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 20 | 50 | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1403520
116 | Chandpur 200MW (Desh energy) |  |  |  |  | 0 | 12 | 62 | 68 | 68 | 50 | 50 | 55 | 68 | 50 | 50 | 16 | 32 | 118 |  | 154 | 150 | 120 | 120 | 120 | 120 | 120 | 1533600
117 | Ashuganj 150MW PP (Midland) | [7 empty] | 5 | 10 | 10 | 10 | 10 |  |  |  |  | 16 | 137 |  | 150 | 150 | 150 | 150 | 80 | 80 | 10 | 955127
118 | Bibiyana-III 400 MW CCPP | 374 | 375 | 374 | 375 | 375 | 410 | 410 | 410 | 410 | 410 | 412 | 412 | 389 | 389 | 351 | 351 | 351 | 399 |  | 398 | 398 | 398 | 399 | 399 | 399 | 399 | 9326000
| Jamalpur 115 MW PP (United) | [9 empty] | 35 | 35 | 68 | 85 | 55 | 55 | 32 | 48 | 115 |  | 115 | 95 | 95 | 95 | 95 | 65 | 25 | 1092000
| Anwara 300 MW PP (United) | [6 empty] | 16 | 66 | 107 | 124 | 125 | 124 | 124 | 124 | 125 | 125 | 140 | 156 |  | 160 | 160 | 161 | 161 | 161 | 161 | 126 | 2263200
| Juldah unit-2 (Acorn) | [11 empty] | 20 | 50 | 20 | 20 | 10 | 44 | 100 |  | 100 | 100 | 100 | 100 | 60 | 10 | 10 | 669120
| Anlima Energy Ltd. | [10 empty] | 15 | 14 | 2 |  |  | 8 | 10 | [8 empty] | 0 | 53945
120 | Eastern Zone Total | 4367 | 4023 | 3906 | 3914 | 3856 | 4144 | 4408 | 4609 | 4803 | 4762 | 4789 | 4933 | 5076 | 4964 | 4945 | 4805 | 5079 | 5866 |  | 6154 | 6065 | 6051 | 5777 | 5355 | 5246 | 4942 | 118490305
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 32 | 32 |  |  |  |  | 0 | 42240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 70 | 70 | 35 | 17 | 90 | 90 | 90 | 53 | 53 | 53 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 53 | 1226880
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 30 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 37 | 10 | 10 | 36 | 10 | 7 | 10 | 36 | 13 |  | 24 | 24 | 27 | 37 | 37 | 36 | 38 | 696990
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 |  |  |  |  | 0 | 36480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 14 | 0 | [5 empty] | 35 | 35 | 34 | 35 | 35 | 33 | 34 | 34 | 34 | 52 | 79 |  | 90 | 92 | 92 | 92 | 92 | 92 | 58 | 985286
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 14 | 14 | 14 | 15 | 14 | 11 | 11 | 9 | 15 | 15 | 15 | 18 | 17 | 16 | 22 | 26 |  | 26 | 27 | 27 | 27 | 26 | 26 | 24 | 421400
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [25 empty] | 0 | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 409 | 408 | 408 | 311 | 313 | 312 | 312 | 312 | 313 | 312 | 456 | 455 | 456 | 456 | 457 | 456 | 456 | 692 |  | 693 | 693 | 692 | 693 | 693 | 409 | 411 | 10725818
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 380 | 550 |  | 550 | 550 | 550 | 550 | 550 | 450 | 410 | 8839700
149
150 | Barapukuria TPP Unit-1 | 95 | 94 | 95 | 95 | 95 | 95 | 94 | 95 | 97 | 95 | 95 | 93 | 94 | 93 | 91 | 94 | 93 | 93 |  | 93 | 94 | 94 | 94 | 94 | 92 | 92 | 2238109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1545000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 146 | 147 | 156 | 155 | 151 | 158 | 150 | 170 | 177 | 157 | 150 | 154 | 177 | 163 | 145 | 150 | 166 | 182 |  | 196 | 169 | 176 | 182 | 178 | 175 | 175 | 4162091
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 161 | 170 | 169 | 165 | 172 | 164 | 168 | 164 | 161 | 167 | 171 | 201 | 166 | 161 | 166 | 194 | 205 |  | 209 | 187 | 191 | 193 | 189 | 186 | 186 | 4489164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 328 | 346 | 347 | 347 | 346 | 347 | 359 | 390 | 400 | 341 | 363 | 364 | 330 | 350 | 356 | 406 | 406 | 427 |  | 425 | 416 | 435 | 434 | 405 | 430 | 400 | 9101727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 0 | 0 | 0 | 0 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 417760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 202572
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 7 | 70 |  | 70 | 70 | 70 | 70 | 36 | 36 | 0 | 376560
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 27 | 102 |  | 113 | 113 | 113 | 113 | 50 |  | 0 | 618240
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 109 | 109 | 50 |  |  |  | 0 | 208128
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 82 | 96 |  | 105 | 86 | 60 | 56 |  |  | 0 | 389760
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 2 | 1 | 1 | 0 | [9 empty] | 23552
178
178