## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-13 | Sunday
|  |  | Date (day): | 2020-12-13 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11750.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13407 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-12 | 2020-12-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 99 | 98 | 100 | 100 |  | 70 | Machine problem
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 6 | 7 | 7 | 100 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 3 | 338 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 337 | 335 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 27 | 64 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 61 | 12 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 48 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 8 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 24 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 82 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 44 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 16 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 293 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 60 | 100 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 70 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2198 | 2768 | 3775 | 4153 | 941 | 960
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 22 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 47 | 47 | 47 | 183 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 200 | 203 | 215 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 16 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 162 | 179 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 684 | 787 | 1438 | 1433 | 693 | 122
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 140 | 135 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 129 | 129
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 100 | 100 | 100
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 146 | 0 | 180 | 41 |  | Gas shortage
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 20 | 20 | 25 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 26 | 26 | 169 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 43 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 6 | 7 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maintenance
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 50 | 90 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 86 | 108 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 55 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 664 | 999 | 1182 | 1765 | 285 | 883
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 107 | 111 | 150 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 72 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 24 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 25 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 10 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 0
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 162 | 342 | 631.6 | 580 | 52 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 15 | 20 | 20 |  | 32 | GT-1 FGMO & GT-2 under S/D.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 20 | 20
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 0 | 152 | 152 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 48 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 32 | 32 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 86 | 86
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 78 | 95 | 150 | 150
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 225 | 285 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 237 | 238 | 400 | 400
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 955 | 1028 | 1165 | 1165 | 178 | 415
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 456 | 669 | 462 | 702
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 240 | 250 | 250 | 160 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 759 | 1169 | 1162 | 1738 | 160 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 26 | 26 | 26
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 38 | 52 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 350 | 490 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 407 | 632 | 831 | 891 | 0 | 194
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 160 | 225 | 225 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 366 | 379 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 70 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 737 | 847 | 1370 | 1493 | 171 | 446
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 76 | 75 | 76
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 95 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 78 | 171 | 196 | 189 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 6644 | 8743 | 11750.6 | 13407 | 2480 | 3492
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6302.7949 | 8294 | 11147.1436 | 12718.4786
| A. |  | 2020-12-12 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 8743 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5083 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8743 | MW
| 3 | Day peak Generation : |  |  | 6644 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8294 | MW
| 4 | Evening peak Generation : |  |  | 8743 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 164.3657 | MKWHr | By Solar | 0.14446 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 107.136 | MKWHr |  | By Oil: | 31.8168 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.6678 | MKWHr |  | By Hydro: | 1.0973 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2480 | MW | Dhaka | 3001 | 3001 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3492 | MW | Chittagong | 856 | 856 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5972 | MW | Khulna | 1050 | 1050 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 851.9 | MMCFD |  |  | Rajshahi | 836 | 836 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 123563365.072 | ii) Oil : | Taka | 257514063.2 | Comilla | 763 | 763 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 54118531.97 | Total | Taka | 435195960.242 | Mymensingh | 659 | 659 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.773 | MKWHr. | Sylhet | 318 | 318 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -20 | MW (E to W) at | 19:00 | hrs | Barisal | 229 | 229 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -173 | MW at | 7:00 | hrs | Rangpur | 582 | 582 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 22.7° C |  |  | Total | 8294 | 8294 |  | 0
| B. |  | 2020-12-13 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 26.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13407 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
| 4 | Reserve(Generation end) |  |  |  | 4207 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 172.9571 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5400 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.52 | MKWHr. | ii) HVDC Flow at Peak Time |  | 669 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9834 | MKWHr. | iii) Maximum HVDC Flow : |  | 670 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.35 |  | (b) Today: | 99.28 |  | (c) Rule Curve: |  | 104.9
.

## YesterdayGen
2020-12-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 393 | 303 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 22 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 42 | 100 | 120 | 100 | 0 | 0 | 0 | 8 | 0 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 21 | 70 | 163 | 0 | 20 | 0 | 30 | 0 | 53 | 50 | 130 | 159 | 20 | 79 | 0 | 75 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 411 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 156 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 3917 | 1705 | 5622 | 2709 | 411 | 1840 | 76 | 473 | 43 | 0 | 70 | 0 | 0 | 99.36
2:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 393 | 305 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 22 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 100 | 120 | 100 | 0 | 0 | 0 | 8 | 0 | 26 | 56 | 0 | 15 | 0 | 0 | 0 | 19 | 0 | 0 | 21 | 66 | 164 | 0 | 20 | 0 | 30 | 0 | 53 | 50 | 130 | 158 | 20 | 80 | 0 | 75 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 411 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 158 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 |  | 3812 | 1552 | 5364 | 2732 | 411 | 1740 | 0 | 373 | 42 | 0 | 66 | 0 | 0 | 99.36
3:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 393 | 304 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 100 | 120 | 100 | 0 | 0 | 0 | 8 | 0 | 26 | 56 | 0 | 15 | 0 | 0 | 0 | 19 | 0 | 0 | 21 | 66 | 164 | 0 | 20 | 0 | 30 | 0 | 11 | 10 | 130 | 159 | 20 | 20 | 0 | 75 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 410 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 158 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 |  | 3679 | 1527 | 5206 | 2737 | 410 | 1628 | 0 | 323 | 42 | 0 | 66 | 0 | 0 | 99.36
4:00 | 0 | 99 | 0 | 115 | 200 | 6 | 0 | 390 | 303 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 100 | 120 | 100 | 0 | 0 | 0 | 8 | 0 | 23 | 56 | 0 | 15 | 0 | 0 | 0 | 19 | 0 | 0 | 18 | 66 | 166 | 0 | 20 | 0 | 30 | 0 | 11 | 10 | 130 | 158 | 20 | 20 | 0 | 75 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 167 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 |  | 3644 | 1444 | 5088 | 2742 | 314 | 1599 | 0 | 323 | 44 | 0 | 66 | 0 | 0 | 99.35
5:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 393 | 304 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 100 | 120 | 100 | 0 | 0 | 0 | 8 | 0 | 23 | 55 | 0 | 15 | 0 | 0 | 0 | 19 | 0 | 0 | 15 | 64 | 166 | 0 | 20 | 0 | 30 | 0 | 11 | 10 | 130 | 158 | 20 | 10 | 0 | 85 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 174 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 |  | 3622 | 1461 | 5083 | 2763 | 314 | 1574 | 0 | 323 | 45 | 0 | 64 | 0 | 0 | 99.35
6:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 232 | 339 |  | 0 | 340 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 42 | 135 | 148 | 100 | 0 | 0 | 0 | 8 | 0 | 19 | 56 | 0 | 36 | 0 | 0 | 0 | 19 | 8 | 3 | 15 | 62 | 162 | 0 | 20 | 0 | 30 | 0 | 5 | 5 | 110 | 158 | 20 | 40 | 0 | 90 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 2 | 314 | 3 | 0 | 0 | 0 | 85 | 35 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 |  | 314 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 |  | 3873 | 1518 | 5391 | 2654 | 314 | 1716 | 256 | 343 | 46 | 0 | 62 | 0 | 0 | 99.35
7:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 0 | 323 |  | 0 | 400 | 0 | 7 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 38 | 138 | 150 | 135 | 0 | 0 | 0 | 8 | 0 | 19 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 60 | 164 | 0 | 20 | 0 | 30 | 0 | 5 | 5 | 110 | 155 | 20 | 70 | 0 | 85 | 0 | 0 | 0 | 290 | 0 | 2 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 5 | 312 | 46 | 0 | 0 | 0 | 117 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 |  | 314 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 179 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 |  | 4136 | 1580 | 5716 | 2609 | 314 | 1793 | 497 | 396 | 47 | 0 | 60 | 0 | 0 | 99.34
8:00 | 0 | 100 | 0 | 115 | 300 | 6 | 0 | 0 | 324 |  | 0 | 400 | 0 | 7 | 0 | 22 | 0 | 0 | 0 | 60 | 0 | 40 | 8 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 8 | 140 | 150 | 135 | 0 | 0 | 0 | 8 | 0 | 19 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 13 | 66 | 166 | 6 | 20 | 0 | 20 | 0 | 5 | 5 | 110 | 157 | 20 | 75 | 0 | 95 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 42 | 2 | 100 | 50 | 7 | 232 | 96 | 0 | 0 | 1 | 155 | 54 | 0 | 0 | 0 | 10 | 0 | 17 | 3 | 0 | 0 |  | 314 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 195 | 0 | 368 | 53 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 |  | 4398 | 1800 | 6198 | 2584 | 314 | 1714 | 972 | 455 | 47 | 40 | 66 | 6 | 0 | 99.34
9:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 0 | 324 |  | 0 | 400 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 90 | 0 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 12 | 25 | 17 | 13 | 0 | 47 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 140 | 150 | 135 | 0 | 0 | 0 | 8 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 74 | 163 | 24 | 20 | 0 | 20 | 0 | 5 | 5 | 110 | 159 | 20 | 75 | 0 | 96 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 82 | 0 | 100 | 50 | 6 | 232 | 115 | 0 | 0 | 1 | 158 | 54 | 0 | 0 | 1 | 40 | 0 | 17 | 6 | 0 | 0 |  | 314 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 200 | 0 | 403 | 90 | 0 | 109 | 0 | 0 | 0 | 2 | 20 | 400 | 0 | 0 | 0 |  | 4652 | 1984 | 6636 | 2546 | 314 | 1745 | 1362 | 475 | 47 | 64 | 74 | 9 | 0 | 99.34
10:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 0 | 300 |  | 0 | 370 | 0 | 7 | 0 | 35 | 0 | 0 | 0 | 94 | 0 | 50 | 7 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 12 | 25 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 140 | 150 | 135 | 0 | 0 | 0 | 8 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 5 | 18 | 80 | 145 | 0 | 20 | 0 | 20 | 0 | 5 | 5 | 110 | 160 | 20 | 77 | 0 | 83 | 0 | 0 | 0 | 160 | 0 | 2 | 0 | 275 | 0 | 0 | 0 | 0 | 95 | 0 | 100 | 50 | 6 | 236 | 75 | 0 | 0 | 2 | 161 | 54 | 0 | 0 | 28 | 90 | 0 | 48 | 6 | 0 | 0 |  | 315 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 200 | 0 | 336 | 70 | 0 | 111 | 0 | 0 | 0 | 3 | 90 | 350 | 0 | 0 | 0 |  | 4518 | 1904 | 6422 | 2475 | 315 | 1513 | 1505 | 425 | 48 | 50 | 80 | 11 | 0 | 99.33
11:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 0 | 310 |  | 0 | 370 | 0 | 48 | 7 | 41 | 0 | 0 | 0 | 100 | 16 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 12 | 25 | 17 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 18 | 86 | 118 | 0 | 20 | 0 | 20 | 0 | 5 | 5 | 110 | 155 | 20 | 77 | 0 | 85 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 92 | 0 | 100 | 50 | 0 | 236 | 25 | 0 | 0 | 2 | 161 | 54 | 0 | 0 | 28 | 100 | 0 | 90 | 10 | 0 | 0 |  | 456 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 200 | 0 | 341 | 70 | 0 | 111 | 0 | 0 | 0 | 3 | 70 | 350 | 0 | 0 | 0 |  | 4498 | 2007 | 6505 | 2440 | 456 | 1456 | 1564 | 425 | 47 | 16 | 86 | 15 | 0 | 99.33
12:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 3 | 337 |  | 0 | 370 | 0 | 85 | 27 | 41 | 0 | 0 | 0 | 100 | 40 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 12 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 18 | 86 | 107 | 0 | 20 | 0 | 20 | 0 | 5 | 5 | 130 | 159 | 20 | 76 | 0 | 78 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 50 | 0 | 237 | 25 | 0 | 0 | 4 | 162 | 54 | 0 | 0 | 28 | 100 | 0 | 90 | 10 | 0 | 0 |  | 456 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 195 | 0 | 366 | 53 | 0 | 111 | 0 | 0 | 0 | 4 | 35 | 350 | 0 | 0 | 0 |  | 4663 | 1981 | 6644 | 2416 | 456 | 1608 | 1575 | 424 | 45 | 16 | 86 | 18 | 0 | 99.33
13:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 38 | 337 |  | 0 | 420 | 0 | 93 | 52 | 41 | 0 | 0 | 0 | 100 | 40 | 32 | 19 | 0 | 0 | 0 | 54 | 55 | 12 | 0 | 25 | 12 | 25 | 17 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 18 | 88 | 90 | 0 | 20 | 1 | 20 | 0 | 5 | 5 | 130 | 160 | 20 | 75 | 0 | 75 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 68 | 0 | 90 | 50 | 0 | 237 | 44 | 0 | 0 | 4 | 162 | 54 | 0 | 0 | 28 | 100 | 0 | 90 | 19 | 0 | 20 |  | 450 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 188 | 0 | 343 | 53 | 0 | 111 | 0 | 0 | 0 | 4 | 60 | 360 | 0 | 0 | 0 |  | 4940 | 2016 | 6956 | 2408 | 450 | 1726 | 1712 | 434 | 44 | 66 | 88 | 28 | 6956 | 99.32
14:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 69 | 240 |  | 0 | 300 | 0 | 96 | 70 | 41 | 0 | 0 | 0 | 100 | 24 | 32 | 37 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 12 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 18 | 88 | 90 | 0 | 20 | 1 | 20 | 0 | 5 | 5 | 110 | 161 | 20 | 76 | 0 | 75 | 0 | 0 | 0 | 255 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 82 | 0 | 100 | 50 | 0 | 239 | 45 | 0 | 0 | 3 | 126 | 54 | 0 | 0 | 28 | 100 | 0 | 0 | 13 | 0 | 20 |  | 433 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 3 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 160 | 0 | 287 | 53 | 0 | 111 | 0 | 0 | 0 | 4 | 70 | 350 | 0 | 0 | 0 |  | 4658 | 1914 | 6572 | 2413 | 433 | 1386 | 1695 | 425 | 45 | 66 | 88 | 21 | 0 | 99.32
15:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 183 | 240 |  | 0 | 280 | 0 | 98 | 70 | 41 | 0 | 0 | 0 | 54 | 8 | 32 | 49 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 25 | 12 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 15 | 86 | 90 | 0 | 20 | 1 | 20 | 0 | 5 | 5 | 110 | 160 | 20 | 79 | 0 | 75 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 250 | 0 | 0 | 0 | 0 | 82 | 0 | 75 | 50 | 0 | 239 | 45 | 0 | 0 | 2 | 124 | 54 | 0 | 0 | 28 | 60 | 0 | 14 | 9 | 0 | 0 |  | 433 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 130 | 0 | 257 | 70 | 0 | 50 | 0 | 0 | 0 | 2 | 0 | 300 | 0 | 0 | 0 |  | 4607 | 1684 | 6291 | 2508 | 433 | 1353 | 1412 | 374 | 45 | 66 | 86 | 14 | 0 | 99.32
16:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 319 | 335 |  | 0 | 400 | 0 | 100 | 64 | 41 | 0 | 0 | 0 | 10 | 8 | 32 | 71 | 0 | 0 | 6 | 54 | 55 | 17 | 16 | 25 | 12 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 135 | 150 | 135 | 0 | 0 | 15 | 0 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 18 | 86 | 107 | 3 | 20 | 0 | 20 | 0 | 5 | 5 | 110 | 0 | 20 | 78 | 0 | 75 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 200 | 0 | 0 | 0 | 0 | 58 | 0 | 62 | 50 | 0 | 238 | 61 | 0 | 0 | 1 | 88 | 54 | 0 | 0 | 28 | 30 | 0 | 82 | 7 | 0 | 0 |  | 433 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 130 | 0 | 279 | 70 | 0 | 50 | 0 | 0 | 0 | 1 | 0 | 300 | 0 | 0 | 0 |  | 4705 | 1718 | 6423 | 2525 | 433 | 1624 | 1262 | 373 | 45 | 66 | 86 | 9 | 0 | 99.31
17:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 347 | 335 |  | 0 | 380 | 0 | 100 | 64 | 41 | 0 | 0 | 0 | 20 | 8 | 32 | 74 | 0 | 0 | 20 | 54 | 55 | 17 | 16 | 25 | 12 | 25 | 17 | 16 | 0 | 47 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 18 | 135 | 150 | 100 | 0 | 0 | 145 | 0 | 0 | 26 | 5 | 0 | 1 | 0 | 0 | 4 | 21 | 8 | 0 | 19 | 90 | 109 | 22 | 20 | 0 | 20 | 0 | 13 | 10 | 110 | 0 | 20 | 78 | 0 | 95 | 0 | 0 | 0 | 290 | 0 | 8 | 0 | 250 | 0 | 0 | 0 | 0 | 50 | 0 | 62 | 50 | 1 | 238 | 96 | 0 | 0 | 0 | 126 | 54 | 0 | 0 | 28 | 85 | 0 | 90 | 0 | 0 | 0 |  | 433 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 130 | 0 | 258 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 0 |  | 5142 | 1792 | 6934 | 2677 | 433 | 1597 | 1584 | 373 | 47 | 133 | 90 | 0 | 0 | 99.31
18:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 346 | 335 |  | 0 | 420 | 0 | 100 | 64 | 41 | 0 | 0 | 0 | 48 | 8 | 64 | 64 | 0 | 0 | 24 | 54 | 55 | 17 | 16 | 25 | 8 | 25 | 25 | 16 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 14 | 135 | 150 | 100 | 0 | 0 | 143 | 8 | 0 | 26 | 5 | 0 | 39 | 0 | 0 | 43 | 21 | 8 | 33 | 21 | 110 | 109 | 50 | 20 | 0 | 15 | 20 | 51 | 40 | 163 | 0 | 20 | 78 | 0 | 105 | 0 | 0 | 0 | 290 | 0 | 8 | 0 | 280 | 0 | 0 | 5 | 0 | 87 | 0 | 100 | 50 | 5 | 238 | 115 | 0 | 0 | 0 | 176 | 54 | 0 | 0 | 24 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 41 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 154 | 0 | 424 | 105 | 0 | 111 | 0 | 108 | 0 | 0 | 95 | 340 | 0 | 0 | 0 |  | 5731 | 2708 | 8439 | 2776 | 669 | 1973 | 2249 | 415 | 46 | 201 | 110 | 0 | 0 | 99.31
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 338 | 335 |  | 0 | 420 | 0 | 100 | 64 | 55 | 0 | 0 | 0 | 48 | 8 | 82 | 61 | 0 | 0 | 24 | 54 | 55 | 17 | 16 | 25 | 19 | 25 | 17 | 16 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 22 | 15 | 16 | 135 | 150 | 100 | 0 | 0 | 146 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 108 | 111 | 72 | 20 | 0 | 15 | 20 | 48 | 50 | 163 | 0 | 20 | 78 | 0 | 95 | 0 | 0 | 0 | 285 | 8 | 8 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 90 | 6 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 55 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 160 | 0 | 379 | 105 | 0 | 111 | 0 | 95 | 0 | 0 | 70 | 490 | 0 | 0 | 0 |  | 5924 | 2819 | 8743 | 2749 | 669 | 1936 | 2441 | 566 | 47 | 227 | 108 | 0 | 0 | 99.3
19:30 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 343 | 335 |  | 0 | 420 | 0 | 50 | 64 | 55 | 0 | 0 | 0 | 48 | 8 | 82 | 60 | 0 | 0 | 24 | 54 | 55 | 17 | 16 | 25 | 24 | 25 | 33 | 16 | 0 | 48 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 45 | 15 | 18 | 135 | 150 | 100 | 0 | 0 | 144 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 108 | 110 | 72 | 20 | 0 | 15 | 20 | 48 | 50 | 130 | 0 | 20 | 78 | 0 | 105 | 0 | 0 | 0 | 300 | 8 | 5 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 100 | 6 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 55 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 235 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 160 | 0 | 424 | 105 | 0 | 111 | 0 | 35 | 0 | 0 | 35 | 500 | 5 | 0 | 0 |  | 5921 | 2794 | 8715 | 2774 | 669 | 1969 | 2344 | 576 | 48 | 227 | 108 | 0 | 0 | 0
20:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 338 | 335 |  | 0 | 420 | 0 | 60 | 64 | 55 | 0 | 0 | 0 | 48 | 8 | 82 | 64 | 0 | 0 | 24 | 35 | 55 | 17 | 16 | 25 | 28 | 25 | 33 | 16 | 0 | 48 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 40 | 15 | 21 | 135 | 150 | 100 | 0 | 0 | 147 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 102 | 105 | 72 | 20 | 0 | 20 | 20 | 50 | 50 | 130 | 0 | 20 | 78 | 0 | 95 | 0 | 0 | 0 | 290 | 8 | 7 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 100 | 8 | 237 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 55 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 230 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 96 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 388 | 105 | 0 | 111 | 0 | 35 | 0 | 0 | 35 | 500 | 5 | 0 | 0 |  | 5896 | 2716 | 8612 | 2763 | 669 | 1891 | 2336 | 576 | 48 | 227 | 102 | 0 | 0 | 99.3
21:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 337 | 336 |  | 0 | 400 | 0 | 50 | 55 | 55 | 0 | 0 | 0 | 40 | 8 | 64 | 71 | 0 | 0 | 24 | 35 | 55 | 17 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 15 | 23 | 135 | 150 | 100 | 0 | 0 | 146 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 104 | 105 | 72 | 20 | 0 | 20 | 20 | 48 | 50 | 130 | 0 | 36 | 78 | 0 | 95 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 300 | 0 | 0 | 24 | 0 | 78 | 0 | 100 | 100 | 8 | 236 | 115 | 0 | 0 | 0 | 189 | 54 | 0 | 0 | 34 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 215 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 96 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 391 | 105 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 500 | 6 | 0 | 0 |  | 5828 | 2536 | 8364 | 2774 | 669 | 1876 | 2109 | 575 | 48 | 209 | 104 | 0 | 0 | 99.3
22:00 | 0 | 97 | 0 | 115 | 300 | 6 | 0 | 335 | 334 |  | 0 | 400 | 0 | 50 | 15 | 40 | 0 | 0 | 0 | 0 | 0 | 16 | 71 | 0 | 0 | 0 | 35 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 15 | 29 | 135 | 150 | 100 | 0 | 0 | 147 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 24 | 21 | 8 | 25 | 21 | 98 | 111 | 42 | 20 | 0 | 20 | 20 | 50 | 50 | 130 | 7 | 36 | 78 | 0 | 95 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 150 | 0 | 0 | 0 | 0 | 45 | 0 | 100 | 100 | 8 | 236 | 115 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 670 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 372 | 105 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 500 | 5 | 0 | 0 |  | 5298 | 2373 | 7671 | 2768 | 670 | 1851 | 1575 | 576 | 48 | 85 | 98 | 0 | 0 | 99.29
23:00 | 0 | 100 | 0 | 115 | 300 | 6 | 0 | 333 | 334 |  | 0 | 400 | 0 | 50 | 15 | 40 | 0 | 0 | 0 | 0 | 0 | 16 | 74 | 0 | 0 | 0 | 35 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 32 | 135 | 135 | 100 | 0 | 0 | 95 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 25 | 21 | 8 | 25 | 21 | 92 | 111 | 24 | 20 | 0 | 20 | 20 | 50 | 47 | 130 | 12 | 36 | 78 | 0 | 95 | 0 | 0 | 0 | 270 | 16 | 11 | 0 | 150 | 0 | 0 | 0 | 0 | 28 | 0 | 100 | 100 | 5 | 239 | 115 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 386 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 364 | 105 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 500 | 6 | 0 | 0 |  | 5171 | 2026 | 7197 | 2704 | 386 | 1831 | 1493 | 576 | 47 | 68 | 92 | 0 | 0 | 99.29
24:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 339 | 324 |  | 0 | 380 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 35 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 32 | 135 | 120 | 100 | 0 | 0 | 28 | 8 | 0 | 23 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 80 | 113 | 16 | 20 | 0 | 20 | 20 | 50 | 50 | 130 | 116 | 36 | 78 | 0 | 95 | 0 | 0 | 0 | 230 | 16 | 11 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 6 | 237 | 115 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 |  | 386 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 366 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 470 | 35 | 0 | 0 |  | 4940 | 1869 | 6809 | 2723 | 386 | 1828 | 1149 | 546 | 45 | 52 | 80 | 0 | 0 | 99.29
KWH | 0 | 2526200 | 0 | 2772000 | 7228636 | 145318 | 0 | 5659000 | 7562000 |  | 0 | 8800250 | 0 | 1148160 | 694944 | 726344 | 0 | 0 | 0 | 958080 | 244224 | 722880 | 806989 | 0 | 0 | 173184 | 943560 | 959117 | 224080 | 173988 | 600000 | 538200 | 586300 | 654500 | 83004 | 0 | 1097280 | 0 | 0 | 0 | 0 | 4875813 | 0 | 0 | 0 |  | 63840 | 0 | 251862 | 0 | 0 | 332640 | 372144 | 552000 | 3193178 | 3384090 | 2795022 | 0 | 0 | 1005000 | 150545 | 0 | 552312 | 538080 | 0 | 748801 | 0 | 0 | 282998 | 473760 | 159120 | 320700 | 446390 | 1983360 | 3036520 | 447360 | 431244 | 3800 | 544000 | 124440 | 576000 | 617328 | 3234845 | 2331000 | 530400 | 1640640 | 0 | 2122630 | 0 | 0 | 0 | 6661200 | 69120 | 110000 | 0 | 4315635 | 0 | 0 | 93600 | 0 | 1172160 | 1755 | 1648320 | 1272480 | 78618 | 7457000 | 1586400 | 0 | 0 | 21000 | 2855345 | 1094527 | 0 | 0 | 493080 | 1346880 | 0 | 1151040 | 97690 | 0 | 38890 |  | 10520000 | 0 | 5976288 | 0 | 382080 | 0 | 0 | 0 | 0 | 0 | 121125 | 0 | 487900 | 447360 | 0 | 0 | 0 | 0 | 0 | 760472 | 8600 | 0 | 126 | 0 | 0 | 393120 | 0 | 203166 | 1766399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759937 | 0 | 4302445 | 0 | 8562273 | 1378080 | 0 | 1656480 | 0 | 220800 | 0 | 20211 | 631392 | 9901400 | 151170 | 0 | 0 |  | 115714840 | 48650824 | 164365664 | 65554606 | 10520000 | 41581407 | 30081416 | 11667799 | 1097280 | 1735340 | 1983360 | 144456 | 0
Fuel Cost | 0 | 3738776 | 0 | 4074840 | 8023785.96 | 191819.76 | 0 | 5715590 | 7788860 |  | 0 | 9592272.5 | 0 | 8714534.4 | 4788164.16 | 6144870.24 | 0 | 0 | 0 | 7214342.4 | 2227322.88 | 7113139.2 | 7440438.58 | 0 | 0 | 1574242.56 | 6887988 | 7413974.41 | 2209428.8 | 130491 | 450000 | 0 | 0 | 0 | 802648.68 | 0 | 296265.6 | 0 | 0 | 0 | 0 | 5314636.17 | 0 | 0 | 0 |  | 0 | 0 | 2443061.4 | 0 | 0 | 2634508.8 | 468901.44 | 1639440 | 4725903.44 | 5008453.2 | 4108682.34 | 0 | 0 | 924600 | 194203.05 | 0 | 624112.56 | 753312 | 0 | 1280449.71 | 0 | 0 | 2702630.9 | 601675.2 | 119340 | 561225 | 334792.5 | 14875200 | 3218711.2 | 4062028.8 | 547679.88 | 60572 | 892160 | 199104 | 1025280 | 963031.68 | 3687723.3 | 2424240 | 1044888 | 3133622.4 | 0 | 3672149.9 | 0 | 0 | 0 | 6727812 | 51840 | 83600 | 0 | 32626200.6 | 0 | 0 | 486720 | 0 | 11534054.4 | 20515.95 | 13433808 | 13806408 | 554256.9 | 6935010 | 14467968 | 0 | 0 | 0 | 21586408.2 | 9533330.17 | 0 | 0 | 4225695.6 | 8970220.8 | 0 | 0 | 0 | 0 | 0 |  | 60595200 | 0 | 6275102.4 | 0 | 3003148.8 | 0 | 0 | 0 | 0 | 0 | 1262122.5 | 0 | 756245 | 4366233.6 | 0 | 0 | 0 | 0 | 0 | 6730177.2 | 66220 | 0 | 1220.94 | 0 | 0 | 754790.4 | 0 | 153796.662 | 10651385.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1139905.5 | 0 | 5033860.65 | 0 | 8476650.27 | 14387155.2 | 0 | 15719995.2 | 0 | 1713408 | 0 | 223331.55 | 4665986.88 | 43467146 | 0 | 0 | 0 |  | 321823962.62 | 189443082.722 | 511267045.342 | 75457947.502 | 60595200 | 48105417.57 | 241226464.46 | 54118531.97 | 296265.6 | 16287598.74 | 14875200 | 304419.5 | 0
Yesterday Day Peak | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 3 | 337 |  | 0 | 370 | 0 | 85 | 27 | 41 | 0 | 0 | 0 | 100 | 40 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 12 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 140 | 150 | 135 | 0 | 0 | 0 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 18 | 86 | 107 | 0 | 20 | 0 | 20 | 0 | 5 | 5 | 130 | 159 | 20 | 76 | 0 | 78 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 50 | 0 | 237 | 25 | 0 | 0 | 4 | 162 | 54 | 0 | 0 | 28 | 100 | 0 | 90 | 10 | 0 | 0 |  | 456 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 195 | 0 | 366 | 53 | 0 | 111 | 0 | 0 | 0 | 4 | 35 | 350 | 0 | 0 | 0 |  | 6644 | DayPeak
Yesterday Evening Peak | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 338 | 335 | 0 | 0 | 420 | 0 | 100 | 64 | 55 | 0 | 0 | 0 | 48 | 8 | 82 | 61 | 0 | 0 | 24 | 54 | 55 | 17 | 16 | 25 | 19 | 25 | 17 | 16 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 22 | 15 | 16 | 135 | 150 | 100 | 0 | 0 | 146 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 108 | 111 | 72 | 20 | 0 | 15 | 20 | 48 | 50 | 163 | 0 | 20 | 78 | 0 | 95 | 0 | 0 | 0 | 285 | 8 | 8 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 90 | 6 | 238 | 115 | 0 | 0 | 0 | 179 | 54 | 0 | 0 | 55 | 100 | 0 | 70 | 0 | 0 | 0 |  | 669 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 160 | 0 | 379 | 105 | 0 | 111 | 0 | 95 | 0 | 0 | 70 | 490 | 0 | 0 | 0 |  | 8743 | EvPeak
Forecast for Evening | 0 | 100 | 0 | 115 | 300 | 7 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 47 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 85 | 100 | 102 | 50 | 15 | 20 | 135 | 129 | 100 | 0 | 0 | 180 | 26 | 0 | 20 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 148 | 150 | 95 | 20 | 0 | 20 | 20 | 51 | 44 | 163 | 152 | 32 | 86 | 0 | 150 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 702 | 16 | 250 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 34 | 50 | 50 | 52 | 33 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 0
Forecast for Day | 0 | 100 | 0 | 115 | 300 | 7 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 12 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 47 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 85 | 100 | 102 | 50 | 15 | 10 | 135 | 129 | 100 | 0 | 0 | 0 | 26 | 0 | 20 | 10 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 139 | 150 | 95 | 20 | 1.6 | 20 | 20 | 51 | 44 | 163 | 152 | 32 | 86 | 0 | 150 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 7 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 462 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 25 | 65 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 34 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 225 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 0
Generation at 08:00(Today) | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 352 | 274 | 0 | 0 | 350 | 0 | 53 | 0 | 15 | 0 | 0 | 0 | 16 | 0 | 0 | 42 | 0 | 0 | 0 | 54 | 35 | 0 | 16 | 25 | 33 | 25 |  | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 15 | 15 | 100 | 100 | 100 | 0 | 0 | 188 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 70 | 110 | 21 | 20 | 0 | 20 | 20 | 48 | 50 | 110 | 156 | 36 | 80 | 0 | 96 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 68 | 6 | 293 | 62 | 0 | 0 | 0 | 150 | 54 | 0 | 0 | 1 | 100 | 0 | 90 | 3 | 0 | 0 | 0 | 299 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 170 | 0 | 371 | 90 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 440 | 7 | 0 | 0 | 0
199
| Minimum Generation |  | 5083 | 5:00
| Highest Generation |  | 8743 | 19:00
| Day Peak Generation |  | 6644 | 12:00
| Evening Peak Generation |  | 8743 | 19:00
| HVDC Max Flow |  | 670 | 22:00
| HVDC EvPeak Flow |  | 669 | 19:00
| Load factor L.F |  | 78.33%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-13
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6644 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5400 | MW
Evening Peak Generation : |  | 8743 | MW Hour : | 19:00 | Available Max Generation : |  | 13407 | MW
E.P. Demand (at gen end) : |  | 8743 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 8743 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4207 | MW
Total Gen. (MKWH) : |  | 164.3657 | System Load Factor : | 78.33% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -173 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-13
Actual : | 99.28 | Ft.(MSL) , | Rule curve : | 104.9 | Ft.( MSL )
Gas Consumed : | Total = | 851.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 123563365.072
: |  | Coal : | 54118531.97 | Oil : | 257514063.2 | Total : | 435195960.242
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3259.3617 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1103.3711 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 987.6944 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 892.1494 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 806.3967 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 650.721 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 370.2754 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 167.7132 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 501.8376 |  |  | 0 | 0%
Total | 0 |  | 8739.5204 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71,100 MW | 11) Fenchugonj CCPP Phase-2
|  |  |  | 3) Ghorasal Unit-1,2,4 | 12) Summit Bibiyana-2
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9)Ashuganj(S)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) AKSML-BSRM 230 kV Ckt was under shut down from 08:33 to 15:29 for A/M.
b) Mymensing-Valuka 132 kV Ckt-2 was under shut down from 08:26 to 16:24 for A/M.
c) Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-1 was under shut down from 09:06 to 14:34 for A/M.
d) Daudkandi-Sonargaon 132 kV Ckt-1 was under shut down from 08:23 to 16:22 for A/M.
e) Ghorasal-Ashuganj 230 kV Ckt-1 was under shut down from 08:54 to 17:16 for A/M.
f) Faridpur-Bheramara 132 kV Ckt-2 was under shut down from 08:11 to 15:42 for A/M.
g) Maniknagar-Narinda 132 kV Ckt-2 was under shut down from 09:14 to 17:32 for A/M.
h) Khulna(S)-Satkhira 132 kV Ckt-2 was under shut down from 09:07 to 16:34 for A/M.
i) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 09:38 to 15:59 for A/M.
j) Rangpur-Rangpur confidence 132 kV Ckt-2 was under shut down from 09:32 to 16:04 for A/M.
k) Saidpur-Purbasadipur 132 kV Ckt-2 was under shut down from 08:41 to 16:39 for A/M.
l) Baghabari-Ishurdi 132 kV Ckt was under shut down from 08:55 to 17:54 for A/M.
m) Pabna-Shahjadpur 132 kV Ckt-1 was under shut down from 09:52 to 12:56 for A/M.
n) Bibiyana-Kaliakoir 400 kV Ckt-1 was shut down at 09*:17 for D/W.
o) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 09:17 to 20:11 for A/M.
p) Rajshahi-HVDC 230 kV Ckt-1 was under shut down from 11:24 to 16:59 for A/M.
q) Sikalbaha-Shahmirpur 132 kV Ckt-2 was under shut down from 07:42 to 16:23 for D/W.
r) Khulna©-Noapara 132 kV Ckt-1 was under shut down from 07:18 to 14:16 for A/M.
s) Cumilla(S) 132/33 kV T-1 transformer was under shut down from 08:20 to 15:46 for A/M.
t) Jhenaidah 132/33 kV T-1 transformer was under shut down from 09:02 to 14:37 for A/M.
t) Palashbari 132/33 kV T-4 transformer was under shut down from 08:05 to 17:25 for A/M.
u) Tongi 230/132 kV T-2 transformer was under shut down from 09:40 to 13:48 for A/M.
v) Aminbazar 132/33 kV T-1 transformer was under shut down from 10:22 to 16:30 for A/M.
w) Savar 132/33 kV T-1 transformer was under shut down from 09:24 to 16:26 for A/M.
x) Shahjibazar 132/33 kV T-2 transformer was shut down at 08:31 for A/M.
y) Haripur 230/132 kV T-3 transformer was under shut down from 08:35 to 17:02 for A/M.
z) Rajshahi new 132/33 kV T-1 transformer was under shut down from 08:29 to 17:19 for A/M.
aa) Cumilla(N) 132/33 kV T-4 transformer was under shut down from 10:29 to 16:32 for A/M.
ab) Hasnabad 230/132 kV T-1 transformer was under shut down from 11:12 to 17:25 for A/M.
ac) After maintenance Haripur-412 MW CCPP GT & ST were synchronized at 11:40 & 13:36 respectively.
ad) Shahjibazar-330 MW CCPP GT & ST tripped at 15:09 and were synchronized at 21:44 & 23:07 respectively.
ae) After maintenance Ashuganj-225 MW CCPP GT & ST were synchronized at 15:58 & 01:59 respectively.
af) Patuakhali 132/33 kV T-2 transformer was under shut down from 15:26 to 16:40 for oil filling.
ag) Khulna©-Noapara 132 kV Ckt-1 tripped at 21:17 showing O/C & E/F relays and was switched on at 21:27.
ah) Summit Bibiyana-2 was shut down at 07:31(13/12/20) for maintenance.
ai) Rampura-Bhulta 230 kV Ckt-2 is under shut down since 07:40(13/12/20) for A/M.
aj) Khulna©-Noapara 132 kV Ckt-1 is under shut down since 07:31(13/12/20) for A/M.
ak) Kallyanpur 132 kV Bus is under shut down since 07:48(13/12/20) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 98 | 2526200 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7228636 | Machine problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 6 | 145318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 5659000 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 335 | 7562000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8800250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1148160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 694944 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 726344
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 61 | 806989 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 173988 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 48 | 958080 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 244224 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 24 | 173184 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 943560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 722880 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 959117
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 224080 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 1138200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 586300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 654500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 16 | 83004 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4315635
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 100 | 1172160 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1151040 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 6057 | 2768 | 51569793
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 1755
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 332640 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 47 | 1097280 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4875813
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 251862 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1648320
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 372144 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 552000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 179 | 2855345 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1094527
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1346880
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 38890
| Chattogram area Total |  |  |  | 2266 | 787 | 14488456
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 3193178
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 3384090
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2795022 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 146 | 1005000
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 552312 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 538080 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 150545 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 748801
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 78618 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 90 | 1272480 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 473760
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 159120 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 1983360
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 320700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 282998
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 446390
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 493080 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 999 | 17877534
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 111 | 3036520 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 431244
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 447360 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 24 | 93600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1586400 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 97690
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 63840
| Mymensingh Area Total |  |  |  | 687 | 342 | 5760454
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 15 | 544000 | Gas shortage
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 124440 | Gas shortage
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3234845
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 2331000 | Gas shortage & GT-1 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 576000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 617328
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 110000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 530400 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1640640
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2122630
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 69120 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6661200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 238 | 7457000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1028 | 26018603
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 669 | 10520000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 382080
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 240 | 5976288 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 121125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1378080
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1169 | 18377573
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 447360 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 487900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 52 | 759937
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 490 | 9901400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 151170
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 632 | 11747767
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 8600 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 126 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4302445 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 379 | 8562273 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 393120
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203166
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 760472 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1656480
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 631392 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 847 | 16518074
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1766399
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 95 | 220800 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20211
| Rangpur Area Total |  |  |  | 605 | 171 | 2007410
| Total |  |  |  | 20104 | 8743 | 164365664
| Eastern Grid Total |  |  |  | 13978 | 5924 | 115714840
| Western Grid Total |  |  |  | 6126 | 2819 | 48650824
| National Grid Total |  |  |  | 20104 | 8743 | 164365664
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-12
| (a) ENTIRE EASTERN GRID : |  | 5597 | MW | (b) ENTIRE WESTERN GRID : |  | 2697 | MW
| i) Dhaka area |  | 3001 | MW | i) Khulna area |  | 1050 | MW
| ii) Chittagong area |  | 856 | MW | ii) Rajshahi area |  | 836 | MW
| iii) Comilla area |  | 763 | MW | iii) Barisal area |  | 229 | MW
| iv) Mymensingh area |  | 659 | MW | iv) Rangpur area |  | 582 | MW
| v) Sylhet area |  | 318 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8294 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 18:30 | Jamalpur | 87 | 20:00 | Benapol | 34 | 18:00
| Munsiganj | 82 | 19:30 | Sherpur | 86 | 18:30 | Jhenida | 78 | 18:00
| Sonargaon | 57 | 12:00 | Srimongal | 39 | 19:30 | Bottail | 94 | 18:00
| Shyampur | 152 | 16:00 | Shahjibazar | 67 | 18:30 | G.K Project | 35 | 18:00
| Bhulta | 136 | 24:00 | Fenchuganj | 24 | 18:00 | Faridpur | 130 | 18:30
| Madanganj | 44 | 19:30 | Kulawara | 30 | 19:00 | Madaripur | 64 | 20:00
| Shitalakhya | 106 | 11:00 | Sylhet | 85 | 17:00 | Sariatpur | 42 | 19:30
| Rahim steel | 7 | 1:00 | Chatak | 20 | 18:00 | Gopalganj | 58 | 18:30
| Matuail | 42 | 8:00 | Sunamganj | 26 | 19:00 | Bagerhat | 80 | 19:00
| Ghorasal | 62 | 18:00 | Biani Bazar | 38 | 18:00 | Mongla | 34 | 12:00
| Narsingdi | 123 | 20:00 | Comilla (S) | 110 | 18:00 | Satkhira | 75 | 18:30
| Haripur (SBU) | 86 | 19:00 | Comilla(N) | 77 | 20:00 | Gallamari | 20 | 22:00
| Ullon | 40 | 18:30 | Chandpur | 74 | 20:00 | Magura | 36 | 18:00
| Hasnabad | 138 | 19:00 | Feni | 79 | 19:00 | Norail | 24 | 18:00
| Magbazar | 63 | 13:00 | Chowmuhani | 124 | 18:00 | Chuadanga | 61 | 18:30
| Maniknagar | 62 | 13:00 | Ashuganj | 46 | 19:00 | Barisal(N) | 28 | 19:30
| Bangabhaban | 12 | 10:00 | Daudkandi | 96 | 19:00 | Barisal (S) | 70 | 20:00
| Narinda | 62 | 19:30 | B.Baria | 90 | 18:30 | Patuakhali | 78 | 20:00
| Dhanmondi | 87 | 14:00 | Ramganj | 56 | 20:00 | Bhandaria | 40 | 19:00
| Lalbag | 66 | 13:00 | Chaddagram | 22 | 18:00 | Borhan Uddin | 26 | 21:00
| Madartek | 44 | 18:30 | PHP | 11 | 14:00 | Ishurdi | 49 | 18:00
| Dhaka University |  |  | Madunaghat | 43 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.5 | Hathazari | 72 | 0.77083 | Natore | 80 | 0.75
| Fatullah | 31 | 10:00 | Khulshi | 140 | 18:30 | Bogra | 113 | 18:30
| Mirpur | 68 | 14:00 | Halishahar | 91 | 18:00 | Noagaon | 80 | 19:00
| Kalyanpur | 63 | 18:00 | Baraulia | 154 | 12:00 | Rajshahi | 95 | 19:30
| Gulshan | 66 | 13:00 | Sikalbaha | 21 | 19:30 | Rajshahi New | 7 | 20:00
| Uttara | 61 | 14:00 | Dohazari | 54 | 19:30 | C.Nawabganj | 54 | 20:00
| Uttara New | 22 | 12:00 | Cox'sbazar | 77 | 19:00 | Amnura | 28 | 20:00
| Kamrangirchar | 70 | 13:00 | Chandraghona | 20 | 18:00 | Pabna | 82 | 18:30
| Savar | 111 | 16:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 67 | 18:00
| Bhasantec | 94 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 55 | 19:00
| Agargaon | 41 | 13:00 | Bakulia | 69 | 18:00 | Niyamatpur | 39 | 18:00
| Satmosjid | 64 | 0.54167 | Julda | 14 | 0.041667 | Joypurhat | 40 | 0.79167
| Tongi | 83 | 18:00 | TK chemical | 20 | 20:00 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 170 | 19:00 | Modern Steel | 15 | 3:00 | Mohastangor | 32 | 18:00
| Basundhara | 85 | 18:00 | Shahmirpur | 17 | 18:00 | Rangpur | 105 | 18:30
| Manikganj | 44 | 18:30 | Khagrachhari | 18 | 6:00 | Lalmonirhat | 41 | 19:00
| Joydevpur | 112 | 18:30 | Matarbari | 25 | 20:00 | Saidpur | 85 | 18:00
| New Tongi | 83 | 15:00 | Baroiar Hat | 20 | 18:00 | Purbasadipur | 84 | 20:00
| Kodda | 168 | 18:00 | Rangamati | 8 | 13:00 | Thakurgaon | 59 | 19:00
| Dhamrai | 68 | 18:30 | Abul Khair 230 | 140 | 23:00 | Palashbari | 94 | 18:00
| Rajendrapur | 70 | 18:30 | BSRM | 152 | 3:00 | Barapukuria | 38 | 19:30
| Valuka | 70 | 18:00 | GPH Ispat | 74 | 19:30 | Panchagar | 45 | 18:00
| Tangail | 130 | 18:30 | Goalpara | 16 | 20:00 | Joldhaka | 19 | 18:30
| Mymensing | 147 | 18:30 | Central s/s | 81 | 18:30 | Kurigram | 41 | 18:30
| Kishorganj | 76 | 20:00 | Noapara | 51 | 18:30
| Netrokona | 79 | 19:30 | Jessore | 74 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 6:00 | 408 | 3:00 | Kaliakoir | 399 | 0.125 | 380 | 0.625
| Bheramara | 411 | 24:00 | 399 | 10:00 | Bhulta | 385 | 0.33333 | 373 | 0.625
| Ashuganj(N) | 388 | 8:00 | 379 | 18:00 | Gopalganj | 421 | 0.16667 | 404 | 0.77083
| Payra | 421 | 8:00 | 410 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 238 | 1:00 | Comilla (N) | 239 | 8:00 | 235 | 18:00
| Ishurdi | 240 | 4:00 | 234 | 15:00 | Hathazari | 230 | 6:00 | 216 | 18:00
| Ashuganj | 240 | 8:00 | 234 | 16:00 | Megnaghat | 235 | 24:00 | 232 | 1:00
| Serajganj | 233 | 4:00 | 230 | 10:00 | Fenchuganj | 247 | 8:00 | 241 | 5:00
| Baghabari | 245 | 6:00 | 240 | 1:00 | Siddhirganj | 234 | 8:00 | 229 | 12:00
| Barapukuria | 233 | 3:00 | 226 | 19:30 | Maniknagar | 233 | 8:00 | 227 | 15:00
| Bogra | 235 | 5:00 | 227 | 21:00 | Agargaon | 234 | 10:00 | 226 | 18:00
| Rajshahi | 230 | 2:00 | 224 | 17:00 | Barisal | 252 | 9:00 | 240 | 18:00
| Khulna South | 237 | 4:00 | 229 | 14:00 | AKSML | 225 | 19:00 | 212 | 3:00
| Rampura | 231 | 8:00 | 229 | 11:00 | BSRM | 228 | 21:00 | 213 | 3:00
| Haripur | 232 | 7:00 | 228 | 11:00 | Bibiyana | 244 | 6:00 | 239 | 13:00
| Hasnabad | 232 | 5:00 | 227 | 12:00 | Bhulta | 233 | 19:00 | 228 | 17:00
| Shyampur | 231 | 8:00 | 220 | 16:00 | Ashuganj (S) | 237 | 8:00 | 231 | 15:00
| Aminbazar | 234 | 7:00 | 228 | 17:00 | Kaliakoir | 235 | 8:00 | 226 | 15:00
| Tongi | 230 | 7:00 | 224 | 15:00 | GPH | 225 | 8:00 | 220 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 8:00 | 137 | 1:00 | Madanhat | 138 | 0.79167 | 131 | 0.58333
| Munsiganj | 142 | 13:00 | 136 | 1:00 | Hathazari | 137 | 0.16667 | 133 | 0.45833
| Sonargaon | 139 | 23:00 | 134 | 9:00 | Khulshi | 134 | 0.33333 | 127 | 0.125
| Shyampur | 134 | 6:00 | 129 | 16:00 | Halishahar | 136 | 0.875 | 128 | 0.041667
| Bhulta | 134 | 2:00 | 130 | 15:00 | Baraulia | 135 | 0.33333 | 130 | 0.625
| Madanganj | 142 | 14:00 | 136 | 1:00 | Sikalbaha | 136 | 0.79167 | 127 | 0.125
| Shitalakhya | 142 | 21:00 | 136 | 10:00 | Dohazari | 134 | 0.875 | 128 | 0.041667
| Rahim steal | 139 | 7:00 | 137 | 1:00 | Cox'sbazar | 129 | 0.33333 | 119 | 0.75
| Matuail | 140 | 8:00 | 137 | 1:00 | Chandraghona | 136 | 0.79167 | 129 | 0.125
| Ghorasal | 140 | 1:00 | 136 | 16:00 | Kaptai | 135 | 0.041667 | 132 | 0.5
| Narsinghdi | 138 | 11:00 | 135 | 1:00 | A. Khaer Stl. | 135 | 0.95833 | 130 | 0.125
| Haripur (SBU) | 140 | 14:00 | 136 | 1:00 | Bakulia | 135 | 0.33333 | 128 | 0.20833
| Ullon | 133 | 6:00 | 130 | 11:00 | Julda | 135 | 0.29167 | 128 | 0.041667
| Hasnabad | 140 | 4:00 | 135 | 10:00 | TK Chemical | 136 | 0.8125 | 132 | 0.375
| Magbazar | 135 | 8:00 | 130 | 11:00 | Modern Steel | 135 | 0.83333 | 126 | 0.083333
| Maniknagar | 138 | 1:00 | 127 | 15:00 | Shahmirpur | 137 | 0.5 | 131 | 0.66667
| Bangabhaban | 138 | 1:00 | 127 | 15:00 | Khagrachhari | 135 | 0.25 | 129 | 0.125
| Narinda | 138 | 1:00 | 127 | 15:00 | Matarbari | 133 | 0.83333 | 128 | 0.625
| Dhanmondi | 133 | 6:00 | 130 | 11:00 | Baroiar Hat | 138 | 0.41667 | 134 | 0.041667
| Lalbag | 140 | 8:00 | 134 | 12:00 | Rangamati | 136 | 22:00 | 130 | 15:00
| Madartek | 133 | 6:00 | 129 | 18:00 | Goalpara S/S | 139 | 6:00 | 134 | 14:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 11:00 | 132 | 0.54167
| Aftabnagar | 133 | 4:00 | 129 | 15:00 | Noapara | 138 | 4:00 | 131 | 0.58333
| Fatuiiah | 136 | 6:00 | 130 | 10:00 | Jessore | 135 | 2:00 | 129 | 0.5
| Mirpur | 131 | 2:00 | 126 | 15:00 | Benapol | 137 | 0.16667 | 130 | 0.54167
| Kalyanpur | 132 | 2:00 | 127 | 16:00 | Jhenida | 136 | 2:00 | 128 | 0.75
| Gulshan | 132 | 6:00 | 129 | 12:00 | Bottail | 139 | 0.16667 | 133 | 0.58333
| Uttara | 138 | 8:00 | 132 | 14:00 | G.K Project | 141 | 0.25 | 138 | 0.875
| Uttara New | 130 | 1:00 | 125 | 16:00 | Faridpur | 139 | 0.16667 | 133 | 0.75
| Kamrangirchar | 139 | 3:00 | 131 | 15:00 | Madaripur | 140 | 0.125 | 135 | 0.5
| Savar | 130 | 8:00 | 126 | 13:00 | Shariyatpur S/S | 141 | 5:00 | 135 | 0.75
| Bhasantec | 136 | 8:00 | 131 | 18:00 | Gopalganj | 143 | 0.66667 | 135 | 0.77083
| Agargaon | 137 | 8:00 | 132 | 18:00 | Bagerhat | 140 | 4:00 | 134 | 0.58333
| Satmosjid | 135 | 1:00 | 132 | 18:00 | Mongla | 137 | 9:00 | 131 | 0.58333
| Tongi | 141 | 8:00 | 135 | 15:00 | Satkhira | 138 | 9:00 | 132 | 14:00
| Kabirpur | 137 | 6:00 | 128 | 18:30 | Gallamari | 140 | 0.8125 | 136 | 0.875
| Basundhara | 135 | 21:00 | 129 | 18:00 | Magura | 136 | 5:00 | 127 | 0.75
| Manikganj | 142 | 19:30 | 135 | 16:00 | Norail | 137 | 0.16667 | 126 | 0.75
| Joydevpur | 140 | 17:00 | 138 | 22:00 | Chuadanga | 134 | 6:00 | 124 | 0.77083
| New Tongi | 139 | 8:00 | 133 | 12:00 | Barisal(N) | 141 | 4:00 | 136 | 18:00
| Kodda | 136 | 20:00 | 129 | 16:00 | Barisal (S) | 140 | 0.29167 | 136 | 0.45833
| Dhamrai | 136 | 8:00 | 127 | 18:00 | Patuakhali(S) | 138 | 0.16667 | 132 | 0.70833
| Rajendrapur | 139 | 9:00 | 134 | 13:00 | Bhandaria | 140 | 0.41667 | 133 | 0.75
| Valuka | 135 | 8:00 | 120 | 18:00 | Ishurdi | 140 | 4:00 | 137 | 9:00
| Tangail | 136 | 4:00 | 125 | 18:00 | Ruppur Paromanobik | 140 | 4:00 | 136 | 12:00
| Mymensing | 135 | 8:00 | 124 | 18:30 | Natore | 140 | 3:00 | 135 | 19:30
| Kishorganj | 134 | 9:00 | 124 | 18:00 | Bogra | 139 | 14:00 | 134 | 20:00
| Netrokona | 134 | 8:00 | 120 | 18:00 | Noagaon | 135 | 10:00 | 129 | 19:30
| Jamalpur | 140 | 9:00 | 128 | 1:00 | Rajshahi | 141 | 6:00 | 137 | 19:30
| Sherpur | 138 | 8:00 | 126 | 1:00 | Rajshahi New | 142 | 4:00 | 137 | 12:00
| Srimongal | 138 | 4:00 | 135 | 15:00 | C.Nawabganj | 141 | 6:00 | 136 | 12:00
| Shahjibazar | 136 | 7:00 | 132 | 20:00 | Amnura | 141 | 14:00 | 136 | 12:00
| Fenchuganj | 139 | 23:00 | 135 | 3:00 | Pabna | 139 | 2:00 | 135 | 20:00
| Khulawara | 138 | 24:00 | 135 | 13:00 | Shahjadpur | 141 | 15:00 | 140 | 1:00
| Sylhet | 136 | 24:00 | 133 | 12:00 | Serajganj | 136 | 4:00 | 134 | 19:30
| Chatak | 135 | 24:00 | 131 | 18:00 | Niyamatpur | 134 | 4:00 | 128 | 19:30
| Sunamganj | 134 | 1:00 | 131 | 18:00 | Joypurhat | 135 | 1:00 | 130 | 19:30
| Biani Bazar | 135 | 2:00 | 132 | 13:00 | Sherpur(Bogura) | 138 | 5:00 | 134 | 20:00
| Comilla(s) | 131 | 6:00 | 125 | 18:00 | Mohastangor | 138 | 10:00 | 132 | 19:30
| Comilla(n) | 143 | 14:00 | 139 | 18:00 | Rangpur | 130 | 6:00 | 122 | 19:00
| Chandpur | 143 | 14:00 | 136 | 1:00 | Lalmonirhat | 132 | 6:00 | 122 | 20:00
| Feni | 140 | 19:00 | 134 | 18:00 | Saidpur | 132 | 6:00 | 122 | 20:00
| Chowmuhani | 138 | 13:00 | 131 | 18:00 | Purbasadipur | 130 | 5:00 | 119 | 19:30
| Ashuganj | 139 | 6:00 | 133 | 13:00 | Thakurgaon | 130 | 1:00 | 119 | 19:30
| Daudkandi | 140 | 8:00 | 137 | 18:00 | Palashbari | 133 | 4:00 | 126 | 19:30
| B.Baria | 133 | 7:00 | 129 | 20:00 | Barapukuria | 133 | 3:00 | 126 | 19:30
| Ramganj | 137 | 19:30 | 134 | 9:00 | Panchagar | 130 | 4:00 | 117 | 19:30
| Chaddagram | 140 | 7:00 | 137 | 15:00 | Joldhaka | 130 | 4:00 | 118 | 19:30
| PHP | 139 | 9:00 | 132 | 18:00 | Kurigram | 129 | 0.083333 | 120 | 0.8125

## L-Curve
Date | 2020-12-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 83 | 4940 | 1869 | 6809 |  |  |  | QF-LDC-11
0:30 | 48.5 | 4428.5 | 1787 | 6215.5 | Date: | 2020-12-12
1:00 | 14 | 3917 | 1705 | 5622
1:30 | 24 | 3864.5 | 1628.5 | 5493
2:00 | 34 | 3812 | 1552 | 5364
2:30 | 41 | 3745.5 | 1539.5 | 5285 | [5 empty] | Gen. at Eve. Peak | 8743 | 8743 MW (19:00 )
3:00 | 48 | 3679 | 1527 | 5206 | [6 empty] | 19:00
3:30 | 59 | 3661.5 | 1485.5 | 5147 | [5 empty] | Gen. at Day Peak | 6644 | 6644 MW (12:00 )
4:00 | 70 | 3644 | 1444 | 5088 | [6 empty] | 12:00
4:30 | 53.5 | 3633 | 1452.5 | 5085.5 | [5 empty] | Highest Generation | 8743
5:00 | 37 | 3622 | 1461 | 5083 | [6 empty] | 19:00
5:30 | 50 | 3747.5 | 1489.5 | 5237
6:00 | 63 | 3873 | 1518 | 5391
6:30 | 118 | 4004.5 | 1549 | 5553.5
7:00 | 173 | 4136 | 1580 | 5716
7:30 | 131.5 | 4267 | 1690 | 5957
8:00 | 90 | 4398 | 1800 | 6198
8:30 | 76 | 4525 | 1892 | 6417
9:00 | 62 | 4652 | 1984 | 6636
9:30 | 95 | 4585 | 1944 | 6529
10:00 | 128 | 4518 | 1904 | 6422
10:30 | 181.5 | 4508 | 1955.5 | 6463.5
11:00 | 235 | 4498 | 2007 | 6505
11:30 | 156.5 | 4580.5 | 1994 | 6574.5
12:00 | 78 | 4663 | 1981 | 6644
12:30 | 50 | 4801.5 | 1998.5 | 6800
13:00 | 22 | 4940 | 2016 | 6956
13:30 | 16 | 4799 | 1965 | 6764
14:00 | 10 | 4658 | 1914 | 6572
14:30 | 47.5 | 4632.5 | 1799 | 6431.5
15:00 | 85 | 4607 | 1684 | 6291
15:30 | 70 | 4656 | 1701 | 6357
16:00 | 55 | 4705 | 1718 | 6423
16:30 | 73 | 4923.5 | 1755 | 6678.5
17:00 | 91 | 5142 | 1792 | 6934
17:30 | 48 | 5436.5 | 2250 | 7686.5
18:00 | 5 | 5731 | 2708 | 8439
18:30 | 12.5 | 5827.5 | 2763.5 | 8591
19:00 | 20 | 5924 | 2819 | 8743
19:30 | 29 | 5921 | 2794 | 8715
20:00 | 90 | 5896 | 2716 | 8612 |  |  |  | Executive Engineer
20:30 | 97.5 | 5862 | 2626 | 8488 |  |  |  | Network Operation Division
21:00 | 105 | 5828 | 2536 | 8364
21:30 | 71.5 | 5563 | 2454.5 | 8017.5
22:00 | 38 | 5298 | 2373 | 7671 |  |  |  |  | Page 6 of 7
22:30 | 64 | 5234.5 | 2199.5 | 7434
23:00 | 90 | 5171 | 2026 | 7197
23:30 | 86.5 | 5055.5 | 1947.5 | 7003
24:00 | 83 | 4940 | 1869 | 6809
8743 MW (19:00 )
6644 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-12 |  | Energy | 164365664
[11 empty] | 2020-12-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2723 | 386 | 1828 | 1493 | 546 | 45 | 52 | 0 | 80 | 0
0:30 | 2716 | 398.5 | 1834 | 784.5 | 509.5 | 44 | 26 | 0 | 75 | 0 | Date: | 2020-12-12
1:00 | 2709 | 411 | 1840 | 76 | 473 | 43 | 0 | 0 | 70 | 0
1:30 | 2720.5 | 411 | 1790 | 38 | 423 | 42.5 | 0 | 0 | 68 | 0 | [7 empty] | Total Energy | 164.3657 | Total Energy Gen 164.366 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.366 MKWHr
2:00 | 2732 | 411 | 1740 | 0 | 373 | 42 | 0 | 0 | 66 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2734.5 | 410.5 | 1684 | 0 | 348 | 42 | 0 | 0 | 66 | 0 | [7 empty] | Energy Requirement | 164.3657
3:00 | 2737 | 410 | 1628 | 0 | 323 | 42 | 0 | 0 | 66 | 0
3:30 | 2739.5 | 362 | 1613.5 | 0 | 323 | 43 | 0 | 0 | 66 | 0 | [6 empty] | Shortage
4:00 | 2742 | 314 | 1599 | 0 | 323 | 44 | 0 | 0 | 66 | 0
4:30 | 2752.5 | 314 | 1586.5 | 0 | 323 | 44.5 | 0 | 0 | 65 | 0
5:00 | 2763 | 314 | 1574 | 0 | 323 | 45 | 0 | 0 | 64 | 0
5:30 | 2708.5 | 314 | 1645 | 128 | 333 | 45.5 | 0 | 0 | 63 | 0
6:00 | 2654 | 314 | 1716 | 256 | 343 | 46 | 0 | 0 | 62 | 0
6:30 | 2631.5 | 314 | 1754.5 | 376.5 | 369.5 | 46.5 | 0 | 0 | 61 | 1 |  |  |  |  | Coal
7:00 | 2609 | 314 | 1793 | 497 | 396 | 47 | 0 | 0 | 60 | 2
7:30 | 2596.5 | 314 | 1753.5 | 734.5 | 425.5 | 47 | 20 | 0 | 63 | 4.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2584 | 314 | 1714 | 972 | 455 | 47 | 40 | 0 | 66 | 7
8:30 | 2565 | 314 | 1729.5 | 1167 | 465 | 47 | 52 | 0 | 70 | 10.5
9:00 | 2546 | 314 | 1745 | 1362 | 475 | 47 | 64 | 0 | 74 | 14
9:30 | 2510.5 | 314.5 | 1629 | 1433.5 | 450 | 47.5 | 57 | 0 | 77 | 23.5
10:00 | 2475 | 315 | 1513 | 1505 | 425 | 48 | 50 | 0 | 80 | 33
10:30 | 2457.5 | 385.5 | 1484.5 | 1534.5 | 425 | 47.5 | 33 | 0 | 83 | 44
11:00 | 2440 | 456 | 1456 | 1564 | 425 | 47 | 16 | 0 | 86 | 55
11:30 | 2428 | 456 | 1532 | 1569.5 | 424.5 | 46 | 16 | 0 | 86 | 56
12:00 | 2416 | 456 | 1608 | 1575 | 424 | 45 | 16 | 0 | 86 | 57
12:30 | 2412 | 453 | 1667 | 1643.5 | 429 | 44.5 | 41 | 0 | 87 | 55.5
13:00 | 2408 | 450 | 1726 | 1712 | 434 | 44 | 66 | 0 | 88 | 54
13:30 | 2408 | 450 | 1726 | 1712 | 434 | 44 | 66 | 0 | 88 | 54
14:00 | 2408 | 450 | 1726 | 1712 | 434 | 44 | 66 | 0 | 88 | 54
14:30 | 2458 | 441.5 | 1539.5 | 1562 | 404 | 44.5 | 66 | 0 | 87 | 40.5
15:00 | 2508 | 433 | 1353 | 1412 | 374 | 45 | 66 | 0 | 86 | 27
15:30 | 2516.5 | 433 | 1488.5 | 1337 | 373.5 | 45 | 66 | 0 | 86 | 19
16:00 | 2525 | 433 | 1624 | 1262 | 373 | 45 | 66 | 0 | 86 | 11
16:30 | 2601 | 433 | 1610.5 | 1423 | 373 | 46 | 99.5 | 0 | 88 | 5.5
17:00 | 2677 | 433 | 1597 | 1584 | 373 | 47 | 133 | 0 | 90 | 0
17:30 | 2726.5 | 551 | 1785 | 1916.5 | 394 | 46.5 | 167 | 0 | 100 | 0
18:00 | 2776 | 669 | 1973 | 2249 | 415 | 46 | 201 | 0 | 110 | 0
18:30 | 2762.5 | 669 | 1954.5 | 2345 | 490.5 | 46.5 | 214 | 0 | 109 | 0
19:00 | 2749 | 669 | 1936 | 2441 | 566 | 47 | 227 | 0 | 108 | 0
19:30 | 2774 | 669 | 1969 | 2344 | 576 | 48 | 227 | 0 | 108 | 0
20:00 | 2763 | 669 | 1891 | 2336 | 576 | 48 | 227 | 0 | 102 | 0
20:30 | 2768.5 | 669 | 1883.5 | 2222.5 | 575.5 | 48 | 218 | 0 | 103 | 0
21:00 | 2774 | 669 | 1876 | 2109 | 575 | 48 | 209 | 0 | 104 | 0
21:30 | 2771 | 669.5 | 1863.5 | 1842 | 575.5 | 48 | 147 | 0 | 101 | 0
22:00 | 2768 | 670 | 1851 | 1575 | 576 | 48 | 85 | 0 | 98 | 0
22:30 | 2736 | 528 | 1841 | 1534 | 576 | 47.5 | 76.5 | 0 | 95 | 0
23:00 | 2704 | 386 | 1831 | 1493 | 576 | 47 | 68 | 0 | 92 | 0
23:30 | 2713.5 | 386 | 1829.5 | 1493 | 561 | 46 | 60 | 0 | 86 | 0 | Max Temp. in Dhaka |  | 22.7° C
24:00 | 2723 | 386 | 1828 | 1493 | 546 | 45 | 52 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
Total Energy Gen 164.366 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.366 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 42 | 42 | 44 | 45 | 46 | 47 | 47 | 47 | 48 | 47 | 45 | 44 | 45 | 45 | 45 | 47 | 46 |  | 47 | 48 | 48 | 48 | 48 | 47 | 45 | 1097280
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 2 | [8 empty] | 0 | [9 empty] | 1755
6 | Sikalbaha 225MW CCPP (Gas) | 207 | 204 | 215 | 203 | 203 | 211 | 229 | 226 | 213 | 202 | 217 | 200 | 209 | 203 | 204 | 203 | 204 | 216 |  | 203 | 203 | 203 | 203 | 203 | 202 | 202 | 4875813
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 51 | 51 |  | 51 | 51 | 51 | 51 | 17 |  | 0 | 251862
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 40 | 100 | 235 | 275 | 281 | 293 | 300 | 300 | 250 | 200 | 250 | 280 |  | 300 | 300 | 300 | 300 | 150 | 150 | 65 | 4315635
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 150545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 98 | 98 | 98 | 99 | 99 | 98 | 98 | 100 | 99 | 99 | 99 | 99 | 99 | 98 | 99 | 99 | 99 | 98 |  | 98 | 98 | 99 | 99 | 97 | 100 | 99 | 2526200
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7228636
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 135 | 138 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3193178
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 120 | 148 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 135 | 120 | 3384090
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2795022
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 23 | 23 | 19 | 19 | 19 | 23 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 552312
33 | Ashuganj 225 MW CCPP | [15 empty] | 15 | 145 | 143 |  | 146 | 144 | 147 | 146 | 147 | 95 | 28 | 1005000
34 | Ashuganj 450 MW CCPP(South)
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 55 | 56 | 56 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 538080
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 393 | 393 | 393 | 390 | 393 | 232 | [5 empty] | 3 | 38 | 69 | 183 | 319 | 347 | 346 |  | 338 | 343 | 338 | 337 | 335 | 333 | 339 | 5659000
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 340 | 340 | 340 | 340 | 340 | 400 | 400 | 400 | 370 | 370 | 370 | 420 | 300 | 280 | 400 | 380 | 420 |  | 420 | 420 | 420 | 400 | 400 | 400 | 380 | 8800250
41 | Haripur 360MW CCPP(HPL) | 303 | 305 | 304 | 303 | 304 | 339 | 323 | 324 | 324 | 300 | 310 | 337 | 337 | 240 | 240 | 335 | 335 | 335 |  | 335 | 335 | 335 | 336 | 334 | 334 | 324 | 7562000
42 | RPCL 210MW CCPP | 163 | 164 | 164 | 166 | 166 | 162 | 164 | 166 | 163 | 145 | 118 | 107 | 90 | 90 | 90 | 107 | 109 | 109 |  | 111 | 110 | 105 | 105 | 111 | 111 | 113 | 3036520
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 6 | 6 | 10 | 10 | 19 | 13 | 9 | 7 | 0 | [9 empty] | 97690
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 |  | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 544000
45 | Fenchugonj CCPP Phase-2 | [17 empty] | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 124440
46 | Shajibazar 330 MW CCPP | 159 | 158 | 159 | 158 | 158 | 158 | 155 | 157 | 159 | 160 | 155 | 159 | 160 | 161 | 160 | [8 empty] | 7 | 12 | 116 | 2331000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 36 | 36 | 36 | 36 | 530400
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 80 | 20 | 20 | 10 | 40 | 70 | 75 | 75 | 77 | 77 | 76 | 75 | 76 | 79 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1640640
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 75 | 75 | 75 | 75 | 85 | 90 | 85 | 95 | 96 | 83 | 85 | 78 | 75 | 75 | 75 | 75 | 95 | 105 |  | 95 | 105 | 95 | 95 | 95 | 95 | 95 | 2122630
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | [5 empty] | 2 | 2 |  |  | 2 |  |  | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 5 | 7 | 8 | 11 | 11 | 11 | 110000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 13 | 51 |  | 48 | 48 | 50 | 48 | 50 | 50 | 50 | 576000
56 | Shahjahanulla 25 MW PP | [19 empty] | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 69120
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 275 | 280 | 300 | 280 | 300 | 290 | 290 | 270 | 160 | 160 | 225 | 295 | 255 | 270 | 300 | 290 | 290 |  | 285 | 300 | 290 | 290 | 280 | 270 | 230 | 6661200
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 12 | 55 | 55 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 224080
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 16 | 21 | 26 | [11 empty] | 63840
60 | Barabkunda 22 MW PP (Regent) |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 372144
61 | Narshingdi 22 MW PP (Doreen) | [11 empty] | 16 |  |  | 13 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 173988
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431244
63 | Impoprt (Tripura) | 70 | 66 | 66 | 66 | 64 | 62 | 60 | 66 | 74 | 80 | 86 | 86 | 88 | 88 | 86 | 86 | 90 | 110 |  | 108 | 108 | 102 | 104 | 98 | 92 | 80 | 1983360
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 5 | 5 | 42 | 38 | 8 | 5 | 4 | 4 | 4 | 9 | 6 | 5 | 6 | 18 | 14 |  | 16 | 18 | 21 | 23 | 29 | 32 | 32 | 552000
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 473760
66 | Feni 11 MW PP (Doreen) | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159120
67 | Jangalia 33MW PP (Summit) | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 33 | 33 | 5 | [7 empty] | 33 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 320700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 18 | 15 | 15 | 15 | 13 | 12 | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 446390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 |  | 19 | 24 | 28 | 32 | 33 | 33 | 33 | 538200
71 | Maona 33 MW PP(Summit) | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 586300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 654500
73 | Ghorashal 108MW PP (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 145318
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [8 empty] | 1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 |  | 55 | 55 | 55 | 34 |  |  | 0 | 493080
Manikgonj 162MW PP(MPGL)
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 8 | 60 | 90 | 94 | 100 | 100 | 100 | 100 | 54 | 10 | 20 | 48 |  | 48 | 48 | 48 | 40 |  |  | 0 | 958080
78 | Gazipur 52 MW PP | [8 empty] | 13 | [7 empty] | 16 | 16 |  | 16 | 16 | 16 |  |  |  | 0 | 83004
79 | Kodda 150MW PP | [7 empty] | 40 | 64 | 50 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 64 |  | 82 | 82 | 82 | 64 | 16 | 16 | 0 | 722880
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 6 | 24 | [6 empty] | 3 | 22 | 50 |  | 72 | 72 | 72 | 72 | 42 | 24 | 16 | 447360
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 4 | 43 |  | 52 | 52 | 52 | 52 | 24 | 25 |  | 282998
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 2 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 21000
| Jodiac Power | 54 |  |  |  |  | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1094527
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [10 empty] | 7 | 27 | 52 | 70 | 70 | 64 | 64 | 64 |  | 64 | 64 | 64 | 55 | 15 | 15 | 0 | 694944
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 1 | 8 | 12 | 7 | 11 | 12 | 19 | 37 | 49 | 71 | 74 | 64 |  | 61 | 60 | 64 | 71 | 71 | 74 | 73 | 806989
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [5 empty] | 6 | 7 | 7 | 7 | 7 | 48 | 85 | 93 | 96 | 98 | 100 | 100 | 100 |  | 100 | 50 | 60 | 50 | 50 | 50 | 50 | 1148160
| Meghnaghat 104 MW PP (OPCL) | [5 empty] | 11 | 17 | 17 | 17 | 48 | 90 | 90 | 90 |  | 14 | 82 | 90 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1151040
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 40 |  | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 617328
93 | Ashuganj 51 MW PP (Midland) | 51 | 15 | 15 | 15 | 15 | 36 | 51 | 51 | 51 | 51 | [6 empty] | 1 | 39 |  | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 748801
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 16 | 40 | 40 | 24 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 244224
95 | Patenga 50MW PP (Baraka) | 6 |  |  |  |  | 3 | 18 | 18 | [11 empty] | 22 | 45 | 40 | 50 | 50 | 50 | 50 | 332640
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW | [15 empty] | 6 | 20 | 24 |  | 24 | 24 | 24 | 24 |  |  | 0 | 173184
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 5 | 22 | 30 | 35 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 726344
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 959117
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 110 | 110 | 110 | 110 | 163 |  | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 3234845
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 0 | [10 empty] | 3800
103 | Kamalaghat 54 MW PP(Banco Energy) | [5 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 943560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 5 |  | 24 | 24 | 24 | 24 |  |  | 0 | 93600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 42 | 82 | 95 | 92 | 60 | 68 | 82 | 82 | 58 | 50 | 87 |  | 100 | 100 | 100 | 78 | 45 | 28 | 0 | 1172160
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 10 | 40 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 75 | 62 | 62 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1648320
116 | Chandpur 200MW (Desh energy) | [5 empty] | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1272480
117 | Ashuganj 150MW PP (Midland) | [5 empty] | 2 | 5 | 7 | 6 | 6 | [6 empty] | 1 | 5 |  | 6 | 6 | 8 | 8 | 8 | 5 | 6 | 78618
118 | Bibiyana-III 400 MW CCPP | 351 | 351 | 351 | 351 | 351 | 314 | 312 | 232 | 232 | 236 | 236 | 237 | 237 | 239 | 239 | 238 | 238 | 238 |  | 238 | 238 | 237 | 236 | 236 | 239 | 237 | 7457000
| Jamalpur 115 MW PP (United) | [5 empty] | 3 | 46 | 96 | 115 | 75 | 25 | 25 | 44 | 45 | 45 | 61 | 96 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1586400
| Anwara 300 MW PP (United) | 16 |  |  |  |  | 85 | 117 | 155 | 158 | 161 | 161 | 162 | 162 | 126 | 124 | 88 | 126 | 176 |  | 179 | 179 | 179 | 189 | 180 | 180 | 180 | 2855345
| Juldah unit-2 (Acorn) | [7 empty] | 10 | 40 | 90 | 100 | 100 | 100 | 100 | 60 | 30 | 85 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1346880
| Anlima Energy Ltd. | [12 empty] | 20 | 20 | [11 empty] | 0 | 38890
120 | Eastern Zone Total | 3917 | 3812 | 3679 | 3644 | 3623 | 3873 | 4136 | 4398 | 4652 | 4518 | 4498 | 4663 | 4940 | 4658 | 4607 | 4705 | 5142 | 5731 |  | 5924 | 5921 | 5896 | 5828 | 5298 | 5171 | 4940 | 115714840
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 99 |  | 115 | 115 | 99 | 41 | 16 |  | 0 | 382080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 53 | 90 | 70 | 70 | 53 | 53 | 53 | 70 | 70 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 1378080
130
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | [20 empty] | 5 | 5 | 6 | 5 | 6 | 35 | 151170
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 41 |  | 64 | 80 | 96 | 96 | 80 | 48 | 0 | 447360
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 47 | 14 | 14 | 14 | 13 | 12 | 13 | 23 | 42 | 43 | 23 | 38 | 52 | 52 | 50 | 52 | 51 | 52 |  | 52 | 51 | 13 | 13 | 13 | 13 | 13 | 759937
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 21 | 18 | 21 | 20 | 14 | 14 | 11 | 18 | 19 | 22 | 21 | 19 | 21 | 20 | 26 |  | 26 | 26 | 27 | 27 | 26 | 23 | 23 | 487900
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 |  |  |  | 0 | 121125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 411 | 411 | 410 | 314 | 314 | 314 | 314 | 314 | 314 | 315 | 456 | 456 | 450 | 433 | 433 | 433 | 433 | 669 |  | 669 | 669 | 669 | 669 | 670 | 386 | 386 | 10520000
147 | Bheramara 410 MW CCPP | 215 | 225 | 225 | 240 | 245 | 250 | 255 | 290 | 285 | 270 | 260 | 250 | 235 | 235 | 235 | 245 | 250 | 250 |  | 240 | 235 | 230 | 215 | 195 | 190 | 185 | 5976288
148 | Payra 1320 MW | 400 | 300 | 250 | 250 | 250 | 270 | 320 | 380 | 400 | 350 | 350 | 350 | 360 | 350 | 300 | 300 | 300 | 340 |  | 490 | 500 | 500 | 500 | 500 | 500 | 470 | 9901400
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 73 | 73 | 73 | 76 | 75 | 75 | 75 | 75 | 74 | 74 | 75 | 74 | 73 | 73 | 75 |  | 76 | 76 | 76 | 75 | 76 | 76 | 76 | 1766399
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 156 | 158 | 158 | 167 | 174 | 177 | 179 | 195 | 200 | 200 | 200 | 195 | 188 | 160 | 130 | 130 | 130 | 154 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4302445
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 372 | 344 | 371 | 360 | 369 | 374 | 376 | 368 | 403 | 336 | 341 | 366 | 343 | 287 | 257 | 279 | 258 | 424 |  | 379 | 424 | 388 | 391 | 372 | 364 | 366 | 8562273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 393120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 203166
165 | Amnura 50 MW PP(Sinha) | [13 empty] | 3 | [11 empty] | 0 | 8600
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [26 empty] | 126
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 34 | 34 | 34 | 34 | 50 | 86 |  | 94 | 94 | 94 | 94 | 52 | 52 | 52 | 760472
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 58 | 109 | 111 | 111 | 111 | 111 | 111 | 50 | 50 | 70 | 111 |  | 111 | 111 | 111 | 111 | 70 | 70 | 35 | 1656480
172 | Confidence Power Bogura Unit-1 113 MW | [8 empty] | 20 | 90 | 70 | 35 | 60 | 70 |  |  | 25 | 95 |  | 70 | 35 | 35 |  |  |  | 0 | 631392
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 108 |  | 95 | 35 | 35 |  |  |  | 0 | 220800
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 2 | 3 | 3 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 20211
178
178