## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-14 | Monday
|  |  | Date (day): | 2020-12-14 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11975.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13483 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-13 | 2020-12-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 99 | 98 | 100 | 100 |  | 70 | Machine problem
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 305 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 6 | 7 | 7 | 100 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 369 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 295 | 290 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 31 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 57 | 60 | 40 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 60 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 60 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 3 | 64 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 12 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 58 | 58 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 8 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 157 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 65 | 130 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2392 | 2831 | 3644 | 3994 | 941 | 957
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 47 | 47 | 183 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 202 | 216 | 215 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 25 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 161 | 156 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 53 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 20 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 753 | 814 | 1440 | 1435 | 693 | 120
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 80 | 100 | 100
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 80 | 100 | 100
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 219 | 191 | 210 | 220 |  |  | Gas shortage
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 20 | 20 | 25 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 26 | 26 | 169 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 8 | 143 | 50 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maintenance
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 71 | 86 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 110 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 24 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 46 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 822 | 1005 | 1371 | 1741 | 244 | 883
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 107 | 101 | 150 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 50 |  | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 233 | 308 | 558.6 | 602 | 52 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 20 | 20 | 20 |  | 32 | GT-1 FGMO & GT-2 under S/D.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 22 | 22 | 22
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 122 | 156 | 156 | 156 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 50 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 36 | 36 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 79 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 95 | 130 | 150 | 150
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 303 | 238 | 400 | 400
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 20 | 20 | 20
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 909 | 996 | 1195 | 1195 | 178 | 415
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 536 | 774 | 549 | 790
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 180 | 180 | 410 | 410 | 160 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 105 | 105
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 806 | 1084 | 1409 | 1986 | 160 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 27 | 26 | 26
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 13 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 380 | 510 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 5 | 33 | 36 | 33
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 418 | 647 | 867 | 924 | 0 | 194
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 34 | 34 |  | 16 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 1 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 152 | 155 | 225 | 225 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 420 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 42 | 94 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 696 | 825 | 1370 | 1493 | 171 | 446
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 76 | 0 | 0 |  |  | Under maint
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 82 | 189 | 121 | 113 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7111 | 8699 | 11975.6 | 13483 | 2439 | 3487
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6727.6158 | 8230 | 11329.9446 | 12756.0743
| A. |  | 2020-12-13 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 8699 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5400 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8699 | MW
| 3 | Day peak Generation : |  |  | 7111 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8230 | MW
| 4 | Evening peak Generation : |  |  | 8699 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 169.2268 | MKWHr | By Solar | 0.25219 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 106.0394 | MKWHr |  | By Oil: | 34.9737 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.9328 | MKWHr |  | By Hydro: | 1.1044 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2439 | MW | Dhaka | 2968 | 2968 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3487 | MW | Chittagong | 866 | 866 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5926 | MW | Khulna | 1037 | 1037 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 868.42 | MMCFD |  |  | Rajshahi | 857 | 857 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 121586940.724 | ii) Oil : | Taka | 277813157.98 | Comilla | 759 | 759 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 59721306.27 | Total | Taka | 459121404.974 | Mymensingh | 624 | 624 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.7805 | MKWHr. | Sylhet | 311 | 311 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -92 | MW (E to W) at | 19:30 | hrs | Barisal | 235 | 235 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -214 | MW at | 18:00 | hrs | Rangpur | 573 | 573 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.7° C |  |  | Total | 8230 | 8230 |  | 0
| B. |  | 2020-12-14 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 27.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13483 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
| 4 | Reserve(Generation end) |  |  |  | 4383 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 177.0277 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5589 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8815 | MKWHr. | ii) HVDC Flow at Peak Time |  | 774 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0429 | MKWHr. | iii) Maximum HVDC Flow : |  | 774 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.28 |  | (b) Today: | 99.25 |  | (c) Rule Curve: |  | 104.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. |  | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 99 | 0 | 115 | 200 | 6 | 0 | 335 | 325 |  | 0 | 380 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 15 | 32 | 135 | 120 | 100 | 0 | 0 | 43 | 8 | 0 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 76 | 111 | 0 | 20 | 0 | 20 | 20 | 50 | 50 | 130 | 154 | 36 | 79 | 0 | 96 | 0 | 0 | 0 | 100 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 100 | 0 | 236 | 45 | 0 | 0 | 0 | 107 | 54 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 |  |  | 395 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 162 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 35 | 0 | 0 |  | 4270 | 1760 | 6030 | 2661 | 395 | 1730 | 578 | 546 | 44 | 0 | 76 | 0 | 0 | 99.28
2:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 336 | 324 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 8 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 15 | 32 | 135 | 120 | 100 | 0 | 0 | 45 | 8 | 0 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 70 | 110 | 0 | 20 | 0 | 20 | 20 | 50 | 50 | 130 | 157 | 36 | 80 | 0 | 96 | 0 | 0 | 0 | 80 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 236 | 16 | 0 | 0 | 0 | 34 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  |  | 394 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 174 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 22 | 0 | 0 |  | 3941 | 1746 | 5687 | 2635 | 394 | 1714 | 313 | 517 | 44 | 0 | 70 | 0 | 0 | 99.28
3:00 | 0 | 98 | 0 | 115 | 200 | 6 | 0 | 343 | 325 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 33 | 135 | 120 | 100 | 0 | 0 | 125 | 8 | 0 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 60 | 110 | 0 | 20 | 0 | 20 | 20 | 5 | 5 | 130 | 157 | 36 | 79 | 0 | 96 | 0 | 0 | 0 | 70 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 236 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 394 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 181 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 23 | 0 | 0 |  | 3821 | 1733 | 5554 | 2741 | 394 | 1599 | 201 | 516 | 43 | 0 | 60 | 0 | 0 | 99.28
4:00 | 0 | 99 | 0 | 115 | 200 | 6 | 0 | 357 | 324 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 38 | 125 | 120 | 100 | 0 | 0 | 215 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 54 | 110 | 0 | 20 | 0 | 20 | 20 | 5 | 5 | 163 | 160 | 35 | 5 | 0 | 107 | 0 | 0 | 0 | 50 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 299 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 182 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 23 | 0 | 0 |  | 3757 | 1691 | 5448 | 2900 | 299 | 1564 | 72 | 516 | 43 | 0 | 54 | 0 | 0 | 99.28
5:00 | 0 | 99 | 0 | 115 | 200 | 6 | 0 | 354 | 325 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 15 | 42 | 125 | 120 | 100 | 0 | 0 | 200 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 62 | 110 | 0 | 20 | 0 | 20 | 20 | 5 | 5 | 163 | 157 | 35 | 5 | 0 | 98 | 0 | 0 | 0 | 50 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 299 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 185 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 22 | 0 | 0 |  | 3707 | 1693 | 5400 | 2851 | 299 | 1567 | 60 | 517 | 44 | 0 | 62 | 0 | 0 | 99.28
6:00 | 0 | 99 | 0 | 115 | 200 | 6 | 0 | 365 | 324 |  | 0 | 420 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 13 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 15 | 42 | 125 | 120 | 100 | 0 | 0 | 190 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 66 | 112 | 0 | 20 | 0 | 20 | 20 | 30 | 20 | 163 | 166 | 36 | 40 | 0 | 95 | 0 | 0 | 0 | 45 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 0 | 325 | 0 | 0 | 0 | 0 | 33 | 54 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  |  | 299 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 186 | 0 | 374 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 460 | 23 | 0 | 0 |  | 4006 | 1698 | 5704 | 2951 | 299 | 1621 | 184 | 538 | 45 | 0 | 66 | 0 | 0 | 99.28
7:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 356 | 301 |  | 0 | 350 | 0 | 40 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 40 | 100 | 100 | 100 | 0 | 0 | 208 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 60 | 110 | 0 | 20 | 0 | 20 | 20 | 48 | 47 | 110 | 150 | 36 | 80 | 0 | 95 | 0 | 0 | 0 | 40 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 58 | 63 | 5 | 349 | 0 | 0 | 0 | 0 | 85 | 54 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 |  |  | 299 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 165 | 0 | 358 | 53 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 430 | 6 | 0 | 0 |  | 4318 | 1698 | 6016 | 3014 | 299 | 1520 | 568 | 507 | 47 | 0 | 60 | 1 | 0 | 99.27
8:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 352 | 274 |  | 0 | 350 | 0 | 53 | 0 | 15 | 0 | 0 | 0 | 16 | 0 | 0 | 42 | 0 | 0 | 0 | 54 | 35 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 15 | 15 | 100 | 100 | 100 | 0 | 0 | 188 | 8 | 0 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 70 | 110 | 21 | 20 | 0 | 20 | 20 | 48 | 50 | 110 | 156 | 36 | 80 | 0 | 96 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 68 | 6 | 293 | 62 | 0 | 0 | 0 | 150 | 54 | 0 | 0 | 1 | 100 | 0 | 90 | 3 | 0 | 0 |  |  | 299 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 170 | 0 | 371 | 90 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 440 | 7 | 0 | 0 |  | 4613 | 1796 | 6409 | 2951 | 299 | 1441 | 1074 | 519 | 47 | 0 | 70 | 8 | 0 | 99.27
9:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 352 | 274 |  | 0 | 350 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 48 | 15 | 8 | 100 | 100 | 80 | 0 | 0 | 203 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 78 | 109 | 32 | 20 | 1 | 20 | 20 | 48 | 50 | 110 | 157 | 36 | 77 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 18 | 8 | 100 | 68 | 6 | 303 | 115 | 0 | 0 | 1 | 158 | 54 | 0 | 0 | 9 | 100 | 0 | 90 | 11 | 0 | 0 |  |  | 299 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 170 | 0 | 410 | 90 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 410 | 6 | 0 | 0 |  | 4948 | 1889 | 6837 | 2981 | 299 | 1458 | 1433 | 489 | 47 | 31 | 78 | 21 | 0 | 99.27
10:00 | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 345 | 274 |  | 0 | 350 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 6 | 100 | 100 | 80 | 0 | 0 | 200 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 84 | 111 | 8 | 20 | 0 | 20 | 20 | 48 | 50 | 110 | 156 | 20 | 77 | 0 | 96 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 120 | 0 | 0 | 0 | 0 | 63 | 13 | 100 | 68 | 5 | 304 | 115 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 9 | 100 | 0 | 90 | 12 | 0 | 0 |  |  | 299 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 170 | 0 | 390 | 90 | 0 | 111 | 0 | 0 | 0 | 1 | 0 | 410 | 15 | 0 | 0 |  | 4973 | 1855 | 6828 | 2922 | 299 | 1446 | 1484 | 487 | 47 | 33 | 84 | 26 | 0 | 99.27
11:00 | 0 | 99 | 0 | 115 | 305 | 6 | 0 | 339 | 274 |  | 0 | 350 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 6 | 100 | 100 | 80 | 0 | 0 | 214 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 86 | 109 | 8 | 20 | 0 | 20 | 20 | 49 | 50 | 110 | 156 | 20 | 80 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 145 | 0 | 0 | 0 | 0 | 63 | 15 | 100 | 68 | 3 | 305 | 85 | 0 | 0 | 0 | 160 | 36 | 0 | 0 | 9 | 100 | 0 | 90 | 15 | 0 | 19 |  |  | 536 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 2 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 165 | 0 | 330 | 90 | 0 | 111 | 0 | 0 | 0 | 3 | 0 | 370 | 21 | 0 | 0 |  | 5015 | 1999 | 7014 | 2951 | 536 | 1393 | 1476 | 448 | 47 | 44 | 86 | 33 | 0 | 99.27
12:00 | 0 | 99 | 0 | 115 | 305 | 6 | 0 | 356 | 295 |  | 0 | 400 | 0 | 100 | 0 | 31 | 0 | 0 | 0 | 60 | 0 | 3 | 57 | 0 | 0 | 0 | 54 | 55 | 12 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 3 | 100 | 100 | 80 | 0 | 0 | 219 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 88 | 107 | 8 | 20 | 0 | 20 | 20 | 50 | 49 | 130 | 122 | 20 | 80 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 157 | 0 | 0 | 0 | 0 | 65 | 17 | 100 | 71 | 8 | 303 | 85 | 0 | 0 | 0 | 161 | 36 | 0 | 0 | 0 | 100 | 0 | 90 | 13 | 0 | 20 |  |  | 536 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 1 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 152 | 0 | 360 | 90 | 0 | 111 | 0 | 0 | 0 | 4 | 0 | 380 | 5 | 0 | 0 |  | 5109 | 2002 | 7111 | 2885 | 536 | 1497 | 1521 | 458 | 46 | 46 | 88 | 34 | 0 | 99.27
13:00 | 0 | 99 | 0 | 115 | 305 | 6 | 0 | 338 | 308 |  | 0 | 400 | 0 | 100 | 0 | 53 | 0 | 0 | 0 | 98 | 0 | 16 | 60 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 18 | 4 | 100 | 100 | 80 | 0 | 0 | 217 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 90 | 102 | 8 | 20 | 0 | 20 | 22 | 50 | 49 | 130 | 120 | 20 | 80 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 225 | 0 | 0 | 0 | 0 | 101 | 16 | 100 | 85 | 6 | 303 | 85 | 0 | 0 | 0 | 161 | 44 | 0 | 0 | 0 | 100 | 20 | 90 | 14 | 0 | 28 |  |  | 537 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 6 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 161 | 0 | 360 | 90 | 0 | 111 | 0 | 0 | 0 | 2 | 20 | 390 | 5 | 0 | 0 |  | 5337 | 2032 | 7369 | 2873 | 537 | 1512 | 1747 | 469 | 45 | 64 | 90 | 32 | 7369 | 99.27
14:00 | 0 | 99 | 0 | 115 | 250 | 6 | 0 | 339 | 320 |  | 0 | 320 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 100 | 0 | 16 | 52 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 18 | 8 | 100 | 100 | 80 | 0 | 0 | 150 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 90 | 91 | 8 | 20 | 0 | 20 | 22 | 50 | 20 | 110 | 157 | 20 | 80 | 0 | 96 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 235 | 0 | 0 | 0 | 0 | 100 | 13 | 100 | 85 | 6 | 240 | 85 | 0 | 0 | 0 | 161 | 46 | 0 | 0 | 0 | 100 | 20 | 90 | 25 | 0 | 0 |  |  | 537 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 319 | 90 | 0 | 111 | 0 | 0 | 0 | 3 | 35 | 360 | 0 | 0 | 0 |  | 5060 | 1935 | 6995 | 2671 | 537 | 1352 | 1757 | 438 | 44 | 65 | 90 | 41 | 0 | 99.27
15:00 | 0 | 100 | 0 | 115 | 290 | 6 | 0 | 337 | 300 |  | 0 | 380 | 0 | 100 | 0 | 40 | 0 | 0 | 0 | 100 | 0 | 16 | 60 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 18 | 5 | 100 | 100 | 80 | 0 | 0 | 183 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 86 | 89 | 8 | 20 | 0 | 20 | 22 | 25 | 20 | 110 | 156 | 20 | 50 | 0 | 75 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 195 | 0 | 0 | 0 | 0 | 100 | 9 | 100 | 85 | 5 | 240 | 85 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 100 | 20 | 90 | 14 | 0 | 0 |  |  | 537 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 6 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 147 | 0 | 317 | 70 | 0 | 111 | 0 | 0 | 0 | 1 | 35 | 350 | 0 | 0 | 0 |  | 5023 | 1906 | 6929 | 2728 | 537 | 1330 | 1697 | 427 | 44 | 56 | 86 | 24 | 0 | 99.27
16:00 | 0 | 99 | 0 | 115 | 290 | 6 | 0 | 352 | 280 |  | 0 | 380 | 0 | 100 | 0 | 40 | 0 | 0 | 0 | 85 | 0 | 16 | 57 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 32 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 17 | 8 | 100 | 100 | 80 | 0 | 0 | 194 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 16 | 90 | 87 | 8 | 20 | 0 | 20 | 22 | 25 | 20 | 110 | 155 | 20 | 10 | 0 | 80 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 195 | 0 | 0 | 0 | 0 | 85 | 4 | 100 | 85 | 13 | 239 | 85 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 100 | 20 | 90 | 6 | 0 | 0 |  |  | 537 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 161 | 0 | 368 | 70 | 0 | 70 | 0 | 0 | 0 | 1 | 0 | 350 | 7 | 0 | 0 |  | 4924 | 1884 | 6808 | 2723 | 537 | 1330 | 1596 | 426 | 45 | 50 | 90 | 11 | 0 | 99.26
17:00 | 0 | 99 | 0 | 115 | 260 | 6 | 0 | 346 | 240 |  | 0 | 300 | 0 | 100 | 6 | 40 | 0 | 0 | 0 | 80 | 66 | 28 | 51 | 0 | 0 | 1 | 54 | 55 | 17 | 19 | 25 | 32 | 25 | 33 | 20 | 0 | 45 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 22 | 0 | 85 | 0 | 42 | 50 | 17 | 12 | 80 | 85 | 80 | 0 | 0 | 191 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 2 | 21 | 5 | 25 | 16 | 88 | 107 | 8 | 20 | 0 | 20 | 22 | 25 | 20 | 110 | 157 | 20 | 10 | 0 | 68 | 18 | 0 | 0 | 0 | 16 | 5 | 0 | 230 | 0 | 0 | 8 | 0 | 105 | 0 | 100 | 75 | 45 | 239 | 115 | 9 | 0 | 0 | 107 | 54 | 0 | 34 | 27 | 100 | 20 | 90 | 1 | 54 | 0 |  |  | 537 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 6 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 150 | 0 | 250 | 70 | 0 | 92 | 0 | 35 | 0 | 0 | 25 | 280 | 6 | 0 | 0 |  | 5208 | 1811 | 7019 | 2710 | 537 | 1091 | 2027 | 356 | 45 | 164 | 88 | 1 | 0 | 99.26
18:00 | 0 | 99 | 0 | 115 | 280 | 6 | 0 | 328 | 300 |  | 0 | 350 | 0 | 100 | 30 | 55 | 0 | 0 | 0 | 100 | 102 | 100 | 59 | 0 | 0 | 6 | 54 | 55 | 52 | 19 | 25 | 32 | 25 | 17 | 43 | 0 | 45 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 |  | 22 | 0 | 85 | 0 | 77 | 50 | 17 | 17 | 80 | 80 | 80 | 0 | 0 | 166 | 8 | 0 | 26 | 20 | 0 | 51 | 0 | 0 | 13 | 21 | 5 | 25 | 21 | 112 | 107 | 36 | 20 | 0 | 20 | 22 | 50 | 43 | 163 | 153 | 20 | 79 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 300 | 0 | 0 | 29 | 0 | 141 | 0 | 100 | 2 | 125 | 239 | 115 | 17 | 0 | 0 | 107 | 53 | 0 | 34 | 46 | 100 | 20 | 90 | 0 | 55 | 0 |  |  | 774 | 0 | 155 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 153 | 0 | 395 | 90 | 0 | 111 | 0 | 108 | 0 | 0 | 35 | 320 | 34 | 0 | 0 |  | 6004 | 2561 | 8565 | 2726 | 774 | 1577 | 2670 | 396 | 45 | 265 | 112 | 0 | 0 | 99.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 98 | 0 | 115 | 280 | 6 | 0 | 338 | 300 |  | 0 | 380 | 0 | 100 | 15 | 55 | 0 | 0 | 0 | 100 | 60 | 100 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 8 | 25 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 22 | 0 | 85 | 0 | 38 | 50 | 17 | 23 | 80 | 80 | 80 | 0 | 0 | 186 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 5 | 25 | 21 | 106 | 100 | 50 | 20 | 0 | 20 | 22 | 53 | 50 | 163 | 157 | 20 | 79 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 8 | 0 | 149 | 0 | 100 | 80 | 145 | 239 | 115 | 0 | 0 | 0 | 144 | 53 | 0 | 0 | 46 | 100 | 20 | 90 | 0 | 18 | 0 |  |  | 773 | 0 | 165 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 156 | 0 | 370 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 35 | 430 | 35 | 0 | 0 |  | 6015 | 2673 | 8688 | 2779 | 773 | 1585 | 2615 | 506 | 45 | 279 | 106 | 0 | 0 | 99.26
19:30 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 369 | 290 |  | 0 | 420 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 100 | 60 | 64 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 0 | 50 | 17 | 25 | 80 | 80 | 80 | 0 | 0 | 191 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 25 | 21 | 110 | 101 | 50 | 20 | 0 | 20 | 22 | 53 | 50 | 163 | 156 | 20 | 79 | 0 | 130 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 130 | 0 | 100 | 86 | 143 | 238 | 115 | 0 | 0 | 0 | 156 | 53 | 0 | 0 | 46 | 100 | 20 | 90 | 0 | 0 | 0 |  |  | 774 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 155 | 0 | 420 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 510 | 33 | 0 | 0 |  | 5954 | 2745 | 8699 | 2875 | 774 | 1665 | 2434 | 586 | 46 | 209 | 110 | 0 | 0 | 0
20:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 350 | 290 |  | 0 | 420 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 100 | 55 | 64 | 52 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 20 | 0 | 51 | 0 | 0 | 50 | 17 | 29 | 80 | 80 | 80 | 0 | 0 | 196 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 25 | 21 | 110 | 102 | 67 | 20 | 0 | 20 | 22 | 53 | 50 | 130 | 156 | 20 | 79 | 0 | 129 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 136 | 0 | 100 | 92 | 143 | 239 | 115 | 0 | 0 | 0 | 160 | 51 | 0 | 0 | 46 | 100 | 20 | 90 | 0 | 0 | 0 |  |  | 774 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 75 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 156 | 0 | 385 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 510 | 9 | 0 | 0 |  | 5925 | 2674 | 8599 | 2858 | 774 | 1578 | 2437 | 585 | 48 | 209 | 110 | 0 | 0 | 99.26
21:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 340 | 291 |  | 0 | 420 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 100 | 7 | 32 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 16 | 0 | 17 | 0 | 0 | 50 | 17 | 31 | 80 | 80 | 80 | 0 | 0 | 187 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 25 | 21 | 102 | 102 | 95 | 20 | 0 | 20 | 22 | 53 | 50 | 130 | 157 | 20 | 79 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 106 | 0 | 100 | 100 | 147 | 239 | 115 | 0 | 0 | 0 | 161 | 53 | 0 | 0 | 8 | 100 | 20 | 90 | 0 | 0 | 0 |  |  | 774 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 80 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 167 | 0 | 413 | 90 | 0 | 111 | 0 | 40 | 0 | 0 | 0 | 530 | 9 | 0 | 0 |  | 5727 | 2675 | 8402 | 2856 | 774 | 1608 | 2265 | 606 | 48 | 143 | 102 | 0 | 0 | 99.26
22:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 337 | 291 |  | 0 | 420 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 60 | 0 | 32 | 62 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 17 | 37 | 80 | 80 | 80 | 0 | 0 | 183 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 100 | 103 | 95 | 20 | 0 | 20 | 22 | 53 | 50 | 130 | 158 | 20 | 79 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 245 | 0 | 0 | 0 | 0 | 86 | 0 | 100 | 100 | 123 | 239 | 115 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 60 | 20 | 90 | 0 | 0 | 0 |  |  | 774 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 173 | 0 | 288 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 540 | 8 | 0 | 0 |  | 5425 | 2478 | 7903 | 2890 | 774 | 1487 | 1864 | 615 | 48 | 125 | 100 | 0 | 0 | 99.26
23:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 345 | 291 |  | 0 | 380 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 67 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 17 | 38 | 80 | 80 | 80 | 0 | 0 | 184 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 92 | 106 | 64 | 20 | 0 | 20 | 22 | 53 | 50 | 130 | 156 | 20 | 79 | 0 | 133 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 42 | 0 | 100 | 100 | 122 | 238 | 115 | 0 | 0 | 0 | 160 | 48 | 0 | 0 | 0 | 30 | 20 | 90 | 0 | 0 | 0 |  |  | 641 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 185 | 0 | 430 | 90 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 480 | 36 | 0 | 0 |  | 5039 | 2331 | 7370 | 2961 | 641 | 1616 | 1440 | 555 | 49 | 16 | 92 | 0 | 0 | 99.26
24:00 | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 350 | 291 |  | 0 | 400 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 32 | 17 | 38 | 80 | 80 | 80 | 0 | 0 | 190 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 82 | 109 | 0 | 20 | 0 | 20 | 22 | 53 | 50 | 150 | 156 | 20 | 79 | 0 | 121 | 19 | 0 | 0 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 132 | 238 | 85 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 0 | 30 | 20 | 90 | 0 | 0 | 0 |  |  | 404 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 197 | 0 | 423 | 53 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 480 | 36 | 0 | 0 |  | 4829 | 1964 | 6793 | 2993 | 404 | 1648 | 1137 | 480 | 49 | 0 | 82 | 0 | 0 | 99.26
KWH | 0 | 2536900 | 0 | 2740500 | 7166555 | 210136 | 0 | 8410110 | 7128000 |  | 0 | 8790500 | 0 | 1780800 | 64224 | 645571 | 0 | 0 | 0 | 1216320 | 261360 | 422400 | 1284103 | 0 | 0 | 31440 | 1019520 | 859574 | 334383 | 359316 | 600000 | 700020 | 593600 | 699100 | 79020 | 0 | 1104436 | 0 | 0 | 0 | 0 | 4758231 | 0 | 0 | 0 |  | 233520 | 0 | 291730 | 0 | 167040 | 983040 | 376464 | 559680 | 2560474 | 2394590 | 2093762 | 0 | 0 | 4261000 | 200727 | 0 | 547416 | 412800 | 0 | 1274685 | 0 | 0 | 108466 | 499500 | 163080 | 615900 | 473270 | 2042880 | 2454000 | 598080 | 430200 | 700 | 477000 | 503640 | 959400 | 980424 | 3319527 | 3428000 | 625536 | 1534080 | 0 | 2477280 | 157000 | 0 | 0 | 462300 | 364248 | 160000 | 0 | 3387272 | 0 | 0 | 72000 | 0 | 1393200 | 103005 | 1854720 | 1701120 | 1057163 | 6331000 | 1878000 | 26712 | 0 | 0 | 2895491 | 1242672 | 0 | 55860 | 228480 | 1552320 | 220400 | 1738560 | 128690 | 123840 | 53945 |  |  | 11881455 | 0 | 4784832 | 0 | 146880 | 0 | 0 | 0 | 0 | 0 | 74625 | 0 | 512400 | 423168 | 0 | 0 | 0 | 0 | 0 | 784000 | 59580 | 0 | 18363 | 0 | 0 | 513600 | 0 | 200862 | 1796509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 4326291 | 0 | 9164454 | 1508640 | 0 | 1695360 | 0 | 416640 | 0 | 19792 | 204480 | 11136300 | 526280 | 0 | 0 |  | 119032008 | 50194831 | 169226839 | 69490077 | 11881455 | 36549313 | 33457189 | 12932809 | 1104436 | 1516493 | 2042880 | 252187 | 0
Fuel Cost | 0 | 3754612 | 0 | 4028535 | 7954876.05 | 277379.52 | 0 | 8494211.1 | 7341840 |  | 0 | 9581645 | 0 | 13516272 | 442503.36 | 5461530.66 | 0 | 0 | 0 | 9158889.6 | 2383603.2 | 4156416 | 11839429.66 | 0 | 0 | 285789.6 | 7442496 | 6644507.02 | 3297016.38 | 269487 | 450000 | 0 | 0 | 0 | 764123.4 | 0 | 298197.72 | 0 | 0 | 0 | 0 | 5186471.79 | 0 | 0 | 0 |  | 0 | 0 | 2829781 | 0 | 1453248 | 7785676.8 | 474344.64 | 1662249.6 | 3789501.52 | 3543993.2 | 3077830.14 | 0 | 0 | 3920120 | 258937.83 | 0 | 618580.08 | 577920 | 0 | 2179711.35 | 0 | 0 | 1035850.3 | 634365 | 122310 | 1077825 | 354952.5 | 15321600 | 2601240 | 5430566.4 | 546354 | 11158 | 782280 | 805824 | 1707732 | 1529461.44 | 3784260.78 | 3565120 | 1232305.92 | 2930092.8 | 0 | 4285694.4 | 343830 | 0 | 0 | 466923 | 273186 | 121600 | 0 | 25607776.32 | 0 | 0 | 374400 | 0 | 13709088 | 1204128.45 | 15115968 | 18457152 | 7452999.15 | 5887830 | 17127360 | 252428.4 | 0 | 0 | 21889911.96 | 10823673.12 | 0 | 557482.8 | 1958073.6 | 10338451.2 | 0 | 0 | 0 | 0 | 0 |  |  | 68437180.8 | 0 | 5024073.6 | 0 | 1154476.8 | 0 | 0 | 0 | 0 | 0 | 777592.5 | 0 | 794220 | 4130119.68 | 0 | 0 | 0 | 0 | 0 | 6938400 | 458766 | 0 | 177937.47 | 0 | 0 | 986112 | 0 | 152052.534 | 10832949.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 5061760.47 | 0 | 9072809.46 | 15750201.6 | 0 | 16088966.4 | 0 | 3233126.4 | 0 | 218701.6 | 1511107.2 | 48888357 | 0 | 0 | 0 |  | 344922980.76 | 199689390.784 | 544612371.544 | 78435165.944 | 68437180.8 | 43151774.78 | 263710623.51 | 59721306.27 | 298197.72 | 14102534.47 | 15321600 | 1433988.05 | 0
Yesterday Day Peak | 0 | 99 | 0 | 115 | 305 | 6 | 0 | 356 | 295 |  | 0 | 400 | 0 | 100 | 0 | 31 | 0 | 0 | 0 | 60 | 0 | 3 | 57 | 0 | 0 | 0 | 54 | 55 | 12 | 16 | 25 | 33 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 3 | 100 | 100 | 80 | 0 | 0 | 219 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 15 | 88 | 107 | 8 | 20 | 0 | 20 | 20 | 50 | 49 | 130 | 122 | 20 | 80 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 157 | 0 | 0 | 0 | 0 | 65 | 17 | 100 | 71 | 8 | 303 | 85 | 0 | 0 | 0 | 161 | 36 | 0 | 0 | 0 | 100 | 0 | 90 | 13 | 0 | 20 |  |  | 536 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 1 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 152 | 0 | 360 | 90 | 0 | 111 | 0 | 0 | 0 | 4 | 0 | 380 | 5 | 0 | 0 |  | 7111 | DayPeak
Yesterday Evening Peak | 0 | 98 | 0 | 115 | 300 | 6 | 0 | 369 | 290 | 0 | 0 | 420 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 100 | 60 | 64 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 0 | 50 | 17 | 25 | 80 | 80 | 80 | 0 | 0 | 191 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 8 | 25 | 21 | 110 | 101 | 50 | 20 | 0 | 20 | 22 | 53 | 50 | 163 | 156 | 20 | 79 | 0 | 130 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 130 | 0 | 100 | 86 | 143 | 238 | 115 | 0 | 0 | 0 | 156 | 53 | 0 | 0 | 46 | 100 | 20 | 90 | 0 | 0 | 0 |  |  | 774 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 155 | 0 | 420 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 510 | 33 | 0 | 0 |  | 8699 | EvPeak
Forecast for Evening | 0 | 100 | 0 | 115 | 300 | 7 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 33 | 52 | 0 | 47 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 17 | 20 | 100 | 100 | 100 | 0 | 0 | 220 | 26 | 0 | 20 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 148 | 150 | 95 | 20 | 0 | 20 | 22 | 51 | 44 | 163 | 156 | 36 | 86 | 0 | 150 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 20 | 90 | 0 | 0 |  |  |  | 790 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 34 | 50 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 33
Forecast for Day | 0 | 100 | 0 | 115 | 300 | 7 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 40 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 33 | 52 | 0 | 47 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 17 | 10 | 100 | 100 | 100 | 0 | 0 | 210 | 26 | 0 | 20 | 10 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 139 | 150 |  | 20 | 1.6 | 20 | 22 | 51 | 44 | 163 | 156 | 36 | 86 | 0 | 150 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 50 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 20 | 90 | 50 | 0 |  |  |  | 549 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 65 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 34 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 225 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 36
Generation at 08:00(Today) | 0 | 99 | 0 | 115 | 300 | 6 | 0 | 373 | 253 | 0 | 0 | 390 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 |  | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 37 | 17 | 10 | 80 | 80 | 80 | 0 | 0 | 185 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 78 | 110 | 0 | 20 | 0 | 20 | 22 | 53 | 50 | 163 | 156 | 36 | 80 | 0 | 136 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 7 | 100 | 68 | 0 | 278 | 115 | 0 | 0 | 1 | 155 | 54 | 0 | 0 | 0 | 55 | 20 | 20 | 4 | 0 | 0 | 0 | 0 | 496 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 189 | 0 | 438 | 53 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 460 | 36 | 0 | 0 | 0
199
| Minimum Generation |  | 5400 | 5:00
| Highest Generation |  | 8699 | 19:30
| Day Peak Generation |  | 7111 | 12:00
| Evening Peak Generation |  | 8699 | 19:30
| HVDC Max Flow |  | 774 | 18:00
| HVDC EvPeak Flow |  | 774 | 19:30
| Load factor L.F |  | 81.06%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-14
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7111 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5589 | MW
Evening Peak Generation : |  | 8699 | MW Hour : | 19:30 | Available Max Generation : |  | 13483 | MW
E.P. Demand (at gen end) : |  | 8699 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 8699 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4383 | MW
Total Gen. (MKWH) : |  | 169.2268 | System Load Factor : | 81.06% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -214 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-14
Actual : | 99.25 | Ft.(MSL) , | Rule curve : | 104.8 | Ft.( MSL )
Gas Consumed : | Total = | 868.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 121586940.724
: |  | Coal : | 59721306.27 | Oil : | 277813157.98 | Total : | 459121404.974
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3216.1884 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1088.3768 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 974.2042 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 879.94 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 795.3742 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 641.8254 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 365.7042 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.4335 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 494.975 |  |  | 0 | 0%
Total | 0 |  | 8622.0217 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 & 2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71,100 MW | 11) Fenchugonj CCPP Phase-2
|  |  |  | 3) Ghorasal Unit-1,2,4 | 12) Summit Bibiyana-2
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9)Ashuganj(S)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kallyanpur 132 kV Reserve Bus was under shut down from 07:48 to 20:10 for A/M.
b) Savar 132/33 kV T-1 transformer was under shut down from 09:30 to 16:54 for A/M.
c) Siddirganj 230/132 KV Auto MRT-1 transformer was under shut down from 09:11 to 20:54 for A/M.
d) Matuail-Maniknagar 132 kV Ckt-1 was under shut down from 08:43 to 16:58 for A/M.
e) Mymensing-Valuka 132 kV Ckt-2 was under shut down from 08:25 to 16:23 for A/M.
f) Hasnabad 230/132 kV Auto Tr-01 transformer was under shut down from 09:04 to 17:48 for A/M.
g) Kallyanpur-Lalbagh 132 kV Ckt-2 along with Aminbazar-CLC power station 132 kV was under shut
down from 09:14 to 16:21 for C/M.
h) Rajshahi New 132/33 kV T1 transformer was under shut down from 08:28 to 20:04 for A/M.
i) Cumilla(S) 132/33 kV T-2 transformer was under shut down from 08:26 to 15:43 for A/M.
j) Daudkandi-Sonargaon 132 kV Ckt-1 was under shut down from 08:38 to 16:30 for A/M.
k) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 09:28 to 15:55 for A/M.
l) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 08:52 to 17:07 for A/M.
m) Haripur-Madanganj 132 kV Ckt was under shut down from 09:52 to 13:42 for A/M.
n) Shahmirpur-Sikalbaha 132 kV Ckt-2 was under shut down from 08:21 to 16:44 for D/W.
o) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 09:17 to 20:11 for A/M.
p) Rajshahi-HVDC 230 kV Ckt-1 was under shut down from 11:24 to 16:59 for A/M.
q) Sikalbaha-Shahmirpur 132 kV Ckt-2 was under shut down from 07:42 to 16:23 for D/W.
r) Saidpur- Purbasadipur 132 kV Ckt-2 was under shut down from 08:46 to 16:02 for A/M.
s) Purbasadipur-Thakurgaon 132 kV Ckt-1 was under shut down from 09:01 to 17:28 for A/M.
t) Jhenaidah 132/33 kV T-2 transformer was under shut down from 09:03 to 14:53 for A/M.
u) Rangpur-Rangpur Confidence 132 kV Ckt-2 was under shut down from 09:11 to 16:52 for C/M.
v) Faridpur-Bheramara 132 kV Ckt-2 was under shut down from 08:42 to 14:39 for A/M.
w) Khulna(South)-Satkhira 132 kV Ckt-2 was under shut down from 08:40 to 17:45 for A/M.
x) Baghabari-Ishwardi 132 kV Ckt was under shut down from 08:44 to 17:21 for A/M.
y) Rajshahi-Bheramara HVDC 230 kV Ckt was under shut down from 11:28 to 20:23 for D/W.
z) Bagerhat-Goalpara 132 kV Ckt was under shut down from 09:39 to 14:30 for TRTUD testing purpose.
aa) Kodda 132/33 kV T-3 transformer was under shut down from 12:38 to 14:03 for A/M.
ab) Hathazari 230/132 kV T-02 transformer was switched on at 17:39.
ac) Chapai 132/33 kV T-1 transformer was under shut down from 16:38 to 19:17 due to Y-phase DS
flashing.
ad) Shahjibazar 132/33 kV T2 transformer was switched on at 20:37.
ae) Barapukuria unit-1 was force shut down at 23:43 due to flame was coming out from boiler.
af) Khulna(S)-Satkhira 132 kV Ckt-2 was shut down at 07:58(14-12-2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 98 | 2536900 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7166555 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 6 | 210136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 369 | 8410110 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 290 | 7128000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8790500 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1780800
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 64224 | Reserve.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 645571
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 60 | 1284103 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 359316 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1216320
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 60 | 261360 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 31440 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1019520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 422400 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 859574
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 334383
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1300020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 593600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 699100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 79020 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3387272
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 1393200 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 26712 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1738560 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 123840 | On test
| Dhaka area Total |  |  |  | 6057 | 2831 | 54603036
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 103005
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 983040
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1104436 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 216 | 4758231
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 291730 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1854720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 376464 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 559680
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 167040 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 0
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 156 | 2895491 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 53 | 1242672
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1552320
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 53945
| Chattogram area Total |  |  |  | 2266 | 814 | 15942774
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2560474 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2394590 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2093762 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4261000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 547416 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 412800 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1274685
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 1057163 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 86 | 1701120 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 499500
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 163080 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2042880
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 615900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 24 | 108466 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 473270
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 55860 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 228480 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1005 | 20691173
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 2454000 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 430200
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 50 | 598080 | Load increasing
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 700
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 72000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1878000 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 128690
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 22 | 233520
| Mymensingh Area Total |  |  |  | 687 | 308 | 5795190
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 477000 | Gas shortage
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 503640 | Gas shortage
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3319527
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 156 | 3428000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 959400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 980424
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 160000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 625536 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1534080
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 2477280
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 157000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 364248 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 462300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 238 | 6331000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 20 | 220400 | On test
| Sylhet Area Total |  |  |  | 1988 | 996 | 21999835
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 774 | 11881455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 146880 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 4784832 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 74625 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1508640 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1084 | 18396432
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 423168 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 512400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 13 | 320
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 510 | 11136300
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 33 | 526280
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 647 | 12598468
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 59580 | High Voltage.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 18363 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under maintenance
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 155 | 4326291 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 9164454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 513600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 200862
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 784000 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1695360
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 204480 | Reserve.
| Rajshahi Area Total |  |  |  | 2183 | 825 | 16966990
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1796509
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 416640
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19792
| Rangpur Area Total |  |  |  | 605 | 189 | 2232941
| Total |  |  |  | 20104 | 8699 | 169226839
| Eastern Grid Total |  |  |  | 13978 | 5954 | 119032008
| Western Grid Total |  |  |  | 6126 | 2745 | 50194831
| National Grid Total |  |  |  | 20104 | 8699 | 169226839
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-13
| (a) ENTIRE EASTERN GRID : |  | 5528 | MW | (b) ENTIRE WESTERN GRID : |  | 2702 | MW
| i) Dhaka area |  | 2968 | MW | i) Khulna area |  | 1037 | MW
| ii) Chittagong area |  | 866 | MW | ii) Rajshahi area |  | 857 | MW
| iii) Comilla area |  | 759 | MW | iii) Barisal area |  | 235 | MW
| iv) Mymensingh area |  | 624 | MW | iv) Rangpur area |  | 573 | MW
| v) Sylhet area |  | 311 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8230 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 104 | 12:00 | Jamalpur | 82 | 22:00 | Benapol | 34 | 18:00
| Munsiganj | 84 | 20:00 | Sherpur | 86 | 20:00 | Jhenida | 78 | 18:30
| Sonargaon | 53 | 1:00 | Srimongal | 39 | 18:00 | Bottail | 94 | 18:00
| Shyampur | 166 | 13:00 | Shahjibazar | 70 | 19:00 | G.K Project | 34 | 18:00
| Bhulta | 140 | 22:00 | Fenchuganj | 26 | 18:30 | Faridpur | 130 | 18:30
| Madanganj | 48 | 20:00 | Kulawara | 27 | 18:00 | Madaripur | 58 | 18:30
| Shitalakhya | 84 | 15:00 | Sylhet | 79 | 18:00 | Sariatpur | 40 | 19:30
| Rahim steel | 7 | 12:00 | Chatak | 19 | 18:00 | Gopalganj | 57 | 18:30
| Matuail | 57 | 9:00 | Sunamganj | 27 | 18:30 | Bagerhat | 79 | 18:30
| Ghorasal | 68 | 18:30 | Biani Bazar | 34 | 18:00 | Mongla | 36 | 10:00
| Narsingdi | 127 | 21:00 | Comilla (S) | 112 | 18:00 | Satkhira | 75 | 18:30
| Haripur (SBU) | 106 | 19:00 | Comilla(N) | 71 | 18:30 | Gallamari | 35 | 13:00
| Ullon | 40 | 14:00 | Chandpur | 65 | 18:30 | Magura | 38 | 18:00
| Hasnabad | 145 | 18:30 | Feni | 83 | 18:00 | Norail | 24 | 18:00
| Magbazar | 65 | 15:00 | Chowmuhani | 116 | 18:00 | Chuadanga | 61 | 18:00
| Maniknagar | 66 | 13:00 | Ashuganj | 45 | 13:00 | Barisal(N) | 29 | 20:00
| Bangabhaban | 20 | 10:00 | Daudkandi | 104 | 19:00 | Barisal (S) | 68 | 18:00
| Narinda | 74 | 18:30 | B.Baria | 95 | 19:30 | Patuakhali | 79 | 20:00
| Dhanmondi | 92 | 12:00 | Ramganj | 66 | 20:00 | Bhandaria | 40 | 18:30
| Lalbag | 68 | 17:00 | Chaddagram | 23 | 19:30 | Borhan Uddin | 25 | 19:00
| Madartek | 44 | 18:00 | PHP | 4 | 4:00 | Ishurdi | 49 | 19:00
| Dhaka University |  |  | Madunaghat | 41 | 18:00 | Ruppur Paromanobik | 2 | 19:00
| Aftabnagar | 6 | 0.5 | Hathazari | 72 | 0.77083 | Natore | 79 | 0.8125
| Fatullah | 31 | 9:00 | Khulshi | 168 | 18:00 | Bogra | 120 | 18:30
| Mirpur | 68 | 18:00 | Halishahar | 93 | 12:00 | Noagaon | 81 | 19:00
| Kalyanpur | 63 | 18:00 | Baraulia | 131 | 14:00 | Rajshahi | 97 | 20:00
| Gulshan | 72 | 13:00 | Sikalbaha | 22 | 18:00 | Rajshahi New | 8 | 20:00
| Uttara | 65 | 18:00 | Dohazari | 58 | 18:00 | C.Nawabganj | 50 | 18:30
| Uttara New | 23 | 18:00 | Cox'sbazar | 62 | 19:00 | Amnura | 28 | 19:00
| Kamrangirchar | 71 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 77 | 19:00
| Savar | 101 | 18:00 | Kaptai | 3 | 8:00 | Shahjadpur | 74 | 19:00
| Bhasantec | 96 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 65 | 19:00
| Agargaon | 43 | 18:00 | Bakulia | 70 | 18:00 | Niyamatpur | 37 | 18:30
| Satmosjid | 61 | 0.75 | Julda | 15 | 0.041667 | Joypurhat | 41 | 0.79167
| Tongi | 92 | 12:00 | TK chemical | 22 | 18:00 | Sherpur(Bogura) | 40 | 18:30
| Kabirpur | 176 | 18:00 | Modern Steel | 8 | 1:00 | Mohastangor | 32 | 18:00
| Basundhara | 87 | 18:00 | Shahmirpur | 19 | 19:00 | Rangpur | 105 | 19:00
| Manikganj | 46 | 19:30 | Khagrachhari | 18 | 17:00 | Lalmonirhat | 44 | 18:00
| Joydevpur | 113 | 18:00 | Matarbari | 25.5 | 18:00 | Saidpur | 87 | 18:30
| New Tongi | 83 | 15:00 | Baroiar Hat | 20 | 18:00 | Purbasadipur | 88 | 18:00
| Kodda | 194 | 18:30 | Rangamati | 8 | 13:00 | Thakurgaon | 62 | 19:00
| Dhamrai | 76 | 18:00 | Abul Khair 230 | 163 | 10:00 | Palashbari | 86 | 18:00
| Rajendrapur | 72 | 21:00 | BSRM | 145 | 5:00 | Barapukuria | 38 | 18:00
| Valuka | 68 | 18:00 | GPH Ispat | 74 | 6:00 | Panchagar | 41 | 18:00
| Tangail | 130 | 18:00 | Goalpara | 17 | 13:00 | Joldhaka | 19 | 18:30
| Mymensing | 149 | 19:30 | Central s/s | 78 | 18:30 | Kurigram | 39 | 18:00
| Kishorganj | 82 | 20:00 | Noapara | 47 | 18:00
| Netrokona | 81 | 18:00 | Jessore | 80 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 414 | 18:00 | 406 | 19:00 | Kaliakoir | 387 | 0.70833 | 374 | 0.45833
| Bheramara | 410 | 1:00 | 400 | 10:00 | Bhulta | 381 | 0.75 | 374 | 0.41667
| Ashuganj(N) | 383 | 17:00 | 377 | 11:00 | Gopalganj | 415 | 0.70833 | 397 | 0.8125
| Payra | 418 | 8:00 | 407 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 235 | 24:00 | Comilla (N) | 239 | 20:00 | 234 | 11:00
| Ishurdi | 239 | 6:00 | 229 | 19:30 | Hathazari | 224 | 19:00 | 214 | 8:00
| Ashuganj | 236 | 17:00 | 232 | 15:00 | Megnaghat | 236 | 6:00 | 230 | 11:00
| Serajganj | 232 | 15:00 | 229 | 8:00 | Fenchuganj | 246 | 17:00 | 240 | 14:00
| Baghabari | 242 | 4:00 | 238 | 8:00 | Siddhirganj | 232 | 8:00 | 227 | 15:00
| Barapukuria | 232 | 4:00 | 225 | 8:00 | Maniknagar | 231 | 8:00 | 226 | 11:00
| Bogra | 234 | 17:00 | 227 | 19:30 | Agargaon | 230 | 6:00 | 225 | 11:00
| Rajshahi | 230 | 3:00 | 223 | 8:00 | Barisal | 243 | 19:00 | 229 | 14:00
| Khulna South | 235 | 6:00 | 220 | 20:00 | AKSML | 227 | 8:00 | 216 | 4:00
| Rampura | 230 | 4:00 | 227 | 11:00 | BSRM | 228 | 16:00 | 218 | 4:00
| Haripur | 231 | 18:00 | 226 | 11:00 | Bibiyana | 244 | 18:00 | 239 | 7:00
| Hasnabad | 231 | 21:00 | 225 | 12:00 | Bhulta | 233 | 19:00 | 228 | 17:00
| Shyampur | 229 | 8:00 | 220 | 11:00 | Ashuganj (S) | 235 | 18:30 | 231 | 11:00
| Aminbazar | 231 | 1:00 | 226 | 16:00 | Kaliakoir | 226 | 1:00 | 219 | 12:00
| Tongi | 230 | 18:00 | 224 | 5:00 | GPH | 227 | 1:00 | 216 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 20:00 | 136 | 3:00 | Madanhat | 137 | 0.70833 | 132 | 0.5
| Munsiganj | 142 | 17:00 | 133 | 11:00 | Hathazari | 137 | 0.75 | 132 | 0.29167
| Sonargaon | 138 | 18:00 | 135 | 7:00 | Khulshi | 135 | 0.70833 | 129 | 0.20833
| Shyampur | 134 | 21:00 | 128 | 11:00 | Halishahar | 136 | 0.79167 | 130 | 0.20833
| Bhulta | 134 | 20:00 | 132 | 1:00 | Baraulia | 135 | 0.70833 | 130 | 0.5
| Madanganj | 142 | 20:00 | 134 | 12:00 | Sikalbaha | 137 | 0.79167 | 130 | 0.125
| Shitalakhya | 142 | 18:00 | 132 | 16:00 | Dohazari | 134 | 0.70833 | 128 | 0.16667
| Rahim steal | 140 | 18:00 | 137 | 11:00 | Cox'sbazar | 129 | 0.70833 | 120 | 0.25
| Matuail | 140 | 20:00 | 136 | 3:00 | Chandraghona | 136 | 0.29167 | 129 | 0.20833
| Ghorasal | 140 | 1:00 | 14 | 16:00 | Kaptai | 135 | 0.75 | 132 | 0.29167
| Narsinghdi | 138 | 6:00 | 135 | 3:00 | A. Khaer Stl. | 135 | 0.70833 | 129 | 0.25
| Haripur (SBU) | 140 | 17:00 | 138 | 1:00 | Bakulia | 134 | 0.33333 | 129 | 0.083333
| Ullon | 134 | 6:00 | 128 | 11:00 | Julda | 137 | 0.66667 | 130 | 0.16667
| Hasnabad | 138 | 4:00 | 130 | 19:00 | TK Chemical | 137 | 0.75 | 131 | 0.5
| Magbazar | 138 | 4:00 | 128 | 19:00 | Modern Steel | 136 | 0.70833 | 129 | 0.041667
| Maniknagar | 138 | 4:00 | 128 | 19:00 | Shahmirpur | 137 | 0.70833 | 128 | 0.125
| Bangabhaban | 132 | 2:00 | 128 | 14:00 | Khagrachhari | 136 | 0.70833 | 130 | 0.16667
| Narinda | 139 | 1:00 | 132 | 16:00 | Matarbari | 135 | 0.66667 | 128 | 0.16667
| Dhanmondi | 132 | 3:00 | 128 | 11:00 | Baroiar Hat | 138 | 0.66667 | 134 | 0.41667
| Lalbag | 132 | 1:00 | 132 | 16:00 | Rangamati | 136 | 17:00 | 130 | 4:00
| Madartek | 132 | 6:00 | 128 | 11:00 | Goalpara S/S | 138 | 3:00 | 131 | 20:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 6:00 | 130 | 0.83333
| Aftabnagar | 132 | 6:00 | 128 | 11:00 | Noapara | 138 | 6:00 | 128 | 0.83333
| Fatuiiah | 135 | 22:00 | 128 | 11:00 | Jessore | 135 | 1:00 | 125 | 0.83333
| Mirpur | 130 | 6:00 | 126 | 12;00 | Benapol | 136 | 0.20833 | 126 | 0.75
| Kalyanpur | 130 | 6:00 | 127 | 12;00 | Jhenida | 134 | 2:00 | 124 | 0.8125
| Gulshan | 134 | 6:00 | 128 | 12;00 | Bottail | 137 | 0.20833 | 130 | 0.875
| Uttara | 128 | 6:00 | 131 | 12;00 | G.K Project | 141 | 0.25 | 136 | 0.8125
| Uttara New | 137 | 6:00 | 126 | 12;00 | Faridpur | 136 | 0.083333 | 130 | 0.8125
| Kamrangirchar | 128 | 6:00 | 129 | 12;00 | Madaripur | 137 | 0.20833 | 132 | 0.8125
| Savar | 134 | 6:00 | 125 | 12;00 | Shariyatpur S/S | 139 | 7:00 | 132 | 0.83333
| Bhasantec | 134 | 6:00 | 130 | 12;00 | Gopalganj | 140 | 0.70833 | 133 | 0.8125
| Agargaon | 134 | 6:00 | 131 | 12;00 | Bagerhat | 140 | 7:00 | 130 | 0.83333
| Satmosjid | 135 | 5:00 | 130 | 12;00 | Mongla | 137 | 6:00 | 128 | 0.83333
| Tongi | 139 | 19:00 | 134 | 10:00 | Satkhira | 137 | 4:00 | 129 | 19:30
| Kabirpur | 132 | 22:00 | 126 | 11:00 | Gallamari | 140 | 0.25 | 132 | 0.8125
| Basundhara | 139 | 17:00 | 131 | 21:00 | Magura | 135 | 4:00 | 124 | 0.83333
| Manikganj | 143 | 17:00 | 134 | 16:00 | Norail | 136 | 0.16667 | 124 | 0.83333
| Joydevpur | 140 | 18:00 | 136 | 9:00 | Chuadanga | 133 | 4:00 | 121 | 0.75
| New Tongi | 138 | 18:00 | 132 | 11:00 | Barisal(N) | 139 | 6:00 | 130 | 14:00
| Kodda | 139 | 17:00 | 127 | 8:00 | Barisal (S) | 139 | 0.16667 | 131 | 0.58333
| Dhamrai | 132 | 22:00 | 126 | 11:00 | Patuakhali(S) | 135 | 0.16667 | 129 | 0.58333
| Rajendrapur | 137 | 18:00 | 130 | 12:00 | Bhandaria | 138 | 0.16667 | 129 | 0.58333
| Valuka | 130 | 8:00 | 124 | 18:00 | Ishurdi | 139 | 6:00 | 135 | 20:00
| Tangail | 133 | 2:00 | 129 | 7:00 | Ruppur Paromanobik | 139 | 1:00 | 134 | 20:00
| Mymensing | 132 | 8:00 | 124 | 7:00 | Natore | 138 | 17:00 | 134 | 20:00
| Kishorganj | 132 | 1:00 | 127 | 19:30 | Bogra | 137 | 17:00 | 133 | 20:00
| Netrokona | 131 | 23:00 | 126 | 5:00 | Noagaon | 134 | 15:00 | 128 | 19:30
| Jamalpur | 139 | 20:00 | 127 | 1:00 | Rajshahi | 141 | 6:00 | 135 | 19:30
| Sherpur | 138 | 20:00 | 124 | 4:00 | Rajshahi New | 140 | 17:00 | 137 | 19:00
| Srimongal | 138 | 4:00 | 136 | 16:00 | C.Nawabganj | 140 | 6:00 | 136 | 8:00
| Shahjibazar | 135 | 1:00 | 134 | 3:00 | Amnura | 141 | 14:00 | 135 | 8:00
| Fenchuganj | 139 | 13:00 | 136 | 12:00 | Pabna | 138 | 5:00 | 133 | 20:00
| Khulawara | 138 | 1:00 | 136 | 12:00 | Shahjadpur | 141 | 6:00 | 136 | 20:00
| Sylhet | 136 | 1:00 | 134 | 9:00 | Serajganj | 135 | 17:00 | 132 | 20:00
| Chatak | 135 | 1:00 | 133 | 12:00 | Niyamatpur | 134 | 3:00 | 127 | 18:00
| Sunamganj | 136 | 6:00 | 133 | 12:00 | Joypurhat | 136 | 14:00 | 130 | 18:00
| Biani Bazar | 136 | 3:00 | 133 | 15:00 | Sherpur(Bogura) | 137 | 17:00 | 132 | 19:30
| Comilla(s) | 130 | 3:00 | 125 | 13:00 | Mohastangor | 136 | 5:00 | 131 | 20:00
| Comilla(n) | 142 | 7:00 | 140 | 11:00 | Rangpur | 129 | 6:00 | 123 | 18:00
| Chandpur | 144 | 23:00 | 141 | 10:00 | Lalmonirhat | 130 | 17:00 | 122 | 9:00
| Feni | 140 | 17:00 | 136 | 13:00 | Saidpur | 130 | 17:00 | 122 | 19:00
| Chowmuhani | 138 | 19:00 | 132 | 13:00 | Purbasadipur | 128 | 6:00 | 119 | 18:00
| Ashuganj | 136 | 7:00 | 135 | 18:30 | Thakurgaon | 129 | 5:00 | 120 | 18:00
| Daudkandi | 140 | 8:00 | 137 | 11:00 | Palashbari | 132 | 17:00 | 127 | 18:00
| B.Baria | 132 | 7:00 | 131 | 16:00 | Barapukuria | 132 | 17:00 | 125 | 8:00
| Ramganj | 133 | 18:30 | 132 | 13:00 | Panchagar | 129 | 6:00 | 115 | 9:00
| Chaddagram | 142 | 17:00 | 135 | 3:00 | Joldhaka | 130 | 6:00 | 119 | 18:00
| PHP | 137 | 17:00 | 131 | 4:00 | Kurigram | 128 | 0.70833 | 120 | 0.33333

## L-Curve
Date | 2020-12-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 28 | 4829 | 1964 | 6793 |  |  |  | QF-LDC-11
0:30 | 33.5 | 4549.5 | 1862 | 6411.5 | Date: | 2020-12-13
1:00 | 39 | 4270 | 1760 | 6030
1:30 | 31 | 4105.5 | 1753 | 5858.5
2:00 | 23 | 3941 | 1746 | 5687
2:30 | 34 | 3881 | 1739.5 | 5620.5 | [5 empty] | Gen. at Eve. Peak | 8699 | 8699 MW (19:30 )
3:00 | 45 | 3821 | 1733 | 5554 | [6 empty] | 19:30
3:30 | 86 | 3789 | 1712 | 5501 | [5 empty] | Gen. at Day Peak | 7111 | 7111 MW (12:00 )
4:00 | 127 | 3757 | 1691 | 5448 | [6 empty] | 12:00
4:30 | 119.5 | 3732 | 1692 | 5424 | [5 empty] | Highest Generation | 8699
5:00 | 112 | 3707 | 1693 | 5400 | [6 empty] | 19:30
5:30 | 66 | 3856.5 | 1695.5 | 5552
6:00 | 20 | 4006 | 1698 | 5704
6:30 | 30.5 | 4162 | 1698 | 5860
7:00 | 41 | 4318 | 1698 | 6016
7:30 | 110.5 | 4465.5 | 1747 | 6212.5
8:00 | 180 | 4613 | 1796 | 6409
8:30 | 134 | 4780.5 | 1842.5 | 6623
9:00 | 88 | 4948 | 1889 | 6837
9:30 | 53.5 | 4960.5 | 1872 | 6832.5
10:00 | 19 | 4973 | 1855 | 6828
10:30 | 50.5 | 4994 | 1927 | 6921
11:00 | 82 | 5015 | 1999 | 7014
11:30 | 42.5 | 5062 | 2000.5 | 7062.5
12:00 | 3 | 5109 | 2002 | 7111
12:30 | 38 | 5223 | 2017 | 7240
13:00 | 73 | 5337 | 2032 | 7369
13:30 | 72.5 | 5198.5 | 1983.5 | 7182
14:00 | 72 | 5060 | 1935 | 6995
14:30 | 97.5 | 5041.5 | 1920.5 | 6962
15:00 | 123 | 5023 | 1906 | 6929
15:30 | 122 | 4973.5 | 1895 | 6868.5
16:00 | 121 | 4924 | 1884 | 6808
16:30 | 120.5 | 5066 | 1847.5 | 6913.5
17:00 | 120 | 5208 | 1811 | 7019
17:30 | 167 | 5606 | 2186 | 7792
18:00 | 214 | 6004 | 2561 | 8565
18:30 | 180.5 | 6009.5 | 2617 | 8626.5
19:00 | 147 | 6015 | 2673 | 8688
19:30 | 92 | 5954 | 2745 | 8699
20:00 | 157 | 5925 | 2674 | 8599 |  |  |  | Executive Engineer
20:30 | 92.5 | 5826 | 2674.5 | 8500.5 |  |  |  | Network Operation Division
21:00 | 28 | 5727 | 2675 | 8402
21:30 | 19 | 5576 | 2576.5 | 8152.5
22:00 | 10 | 5425 | 2478 | 7903 |  |  |  |  | Page 6 of 7
22:30 | 45 | 5232 | 2404.5 | 7636.5
23:00 | 80 | 5039 | 2331 | 7370
23:30 | 54 | 4934 | 2147.5 | 7081.5
24:00 | 28 | 4829 | 1964 | 6793
8699 MW (19:30 )
7111 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-13 |  | Energy | 169226839
[11 empty] | 2020-12-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2993 | 404 | 1648 | 1440 | 480 | 49 | 0 | 0 | 82 | 0
0:30 | 2827 | 399.5 | 1689 | 1009 | 513 | 46.5 | 0 | 0 | 79 | 0 | Date: | 2020-12-13
1:00 | 2661 | 395 | 1730 | 578 | 546 | 44 | 0 | 0 | 76 | 0
1:30 | 2648 | 394.5 | 1722 | 445.5 | 531.5 | 44 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 169.2268 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2635 | 394 | 1714 | 313 | 517 | 44 | 0 | 0 | 70 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2688 | 394 | 1656.5 | 257 | 516.5 | 43.5 | 0 | 0 | 65 | 0 | [7 empty] | Energy Requirement | 169.2268
3:00 | 2741 | 394 | 1599 | 201 | 516 | 43 | 0 | 0 | 60 | 0
3:30 | 2820.5 | 346.5 | 1581.5 | 136.5 | 516 | 43 | 0 | 0 | 57 | 0 | [6 empty] | Shortage
4:00 | 2900 | 299 | 1564 | 72 | 516 | 43 | 0 | 0 | 54 | 0
4:30 | 2875.5 | 299 | 1565.5 | 66 | 516.5 | 43.5 | 0 | 0 | 58 | 0
5:00 | 2851 | 299 | 1567 | 60 | 517 | 44 | 0 | 0 | 62 | 0
5:30 | 2901 | 299 | 1594 | 122 | 527.5 | 44.5 | 0 | 0 | 64 | 0
6:00 | 2951 | 299 | 1621 | 184 | 538 | 45 | 0 | 0 | 66 | 0
6:30 | 2982.5 | 299 | 1570.5 | 376 | 522.5 | 46 | 0 | 0 | 63 | 0.5 |  |  |  |  | Coal
7:00 | 3014 | 299 | 1520 | 568 | 507 | 47 | 0 | 0 | 60 | 1
7:30 | 2982.5 | 299 | 1480.5 | 821 | 513 | 47 | 0 | 0 | 65 | 4.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2951 | 299 | 1441 | 1074 | 519 | 47 | 0 | 0 | 70 | 8
8:30 | 2966 | 299 | 1449.5 | 1253.5 | 504 | 47 | 15.5 | 0 | 74 | 14.5
9:00 | 2981 | 299 | 1458 | 1433 | 489 | 47 | 31 | 0 | 78 | 21
9:30 | 2951.5 | 299 | 1452 | 1458.5 | 488 | 47 | 32 | 0 | 81 | 23.5
10:00 | 2922 | 299 | 1446 | 1484 | 487 | 47 | 33 | 0 | 84 | 26
10:30 | 2936.5 | 417.5 | 1419.5 | 1480 | 467.5 | 47 | 38.5 | 0 | 85 | 29.5
11:00 | 2951 | 536 | 1393 | 1476 | 448 | 47 | 44 | 0 | 86 | 33
11:30 | 2918 | 536 | 1445 | 1498.5 | 453 | 46.5 | 45 | 0 | 87 | 33.5
12:00 | 2885 | 536 | 1497 | 1521 | 458 | 46 | 46 | 0 | 88 | 34
12:30 | 2879 | 536.5 | 1504.5 | 1634 | 463.5 | 45.5 | 55 | 0 | 89 | 33
13:00 | 2873 | 537 | 1512 | 1747 | 469 | 45 | 64 | 0 | 90 | 32
13:30 | 2873 | 537 | 1512 | 1747 | 469 | 45 | 64 | 0 | 90 | 32
14:00 | 2873 | 537 | 1512 | 1747 | 469 | 45 | 64 | 0 | 90 | 32
14:30 | 2800.5 | 537 | 1421 | 1722 | 448 | 44.5 | 60 | 0 | 88 | 28
15:00 | 2728 | 537 | 1330 | 1697 | 427 | 44 | 56 | 0 | 86 | 24
15:30 | 2725.5 | 537 | 1330 | 1646.5 | 426.5 | 44.5 | 53 | 0 | 88 | 17.5
16:00 | 2723 | 537 | 1330 | 1596 | 426 | 45 | 50 | 0 | 90 | 11
16:30 | 2716.5 | 537 | 1210.5 | 1811.5 | 391 | 45 | 107 | 0 | 89 | 6
17:00 | 2710 | 537 | 1091 | 2027 | 356 | 45 | 164 | 0 | 88 | 1
17:30 | 2718 | 655.5 | 1334 | 2348.5 | 376 | 45 | 214.5 | 0 | 100 | 0.5
18:00 | 2726 | 774 | 1577 | 2670 | 396 | 45 | 265 | 0 | 112 | 0
18:30 | 2752.5 | 773.5 | 1581 | 2642.5 | 451 | 45 | 272 | 0 | 109 | 0
19:00 | 2779 | 773 | 1585 | 2615 | 506 | 45 | 279 | 0 | 106 | 0
19:30 | 2875 | 774 | 1665 | 2434 | 586 | 46 | 209 | 0 | 110 | 0
20:00 | 2858 | 774 | 1578 | 2437 | 585 | 48 | 209 | 0 | 110 | 0
20:30 | 2857 | 774 | 1593 | 2351 | 595.5 | 48 | 176 | 0 | 106 | 0
21:00 | 2856 | 774 | 1608 | 2265 | 606 | 48 | 143 | 0 | 102 | 0
21:30 | 2873 | 774 | 1547.5 | 2064.5 | 610.5 | 48 | 134 | 0 | 101 | 0
22:00 | 2890 | 774 | 1487 | 1864 | 615 | 48 | 125 | 0 | 100 | 0
22:30 | 2925.5 | 707.5 | 1551.5 | 1652 | 585 | 48.5 | 70.5 | 0 | 96 | 0
23:00 | 2961 | 641 | 1616 | 1440 | 555 | 49 | 16 | 0 | 92 | 0
23:30 | 2977 | 522.5 | 1632 | 1440 | 517.5 | 49 | 8 | 0 | 87 | 0 | Max Temp. in Dhaka |  | 25.7° C
24:00 | 2993 | 404 | 1648 | 1440 | 480 | 49 | 0 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 44 | 43 | 43 | 44 | 45 | 47 | 47 | 47 | 47 | 47 | 46 | 45 | 44 | 44 | 45 | 45 | 45 |  | 45 | 46 | 48 | 48 | 48 | 49 | 49 | 1104436
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 8 | 13 | 15 | 17 | 16 | 13 | 9 | 4 | 0 | [9 empty] | 103005
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 202 | 203 | 221 | 202 | 202 | 201 | 201 | 215 | 204 | 232 | 202 | 202 | 193 | 185 | 182 | 195 | 183 |  | 202 | 216 | 202 | 202 | 202 | 204 | 204 | 4758231
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 85 | 85 |  | 85 | 51 | 51 | 17 |  |  |  | 291730
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 15 | 95 | 120 | 145 | 157 | 225 | 235 | 195 | 195 | 230 | 300 |  | 300 | 300 | 300 | 300 | 245 | 95 |  | 3387272
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 99 | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 100 | 99 | 99 | 99 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 2536900
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 300 | 300 | 300 | 305 | 305 | 305 | 250 | 290 | 290 | 260 | 280 |  | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 7166555
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 125 | 125 | 125 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2560474
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 85 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2394590
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2093762
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 19 | 19 | 19 | 19 | 19 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 547416
33 | Ashuganj 225 MW CCPP | 43 | 45 | 125 | 215 | 200 | 190 | 208 | 188 | 203 | 200 | 214 | 219 | 217 | 150 | 183 | 194 | 191 | 166 |  | 186 | 191 | 196 | 187 | 183 | 184 | 190 | 4261000
34 | Ashuganj 450 MW CCPP(South)
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 412800
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 336 | 343 | 357 | 354 | 365 | 356 | 352 | 352 | 345 | 339 | 356 | 338 | 339 | 337 | 352 | 346 | 328 |  | 338 | 369 | 350 | 340 | 337 | 345 | 350 | 8410110
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 400 | 400 | 420 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 320 | 380 | 380 | 300 | 350 |  | 380 | 420 | 420 | 420 | 420 | 380 | 400 | 8790500
41 | Haripur 360MW CCPP(HPL) | 325 | 324 | 325 | 324 | 325 | 324 | 301 | 274 | 274 | 274 | 274 | 295 | 308 | 320 | 300 | 280 | 240 | 300 |  | 300 | 290 | 290 | 291 | 291 | 291 | 291 | 7128000
42 | RPCL 210MW CCPP | 111 | 110 | 110 | 110 | 110 | 112 | 110 | 110 | 109 | 111 | 109 | 107 | 102 | 91 | 89 | 87 | 107 | 107 |  | 100 | 101 | 102 | 102 | 103 | 106 | 109 | 2454000
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 11 | 12 | 15 | 13 | 14 | 25 | 14 | 6 | 1 | [9 empty] | 128690
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 477000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503640
46 | Shajibazar 330 MW CCPP | 154 | 157 | 157 | 160 | 157 | 166 | 150 | 156 | 157 | 156 | 156 | 122 | 120 | 157 | 156 | 155 | 157 | 153 |  | 157 | 156 | 156 | 157 | 158 | 156 | 156 | 3428000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 36 | 35 | 35 | 36 | 36 | 36 | 36 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 625536
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 80 | 79 | 5 | 5 | 40 | 80 | 80 | 77 | 77 | 80 | 80 | 80 | 80 | 50 | 10 | 10 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1534080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 96 | 96 | 96 | 107 | 98 | 95 | 95 | 96 | 95 | 96 | 95 | 95 | 95 | 96 | 75 | 80 | 68 | 120 |  | 120 | 130 | 129 | 120 | 120 | 133 | 121 | 2477280
51 | Sylhet 20 MW GTPP | [16 empty] | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 157000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 160000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 5 | 5 | 5 | 30 | 48 | 48 | 48 | 48 | 49 | 50 | 50 | 50 | 25 | 25 | 25 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 959400
56 | Shahjahanulla 25 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 364248
57 | Bibiana-II 341 MW CCPP (Summit) | 100 | 80 | 70 | 50 | 50 | 45 | 40 | [19 empty] | 462300
| Bibiyana South 400 MW | [12 empty] | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 220400
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 52 |  | 55 | 55 | 55 | 55 |  |  |  | 334383
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 6 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 20 | 16 | 22 | 22 | 22 | 233520
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 376464
61 | Narshingdi 22 MW PP (Doreen) | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 359316
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 430200
63 | Impoprt (Tripura) | 76 | 70 | 60 | 54 | 62 | 66 | 60 | 70 | 78 | 84 | 86 | 88 | 90 | 90 | 86 | 90 | 88 | 112 |  | 106 | 110 | 110 | 102 | 100 | 92 | 82 | 2042880
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 33 | 38 | 42 | 42 | 40 | 15 | 8 | 6 | 6 | 3 | 4 | 8 | 5 | 8 | 12 | 17 |  | 23 | 25 | 29 | 31 | 37 | 38 | 38 | 559680
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499500
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 163080
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 473270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 |  | 33 | 33 | 33 | 29 | 29 | 29 | 29 | 700020
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 593600
72 | Rupganj 33 MW PP(Summit) | 33 | 8 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 17 |  | 8 | 8 | 17 | 25 | 33 | 33 | 33 | 699100
73 | Ghorashal 108MW PP (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 210136
| Feni Lanka Power | [16 empty] | 34 | 34 | [8 empty] | 55860
| Chowmuhani 113 MW | [7 empty] | 1 | 9 | 9 | 9 | [5 empty] | 27 | 46 |  | 46 | 46 | 46 | 8 |  |  |  | 228480
| Manikgonj 162MW PP(MPGL) | [16 empty] | 54 | 55 |  | 18 | [6 empty] | 123840
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 16 | 50 | 50 | 50 | 60 | 98 | 100 | 100 | 85 | 80 | 100 |  | 100 | 100 | 100 | 100 | 60 |  |  | 1216320
78 | Gazipur 52 MW PP | [16 empty] | 20 | 43 |  | 25 | [6 empty] | 79020
79 | Kodda 150MW PP | [11 empty] | 3 | 16 | 16 | 16 | 16 | 28 | 100 |  | 100 | 64 | 64 | 32 | 32 | 16 |  | 422400
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 21 | 32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 |  | 50 | 50 | 67 | 95 | 95 | 64 |  | 598080
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 13 |  | 24 | 24 | 24 | 24 |  |  |  | 108466
| Gazipur 100 MW PP | [16 empty] | 9 | 17 | [8 empty] | 26712
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 36 | 44 | 46 | 54 | 54 | 54 | 53 |  | 53 | 53 | 51 | 53 | 54 | 48 | 54 | 1242672
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 6 | 30 |  | 15 | [6 empty] | 64224
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 73 | 72 | 73 |  |  | 15 | 30 | 42 | 50 | 50 | 50 | 57 | 60 | 52 | 60 | 57 | 51 | 59 |  | 63 | 60 | 52 | 50 | 62 | 67 | 73 | 1284103
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 40 |  |  |  |  | 1 | 40 | 53 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1780800
| Meghnaghat 104 MW PP (OPCL) | 70 | 35 |  |  |  | 10 | 48 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1738560
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 5 | 5 | 5 | 20 | 47 | 50 | 50 | 50 | 50 | 49 | 49 | 20 | 20 | 20 | 20 | 43 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 980424
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1274685
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 66 | 102 |  | 60 | 60 | 55 | 7 |  |  |  | 261360
95 | Patenga 50MW PP (Baraka) | 32 | 32 | 24 | 18 | 6 | 2 | 20 | 36 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 32 | 983040
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 42 | 77 |  | 38 | [6 empty] | 167040
97 | katpotti 52 MW | [16 empty] | 1 | 6 | [8 empty] | 31440
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 6 | 15 | 30 | 30 | 30 | 31 | 53 | 55 | 40 | 40 | 40 | 55 |  | 55 | 55 | 55 | 30 | 30 |  |  | 645571
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 13 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 859574
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 110 | 110 | 110 | 110 | 163 |  | 163 | 163 | 130 | 130 | 130 | 130 | 150 | 3319527
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | [17 empty] | 700
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [5 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1019520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 8 | 29 |  | 8 | [6 empty] | 72000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 18 | 63 | 63 | 65 | 101 | 100 | 100 | 85 | 105 | 141 |  | 149 | 130 | 136 | 106 | 86 | 42 |  | 1393200
115 | Juldah 100 MW PP Unit-3 (Acorn) | 40 |  |  |  |  | 26 | 58 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1854720
116 | Chandpur 200MW (Desh energy) | 100 | 70 | 34 |  |  | 12 | 63 | 68 | 68 | 68 | 68 | 71 | 85 | 85 | 85 | 85 | 75 | 2 |  | 80 | 86 | 92 | 100 | 100 | 100 | 100 | 1701120
117 | Ashuganj 150MW PP (Midland) | [6 empty] | 5 | 6 | 6 | 5 | 3 | 8 | 6 | 6 | 5 | 13 | 45 | 125 |  | 145 | 143 | 143 | 147 | 123 | 122 | 132 | 1057163
118 | Bibiyana-III 400 MW CCPP | 236 | 236 | 236 | 236 | 236 | 325 | 349 | 293 | 303 | 304 | 305 | 303 | 303 | 240 | 240 | 239 | 239 | 239 |  | 239 | 238 | 239 | 239 | 239 | 238 | 238 | 6331000
| Jamalpur 115 MW PP (United) | 45 | 16 | 16 |  |  |  |  | 62 | 115 | 115 | 85 | 85 | 85 | 85 | 85 | 85 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 85 | 1878000
| Anwara 300 MW PP (United) | 107 | 34 |  |  |  | 33 | 85 | 150 | 158 | 162 | 160 | 161 | 161 | 161 | 161 | 161 | 107 | 107 |  | 144 | 156 | 160 | 161 | 161 | 160 | 160 | 2895491
| Juldah unit-2 (Acorn) | [7 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 60 | 30 | 30 | 1552320
| Anlima Energy Ltd. | [10 empty] | 19 | 20 | 28 | [13 empty] | 53945
120 | Eastern Zone Total | 4270 | 3941 | 3821 | 3756 | 3707 | 4006 | 4318 | 4613 | 4948 | 4973 | 5015 | 5109 | 5337 | 5060 | 5023 | 4924 | 5208 | 6004 |  | 6015 | 5954 | 5925 | 5727 | 5425 | 5039 | 4829 | 119032008
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 66 |  | 36 | 16 | 16 | 16 |  |  |  | 146880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [5 empty] | 17 | 53 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 70 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 53 | 1508640
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 35 | 22 | 23 | 23 | 22 | 23 | 6 | 7 | 6 | 15 | 21 | 5 | 5 |  |  | 7 | 6 | 34 |  | 35 | 33 | 9 | 9 | 8 | 36 | 36 | 526280
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 64 |  | 64 | 64 | 75 | 80 | 80 | 39 |  | 423168
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 14 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 320
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 21 | 21 | 21 | 20 | 16 | 20 | 20 | 18 | 20 | 21 | 20 | 19 | 18 | 14 | 26 |  | 27 | 27 | 28 | 27 | 26 | 24 | 23 | 512400
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 16 |  | 40 | 24 | [5 empty] | 74625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 395 | 394 | 394 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 536 | 536 | 537 | 537 | 537 | 537 | 537 | 774 |  | 773 | 774 | 774 | 774 | 774 | 641 | 404 | 11881455
147 | Bheramara 410 MW CCPP | 185 | 185 | 185 | 200 | 200 | 200 | 215 | 215 | 220 | 195 | 190 | 180 | 165 | 160 | 160 | 150 | 145 | 155 |  | 165 | 180 | 180 | 190 | 215 | 250 | 270 | 4784832
148 | Payra 1320 MW | 470 | 440 | 440 | 440 | 440 | 460 | 430 | 440 | 410 | 410 | 370 | 380 | 390 | 360 | 350 | 350 | 280 | 320 |  | 430 | 510 | 510 | 530 | 540 | 480 | 480 | 11136300
149
150 | Barapukuria TPP Unit-1 | 76 | 77 | 76 | 76 | 77 | 78 | 77 | 79 | 79 | 77 | 78 | 78 | 79 | 78 | 77 | 76 | 76 | 76 |  | 76 | 76 | 75 | 76 | 75 | 75 |  | 1796509
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 174 | 181 | 182 | 185 | 186 | 165 | 170 | 170 | 170 | 165 | 152 | 161 | 130 | 147 | 161 | 150 | 153 |  | 156 | 155 | 156 | 167 | 173 | 185 | 197 | 4326291
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 371 | 389 | 373 | 411 | 410 | 374 | 358 | 371 | 410 | 390 | 330 | 360 | 360 | 319 | 317 | 368 | 250 | 395 |  | 370 | 420 | 385 | 413 | 288 | 430 | 423 | 9164454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 513600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 200862
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 6 | 12 |  | 12 | 12 | 12 | 12 |  |  |  | 59580
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [10 empty] | 2 | 1 | 6 | 7 | 6 | [11 empty] | 18363
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 31 | 33 | 42 | 42 | 42 | 42 | 34 | 34 | 51 | 80 |  | 94 | 94 | 94 | 94 | 93 |  |  | 784000
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 1 | 35 | 66 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 70 | 92 | 111 |  | 111 | 111 | 111 | 111 | 70 | 35 | 35 | 1695360
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 20 | 35 | 35 |  | 25 | 35 |  | 35 | [6 empty] | 204480
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 108 |  | 113 | 113 | 113 | 40 |  |  |  | 416640
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 0 | 1 | 3 | 4 | 2 | 3 | 1 | 1 | 0 | [9 empty] | 19792
178
178