## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-18 | Friday
|  |  | Date (day): | 2020-12-18 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12233.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13526 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-17 | 2020-12-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 104 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 363 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 308 | 337 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 360 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 72 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 15 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 70 | 195 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1941 | 2349 | 3694 | 3984 | 841 | 1060
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 48 | 46 | 44 | 46 | 184 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 228 | 206 | 215 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 16 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 123 | 161 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 80 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 12 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 586 | 763 | 1436 | 1433 | 694 | 121
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 100 | 120 | 120
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 190 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 24 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 55 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 73 | 73 | 122 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 150 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 51 | 60 | 60
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 180 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 104 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 16 | 25 | 25 |  | 8 | Engine problem
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 26 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 827 | 1107 | 1452 | 1712 | 410 | 728
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 157 | 126 | 164 | 160 | 42 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 80 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 35 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 39 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 26 | 26 | 26 | 26
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 279 | 367 | 671.6 | 616 | 42 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 32 | GT-1 FGMO & GT-2 under S/D.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 110 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 158 | 150 | 150 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 8 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 20 | 30 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 35 | 33 | 36 | 36 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 74 | 75 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 91 | 130 | 130 | 130
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 120 | 200 | 200 | 200
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 300 | 300 | 300 | 300
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1074 | 1136 | 1280 | 1280 | 178 | 415
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 546 | 782 | 407 | 696
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 390 | 350 | 410 | 410
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 989 | 1254 | 1252 | 1877 | 0 | 88
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 27 | 27 | 27 |  | 6 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 13 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 420 | 530 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 35 | 16 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 487 | 650 | 867 | 927 | 0 | 200
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 162 | 225 | 225 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 347 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 607 | 785 | 1370 | 1494 | 171 | 446
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 85 | 90 | 90 | 90
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 45 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 87 | 135 | 211 | 203 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 6877 | 8546 | 12233.6 | 13526 | 2336 | 3457
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6477.8668 | 8050 | 11523.5759 | 12740.9665
| A. |  | 2020-12-17 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 8546 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 4961 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8546 | MW
| 3 | Day peak Generation : |  |  | 6877 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8050 | MW
| 4 | Evening peak Generation : |  |  | 8546 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 160.7191 | MKWHr | By Solar | 0.35373 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 111.4946 | MKWHr |  | By Oil: | 19.6114 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.3252 | MKWHr |  | By Hydro: | 1.0909 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2336 | MW | Dhaka | 2708 | 2708 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3457 | MW | Chittagong | 958 | 958 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5793 | MW | Khulna | 1042 | 1042 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 884.89 | MMCFD |  |  | Rajshahi | 839 | 839 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 117108859.65 | ii) Oil : | Taka | 150463604.65 | Comilla | 696 | 696 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 61954309.08 | Total | Taka | 329526773.38 | Mymensingh | 677 | 677 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.522 | MKWHr. | Sylhet | 321 | 321 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -18 | MW (E to W) at | 19:30 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -74 | MW at | 18:30 | hrs | Rangpur | 572 | 572 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 26.0° C |  |  | Total | 8050 | 8050 |  | 0
| B. |  | 2020-12-18 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 24.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 7800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13526 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6000 | MW
| 4 | Reserve(Generation end) |  |  |  | 5726 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 146.6895 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5405 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.9251 | MKWHr. | ii) HVDC Flow at Peak Time |  | 782 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9181 | MKWHr. | iii) Maximum HVDC Flow : |  | 782 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.08 |  | (b) Today: | 99.02 |  | (c) Rule Curve: |  | 104.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 300 | 94 | 0 | 351 | 308 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 18 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 184 | 83 | 50 | 23 | 55 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 0 | 18 | 74 | 163 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 110 | 121 | 20 | 10 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 33 | 54 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 413 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 188 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 28 | 0 | 0 |  | 3739 | 1862 | 5601 | 2983 | 413 | 1409 | 131 | 545 | 46 | 0 | 74 | 0 | 0 | 99.08
2:00 | 0 | 0 | 0 | 115 | 300 | 56 | 0 | 353 | 308 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 183 | 45 | 48 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 66 | 164 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 110 | 120 | 20 | 10 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 414 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 190 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 30 | 0 | 0 |  | 3533 | 1850 | 5383 | 2961 | 414 | 1310 | 80 | 506 | 46 | 0 | 66 | 0 | 0 | 99.08
3:00 | 0 | 0 | 0 | 115 | 300 | 24 | 0 | 349 | 266 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 183 | 16 | 47 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 66 | 164 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 110 | 121 | 20 | 10 | 0 | 120 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 413 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 186 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 30 | 0 | 0 |  | 3365 | 1734 | 5099 | 2936 | 413 | 1170 | 43 | 427 | 44 | 0 | 66 | 0 | 0 | 99.08
4:00 | 0 | 0 | 0 | 115 | 300 | 24 | 0 | 358 | 267 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 183 | 16 | 50 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 164 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 110 | 120 | 20 | 10 | 0 | 120 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 317 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 191 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 31 | 0 | 0 |  | 3358 | 1641 | 4999 | 2947 | 317 | 1213 | 26 | 388 | 44 | 0 | 64 | 0 | 0 | 99.08
5:00 | 0 | 0 | 0 | 115 | 300 | 24 | 0 | 355 | 267 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 195 | 16 | 51 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 62 | 164 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 110 | 121 | 20 | 10 | 0 | 98 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 317 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 191 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 31 | 0 | 0 |  | 3312 | 1649 | 4961 | 2943 | 317 | 1181 | 26 | 388 | 44 | 0 | 62 | 0 | 0 | 99.08
6:00 | 0 | 0 | 0 | 115 | 300 | 54 | 0 | 378 | 337 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 29 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 120 | 0 | 0 | 0 | 194 | 26 | 52 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 164 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 130 | 120 | 20 | 10 | 0 | 99 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 317 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 195 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 31 | 0 | 0 |  | 3561 | 1729 | 5290 | 2990 | 317 | 1457 | 26 | 388 | 44 | 0 | 68 | 0 | 0 | 99.08
7:00 | 0 | 0 | 0 | 115 | 300 | 84 | 0 | 372 | 337 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 3 | 16 | 14 | 0 | 120 | 0 | 0 | 0 | 204 | 53 | 51 | 23 | 5 | 0 | 20 | 0 | 0 | 0 | 5 | 11 | 22 | 15 | 68 | 162 | 0 | 0 | 0 | 30 | 43 | 5 | 5 | 130 | 156 | 36 | 40 | 0 | 99 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 413 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 33 | 0 | 0 |  | 3782 | 1852 | 5634 | 3087 | 413 | 1582 | 53 | 387 | 43 | 0 | 68 | 1 | 0 | 99.08
8:00 | 0 | 0 | 0 | 115 | 300 | 95 | 0 | 377 | 337 |  | 0 | 400 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 9 | 20 | 30 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 27 | 16 | 8 | 0 | 120 | 0 | 0 | 0 | 206 | 55 | 51 | 26 | 15 | 0 | 37 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 74 | 163 | 0 | 20 | 0 | 30 | 43 | 22 | 20 | 130 | 158 | 36 | 77 | 0 | 99 | 0 | 0 | 0 | 0 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 1 | 120 | 0 | 0 | 0 | 1 | 33 | 48 | 0 | 0 | 0 | 0 | 300 | 18 | 9 | 0 | 0 | 0 |  | 507 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 201 | 0 | 406 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 8 | 0 | 0 |  | 4123 | 2064 | 6187 | 3152 | 507 | 1663 | 270 | 466 | 45 | 0 | 74 | 10 | 0 | 99.07
9:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 382 | 354 |  | 0 | 350 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 54 | 17 | 0 | 13 | 25 | 9 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 6 | 0 | 150 | 0 | 0 | 0 | 191 | 55 | 51 | 26 | 15 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 78 | 164 | 0 | 20 | 1 | 30 | 43 | 22 | 20 | 130 | 156 | 36 | 74 | 0 | 94 | 0 | 0 | 0 | 0 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | 6 | 120 | 2 | 0 | 0 | 9 | 82 | 54 | 0 | 0 | 4 | 0 | 300 | 54 | 20 | 0 | 0 | 0 |  | 507 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 196 | 0 | 413 | 53 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 420 | 7 | 0 | 0 |  | 4388 | 2104 | 6492 | 3143 | 507 | 1646 | 534 | 507 | 46 | 0 | 78 | 31 | 0 | 99.07
10:00 | 0 | 0 | 0 | 115 | 300 | 95 | 0 | 352 | 304 |  | 0 | 350 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 8 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 4 | 0 | 150 | 0 | 0 | 0 | 184 | 55 | 52 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 80 | 161 | 0 | 20 | 1 | 30 | 43 | 22 | 20 | 110 | 157 | 36 | 74 | 0 | 77 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 66 | 10 | 120 | 16 | 0 | 0 | 3 | 88 | 54 | 0 | 0 | 26 | 0 | 300 | 90 | 31 | 0 | 0 | 0 |  | 555 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 164 | 0 | 322 | 53 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 420 | 6 | 0 | 0 |  | 4404 | 2004 | 6408 | 3041 | 555 | 1492 | 652 | 505 | 46 | 0 | 80 | 37 | 0 | 99.07
11:00 | 0 | 0 | 0 | 115 | 300 | 92 | 0 | 360 | 303 |  | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 4 | 0 | 150 | 0 | 0 | 0 | 194 | 55 | 50 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 82 | 158 | 0 | 20 | 2 | 30 | 43 | 22 | 20 | 110 | 157 | 36 | 74 | 0 | 85 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 68 | 10 | 120 | 16 | 0 | 0 | 4 | 88 | 54 | 0 | 0 | 26 | 0 | 300 | 90 | 36 | 0 | 0 | 0 |  | 546 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 164 | 0 | 364 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 420 | 16 | 0 | 0 |  | 4452 | 2065 | 6517 | 3082 | 546 | 1540 | 650 | 507 | 48 | 0 | 82 | 62 | 0 | 99.07
12:00 | 0 | 0 | 0 | 115 | 300 | 94 | 0 | 374 | 308 |  | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 4 | 0 | 150 | 0 | 0 | 0 | 206 | 55 | 51 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 82 | 157 | 0 | 20 | 2 | 30 | 43 | 22 | 20 | 163 | 157 | 35 | 74 | 0 | 91 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 68 | 10 | 120 | 35 | 0 | 0 | 4 | 123 | 54 | 0 | 0 | 26 | 0 | 300 | 90 | 39 | 0 | 12 | 0 |  | 546 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 177 | 0 | 404 | 53 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 420 | 35 | 0 | 0 |  | 4707 | 2170 | 6877 | 3188 | 546 | 1660 | 784 | 505 | 48 | 0 | 82 | 64 | 0 | 99.06
13:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 375 | 354 |  | 0 | 420 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 7 | 0 | 130 | 0 | 0 | 0 | 186 | 55 | 50 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 17 | 86 | 117 | 0 | 20 | 2 | 30 | 43 | 22 | 20 | 110 | 156 | 34 | 74 | 0 | 121 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 16 | 70 | 73 | 10 | 120 | 45 | 0 | 0 | 4 | 124 | 54 | 0 | 0 | 26 | 0 | 350 | 90 | 33 | 0 | 15 | 0 |  | 546 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 181 | 0 | 364 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 440 | 35 | 0 | 0 |  | 4864 | 2113 | 6977 | 3123 | 546 | 1693 | 864 | 524 | 49 | 34 | 86 | 58 | 6977 | 99.06
14:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 359 | 273 |  | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 6 | 20 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 5 | 0 | 100 | 0 | 0 | 0 | 184 | 55 | 46 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 17 | 90 | 103 | 0 | 20 | 1 | 30 | 43 | 22 | 20 | 110 | 157 | 34 | 77 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 9 | 70 | 85 | 10 | 120 | 45 | 0 | 0 | 3 | 100 | 54 | 0 | 0 | 26 | 0 | 380 | 90 | 27 | 0 | 17 | 0 |  | 546 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 170 | 0 | 330 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 450 | 11 | 0 | 0 |  | 4757 | 2056 | 6813 | 3072 | 546 | 1501 | 943 | 535 | 49 | 34 | 90 | 43 | 0 | 99.06
15:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 354 | 254 |  | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 8 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 2 | 0 | 100 | 0 | 0 | 0 | 183 | 55 | 50 | 24 | 55 | 0 | 44 | 0 | 0 | 0 | 21 | 11 | 25 | 17 | 84 | 104 | 0 | 20 | 1 | 30 | 43 | 5 | 5 | 110 | 158 | 20 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 85 | 10 | 121 | 30 | 0 | 0 | 2 | 35 | 54 | 0 | 0 | 26 | 0 | 400 | 90 | 18 | 0 | 18 | 0 |  | 546 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 157 | 0 | 301 | 53 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 450 | 18 | 0 | 0 |  | 4523 | 1981 | 6504 | 3010 | 546 | 1375 | 838 | 537 | 47 | 34 | 84 | 33 | 0 | 99.06
16:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 370 | 303 |  | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 10 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 5 | 0 | 100 | 0 | 0 | 0 | 192 | 55 | 51 | 24 | 55 | 0 | 44 | 0 | 0 | 0 | 21 | 11 | 25 | 17 | 78 | 104 | 0 | 20 | 0 | 30 | 43 | 5 | 5 | 130 | 158 | 10 | 74 | 0 | 125 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 4 | 20 | 85 | 10 | 100 | 30 | 0 | 0 | 1 | 35 | 54 | 0 | 0 | 26 | 0 | 400 | 90 | 7 | 0 | 14 | 0 |  | 546 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 164 | 0 | 361 | 35 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 450 | 36 | 0 | 0 |  | 4590 | 2000 | 6590 | 2997 | 546 | 1542 | 797 | 537 | 46 | 34 | 78 | 13 | 0 | 99.05
17:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 376 | 354 |  | 0 | 420 | 0 | 35 | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 10 | 86 | 0 | 0 | 0 | 54 | 55 | 10 | 16 | 25 | 20 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 7 | 0 | 100 | 0 | 0 | 0 | 184 | 55 | 52 | 24 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 18 | 86 | 123 | 10 | 20 | 0 | 30 | 43 | 7 | 5 | 130 | 158 | 20 | 71 | 0 | 125 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 85 | 13 | 150 | 30 | 0 | 0 | 0 | 87 | 54 | 0 | 0 | 26 | 28 | 300 | 90 | 1 | 0 | 0 | 0 |  | 546 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 169 | 0 | 364 | 53 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 4862 | 2113 | 6975 | 3019 | 546 | 1706 | 990 | 538 | 45 | 44 | 86 | 1 | 0 | 99.05
18:00 | 0 | 0 | 0 | 115 | 300 | 102 | 0 | 357 | 354 |  | 0 | 420 | 0 | 90 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 48 | 80 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 25 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 12 | 0 | 100 | 0 | 0 | 0 | 189 | 55 | 50 | 24 | 55 | 0 | 51 | 0 | 0 | 14 | 21 | 11 | 25 | 21 | 102 | 125 | 38 | 20 | 0 | 30 | 43 | 8 | 20 | 163 | 156 | 33 | 75 | 0 | 126 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 120 | 86 | 200 | 78 | 0 | 0 | 0 | 157 | 54 | 0 | 0 | 26 | 100 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 165 | 0 | 424 | 90 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 490 | 13 | 0 | 0 |  | 5590 | 2698 | 8288 | 3119 | 782 | 1811 | 1698 | 578 | 44 | 154 | 102 | 0 | 0 | 99.05
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 10 | 115 | 300 | 104 | 0 | 351 | 333 |  | 0 | 360 | 0 | 100 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 16 | 72 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 15 | 0 | 100 | 0 | 0 | 0 | 183 | 55 | 51 | 24 | 55 | 0 | 51 | 0 | 0 | 47 | 21 | 11 | 25 | 21 | 100 | 126 | 74 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 158 | 33 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 150 | 200 | 115 | 0 | 0 | 0 | 157 | 54 | 0 | 0 | 26 | 80 | 300 | 90 | 0 | 0 | 0 | 0 |  | 781 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 170 | 0 | 341 | 90 | 0 | 109 | 0 | 35 | 0 | 0 | 25 | 530 | 15 | 0 | 0 |  | 5696 | 2790 | 8486 | 3127 | 781 | 1613 | 2054 | 619 | 45 | 147 | 100 | 0 | 0 | 99.04
19:30 | 0 | 0 | 0 | 115 | 300 | 104 | 0 | 363 | 337 |  | 0 | 360 | 0 | 100 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 16 | 72 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 16 | 0 | 100 | 0 | 0 | 0 | 190 | 55 | 51 | 24 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 16 | 21 | 104 | 126 | 80 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 158 | 33 | 75 | 0 | 130 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 150 | 200 | 115 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 26 | 80 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 162 | 0 | 347 | 90 | 0 | 111 | 0 | 45 | 0 | 0 | 35 | 530 | 16 | 0 | 0 |  | 5722 | 2824 | 8546 | 3142 | 782 | 1626 | 2079 | 620 | 46 | 147 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 300 | 104 | 0 | 359 | 337 |  | 0 | 360 | 0 | 100 | 10 | 15 | 0 | 0 | 0 | 15 | 0 | 10 | 73 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 17 | 0 | 100 | 0 | 0 | 0 | 184 | 55 | 51 | 26 | 55 | 0 | 51 | 0 | 0 | 51 | 21 | 11 | 16 | 21 | 100 | 126 | 80 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 158 | 33 | 75 | 0 | 123 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 150 | 200 | 115 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 80 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 162 | 0 | 345 | 90 | 0 | 111 | 0 | 40 | 0 | 0 | 35 | 530 | 30 | 0 | 0 |  | 5664 | 2822 | 8486 | 3114 | 782 | 1639 | 2043 | 621 | 46 | 141 | 100 | 0 | 0 | 99.04
21:00 | 0 | 0 | 0 | 115 | 300 | 104 | 0 | 368 | 337 |  | 0 | 360 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 17 | 0 | 100 | 0 | 0 | 0 | 192 | 55 | 51 | 24 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 16 | 21 | 96 | 127 | 50 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 157 | 33 | 75 | 0 | 130 | 18 | 0 | 0 | 0 | 8 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 50 | 200 | 115 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 50 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 166 | 0 | 427 | 90 | 0 | 111 | 0 | 25 | 0 | 0 | 35 | 530 | 35 | 0 | 0 |  | 5342 | 2819 | 8161 | 3165 | 782 | 1726 | 1645 | 621 | 47 | 79 | 96 | 0 | 0 | 99.04
22:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 363 | 337 |  | 0 | 360 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 54 | 35 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 17 | 0 | 100 | 0 | 0 | 0 | 183 | 55 | 51 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 92 | 127 | 0 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 157 | 34 | 75 | 0 | 120 | 18 | 0 | 0 | 0 | 8 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 180 | 0 | 200 | 65 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 164 | 0 | 401 | 90 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 530 | 16 | 0 | 0 |  | 4981 | 2609 | 7590 | 3144 | 782 | 1678 | 1169 | 620 | 47 | 58 | 92 | 0 | 0 | 99.04
23:00 | 0 | 0 | 0 | 115 | 300 | 103 | 0 | 349 | 358 |  | 0 | 360 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 19 | 0 | 120 | 0 | 0 | 0 | 183 | 73 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 88 | 148 | 0 | 20 | 0 | 30 | 43 | 5 | 30 | 110 | 159 | 34 | 75 | 0 | 95 | 18 | 0 | 0 | 0 | 8 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 200 | 35 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 0 | 0 | 0 |  | 590 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 154 | 0 | 375 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 16 | 0 | 0 |  | 4860 | 2308 | 7168 | 3143 | 590 | 1690 | 990 | 619 | 48 | 0 | 88 | 0 | 0 | 99.04
24:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 350 | 359 |  | 0 | 380 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 20 | 0 | 120 | 0 | 0 | 0 | 183 | 73 | 47 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 17 | 21 | 78 | 148 | 0 | 20 | 0 | 30 | 43 | 5 | 30 | 110 | 157 | 34 | 75 | 0 | 96 | 19 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 200 | 24 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 0 | 0 | 0 |  | 401 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 375 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 35 | 0 | 0 |  | 4660 | 2007 | 6667 | 3139 | 401 | 1727 | 685 | 589 | 48 | 0 | 78 | 0 | 0 | 99.03
KWH | 0 | 0 | 10000 | 2740500 | 7189991 | 1991590 | 0 | 8845310 | 7572000 |  | 0 | 8578750 | 0 | 1010880 | 50904 | 91675 | 0 | 0 | 0 | 54720 | 0 | 72480 | 1206014 | 0 | 0 | 0 | 877320 | 558893 | 72935 | 215856 | 600000 | 502560 | 536600 | 818000 | 0 | 0 | 1090909 | 0 | 0 | 0 | 0 | 4885140 | 0 | 0 | 0 |  | 602640 | 0 | 326927 | 0 | 0 | 863520 | 384576 | 269280 | 0 | 2839865 | 0 | 0 | 0 | 4636000 | 1221090 | 1168530 | 529056 | 903360 | 0 | 1003716 | 0 | 0 | 123797 | 372276 | 184680 | 416000 | 460630 | 1918080 | 3353600 | 274560 | 333360 | 10350 | 716000 | 1015440 | 264600 | 590256 | 3101236 | 3352000 | 685632 | 1409280 | 0 | 2715580 | 60000 | 0 | 0 | 0 | 244584 | 149048 | 0 | 1319781 | 0 | 0 | 45600 | 0 | 0 | 81270 | 822720 | 1890240 | 669090 | 3414000 | 920400 | 0 | 0 | 23640 | 1869273 | 1088555 | 0 | 0 | 313320 | 337920 | 7456200 | 1440000 | 223350 | 0 | 82800 | 0 |  | 12925091 | 0 | 8575776 | 0 | 116160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481600 | 381312 | 0 | 0 | 0 | 0 | 0 | 337168 | 0 | 0 | 0 | 0 | 0 | 361680 | 0 | 187380 | 2107636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319859 | 0 | 4488282 | 0 | 8735400 | 1051680 | 0 | 530016 | 0 | 96960 | 0 | 15124 | 111168 | 11217600 | 608454 | 0 | 0 |  | 108070735 | 52648346 | 160719081 | 74082452 | 12925091 | 37412151 | 18874853 | 13325236 | 1090909 | 736575 | 1918080 | 353734 | 0
Fuel Cost | 0 | 0 | 14600 | 4028535 | 7980890.01 | 2628898.8 | 0 | 8933763.1 | 7799160 |  | 0 | 9350837.5 | 0 | 7672579.2 | 350728.56 | 775570.5 | 0 | 0 | 0 | 412041.6 | 0 | 713203.2 | 11119449.08 | 0 | 0 | 0 | 6404436 | 4320242.89 | 719139.1 | 161892 | 450000 | 0 | 0 | 0 | 0 | 0 | 294545.43 | 0 | 0 | 0 | 0 | 5324802.6 | 0 | 0 | 0 |  | 0 | 0 | 3171191.9 | 0 | 0 | 6839078.4 | 484565.76 | 799761.6 | 0 | 4203000.2 | 0 | 0 | 0 | 4265120 | 1575206.1 | 1343809.5 | 597833.28 | 1264704 | 0 | 1716354.36 | 0 | 0 | 1182261.35 | 472790.52 | 138510 | 728000 | 345472.5 | 14385600 | 3554816 | 2493004.8 | 423367.2 | 164979 | 1174240 | 1624704 | 470988 | 920799.36 | 3535409.04 | 3486080 | 1350695.04 | 2691724.8 | 0 | 4697953.4 | 131400 | 0 | 0 | 0 | 183438 | 113276.48 | 0 | 9977544.36 | 0 | 0 | 237120 | 0 | 0 | 950046.3 | 6705168 | 20509104 | 4717084.5 | 3175020 | 8394048 | 0 | 0 | 0 | 14131703.88 | 9481314.05 | 0 | 0 | 2685152.4 | 2250547.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 74448524.16 | 0 | 9004564.8 | 0 | 913017.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746480 | 3721605.12 | 0 | 0 | 0 | 0 | 0 | 2983936.8 | 0 | 0 | 0 | 0 | 0 | 694425.6 | 0 | 141846.66 | 12709045.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479788.5 | 0 | 5251289.94 | 0 | 8648046 | 10979539.2 | 0 | 5029851.84 | 0 | 752409.6 | 0 | 167120.2 | 821531.52 | 49245264 | 0 | 0 | 0 |  | 233199301.85 | 186738286.62 | 419937588.47 | 73786275.99 | 74448524.16 | 43322583.66 | 143595272.75 | 61954309.08 | 294545.43 | 6868331.9 | 14385600 | 1282145.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 300 | 94 | 0 | 374 | 308 |  | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 4 | 0 | 150 | 0 | 0 | 0 | 206 | 55 | 51 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 82 | 157 | 0 | 20 | 2 | 30 | 43 | 22 | 20 | 163 | 157 | 35 | 74 | 0 | 91 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 68 | 10 | 120 | 35 | 0 | 0 | 4 | 123 | 54 | 0 | 0 | 26 | 0 | 300 | 90 | 39 | 0 | 12 | 0 |  | 546 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 177 | 0 | 404 | 53 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 420 | 35 | 0 | 0 |  | 6877 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 300 | 104 | 0 | 363 | 337 | 0 | 0 | 360 | 0 | 100 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 16 | 72 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 26 | 0 | 34 | 0 | 0 | 50 | 16 | 16 | 0 | 100 | 0 | 0 | 0 | 190 | 55 | 51 | 24 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 16 | 21 | 104 | 126 | 80 | 20 | 0 | 30 | 43 | 8 | 30 | 110 | 158 | 33 | 75 | 0 | 130 | 0 | 0 | 0 | 0 | 8 | 11 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 150 | 200 | 115 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 26 | 80 | 300 | 90 | 0 | 0 | 0 | 0 |  | 782 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 162 | 0 | 347 | 90 | 0 | 111 | 0 | 45 | 0 | 0 | 35 | 530 | 16 | 0 | 0 |  | 8546 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 46 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 26 |  | 85 | 100 | 102 | 50 | 16 | 20 | 0 | 120 | 0 | 0 | 0 | 221 | 73 | 60 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 148 | 160 | 95 | 20 | 0 | 30 | 43 | 51 | 44 | 163 | 150 | 36 | 86 | 0 | 130 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 200 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 90 | 0 | 0 |  |  |  | 696 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 34 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 44 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 26 |  | 85 | 100 | 102 | 50 | 16 | 10 | 0 | 120 | 0 | 0 | 0 | 221 | 73 | 60 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 139 | 164 | 95 | 20 | 1.6 | 30 | 43 | 51 | 44 | 163 | 150 | 36 | 86 | 0 | 130 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 200 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 90 | 50 | 0 |  |  |  | 407 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 34 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 300 | 99 | 0 | 363 | 267 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 20 | 16 | 6 | 0 | 100 | 0 | 0 | 0 | 187 | 73 | 52 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 72 | 164 | 0 | 20 | 1 | 30 | 43 | 5 | 49 | 110 | 127 | 34 | 77 | 0 | 127 | 19 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 37 | 0 | 200 | 0 | 0 | 0 | 1 | 102 | 36 | 0 | 0 | 0 | 0 | 300 | 17 | 10 | 0 | 0 | 0 | 0 | 308 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 163 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 16 | 0 | 0 | 0
199
| Minimum Generation |  | 4961 | 5:00
| Highest Generation |  | 8546 | 19:30
| Day Peak Generation |  | 6877 | 12:00
| Evening Peak Generation |  | 8546 | 19:30
| HVDC Max Flow |  | 782 | 18:00
| HVDC EvPeak Flow |  | 782 | 19:30
| Load factor L.F |  | 78.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6877 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5405 | MW
Evening Peak Generation : |  | 8546 | MW Hour : | 19:30 | Available Max Generation : |  | 13526 | MW
E.P. Demand (at gen end) : |  | 8546 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 7800 | MW
Maximum Generation : |  | 8546 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5726 | MW
Total Gen. (MKWH) : |  | 160.7191 | System Load Factor : | 78.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -74 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-18
Actual : | 99.02 | Ft.(MSL) , | Rule curve : | 104.4 | Ft.( MSL )
Gas Consumed : | Total = | 884.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 117108859.65
: |  | Coal : | 61954309.08 | Oil : | 150463604.65 | Total : | 329526773.38
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2752.8778 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 927.4665 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 829.4354 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 748.9167 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 677.0875 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 546.3638 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 316.6493 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 140.969 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 421.3295 |  |  | 0 | 0%
Total | 0 |  | 7361.0955 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71,100 MW | 11) Fenchugonj CCPP Phase-2
|  |  |  | 3) Ghorasal Unit-1,2,4 | 12) Summit Bibiyana-2
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9)Ashuganj(S)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hasnabad 230/132 kV T02 transformer was under shut down from 08:16 to 20:18 for A/M.
b) Gopalganj S/S-Gopalganj 100 MW P/P 132 kV Ckt-2 was under shut down from
08:03 to 16:33 for A/M.
c) Bashundhara 132/33 kV T-3 transformer was under shut down from 09:40 to 14:19 for A/M.
d) Uttara 132/33 kV T-3 transformer was under shut down from 09:22 to 13:20 for A/M.
e) Hathazari-GPH 230 kV Ckt was under shut down from 08:43 to 16:50 for A/M.
f) Kodda 132/33 kV T-2 transformer was under shut down from 08:54 to 17:29 for A/M.
g) Kulaura 132/33 kV T-2 transformer was under shut down from 09:09 to 16:19 for A/M.
h) Feni 132/33 kV T-1 transformer was under shut down from 08:17 to 20:18 for A/M.
i) Siddhirganj 230 KV Busbar-1 was under shut down from 08:36 to 16:16 for A/M.
j) Jamalpur-Mymensing 132 KV Ckt-2 was under shut down from 09:33 to 17:07 for A/M.
k) Fatullah-Shyampur 132 KV Ckt-1 & 2 were under shut down from 09:17 to 15:16 for A/M.
l) Dohazari-Sikalbaha 132 KV Ckt-2 was under shut down from 08:34 to 16:52 for C/M.
m) Mirpur 132/33 kV T-1 transformer was under shut down from 08:52 to 20:07 for A/M.
n) Ullon 132/33 kV T-1 transformer was under shut down from 09:10 to 14:05 for A/M.
o) Ishwardi 132/33 kV T-1 transformer was under shut down from 09:42 to 20:05 for A/M.
p) Bagerhat-Mongla 132 KV Ckt-1 was under shut down from 10:20 to 11:26 for A/M.
q) Mymensingh-Valuka 132 kV Ckt-2 was under shut down from 09:09 to 17:51 for A/M.
r) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 09:46 to 16:58 for A/M.
s) B.Baria 132/33 kV T-2 transformer was under shut down from 09:25 to 12:18 for A/M.
t) Goalpara 132/33 kV T-6 transformer was under shut down from 11:55 to 12:18 due to red
hot maintenance at 33 kV Y-phase bushing.
u) Bibiyana-Kaliakoir 400 kV Ckt-2 was switched on at 16:55.
v) Patuakhali-Payra 132 kV Ckt-1 was switched on at 14:43.
w) Kodda 132 kV Bus-2 was under shut down from 15:46 to 17:40 due to removing rope
of kite.
x) Feni 132 kV Bus was shut down at 06:36(18-12-2020) for A/M.
y) Jhenaidah 132 kV Bus-A & B were shut down at 07:00(18-12-2020) for D/W.
z) Cantonment 132/33 kV T-1 transformer was shut down at 07:13(18-12-2020) for A/M.
aa) Aminbazar-Kallyanpur 132 KV Ckt-1 was shut down at 07:05(18-12-2020) for C/M.
ab) Ghorasal-Ishwardi 230 KV Ckt-1 was shut down at 07:09(18-12-2020) for D/W.
ac) Hasnabad-Lalbag 132 KV Ckt was shut down at 07:42(18-12-2020) for A/M.
ad) Mirpur132/33 kV T-1 transformer was shut down at 07:45(18-12-2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 10000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7189991
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 1991590
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 363 | 8845310 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7572000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8578750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1010880
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 50904 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 91675 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 72 | 1206014 | High Voltage.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 215856 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 15 | 54720 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 877320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 72480 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 558893
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 72935 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1102560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 536600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 818000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1319781 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1440000 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 6057 | 2349 | 46356759
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 81270
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 863520
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1090909 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 206 | 4885140
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 326927 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 822720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 384576 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 269280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23640
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 161 | 1869273 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1088555
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 337920 | Low demand
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 82800
| Chattogram area Total |  |  |  | 2266 | 763 | 12126530
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2839865 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 4636000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 24 | 529056 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 903360 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1221090 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1003716
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 669090
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1168530 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 1890240 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 372276
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 1918080 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 416000 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 123797
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 460630
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 313320 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1107 | 18649730
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3353600 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 333360
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 80 | 274560 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10350
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 45600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 920400 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 223350
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 26 | 602640
| Mymensingh Area Total |  |  |  | 687 | 367 | 5763860
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Gas shortage
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1015440
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3101236 | frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3352000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 8 | 264600 | Line O/L
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 30 | 590256 | Line O/L
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 149048
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 685632 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1409280
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 2715580
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 60000 | Gas shortage
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 244584 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 200 | 3414000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 300 | 7456200 | On test
| Sylhet Area Total |  |  |  | 1988 | 1136 | 25173856
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 782 | 12925091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 116160 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8575776 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1051680 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1254 | 22668707
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 381312 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 481600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 13 | 319859 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 530 | 11217600 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 16 | 608454 | test run
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 650 | 13008825
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under maint.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 4488282 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 347 | 8735400 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 361680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 187380
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 337168
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 530016
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 111168 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 785 | 14751094
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 90 | 2107636
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 45 | 96960 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 15124
| Rangpur Area Total |  |  |  | 605 | 135 | 2219720
| Total |  |  |  | 20104 | 8546 | 160719081
| Eastern Grid Total |  |  |  | 13978 | 5722 | 108070735
| Western Grid Total |  |  |  | 6126 | 2824 | 52648346
| National Grid Total |  |  |  | 20104 | 8546 | 160719081
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-17
| (a) ENTIRE EASTERN GRID : |  | 5360 | MW | (b) ENTIRE WESTERN GRID : |  | 2690 | MW
| i) Dhaka area |  | 2708 | MW | i) Khulna area |  | 1042 | MW
| ii) Chittagong area |  | 958 | MW | ii) Rajshahi area |  | 839 | MW
| iii) Comilla area |  | 696 | MW | iii) Barisal area |  | 237 | MW
| iv) Mymensingh area |  | 677 | MW | iv) Rangpur area |  | 572 | MW
| v) Sylhet area |  | 321 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8050 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 92 | 19:00 | Jamalpur | 83 | 19:00 | Benapol | 34 | 18:30
| Munsiganj | 82 | 20:00 | Sherpur | 86 | 18:00 | Jhenida | 79 | 18:30
| Sonargaon | 58 | 19:30 | Srimongal | 24 | 18:00 | Bottail | 96 | 18:00
| Shyampur | 154 | 12:00 | Shahjibazar | 77 | 18:00 | G.K Project | 35 | 18:30
| Bhulta | 149 | 19:00 | Fenchuganj | 24 | 18:00 | Faridpur | 134 | 19:00
| Madanganj | 44 | 11:00 | Kulawara | 29 | 19:00 | Madaripur | 62 | 19:00
| Shitalakhya | 84 | 17:00 | Sylhet | 84 | 18:30 | Sariatpur | 40 | 18:30
| Rahim steel | 5 | 7:00 | Chatak | 20 | 18:00 | Gopalganj | 58 | 18:30
| Matuail | 45 | 9:00 | Sunamganj | 28 | 18:30 | Bagerhat | 80 | 18:30
| Ghorasal | 61 | 18:30 | Biani Bazar | 37 | 18:30 | Mongla | 36 | 20:00
| Narsingdi | 119 | 19:30 | Comilla (S) | 104 | 19:30 | Satkhira | 73 | 19:30
| Haripur (SBU) | 86 | 17:00 | Comilla(N) | 69 | 19:00 | Gallamari | 22 | 13:00
| Ullon | 42 | 18:30 | Chandpur | 63 | 19:00 | Magura | 38 | 18:00
| Hasnabad | 137 | 19:30 | Feni | 76 | 19:00 | Norail | 24 | 18:30
| Magbazar | 62 | 13:00 | Chowmuhani | 114 | 19:00 | Chuadanga | 60 | 18:00
| Maniknagar | 62 | 12:00 | Ashuganj | 38 | 20:00 | Barisal(N) | 29 | 20:00
| Bangabhaban | 19 | 11:00 | Daudkandi | 100 | 20:00 | Barisal (S) | 68 | 19:30
| Narinda | 66 | 11:00 | B.Baria | 94 | 18:30 | Patuakhali | 81 | 20:00
| Dhanmondi | 90 | 13:00 | Ramganj | 64 | 18:00 | Bhandaria | 40 | 20:00
| Lalbag | 66 | 17:00 | Chaddagram | 25 | 18:30 | Borhan Uddin | 25 | 22:00
| Madartek | 44 | 20:00 | PHP | 9 | 20:00 | Ishurdi | 47 | 18:30
| Dhaka University |  |  | Madunaghat | 42 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 68 | 0.75 | Natore | 79 | 0.75
| Fatullah | 24 | 15:00 | Khulshi | 152 | 13:00 | Bogra | 120 | 18:30
| Mirpur | 62 | 18:30 | Halishahar | 112 | 15:00 | Noagaon | 81 | 19:00
| Kalyanpur | 57 | 18:30 | Baraulia | 122 | 23:00 | Rajshahi | 95 | 19:00
| Gulshan | 72 | 14:00 | Sikalbaha | 20 | 18:30 | Rajshahi New | 8 | 18:00
| Uttara | 62 | 14:00 | Dohazari | 54 | 18:00 | C.Nawabganj | 50 | 19:30
| Uttara New | 20 | 14:00 | Cox'sbazar | 74 | 19:00 | Amnura | 28 | 18:00
| Kamrangirchar | 70 | 18:00 | Chandraghona | 22 | 18:00 | Pabna | 77 | 18:00
| Savar | 92 | 15:00 | Kaptai | 3.6 | 18:00 | Shahjadpur | 70 | 19:30
| Bhasantec | 92 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 58 | 12:00
| Agargaon | 43 | 13:00 | Bakulia | 65 | 18:00 | Niyamatpur | 38 | 18:30
| Satmosjid | 54 | 0.75 | Julda | 18 | 0.41667 | Joypurhat | 42 | 0.77083
| Tongi | 59 | 18:00 | TK chemical | 20.3 | 18:30 | Sherpur(Bogura) | 42 | 18:00
| Kabirpur | 108 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 84 | 18:00 | Shahmirpur | 16 | 18:00 | Rangpur | 107 | 18:00
| Manikganj | 44 | 21:00 | Khagrachhari | 18 | 18:30 | Lalmonirhat | 45 | 19:30
| Joydevpur | 69 | 18:30 | Matarbari | 25 | 18:30 | Saidpur | 80 | 18:00
| New Tongi | 62 | 18:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 86 | 18:30
| Kodda | 146 | 18:00 | Rangamati | 8 | 18:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 64 | 21:00 | Abul Khair 230 | 148 | 0:00 | Palashbari | 88 | 18:30
| Rajendrapur | 64 | 18:30 | BSRM | 106 | 0:00 | Barapukuria | 41 | 20:00
| Valuka | 68 | 18:30 | GPH Ispat | 76 | 1:00 | Panchagar | 41 | 19:00
| Tangail | 140 | 17:00 | Goalpara | 16 | 13:00 | Joldhaka | 25 | 18:00
| Mymensing | 153 | 20:00 | Central s/s | 72 | 18:30 | Kurigram | 41 | 18:00
| Kishorganj | 82 | 20:00 | Noapara | 49 | 19:30
| Netrokona | 82 | 18:30 | Jessore | 72 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 19:00 | 405 | 15:00 | Kaliakoir | 387 | 0.16667 | 371 | 0.5
| Bheramara | 412 | 18:30 | 397 | 10:00 | Bhulta | 380 | 0.79167 | 371 | 0.5
| Ashuganj(N) | 383 | 4:00 | 374 | 12:00 | Gopalganj | 418 | 0.20833 | 391 | 0.75
| Payra | 421 | 3:00 | 404 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 232 | 7:00 | Comilla (N) | 236 | 2:00 | 230 | 16:00
| Ishurdi | 240 | 4:00 | 226 | 18:00 | Hathazari | 223 | 19:00 | 206 | 12:00
| Ashuganj | 235 | 4:00 | 230 | 12:00 | Megnaghat | 233 | 18:30 | 226 | 13:00
| Serajganj | 232 | 5:00 | 225 | 18:00 | Fenchuganj | 244 | 2:00 | 240 | 1:00
| Baghabari | 242 | 4:00 | 234 | 18:30 | Siddhirganj | 232 | 1:00 | 225 | 11:00
| Barapukuria | 232 | 5:00 | 220 | 18:00 | Maniknagar | 230 | 1:00 | 224 | 12:00
| Bogra | 232 | 5:00 | 220 | 18:00 | Agargaon | 230 | 4:00 | 221 | 12:00
| Rajshahi | 273 | 17:00 | 216 | 18:00 | Barisal | 247 | 1:00 | 237 | 18:00
| Khulna South | 236 | 4:00 | 215 | 18:00 | AKSML | 225 | 18:30 | 211 | 12:00
| Rampura | 230 | 1:00 | 227 | 10:00 | BSRM | 227 | 14:00 | 217 | 16:00
| Haripur | 230 | 19:30 | 224 | 11:00 | Bibiyana | 244 | 2:00 | 238 | 7:00
| Hasnabad | 231 | 3:00 | 226 | 16:00 | Bhulta | 232 | 19:00 | 225 | 17:00
| Shyampur | 229 | 3:00 | 220 | 12:00 | Ashuganj (S) | 235 | 19:00 | 229 | 12:00
| Aminbazar | 233 | #REF! | 222 | 12:00 | Kaliakoir | 229 | 4:00 | 221 | 12:00
| Tongi | 228 | 4:00 | 221 | 10:00 | GPH | 222 | 4:00 | 215 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 1:00 | 135 | 12:00 | Madanhat | 135 | 0.79167 | 128 | 0.66667
| Munsiganj | 139 | 19:00 | 135 | 7:00 | Hathazari | 135 | 0.77083 | 128 | 0.5
| Sonargaon | 139 | 20:00 | 135 | 1:00 | Khulshi | 132 | 0.77083 | 124 | 0.5
| Shyampur | 133 | 1:00 | 127 | 12:00 | Halishahar | 134 | 0.83333 | 125 | 0.5
| Bhulta | 132 | 1:00 | 130 | 7:00 | Baraulia | 135 | 0.8125 | 127 | 0.66667
| Madanganj | 136 | 19:00 | 132 | 9:00 | Sikalbaha | 134 | 0.77083 | 127 | 0.45833
| Shitalakhya | 139 | 1:00 | 131 | 12:00 | Dohazari | 131 | 0.77083 | 123 | 0.5
| Rahim steal | 138 | 18:00 | 136 | 11:00 | Cox'sbazar | 124 | 0.33333 | 115 | 0.5
| Matuail | 138 | 1:00 | 135 | 12:00 | Chandraghona | 134 | 0.79167 | 128 | 0.5
| Ghorasal | 138 | 1:00 | 136 | 9:00 | Kaptai | 135 | 0.8125 | 131 | 0.375
| Narsinghdi | 137 | 1:00 | 135 | 12:00 | A. Khaer Stl. | 134 | 0.8125 | 127 | 0.41667
| Haripur (SBU) | 138 | 1:00 | 137 | 3:00 | Bakulia | 133 | 0.77083 | 125 | 0.66667
| Ullon | 132 | 1:00 | 127 | 12:00 | Julda | 134 | 0.75 | 127 | 0.45833
| Hasnabad | 238 | 2:00 | 131 | 12:00 | TK Chemical | 134 | 0.77083 | 127 | 0.625
| Magbazar | 133 | 4:00 | 126 | 12:00 | Modern Steel | 134 | 0.8125 | 126 | 0.45833
| Maniknagar | 138 | 1:00 | 134 | 12:00 | Shahmirpur | 137 | 0.95833 | 127 | 0.45833
| Bangabhaban | 138 | 1:00 | 134 | 12:00 | Khagrachhari | 133 | 0.77083 | 126 | 0.5
| Narinda | 138 | 1:00 | 134 | 12:00 | Matarbari | 131 | 0.875 | 121 | 0.5
| Dhanmondi | 132 | 1:00 | 127 | 12:00 | Baroiar Hat | 135 | 0.75 | 132 | 0.29167
| Lalbag | 129 | 3:00 | 122 | 12:00 | Rangamati | 133 | 18:30 | 127 | 12:00
| Madartek | 132 | 1:00 | 128 | 11:00 | Goalpara S/S | 138 | 4:00 | 127 | 18:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 4:00 | 127 | 0.75
| Aftabnagar | 132 | 1:00 | 128 | 11:00 | Noapara | 138 | 3:00 | 124 | 0.75
| Fatuiiah | 137 | 14:00 | 131 | 16:00 | Jessore | 134 | 3:00 | 122 | 0.75
| Mirpur | 128 | 6:00 | 123 | 13:00 | Benapol | 136 | 0.125 | 120 | 0.75
| Kalyanpur | 129 | 6:00 | 124 | 12:00 | Jhenida | 134 | 6:00 | 120 | 0.75
| Gulshan | 132 | 6:00 | 127 | 12:00 | Bottail | 139 | 0.20833 | 127 | 0.75
| Uttara | 136 | 6:00 | 129 | 12:00 | G.K Project | 141 | 0.25 | 134 | 0.75
| Uttara New | 129 | 6:00 | 122 | 12:00 | Faridpur | 138 | 0.16667 | 127 | 0.75
| Kamrangirchar | 138 | 6:00 | 130 | 12:00 | Madaripur | 138 | 0.20833 | 132 | 0.75
| Savar | 129 | 6:00 | 123 | 12:00 | Shariyatpur S/S | 140 | 5:00 | 131 | 0.79167
| Bhasantec | 135 | 6:00 | 129 | 12:00 | Gopalganj | 142 | 0.25 | 130 | 0.75
| Agargaon | 135 | 6:00 | 132 | 12:00 | Bagerhat | 140 | 3:00 | 125 | 0.75
| Satmosjid | 135 | 6:00 | 129 | 12:00 | Mongla | 136 | 5:00 | 124 | 0.75
| Tongi | 138 | 4:00 | 133 | 13:00 | Satkhira | 138 | 4:00 | 126 | 18:30
| Kabirpur | 133 | 2:00 | 127 | 12:00 | Gallamari | 139 | 0.083333 | 128 | 0.75
| Basundhara | 137 | 2:00 | 130 | 18:00 | Magura | 136 | 4:00 | 121 | 0.77083
| Manikganj | 140 | 4:00 | 133 | 18:00 | Norail | 133 | 0.16667 | 118 | 0.75
| Joydevpur | 140 | 21:00 | 134 | 15:00 | Chuadanga | 133 | 5:00 | 116 | 0.75
| New Tongi | 137 | 4:00 | 130 | 12:00 | Barisal(N) | 141 | 4:00 | 134 | 18:00
| Kodda | 136 | 7:00 | 127 | 21:00 | Barisal (S) | 139 | 0.20833 | 134 | 0.5
| Dhamrai | 132 | 1:00 | 127 | 11:00 | Patuakhali(S) | 137 | 0.16667 | 131 | 0.70833
| Rajendrapur | 138 | 18:30 | 124 | 17:00 | Bhandaria | 139 | 0.20833 | 130 | 0.75
| Valuka | 128 | 18:30 | 122 | 16:00 | Ishurdi | 140 | 4:00 | 131 | 18:00
| Tangail | 132 | 3:00 | 127 | 18:30 | Ruppur Paromanobik | 138 | 1:00 | 132 | 18:00
| Mymensing | 130 | 20:00 | 125 | 8:00 | Natore | 139 | 5:00 | 131 | 12:00
| Kishorganj | 131 | 3:00 | 127 | 8:00 | Bogra | 137 | 5:00 | 126 | 18:00
| Netrokona | 130 | 3:00 | 124 | 16:00 | Noagaon | 134 | 4:00 | 124 | 18:00
| Jamalpur | 137 | 19:00 | 122 | 7:00 | Rajshahi | 140 | 2:00 | 131 | 18:00
| Sherpur | 135 | 19:30 | 120 | 8:00 | Rajshahi New | 142 | 4:00 | 132 | 12:00
| Srimongal | 138 | 9:00 | 136 | 17:00 | C.Nawabganj | 140 | 3:00 | 131 | 12:00
| Shahjibazar | 135 | 1:00 | 133 | 15:00 | Amnura | 139 | 20:00 | 130 | 12:00
| Fenchuganj | 138 | 18:30 | 135 | 3:00 | Pabna | 139 | 4:00 | 130 | 18:00
| Khulawara | 137 | 5:00 | 135 | 13:00 | Shahjadpur | 141 | 1:00 | 135 | 18:00
| Sylhet | 135 | 1:00 | 133 | 12:00 | Serajganj | 135 | 1:00 | 130 | 18:00
| Chatak | 134 | 1:00 | 132 | 17:00 | Niyamatpur | 133 | 4:00 | 121 | 18:00
| Sunamganj | 134 | 1:00 | 132 | 11:00 | Joypurhat | 135 | 1:00 | 124 | 18:00
| Biani Bazar | 135 | 1:00 | 132 | 18:00 | Sherpur(Bogura) | 137 | 4:00 | 128 | 18:00
| Comilla(s) | 131 | 1:00 | 126 | 12:00 | Mohastangor | 136 | 2:00 | 126 | 18:00
| Comilla(n) | 142 | 18:30 | 139 | 11:00 | Rangpur | 128 | 5:00 | 114 | 18:00
| Chandpur | 144 | 9:00 | 138 | 7:00 | Lalmonirhat | 130 | 5:00 | 117 | 18:00
| Feni | 138 | 20:00 | 135 | 12:00 | Saidpur | 130 | 5:00 | 116 | 18:00
| Chowmuhani | 135 | 13:00 | 131 | 7:00 | Purbasadipur | 130 | 3:00 | 112 | 18:00
| Ashuganj | 137 | 1:00 | 135 | 8:00 | Thakurgaon | 130 | 1:00 | 113 | 18:00
| Daudkandi | 140 | 19:00 | 135 | 12:00 | Palashbari | 134 | 13:00 | 121 | 18:00
| B.Baria | 132 | 7:00 | 131 | 20:00 | Barapukuria | 132 | 5:00 | 120 | 18:00
| Ramganj | 138 | 19:00 | 133 | 14:00 | Panchagar | 129 | 2:00 | 112 | 18:00
| Chaddagram | 139 | 19:00 | 136 | 7:00 | Joldhaka | 131 | 2:00 | 112 | 18:00
| PHP | 136 | 18:00 | 133 | 6:00 | Kurigram | 128 | 0.125 | 111 | 0.75

## L-Curve
Date | 2020-12-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 22 | 4660 | 2007 | 6667 |  |  |  | QF-LDC-11
0:30 | 51 | 4199.5 | 1934.5 | 6134 | Date: | 2020-12-17
1:00 | 80 | 3739 | 1862 | 5601
1:30 | 103 | 3636 | 1856 | 5492
2:00 | 126 | 3533 | 1850 | 5383
2:30 | 131 | 3449 | 1792 | 5241 | [5 empty] | Gen. at Eve. Peak | 8546 | 8546 MW (19:30 )
3:00 | 136 | 3365 | 1734 | 5099 | [6 empty] | 19:30
3:30 | 136.5 | 3361.5 | 1687.5 | 5049 | [5 empty] | Gen. at Day Peak | 6877 | 6877 MW (12:00 )
4:00 | 137 | 3358 | 1641 | 4999 | [6 empty] | 12:00
4:30 | 128.5 | 3335 | 1645 | 4980 | [5 empty] | Highest Generation | 8546
5:00 | 120 | 3312 | 1649 | 4961 | [6 empty] | 19:30
5:30 | 137 | 3436.5 | 1689 | 5125.5
6:00 | 154 | 3561 | 1729 | 5290
6:30 | 126.5 | 3671.5 | 1790.5 | 5462
7:00 | 99 | 3782 | 1852 | 5634
7:30 | 60 | 3952.5 | 1958 | 5910.5
8:00 | 21 | 4123 | 2064 | 6187
8:30 | 35.5 | 4255.5 | 2084 | 6339.5
9:00 | 50 | 4388 | 2104 | 6492
9:30 | 83.5 | 4396 | 2054 | 6450
10:00 | 117 | 4404 | 2004 | 6408
10:30 | 159.5 | 4428 | 2034.5 | 6462.5
11:00 | 202 | 4452 | 2065 | 6517
11:30 | 194.5 | 4579.5 | 2117.5 | 6697
12:00 | 187 | 4707 | 2170 | 6877
12:30 | 102 | 4785.5 | 2141.5 | 6927
13:00 | 17 | 4864 | 2113 | 6977
13:30 | 54.5 | 4810.5 | 2084.5 | 6895
14:00 | 92 | 4757 | 2056 | 6813
14:30 | 126 | 4640 | 2018.5 | 6658.5
15:00 | 160 | 4523 | 1981 | 6504
15:30 | 183.5 | 4556.5 | 1990.5 | 6547
16:00 | 207 | 4590 | 2000 | 6590
16:30 | 175.5 | 4726 | 2056.5 | 6782.5
17:00 | 144 | 4862 | 2113 | 6975
17:30 | 84.5 | 5226 | 2405.5 | 7631.5
18:00 | 25 | 5590 | 2698 | 8288
18:30 | 34.5 | 5643 | 2744 | 8387
19:00 | 44 | 5696 | 2790 | 8486
19:30 | 18 | 5722 | 2824 | 8546
20:00 | 25 | 5664 | 2822 | 8486 |  |  |  | Executive Engineer
20:30 | 80.5 | 5503 | 2820.5 | 8323.5 |  |  |  | Network Operation Division
21:00 | 136 | 5342 | 2819 | 8161
21:30 | 124.5 | 5161.5 | 2714 | 7875.5
22:00 | 113 | 4981 | 2609 | 7590 |  |  |  |  | Page 6 of 7
22:30 | 99.5 | 4920.5 | 2458.5 | 7379
23:00 | 86 | 4860 | 2308 | 7168
23:30 | 54 | 4760 | 2157.5 | 6917.5
24:00 | 22 | 4660 | 2007 | 6667
8546 MW (19:30 )
6877 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-17 |  | Energy | 160719081
[11 empty] | 2020-12-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3139 | 401 | 1727 | 990 | 589 | 48 | 0 | 0 | 78 | 0
0:30 | 3061 | 407 | 1568 | 560.5 | 567 | 47 | 0 | 0 | 76 | 0 | Date: | 2020-12-17
1:00 | 2983 | 413 | 1409 | 131 | 545 | 46 | 0 | 0 | 74 | 0
1:30 | 2972 | 413.5 | 1359.5 | 105.5 | 525.5 | 46 | 0 | 0 | 70 | 0 | [7 empty] | Total Energy | 160.7191 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2961 | 414 | 1310 | 80 | 506 | 46 | 0 | 0 | 66 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2948.5 | 413.5 | 1240 | 61.5 | 466.5 | 45 | 0 | 0 | 66 | 0 | [7 empty] | Energy Requirement | 160.7191
3:00 | 2936 | 413 | 1170 | 43 | 427 | 44 | 0 | 0 | 66 | 0
3:30 | 2941.5 | 365 | 1191.5 | 34.5 | 407.5 | 44 | 0 | 0 | 65 | 0 | [6 empty] | Shortage
4:00 | 2947 | 317 | 1213 | 26 | 388 | 44 | 0 | 0 | 64 | 0
4:30 | 2945 | 317 | 1197 | 26 | 388 | 44 | 0 | 0 | 63 | 0
5:00 | 2943 | 317 | 1181 | 26 | 388 | 44 | 0 | 0 | 62 | 0
5:30 | 2966.5 | 317 | 1319 | 26 | 388 | 44 | 0 | 0 | 65 | 0
6:00 | 2990 | 317 | 1457 | 26 | 388 | 44 | 0 | 0 | 68 | 0
6:30 | 3038.5 | 365 | 1519.5 | 39.5 | 387.5 | 43.5 | 0 | 0 | 68 | 0.5 |  |  |  |  | Coal
7:00 | 3087 | 413 | 1582 | 53 | 387 | 43 | 0 | 0 | 68 | 1
7:30 | 3119.5 | 460 | 1622.5 | 161.5 | 426.5 | 44 | 0 | 0 | 71 | 5.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3152 | 507 | 1663 | 270 | 466 | 45 | 0 | 0 | 74 | 10
8:30 | 3147.5 | 507 | 1654.5 | 402 | 486.5 | 45.5 | 0 | 0 | 76 | 20.5
9:00 | 3143 | 507 | 1646 | 534 | 507 | 46 | 0 | 0 | 78 | 31
9:30 | 3092 | 531 | 1569 | 593 | 506 | 46 | 0 | 0 | 79 | 34
10:00 | 3041 | 555 | 1492 | 652 | 505 | 46 | 0 | 0 | 80 | 37
10:30 | 3061.5 | 550.5 | 1516 | 651 | 506 | 47 | 0 | 0 | 81 | 49.5
11:00 | 3082 | 546 | 1540 | 650 | 507 | 48 | 0 | 0 | 82 | 62
11:30 | 3135 | 546 | 1600 | 717 | 506 | 48 | 0 | 0 | 82 | 63
12:00 | 3188 | 546 | 1660 | 784 | 505 | 48 | 0 | 0 | 82 | 64
12:30 | 3155.5 | 546 | 1676.5 | 824 | 514.5 | 48.5 | 17 | 0 | 84 | 61
13:00 | 3123 | 546 | 1693 | 864 | 524 | 49 | 34 | 0 | 86 | 58
13:30 | 3123 | 546 | 1693 | 864 | 524 | 49 | 34 | 0 | 86 | 58
14:00 | 3123 | 546 | 1693 | 864 | 524 | 49 | 34 | 0 | 86 | 58
14:30 | 3066.5 | 546 | 1534 | 851 | 530.5 | 48 | 34 | 0 | 85 | 45.5
15:00 | 3010 | 546 | 1375 | 838 | 537 | 47 | 34 | 0 | 84 | 33
15:30 | 3003.5 | 546 | 1458.5 | 817.5 | 537 | 46.5 | 34 | 0 | 81 | 23
16:00 | 2997 | 546 | 1542 | 797 | 537 | 46 | 34 | 0 | 78 | 13
16:30 | 3008 | 546 | 1624 | 893.5 | 537.5 | 45.5 | 39 | 0 | 82 | 7
17:00 | 3019 | 546 | 1706 | 990 | 538 | 45 | 44 | 0 | 86 | 1
17:30 | 3069 | 664 | 1758.5 | 1344 | 558 | 44.5 | 99 | 0 | 94 | 0.5
18:00 | 3119 | 782 | 1811 | 1698 | 578 | 44 | 154 | 0 | 102 | 0
18:30 | 3123 | 781.5 | 1712 | 1876 | 598.5 | 44.5 | 150.5 | 0 | 101 | 0
19:00 | 3127 | 781 | 1613 | 2054 | 619 | 45 | 147 | 0 | 100 | 0
19:30 | 3142 | 782 | 1626 | 2079 | 620 | 46 | 147 | 0 | 104 | 0
20:00 | 3114 | 782 | 1639 | 2043 | 621 | 46 | 141 | 0 | 100 | 0
20:30 | 3139.5 | 782 | 1682.5 | 1844 | 621 | 46.5 | 110 | 0 | 98 | 0
21:00 | 3165 | 782 | 1726 | 1645 | 621 | 47 | 79 | 0 | 96 | 0
21:30 | 3154.5 | 782 | 1702 | 1407 | 620.5 | 47 | 68.5 | 0 | 94 | 0
22:00 | 3144 | 782 | 1678 | 1169 | 620 | 47 | 58 | 0 | 92 | 0
22:30 | 3143.5 | 686 | 1684 | 1079.5 | 619.5 | 47.5 | 29 | 0 | 90 | 0
23:00 | 3143 | 590 | 1690 | 990 | 619 | 48 | 0 | 0 | 88 | 0
23:30 | 3141 | 495.5 | 1708.5 | 990 | 604 | 48 | 0 | 0 | 83 | 0 | Max Temp. in Dhaka |  | 26.0° C
24:00 | 3139 | 401 | 1727 | 990 | 589 | 48 | 0 | 0 | 78 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 44 | 44 | 44 | 44 | 43 | 45 | 46 | 46 | 48 | 48 | 49 | 49 | 47 | 46 | 45 | 44 |  | 45 | 46 | 46 | 47 | 47 | 48 | 48 | 1090909
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  |  |  | 17 | 17 | 16 | 9 | 10 | 4 | 0 | [9 empty] | 81270
6 | Sikalbaha 225MW CCPP (Gas) | 201 | 202 | 202 | 202 | 203 | 204 | 212 | 217 | 203 | 203 | 204 | 228 | 204 | 203 | 203 | 210 | 204 | 203 |  | 203 | 206 | 203 | 205 | 203 | 204 | 204 | 4885140
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 0 |  |  | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 |  | 0 | 326927
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 22 | 70 | 75 | 90 | 95 | 95 | 95 | 164 |  | 207 | 195 | 195 | 95 | 15 | 15 | 0 | 1319781
19 | Ashuganj 195MW PP (APSCL-United) | 83 | 45 | 16 | 16 | 16 | 26 | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 73 | 73 | 1221090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [19 empty] | 10 | [5 empty] | 0 | 10000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7189991
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 130 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 2839865
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 10 | 10 | 10 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 24 | 24 | 24 |  | 24 | 24 | 26 | 24 | 26 | 26 | 26 | 529056
33 | Ashuganj 225 MW CCPP | 184 | 183 | 183 | 183 | 195 | 194 | 204 | 206 | 191 | 184 | 194 | 206 | 186 | 184 | 183 | 192 | 184 | 189 |  | 183 | 190 | 184 | 192 | 183 | 183 | 183 | 4636000
34 | Ashuganj 450 MW CCPP(South)
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 903360
36 | Chandpur 150 MW CCPP | 50 | 48 | 47 | 50 | 51 | 52 | 51 | 51 | 51 | 52 | 50 | 51 | 50 | 46 | 50 | 51 | 52 | 50 |  | 51 | 51 | 51 | 51 | 51 | 50 | 47 | 1168530
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 353 | 349 | 358 | 355 | 378 | 372 | 377 | 382 | 352 | 360 | 374 | 375 | 359 | 354 | 370 | 376 | 357 |  | 351 | 363 | 359 | 368 | 363 | 349 | 350 | 8845310
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 320 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 420 | 340 | 300 | 320 | 420 | 420 |  | 360 | 360 | 360 | 360 | 360 | 360 | 380 | 8578750
41 | Haripur 360MW CCPP(HPL) | 308 | 308 | 266 | 267 | 267 | 337 | 337 | 337 | 354 | 304 | 303 | 308 | 354 | 273 | 254 | 303 | 354 | 354 |  | 333 | 337 | 337 | 337 | 337 | 358 | 359 | 7572000
42 | RPCL 210MW CCPP | 163 | 164 | 164 | 164 | 164 | 164 | 162 | 163 | 164 | 161 | 158 | 157 | 117 | 103 | 104 | 104 | 123 | 125 |  | 126 | 126 | 126 | 127 | 127 | 148 | 148 | 3353600
43 | Sutiakhali 50 MW Solar PP | [7 empty] | 9 | 20 | 31 | 36 | 39 | 33 | 27 | 18 | 7 | 1 | [9 empty] | 223350
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015440
46 | Shajibazar 330 MW CCPP | 121 | 120 | 121 | 120 | 121 | 120 | 156 | 158 | 156 | 157 | 157 | 157 | 156 | 157 | 158 | 158 | 158 | 156 |  | 158 | 158 | 158 | 157 | 157 | 159 | 157 | 3352000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 36 | 36 | 36 | 36 | 36 | 35 | 34 | 34 | 20 | 10 | 20 | 33 |  | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 685632
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 77 | 74 | 74 | 74 | 74 | 74 | 77 | 75 | 74 | 71 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1409280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 98 | 99 | 99 | 99 | 94 | 77 | 85 | 91 | 121 | 120 | 120 | 125 | 125 | 126 |  | 120 | 130 | 123 | 130 | 120 | 95 | 96 | 2715580
51 | Sylhet 20 MW GTPP | [22 empty] | 18 | 18 | 18 | 19 | 60000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 2 | 2 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 149048
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 5 | 7 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 264600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 14 | 14 | 15 | 15 | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 244584
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 380 | 400 | 400 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7456200
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 10 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 72935
59 | Tangail Palli Power Gen 22 MW | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 602640
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384576
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 13 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 215856
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 333360
63 | Impoprt (Tripura) | 74 | 66 | 66 | 64 | 62 | 68 | 68 | 74 | 78 | 80 | 82 | 82 | 86 | 90 | 84 | 78 | 86 | 102 |  | 100 | 104 | 100 | 96 | 92 | 88 | 78 | 1918080
64 | Malancha, Ctg. EPZ (United) | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 8 | 6 | 4 | 4 | 4 | 7 | 5 | 2 | 5 | 7 | 12 |  | 15 | 16 | 17 | 17 | 17 | 19 | 20 | 269280
65 | Feni 22MW PP (Doreen) | 21 | [5 empty] | 5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 372276
66 | Feni 11 MW PP (Doreen) | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184680
67 | Jangalia 33MW PP (Summit) | [6 empty] | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 16 | 16 | 16 | 25 | 25 | 17 | 416000
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 17 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 460630
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 9 | 9 | 8 | 9 | 9 | 9 | 6 | 8 | 10 | 20 | 25 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 502560
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 536600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 29 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818000
73 | Ghorashal 108MW PP (Regent) | 94 | 56 | 24 | 24 | 24 | 54 | 84 | 95 | 97 | 95 | 92 | 94 | 97 | 97 | 97 | 97 | 97 | 102 |  | 104 | 104 | 104 | 104 | 101 | 103 | 101 | 1991590
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [8 empty] | 4 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 |  |  |  |  | 0 | 313320
Manikgonj 162MW PP(MPGL)
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 15 |  | 15 | 15 | 15 |  |  |  | 0 | 54720
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 10 | 48 |  | 16 | 16 | 10 |  |  |  | 0 | 72480
80 | Jamalpur 95 MW PP(Powerpac) |  | 0 | 0 | [13 empty] | 10 | 38 |  | 74 | 80 | 80 | 50 |  |  | 0 | 274560
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 14 |  | 47 | 52 | 51 |  |  |  |  | 123797
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 9 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23640
| Jodiac Power | 54 | 54 | 17 |  |  |  | 24 | 48 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1088555
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 2 | 15 |  | 15 | 15 | 10 |  |  |  | 0 | 50904
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 8 | 31 | 50 | 50 | 50 | 60 | 86 | 85 | 86 | 86 | 80 |  | 72 | 72 | 73 | 74 | 84 | 86 | 86 | 1206014
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 15 | 50 | 42 | 16 | 16 | 22 | 32 | 32 | 32 | 35 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 1010880
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 18 | 54 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1440000
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 590256
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 44 | 44 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1003716
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | 18 | [5 empty] | 3 | 27 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 863520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 4 | 15 |  | 15 | 15 | 15 | 15 | 15 |  | 0 | 91675
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 |  | 0 | 558893
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 110 | 110 | 163 | 110 | 110 | 110 | 130 | 130 | 163 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3101236
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 10350
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 877320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 45600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [25 empty] | 0 | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 30 | 70 | 70 | 40 | 20 | 50 | 100 |  | 100 | 100 | 100 | 100 | 50 |  | 0 | 822720
116 | Chandpur 200MW (Desh energy) | [7 empty] | 14 | 41 | 66 | 68 | 68 | 73 | 85 | 85 | 85 | 85 | 120 |  | 180 | 180 | 180 | 180 | 180 | 180 | 136 | 1890240
117 | Ashuganj 150MW PP (Midland) | [7 empty] | 1 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 13 | 86 |  | 150 | 150 | 150 | 50 |  |  | 0 | 669090
118 | Bibiyana-III 400 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 100 | 150 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3414000
| Jamalpur 115 MW PP (United) | [8 empty] | 2 | 16 | 16 | 35 | 45 | 45 | 30 | 30 | 30 | 78 |  | 115 | 115 | 115 | 115 | 65 | 35 | 24 | 920400
| Anwara 300 MW PP (United) | 33 | [6 empty] | 33 | 82 | 88 | 88 | 123 | 124 | 100 | 35 | 35 | 87 | 157 |  | 157 | 161 | 161 | 162 | 162 | 162 | 52 | 1869273
| Juldah unit-2 (Acorn) | [16 empty] | 28 | 100 |  | 80 | 80 | 80 | 50 |  |  | 0 | 337920
| Anlima Energy Ltd. | [11 empty] | 12 | 15 | 17 | 18 | 14 | [9 empty] | 0 | 82800
120 | Eastern Zone Total | 3739 | 3533 | 3365 | 3358 | 3312 | 3561 | 3782 | 4123 | 4388 | 4404 | 4452 | 4707 | 4864 | 4757 | 4523 | 4590 | 4862 | 5590 |  | 5696 | 5722 | 5664 | 5342 | 4981 | 4860 | 4660 | 108070735
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 32 |  | 32 | 32 | 32 |  |  |  | 0 | 116160
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 53 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 17 | 1051680
130
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 28 | 30 | 30 | 31 | 31 | 31 | 33 | 8 | 7 | 6 | 16 | 35 | 35 | 11 | 18 | 36 | 36 | 13 |  | 15 | 16 | 30 | 35 | 16 | 16 | 35 | 608454
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 22 | 48 |  | 64 | 64 | 64 | 64 | 64 | 48 | 16 | 381312
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 319859
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 18 | 18 | 19 | 20 | 18 | 17 | 18 | 18 | 19 | 19 | 20 | 19 | 18 | 20 | 25 |  | 26 | 27 | 27 | 27 | 27 | 25 | 23 | 481600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 413 | 414 | 413 | 317 | 317 | 317 | 413 | 507 | 507 | 555 | 546 | 546 | 546 | 546 | 546 | 546 | 546 | 782 |  | 781 | 782 | 782 | 782 | 782 | 590 | 401 | 12925091
147 | Bheramara 410 MW CCPP | 345 | 345 | 350 | 345 | 355 | 365 | 370 | 380 | 360 | 340 | 355 | 390 | 345 | 345 | 305 | 260 | 300 | 340 |  | 340 | 350 | 340 | 345 | 340 | 345 | 345 | 8575776
148 | Payra 1320 MW | 460 | 420 | 340 | 300 | 300 | 300 | 300 | 380 | 420 | 420 | 420 | 420 | 440 | 450 | 450 | 450 | 450 | 490 |  | 530 | 530 | 530 | 530 | 530 | 530 | 500 | 11217600
149
150 | Barapukuria TPP Unit-1 | 85 | 86 | 87 | 88 | 88 | 88 | 87 | 86 | 87 | 85 | 87 | 85 | 84 | 85 | 87 | 87 | 88 | 88 |  | 89 | 90 | 91 | 91 | 90 | 89 | 89 | 2107636
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 190 | 186 | 191 | 191 | 195 | 193 | 201 | 196 | 164 | 164 | 177 | 181 | 170 | 157 | 164 | 169 | 165 |  | 170 | 162 | 162 | 166 | 164 | 154 | 160 | 4488282
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 306 | 332 | 296 | 334 | 332 | 397 | 402 | 406 | 413 | 322 | 364 | 404 | 364 | 330 | 301 | 361 | 364 | 424 |  | 341 | 347 | 345 | 427 | 401 | 375 | 375 | 8735400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) |  | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 361680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 187380
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 72 |  | 97 | 97 | 97 | 45 | 24 |  |  | 337168
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 7 | 84 |  | 109 | 111 | 111 | 111 | 35 |  | 0 | 530016
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 25 | 35 | 35 | 35 |  |  | 0 | 111168
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 35 | 45 | 40 | 25 |  |  | 0 | 96960
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 3 | 2 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 15124
178
178