## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-19 | Saturday
|  |  | Date (day): | 2020-12-19 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12395.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13632 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-18 | 2020-12-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 91 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 377 | 375 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 306 | 354 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 47 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 95 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 32 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 71 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1724 | 2109 | 3694 | 3984 | 841 | 1060
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 44 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 44 | 44 | 44 | 186 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 179 | 214 | 215 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 20 | 18 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 53 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 141 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 35 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 40 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 578 | 703 | 1436 | 1431 | 696 | 121
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 70 | 100 | 100
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 165 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 15 | 265 | 0 | 0 |  | 360 | Under maint.
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 5 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 5 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 8 | 73 | 73 | 122 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 70 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 51 | 60 | 60
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 51 | 50 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 66 | 98 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 0 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 760 | 911 | 1432 | 1692 | 410 | 728
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 144 | 160 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 95 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 26 | 0 | 0 | 0
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 232 | 374 | 641.6 | 580 | 52 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 32 | GT-1 FGMO & GT-2 under S/D.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 30 | 43 | 43
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 128 | 126 | 150 | 150 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 6 | 34 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 30 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 34 | 36 | 36 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 75 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 119 | 130 | 130
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 124 | 119 | 200 | 200
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 196 | 300 | 300 | 300
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 874 | 1105 | 1280 | 1280 | 178 | 415
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 404 | 685 | 549 | 790
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 370 | 410 | 410
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 70 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 804 | 1125 | 1394 | 1971 | 0 | 88
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 27 | 27 |  | 6 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 12 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 260 | 450 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 12 | 36 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 302 | 571 | 867 | 927 | 0 | 200
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 30 | 70 | 70 | 70 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 162 | 225 | 225 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 385 | 365 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 8 | 62 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 623 | 803 | 1440 | 1564 | 171 | 446
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 88 | 87 | 90 | 90
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 100 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 91 | 187 | 211 | 203 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 5988 | 7888 | 12395.6 | 13632 | 2348 | 3457
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5623.6187 | 7408 | 11641.3039 | 12802.4665
| A. |  | 2020-12-18 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 7888 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5405 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7888 | MW
| 3 | Day peak Generation : |  |  | 5988 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7408 | MW
| 4 | Evening peak Generation : |  |  | 7888 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 154.3547 | MKWHr | By Solar | 0.43981 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 115.3961 | MKWHr |  | By Oil: | 13.3437 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.8355 | MKWHr |  | By Hydro: | 1.1367 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2348 | MW | Dhaka | 2351 | 2351 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3457 | MW | Chittagong | 824 | 824 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5805 | MW | Khulna | 1010 | 1010 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 845.31 | MMCFD |  |  | Rajshahi | 793 | 793 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 125952076.22 | ii) Oil : | Taka | 102915350.36 | Comilla | 687 | 687 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 55348484.7 | Total | Taka | 284215911.28 | Mymensingh | 663 | 663 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.3275 | MKWHr. | Sylhet | 295 | 295 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -47 | MW (E to W) at | 19:30 | hrs | Barisal | 226 | 226 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -143 | MW at | 18:00 | hrs | Rangpur | 559 | 559 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 24.2° C |  |  | Total | 7408 | 7408 |  | 0
| B. |  | 2020-12-19 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 23.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13632 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
| 4 | Reserve(Generation end) |  |  |  | 5132 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 166.3305 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4945 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.4124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 685 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7904 | MKWHr. | iii) Maximum HVDC Flow : |  | 689 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.02 |  | (b) Today: | 98.96 |  | (c) Rule Curve: |  | 104.3
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 349 | 359 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 18 | 16 | 19 | 0 | 120 | 0 | 0 | 0 | 183 | 73 | 49 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 74 | 164 | 0 | 20 | 0 | 30 | 43 | 5 | 30 | 110 | 157 | 34 | 75 | 0 | 101 | 18 | 0 | 0 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 200 | 24 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 0 | 0 | 0 |  | 414 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 38 | 0 | 0 |  | 4320 | 1906 | 6226 | 3159 | 414 | 1684 | 294 | 554 | 47 | 0 | 74 | 0 | 0 | 99.03
2:00 | 0 | 0 | 0 | 115 | 300 | 56 | 0 | 360 | 359 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 0 | 120 | 0 | 0 | 0 | 185 | 73 | 51 | 26 | 56 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 18 | 72 | 163 | 0 | 20 | 0 | 30 | 43 | 5 | 5 | 140 | 156 | 20 | 10 | 0 | 95 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 414 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 164 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 3851 | 1949 | 5800 | 3093 | 414 | 1549 | 68 | 557 | 47 | 0 | 72 | 0 | 0 | 99.03
3:00 | 0 | 0 | 0 | 115 | 300 | 27 | 0 | 352 | 359 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 120 | 0 | 0 | 0 | 183 | 73 | 51 | 23 | 20 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 68 | 163 | 0 | 20 | 0 | 30 | 43 | 5 | 5 | 140 | 158 | 20 | 10 | 0 | 95 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 |  | 414 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 161 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 3727 | 1912 | 5639 | 3070 | 414 | 1475 | 26 | 539 | 47 | 0 | 68 | 0 | 0 | 99.03
4:00 | 0 | 0 | 0 | 115 | 300 | 27 | 0 | 351 | 359 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 120 | 0 | 0 | 0 | 183 | 73 | 51 | 23 | 20 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 64 | 166 | 0 | 20 | 0 | 30 | 43 | 5 | 5 | 140 | 156 | 20 | 10 | 0 | 95 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 308 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 160 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 3720 | 1760 | 5480 | 3063 | 308 | 1432 | 26 | 542 | 45 | 0 | 64 | 0 | 0 | 99.03
5:00 | 0 | 0 | 0 | 115 | 300 | 27 | 0 | 357 | 308 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 100 | 0 | 0 | 0 | 193 | 73 | 51 | 23 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 64 | 163 | 0 | 20 | 0 | 30 | 43 | 5 | 5 | 140 | 126 | 20 | 10 | 0 | 95 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 |  | 308 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 153 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 0 |  | 3629 | 1776 | 5405 | 3056 | 308 | 1417 | 26 | 489 | 45 | 0 | 64 | 0 | 0 | 99.02
6:00 | 0 | 0 | 0 | 115 | 300 | 95 | 0 | 363 | 308 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 100 | 0 | 0 | 0 | 183 | 73 | 51 | 23 | 5 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 68 | 164 | 0 | 20 | 0 | 30 | 43 | 5 | 18 | 140 | 127 | 35 | 70 | 0 | 95 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 300 | 6 | 0 | 0 | 0 | 0 |  | 308 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 152 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 0 |  | 3791 | 1735 | 5526 | 3039 | 308 | 1512 | 68 | 486 | 45 | 0 | 68 | 0 | 0 | 99.02
7:00 | 0 | 0 | 0 | 115 | 300 | 99 | 0 | 353 | 267 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 1 | 16 | 4 | 0 | 100 | 0 | 0 | 0 | 186 | 73 | 50 | 23 | 55 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 60 | 165 | 0 | 20 | 0 | 30 | 43 | 5 | 49 | 110 | 127 | 34 | 74 | 0 | 98 | 19 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 34 | 0 | 200 | 0 | 0 | 0 | 0 | 66 | 27 | 0 | 0 | 0 | 0 | 300 | 17 | 1 | 0 | 0 | 0 |  | 308 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 147 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 13 | 0 | 0 |  | 3962 | 1552 | 5514 | 2998 | 308 | 1500 | 214 | 387 | 45 | 0 | 60 | 2 | 0 | 99.02
8:00 | 0 | 0 | 0 | 115 | 300 | 99 | 0 | 363 | 267 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 20 | 16 | 6 | 0 | 100 | 0 | 0 | 0 | 187 | 73 | 52 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 72 | 164 | 0 | 20 | 1 | 30 | 43 | 5 | 49 | 110 | 127 | 34 | 77 | 0 | 127 | 19 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 37 | 0 | 200 | 0 | 0 | 0 | 1 | 102 | 36 | 0 | 0 | 0 | 0 | 300 | 17 | 10 | 0 | 0 | 0 |  | 308 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 163 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 16 | 0 | 0 |  | 4133 | 1670 | 5803 | 3103 | 308 | 1584 | 285 | 387 | 45 | 0 | 72 | 19 | 0 | 99.02
9:00 | 0 | 0 | 0 | 115 | 300 | 99 | 0 | 352 | 270 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 100 | 0 | 0 | 0 | 194 | 73 | 52 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 62 | 163 | 0 | 20 | 1 | 30 | 43 | 5 | 49 | 110 | 128 | 20 | 77 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 40 | 51 | 0 | 200 | 0 | 0 | 0 | 2 | 123 | 36 | 0 | 0 | 0 | 0 | 300 | 17 | 23 | 0 | 0 | 0 |  | 403 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 157 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 11 | 0 | 0 |  | 4090 | 1653 | 5743 | 3013 | 403 | 1527 | 310 | 337 | 45 | 8 | 62 | 38 | 0 | 99.02
10:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 364 | 274 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 0 | 100 | 0 | 0 | 0 | 208 | 73 | 51 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 62 | 162 | 0 | 17 | 2 | 30 | 43 | 5 | 49 | 110 | 129 | 20 | 77 | 0 | 21 | 19 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 51 | 0 | 200 | 0 | 0 | 0 | 3 | 125 | 36 | 0 | 0 | 26 | 0 | 200 | 17 | 35 | 0 | 0 | 0 |  | 403 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 164 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 12 | 0 | 0 |  | 3936 | 1710 | 5646 | 2866 | 403 | 1560 | 308 | 336 | 45 | 8 | 62 | 58 | 0 | 99.01
11:00 | 0 | 0 | 0 | 115 | 300 | 98 | 0 | 374 | 309 |  | 0 | 330 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 12 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 26 | 0 | 0 | 3 | 0 | 0 | 14 | 18 | 0 | 100 | 0 | 0 | 10 | 200 | 73 | 50 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 66 | 160 | 0 | 17 | 2 | 30 | 43 | 5 | 49 | 110 | 126 | 20 | 76 | 0 | 21 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 70 | 51 | 0 | 130 | 0 | 0 | 0 | 4 | 16 | 36 | 0 | 0 | 36 | 60 | 196 | 17 | 39 | 0 | 0 | 0 |  | 403 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 168 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 12 | 0 | 0 |  | 3952 | 1759 | 5711 | 2830 | 403 | 1624 | 333 | 337 | 45 | 8 | 66 | 65 | 0 | 99.01
12:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 377 | 306 |  | 0 | 360 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 |  | 26 | 0 | 0 | 10 | 53 | 0 | 16 | 20 | 0 | 100 | 0 | 0 | 15 | 193 | 73 | 51 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 66 | 142 | 0 | 17 | 2 | 30 | 43 | 6 | 49 | 163 | 128 | 20 | 75 | 0 | 20 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 90 | 51 | 5 | 124 | 0 | 0 | 0 | 4 | 16 | 36 | 0 | 0 | 36 | 90 | 196 | 17 | 45 | 0 | 0 | 0 |  | 404 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 170 | 0 | 385 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 260 | 12 | 0 | 0 |  | 4168 | 1820 | 5988 | 2828 | 404 | 1709 | 507 | 348 | 46 | 8 | 66 | 72 | 0 | 99.01
13:00 | 0 | 0 | 0 | 115 | 300 | 102 | 0 | 380 | 353 |  | 0 | 400 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 |  | 26 | 0 | 0 | 30 | 60 | 0 | 16 | 20 | 0 | 100 | 0 | 0 | 70 | 155 | 73 | 45 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 74 | 121 | 0 | 17 | 2 | 30 | 43 | 28 | 49 | 163 | 126 | 33 | 75 | 0 | 20 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 100 | 51 | 30 | 130 | 0 | 0 | 0 | 4 | 16 | 36 | 0 | 0 | 36 | 90 | 196 | 70 | 40 | 0 | 0 | 0 |  | 404 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 191 | 0 | 373 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 320 | 10 | 0 | 0 |  | 4370 | 1911 | 6281 | 2883 | 404 | 1768 | 622 | 408 | 47 | 8 | 74 | 67 | 6281 | 99.01
14:00 | 0 | 0 | 0 | 115 | 300 | 104 | 0 | 354 | 286 |  | 0 | 330 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 25 | 0 | 16 | 20 | 0 | 80 | 0 | 0 | 45 | 170 | 36 | 47 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 66 | 120 | 0 | 17 | 2 | 30 | 43 | 31 | 49 | 110 | 126 | 20 | 76 | 0 | 77 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 17 | 10 | 120 | 0 | 0 | 0 | 3 | 16 | 17 | 0 | 0 | 36 | 50 | 197 | 35 | 32 | 0 | 0 | 0 |  | 403 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 166 | 0 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 320 | 11 | 0 | 0 |  | 3834 | 1727 | 5561 | 2778 | 403 | 1454 | 343 | 407 | 48 | 8 | 66 | 54 | 0 | 99.01
15:00 | 0 | 0 | 0 | 115 | 300 | 97 | 0 | 352 | 285 |  | 0 | 330 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 14 | 0 | 16 | 7 | 0 | 80 | 0 | 0 | 40 | 173 | 36 | 46 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 64 | 121 | 0 | 20 | 1 | 30 | 43 | 31 | 49 | 110 | 127 | 20 | 76 | 0 | 77 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 17 | 0 | 120 | 0 | 0 | 0 | 2 | 5 | 17 | 0 | 0 | 36 | 30 | 200 | 17 | 24 | 0 | 0 | 0 |  | 404 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 157 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 300 | 35 | 0 | 0 |  | 3702 | 1685 | 5387 | 2777 | 404 | 1440 | 227 | 386 | 49 | 0 | 64 | 40 | 0 | 99
16:00 | 0 | 0 | 0 | 115 | 300 | 25 | 0 | 358 | 287 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 9 | 0 | 70 | 0 | 0 | 240 | 133 | 8 | 52 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 0 | 8 | 12 | 64 | 121 | 0 | 20 | 0 | 30 | 30 | 14 | 10 | 110 | 127 | 20 | 10 | 0 | 77 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 120 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 36 | 0 | 300 | 0 | 10 | 0 | 0 | 0 |  | 404 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 161 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 11 | 0 | 0 |  | 3531 | 1737 | 5268 | 3091 | 404 | 1205 | 103 | 336 | 48 | 0 | 64 | 17 | 0 | 99
17:00 | 0 | 0 | 67 | 115 | 300 | 13 | 0 | 361 | 248 |  | 0 | 300 | 0 | 4 | 7 | 0 | 0 | 0 | 0 | 2 | 0 | 32 | 0 | 0 | 0 | 0 | 30 | 17 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 44 | 0 | 0 | 0 | 16 | 12 | 0 | 70 | 0 | 0 | 250 | 136 | 8 | 46 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 2 | 8 | 18 | 80 | 140 | 5 | 20 | 0 | 30 | 30 | 14 | 10 | 110 | 127 | 20 | 10 | 0 | 102 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 0 | 0 | 0 | 6 | 0 | 50 | 15 | 15 | 120 | 35 | 0 | 0 | 0 | 31 | 22 | 0 | 0 | 36 | 30 | 300 | 30 | 1 | 0 | 0 | 0 |  | 404 | 0 | 340 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 12 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 162 | 0 | 265 | 35 | 0 | 17 | 0 | 37 | 0 | 0 | 0 | 250 | 15 | 0 | 0 |  | 3926 | 1793 | 5719 | 3211 | 404 | 1063 | 460 | 337 | 47 | 116 | 80 | 1 | 0 | 99
18:00 | 0 | 0 | 0 | 115 | 300 | 13 | 0 | 361 | 353 |  | 0 | 420 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 16 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 20 | 16 | 12 | 0 | 70 | 0 | 0 | 260 | 161 | 8 | 51 | 5 | 5 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 20 | 20 | 94 | 143 | 38 | 20 | 0 | 30 | 30 | 31 | 22 | 163 | 126 | 33 | 75 | 0 | 118 | 18 | 0 | 0 | 0 | 8 | 11 | 0 | 75 | 0 | 0 | 5 | 0 | 39 | 0 | 90 | 36 | 58 | 120 | 115 | 0 | 0 | 0 | 101 | 35 | 0 | 0 | 36 | 40 | 300 | 53 | 0 | 0 | 0 | 0 |  | 689 | 0 | 390 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 0 | 0 | 70 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 167 | 0 | 371 | 70 | 0 | 36 | 0 | 37 | 0 | 0 | 0 | 280 | 35 | 0 | 0 |  | 4950 | 2390 | 7340 | 3330 | 689 | 1599 | 1075 | 366 | 44 | 143 | 94 | 0 | 0 | 99
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 300 | 82 | 0 | 362 | 360 |  | 0 | 420 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 15 | 0 | 20 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 20 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 36 | 16 | 18 | 0 | 70 | 0 | 0 | 270 | 160 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 100 | 144 | 92 | 20 | 0 | 30 | 30 | 34 | 30 | 130 | 127 | 34 | 75 | 0 | 119 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 50 | 100 | 122 | 115 | 0 | 0 | 0 | 135 | 35 | 0 | 0 | 0 | 40 | 300 | 71 | 0 | 0 | 0 | 0 |  | 685 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 70 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 343 | 70 | 0 | 99 | 0 | 108 | 0 | 0 | 0 | 420 | 36 | 0 | 0 |  | 5209 | 2636 | 7845 | 3299 | 685 | 1649 | 1430 | 506 | 43 | 133 | 100 | 0 | 0 | 98.99
19:30 | 0 | 0 | 0 | 115 | 300 | 91 | 0 | 375 | 354 |  | 0 | 420 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 44 | 16 | 18 | 0 | 70 | 0 | 0 | 265 | 165 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 98 | 144 | 95 | 20 | 0 | 30 | 30 | 34 | 30 | 163 | 126 | 34 | 75 | 0 | 119 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 50 | 70 | 119 | 115 | 0 | 0 | 0 | 141 | 35 | 0 | 0 | 0 | 40 | 300 | 71 | 0 | 0 | 0 | 0 |  | 685 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 70 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 162 | 0 | 365 | 70 | 0 | 111 | 0 | 100 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 5202 | 2686 | 7888 | 3345 | 685 | 1709 | 1341 | 537 | 44 | 129 | 98 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 366 | 353 |  | 0 | 420 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 45 | 16 | 18 | 0 | 85 | 0 | 0 | 215 | 173 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 98 | 144 | 95 | 20 | 0 | 30 | 30 | 34 | 30 | 163 | 127 | 34 | 76 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 52 | 70 | 122 | 115 | 0 | 0 | 0 | 142 | 35 | 0 | 0 | 0 | 40 | 300 | 71 | 0 | 0 | 0 | 0 |  | 686 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 70 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 320 | 70 | 0 | 111 | 0 | 106 | 0 | 0 | 0 | 450 | 35 | 0 | 0 |  | 5177 | 2621 | 7798 | 3272 | 686 | 1673 | 1357 | 537 | 46 | 129 | 98 | 0 | 0 | 98.99
21:00 | 0 | 0 | 0 | 115 | 300 | 103 | 0 | 354 | 358 |  | 0 | 420 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 46 | 16 | 20 | 0 | 100 | 0 | 0 | 0 | 183 | 8 | 52 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 96 | 145 | 64 | 20 | 0 | 30 | 30 | 34 | 30 | 163 | 128 | 34 | 76 | 0 | 119 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 68 | 70 | 123 | 115 | 0 | 0 | 0 | 143 | 35 | 0 | 0 | 0 | 40 | 300 | 87 | 0 | 0 | 0 | 0 |  | 685 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 48 | 0 | 0 | 70 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 160 | 0 | 360 | 70 | 0 | 111 | 0 | 60 | 0 | 0 | 0 | 500 | 17 | 0 | 0 |  | 5043 | 2642 | 7685 | 3104 | 685 | 1706 | 1348 | 587 | 46 | 113 | 96 | 0 | 0 | 98.99
22:00 | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 349 | 359 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 20 | 0 | 100 | 0 | 0 | 0 | 183 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 88 | 145 | 48 | 20 | 0 | 30 | 30 | 34 | 30 | 163 | 129 | 34 | 76 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 45 | 0 | 0 | 0 | 0 | 22 | 0 | 100 | 68 | 70 | 122 | 115 | 0 | 0 | 0 | 142 | 46 | 0 | 0 | 0 | 40 | 300 | 87 | 0 | 0 | 0 | 0 |  | 401 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 156 | 0 | 347 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 500 | 17 | 0 | 0 |  | 4897 | 2195 | 7092 | 3091 | 401 | 1691 | 1186 | 589 | 46 | 0 | 88 | 0 | 0 | 98.99
23:00 | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 349 | 359 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 17 | 0 | 11 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 20 | 0 | 100 | 0 | 0 | 0 | 183 | 8 | 45 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 80 | 148 | 0 | 20 | 0 | 30 | 30 | 34 | 30 | 130 | 126 | 35 | 76 | 0 | 120 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 68 | 40 | 133 | 75 | 0 | 0 | 0 | 106 | 54 | 0 | 0 | 0 | 0 | 300 | 86 | 0 | 0 | 0 | 0 |  | 401 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 48 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 156 | 0 | 323 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 37 | 0 | 0 |  | 4504 | 2069 | 6573 | 3094 | 401 | 1653 | 710 | 588 | 47 | 0 | 80 | 0 | 0 | 98.99
24:00 | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 349 | 359 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 35 | 0 | 0 | 11 | 25 | 33 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 29 | 0 | 100 | 0 | 0 | 0 | 182 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 72 | 165 | 0 | 20 | 0 | 30 | 30 | 5 | 5 | 130 | 126 | 34 | 76 | 0 | 118 | 19 | 0 | 0 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 120 | 16 | 0 | 0 | 0 | 70 | 54 | 0 | 0 | 0 | 0 | 300 | 85 | 0 | 0 | 0 | 0 |  | 401 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 156 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 36 | 0 | 0 |  | 4195 | 1920 | 6115 | 3101 | 401 | 1611 | 366 | 517 | 47 | 0 | 72 | 0 | 0 | 98.98
KWH | 0 | 0 | 103000 | 2772000 | 7205627 | 1875545 | 0 | 8738820 | 7644000 |  | 0 | 8479250 | 0 | 85440 | 117528 | 12223 | 0 | 0 | 0 | 38400 | 0 | 102720 | 286018 | 0 | 0 | 0 | 688680 | 308501 | 0 | 228024 | 600000 | 546480 | 542300 | 840400 | 0 | 0 | 1136727 | 0 | 0 | 0 | 0 | 4738944 | 0 | 0 | 0 |  | 376320 | 0 | 223696 | 34320 | 175680 | 300480 | 378816 | 377760 | 0 | 2325325 | 0 | 0 | 1405000 | 4359000 | 1154181 | 1157230 | 455472 | 671040 | 0 | 953622 | 0 | 0 | 0 | 276084 | 63360 | 4839000 | 419020 | 1790400 | 3501560 | 385920 | 406008 | 12750 | 717000 | 919440 | 371400 | 786960 | 3379745 | 3010000 | 647040 | 1389120 | 0 | 2106660 | 447000 | 0 | 0 | 0 | 97488 | 104528 | 0 | 534436 | 0 | 0 | 24000 | 0 | 190080 | 118800 | 1150080 | 984960 | 543636 | 3740000 | 812400 | 0 | 0 | 25200 | 1359927 | 711131 | 0 | 0 | 360360 | 528000 | 6617700 | 902400 | 257620 | 0 | 0 | 0 |  | 10412364 | 0 | 8531424 | 0 | 52800 | 0 | 0 | 0 | 0 | 0 | 6375 | 0 | 483000 | 300672 | 0 | 0 | 805000 | 0 | 0 | 320570 | 0 | 0 | 0 | 0 | 0 | 445680 | 0 | 195210 | 2067490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291690 | 0 | 4131382 | 0 | 8508327 | 541920 | 0 | 524064 | 0 | 360000 | 0 | 25444 | 0 | 9768000 | 613473 | 0 | 0 |  | 105969782 | 48384885 | 154354667 | 77971342 | 10412364 | 37424793 | 12696751 | 11835490 | 1136727 | 646986 | 1790400 | 439814 | 0
Fuel Cost | 0 | 0 | 150380 | 4074840 | 7998245.97 | 2475719.4 | 0 | 8826208.2 | 7873320 |  | 0 | 9242382.5 | 0 | 648489.6 | 809767.92 | 103406.58 | 0 | 0 | 0 | 289152 | 0 | 1010764.8 | 2637085.96 | 0 | 0 | 0 | 5027364 | 2384712.73 | 0 | 171018 | 450000 | 0 | 0 | 0 | 0 | 0 | 306916.29 | 0 | 0 | 0 | 0 | 5165448.96 | 0 | 0 | 0 |  | 0 | 0 | 2169851.2 | 327756 | 1528416 | 2379801.6 | 477308.16 | 1121947.2 | 0 | 3441481 | 0 | 0 | 1405000 | 4010280 | 1488893.49 | 1330814.5 | 514683.36 | 939456 | 0 | 1630693.62 | 0 | 0 | 0 | 350626.68 | 47520 | 8468250 | 314265 | 13428000 | 3711653.6 | 3504153.6 | 515630.16 | 203235 | 1175880 | 1471104 | 661092 | 1227657.6 | 3852909.3 | 3130400 | 1274668.8 | 2653219.2 | 0 | 3644521.8 | 978930 | 0 | 0 | 0 | 73116 | 79441.28 | 0 | 4040336.16 | 0 | 0 | 124800 | 0 | 1870387.2 | 1388772 | 9373152 | 10686816 | 3832633.8 | 3478200 | 7409088 | 0 | 0 | 0 | 10281048.12 | 6193951.01 | 0 | 0 | 3088285.2 | 3516480 | 0 | 0 | 0 | 0 | 0 | 0 |  | 59975216.64 | 0 | 8957995.2 | 0 | 415008 | 0 | 0 | 0 | 0 | 0 | 66427.5 | 0 | 748650 | 2934558.72 | 0 | 0 | 1650250 | 0 | 0 | 2837044.5 | 0 | 0 | 0 | 0 | 0 | 855705.6 | 0 | 147773.97 | 12466964.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437535 | 0 | 4833716.94 | 0 | 8423243.73 | 5657644.8 | 0 | 4973367.36 | 0 | 2793600 | 0 | 281156.2 | 0 | 42881520 | 0 | 0 | 0 |  | 198461828.55 | 161337378.86 | 359799207.41 | 82319651.58 | 59975216.64 | 43632424.64 | 96897689.86 | 55348484.7 | 306916.29 | 6017660.5 | 13428000 | 1873163.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 300 | 101 | 0 | 377 | 306 |  | 0 | 360 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 12 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 |  | 26 | 0 | 0 | 10 | 53 | 0 | 16 | 20 | 0 | 100 | 0 | 0 | 15 | 193 | 73 | 51 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 66 | 142 | 0 | 17 | 2 | 30 | 43 | 6 | 49 | 163 | 128 | 20 | 75 | 0 | 20 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 90 | 51 | 5 | 124 | 0 | 0 | 0 | 4 | 16 | 36 | 0 | 0 | 36 | 90 | 196 | 17 | 45 | 0 | 0 | 0 |  | 404 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 170 | 0 | 385 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 260 | 12 | 0 | 0 |  | 5988 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 300 | 91 | 0 | 375 | 354 | 0 | 0 | 420 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 20 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 44 | 16 | 18 | 0 | 70 | 0 | 0 | 265 | 165 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 98 | 144 | 95 | 20 | 0 | 30 | 30 | 34 | 30 | 163 | 126 | 34 | 75 | 0 | 119 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 50 | 70 | 119 | 115 | 0 | 0 | 0 | 141 | 35 | 0 | 0 | 0 | 40 | 300 | 71 | 0 | 0 | 0 | 0 |  | 685 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 70 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 162 | 0 | 365 | 70 | 0 | 111 | 0 | 100 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 7888 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 44 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 85 | 100 | 102 | 50 | 16 | 20 | 0 | 100 | 0 | 0 | 0 | 221 | 73 | 60 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 148 | 150 | 95 | 20 | 0 | 30 | 43 | 51 | 44 | 163 | 150 | 36 | 86 | 0 | 130 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 200 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 90 | 0 | 0 |  |  |  | 790 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 70 | 50 | 40 | 100 | 34 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 0 | 115 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 25 | 33 | 52 | 0 | 44 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 85 | 100 | 102 | 50 | 16 | 10 | 0 | 100 | 0 | 0 | 0 | 221 | 73 | 60 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 139 | 160 | 95 | 20 | 1.6 | 30 | 43 | 51 | 44 | 163 | 150 | 36 | 86 | 0 | 130 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 200 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 90 | 50 | 0 |  |  |  | 549 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 65 | 40 | 0 | 27 | 110 | 0 | 0 | 70 | 0 | 0 | 100 | 34 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 225 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 300 | 93 | 0 | 373 | 324 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 12 | 0 | 0 | 25 | 24 | 20 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 6 | 0 | 140 | 0 | 0 | 0 | 183 | 8 | 48 | 26 | 5 | 0 | 21 | 0 | 0 | 0 | 19 | 8 | 20 | 15 | 62 | 167 | 3 | 20 | 1 | 0 | 20 | 5 | 5 | 110 | 126 | 20 | 40 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 90 | 27 | 2 | 120 | 17 | 0 | 0 | 1 | 66 | 30 | 0 | 0 | 0 | 0 | 300 | 30 | 12 | 0 | 0 | 0 | 0 | 496 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 198 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 14 | 0 | 0 | 0
199
| Minimum Generation |  | 5405 | 5:00
| Highest Generation |  | 7888 | 19:30
| Day Peak Generation |  | 5988 | 12:00
| Evening Peak Generation |  | 7888 | 19:30
| HVDC Max Flow |  | 689 | 18:00
| HVDC EvPeak Flow |  | 685 | 19:30
| Load factor L.F |  | 81.53%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5988 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4945 | MW
Evening Peak Generation : |  | 7888 | MW Hour : | 19:30 | Available Max Generation : |  | 13632 | MW
E.P. Demand (at gen end) : |  | 7888 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 7888 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5132 | MW
Total Gen. (MKWH) : |  | 154.3547 | System Load Factor : | 81.53% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -143 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-19
Actual : | 98.96 | Ft.(MSL) , | Rule curve : | 104.3 | Ft.( MSL )
Gas Consumed : | Total = | 845.31 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125952076.22
: |  | Coal : | 55348484.7 | Oil : | 102915350.36 | Total : | 284215911.28
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2986.6048 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1008.6412 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 902.4671 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 815.0142 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 736.7597 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 594.5215 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 341.3961 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 153.3106 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 458.4815 |  |  | 0 | 0%
Total | 0 |  | 7997.1968 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71,100 MW | 11) Fenchugonj CCPP Phase-2
|  |  |  | 3) Ghorasal Unit-1,2,4 | 12) Summit Bibiyana-2
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9)Ashuganj(S)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bibiyana-Kaliakoir 400 kV Ckt-2 was under shut down from 09:46 to 08:54(19-12-2020)
due to D/W at Kaliakoir end.
b) Sikalbaha 230/132 kV T-01 transformer was under shut down from 10:54 to 15:55 for D/W.
c) Ramganj132/33 kV T-1 transformer was under shut down from 10:20 to 17:50 for D/W.
d) Maniknagar 132 KV Reserve Bus was under shut down from 08:24 to 13:07 for A/M.
e) Ashuganj(S) 450 MW GT was synchronized at 10:19.
f) Shahmirpur-Sikalbaha 132 KV Ckt-2 was under shut down from 08:19 to 16:45 for D/W.
g) Baghabari 71 MW GT was synchronized at 11:55.
h) Aminbazar-Kallyanpur 132 KV Ckt-2 was under shut down from 13:01 to 17:09 for A/M.
i) After maintenance Sylhet 225 MW CCPP STG was synchronized at 13:40.
j) Bakulia 132/33 kV T-1 transformer was shut down at 14:26 for A/M.
k) Ghorasal unit-4 GT was synchronized at 16:41.
l) Ghorasal unit-4 ST was synchronized at 16:47.
m) Ghorasal unit-4 was force shut down at 17:48.
n) Ashuganj(S) 450 MW was force shut down at 20:27 due to acceleration monitoring
overheated.
o) Dohazari-Sikalbaha 132 KV Ckt-1 was shut down at 07:41(19-12-2020) for D/W.
p) Shahmirpur-Sikalbaha 132 KV Ckt-2 was shut down at 07:11(19-12-2020) for D/W.
q) Sylhet 33 kV Bus-1 & 2 were shut down at 07:36(19-12-2020) for C/M. |  |  |  |  | About 34 MW power interruption occurred under Sylhet S/S area
from 07:36(19-12-2020) to till.
r) Jhenaidah 132 kV Bus-A & B were shut down at 07:01(19-12-2020) for C/M. |  |  |  |  | About 40 MW power interruption occurred under Jhenaidah S/S
area from 07:36(19-12-2020) to till.
s) Ishwardi-Bheramara 132 kV Ckt-1 & 2 were shut down at 07:06(19-12-2020) for A/M.
t) Bottail-Jhenaidah 132 KV Ckt-1 was shut down at 06:59(19-12-2020) due to Y-phase
lightning arrester blast at Bottail end.
u) Mirpur 132/33 kV T-3 transformer was shut down at 07:52(19-12-2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 103000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7205627
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 1875545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 8738820 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 354 | 7644000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8479250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 85440 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 117528 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 12223 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 286018 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 228024 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 38400 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 688680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 102720 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 308501
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1146480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 542300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 840400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 534436 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 32 | 190080 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 902400 | Low demand
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 6057 | 2109 | 42841872
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 118800
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 300480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 1136727 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 214 | 4738944
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 223696 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 34320 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1150080
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 378816 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 377760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 175680 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25200
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 141 | 1359927 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 711131 | Engine problem
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 40 | 528000 | Low demand
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0
| Chattogram area Total |  |  |  | 2266 | 703 | 11259561
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 2325325 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 165 | 4359000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 1405000 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 455472 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 671040 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1154181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 953622
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 543636 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1157230 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 50 | 984960 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 276084
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 63360 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 98 | 1790400 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 4839000 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 419020
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 360360 | Reserve.
| Cumilla Area Total |  |  |  | 2980 | 911 | 21757690
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3501560 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 406008
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 385920
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 24000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 812400 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 257620
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 376320
| Mymensingh Area Total |  |  |  | 687 | 374 | 5776578
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Gas shortage
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 919440
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3379745
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 126 | 3010000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 34 | 371400 | Line O/L
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 30 | 786960 | Line O/L
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 104528
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 34 | 647040 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1389120 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 119 | 2106660
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 447000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 97488 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 119 | 3740000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 300 | 6617700 | On test
| Sylhet Area Total |  |  |  | 1988 | 1105 | 24334081
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 685 | 10412364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 52800 | Reserve.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8531424 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 6375 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 541920 | Low demand
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1125 | 19544883
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 300672 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 483000 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 291690 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 450 | 9768000 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 613473 | Test run
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 571 | 11456835
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 805000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under maint.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 4131382 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 365 | 8508327 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 445680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 195210
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 62 | 320570 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 524064
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve.
| Rajshahi Area Total |  |  |  | 2183 | 803 | 14930233
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 87 | 2067490
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 100 | 360000 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25444
| Rangpur Area Total |  |  |  | 605 | 187 | 2452934
| Total |  |  |  | 20104 | 7888 | 154354667
| Eastern Grid Total |  |  |  | 13978 | 5202 | 105969782
| Western Grid Total |  |  |  | 6126 | 2686 | 48384885
| National Grid Total |  |  |  | 20104 | 7888 | 154354667
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-18
| (a) ENTIRE EASTERN GRID : |  | 4820 | MW | (b) ENTIRE WESTERN GRID : |  | 2588 | MW
| i) Dhaka area |  | 2351 | MW | i) Khulna area |  | 1010 | MW
| ii) Chittagong area |  | 824 | MW | ii) Rajshahi area |  | 793 | MW
| iii) Comilla area |  | 687 | MW | iii) Barisal area |  | 226 | MW
| iv) Mymensingh area |  | 663 | MW | iv) Rangpur area |  | 559 | MW
| v) Sylhet area |  | 295 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7408 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 80 | 12:00 | Jamalpur | 91 | 18:30 | Benapol | 34 | 18:30
| Munsiganj | 80 | 20:00 | Sherpur | 88 | 18:00 | Jhenida | 98 | 18:30
| Sonargaon | 47 | 2:00 | Srimongal | 23 | 18:00 | Bottail | 80 | 18:30
| Shyampur | 138 | 7:00 | Shahjibazar | 77 | 19:30 | G.K Project | 34 | 18:30
| Bhulta | 138 | 1:00 | Fenchuganj | 24 | 18:00 | Faridpur | 120 | 19:30
| Madanganj | 36 | 18:30 | Kulawara | 28 | 18:00 | Madaripur | 59 | 20:00
| Shitalakhya | 64 | 1:00 | Sylhet | 76 | 18:00 | Sariatpur | 40 | 19:00
| Rahim steel | 0 | 1:00 | Chatak | 19 | 18:00 | Gopalganj | 56 | 18:30
| Matuail | 39 | 1:00 | Sunamganj | 27 | 18:30 | Bagerhat | 74 | 18:30
| Ghorasal | 51 | 18:30 | Biani Bazar | 36 | 19:00 | Mongla | 34 | 1:00
| Narsingdi | 114 | 20:00 | Comilla (S) | 100 | 19:00 | Satkhira | 74 | 18:30
| Haripur (SBU) | 80 | 19:00 | Comilla(N) | 65 | 18:30 | Gallamari | 22 | 13:00
| Ullon | 36 | 13:00 | Chandpur | 63 | 20:00 | Magura | 46 | 18:30
| Hasnabad | 114 | 20:00 | Feni | 67 | 18:00 | Norail | 28 | 18:00
| Magbazar | 51 | 18:00 | Chowmuhani | 112 | 20:00 | Chuadanga | 70 | 18:30
| Maniknagar | 46 | 12:00 | Ashuganj | 36 | 19:30 | Barisal(N) | 28 | 19:00
| Bangabhaban | 9 | 18:30 | Daudkandi | 84 | 18:30 | Barisal (S) | 60 | 17:00
| Narinda | 56 | 13:00 | B.Baria | 90 | 18:00 | Patuakhali | 73 | 19:30
| Dhanmondi | 67 | 18:00 | Ramganj | 62 | 19:30 | Bhandaria | 40 | 19:30
| Lalbag | 50 | 1:00 | Chaddagram | 22 | 19:00 | Borhan Uddin | 26 | 19:00
| Madartek | 43 | 13:00 | PHP | 9 | 11:00 | Ishurdi | 46 | 19:00
| Dhaka University |  |  | Madunaghat | 35 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 5 | 0.375 | Hathazari | 62 | 0.83333 | Natore | 75 | 0.83333
| Fatullah | 23 | 23:00 | Khulshi | 147 | 21:00 | Bogra | 107 | 18:00
| Mirpur | 57 | 17:00 | Halishahar | 87 | 20:00 | Noagaon | 82 | 19:30
| Kalyanpur | 57 | 13:00 | Baraulia | 124 | 2:00 | Rajshahi | 88 | 20:00
| Gulshan | 58 | 13:00 | Sikalbaha | 18 | 18:00 | Rajshahi New | 8 | 20:00
| Uttara | 57 | 13:00 | Dohazari | 54 | 19:30 | C.Nawabganj | 50 | 20:00
| Uttara New | 17 | 18:00 | Cox'sbazar | 70 | 19:30 | Amnura | 30 | 18:30
| Kamrangirchar | 53 | 12:00 | Chandraghona | 20 | 18:00 | Pabna | 70 | 18:30
| Savar | 75 | 18:30 | Kaptai | 3.5 | 18:00 | Shahjadpur | 65 | 18:00
| Bhasantec | 85 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 50 | 18:30
| Agargaon | 40 | 13:00 | Bakulia | 54 | 13:00 | Niyamatpur | 37 | 18:30
| Satmosjid | 57 | 0.54167 | Julda | 19 | 0.041667 | Joypurhat | 40 | 0.77083
| Tongi | 50 | 19:30 | TK chemical | 21 | 20:00 | Sherpur(Bogura) | 41 | 18:30
| Kabirpur | 92 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 30 | 18:00
| Basundhara | 79 | 13:00 | Shahmirpur | 15 | 1:00 | Rangpur | 98 | 18:00
| Manikganj | 40 | 21:00 | Khagrachhari | 18 | 20:00 | Lalmonirhat | 43 | 18:30
| Joydevpur | 58 | 21:00 | Matarbari | 24.5 | 18:00 | Saidpur | 70 | 18:00
| New Tongi | 51 | 12:00 | Baroiar Hat | 34 | 17:00 | Purbasadipur | 85 | 18:30
| Kodda | 126 | 10:00 | Rangamati | 8 | 12:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 60 | 18:.30 | Abul Khair 230 | 133 | 7:00 | Palashbari | 85 | 18:30
| Rajendrapur | 56 | 20:00 | BSRM | 107 | 4:00 | Barapukuria | 36 | 19:30
| Valuka | 66 | 18:30 | GPH Ispat | 80 | 23:00 | Panchagar | 42 | 18:30
| Tangail | 125 | 19:00 | Goalpara | 14 | 19:30 | Joldhaka | 26 | 9:00
| Mymensing | 148 | 18:30 | Central s/s | 66 | 18:30 | Kurigram | 42 | 18:30
| Kishorganj | 78 | 19:30 | Noapara | 43 | 19:00
| Netrokona | 84 | 18:00 | Jessore | 73 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 17:00 | 406 | 10:00 | Kaliakoir | 387 | 0.70833 | 376 | 0.45833
| Bheramara | 407 | 24:00 | 396 | 18:00 | Bhulta | 387 | 0.70833 | 375 | 0.083333
| Ashuganj(N) | 388 | 21:00 | 378 | 10:00 | Gopalganj | 420 | 0.70833 | 403 | 0.83333
| Payra | 420 | 17:00 | 410 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Comilla (N) | 238 | 18:30 | 232 | 10:00
| Ishurdi | 240 | 6:00 | 230 | 18:00 | Hathazari | 226 | 18:00 | 212 | 16:00
| Ashuganj | 240 | 17:00 | 234 | 9:00 | Megnaghat | 232 | 21:00 | 230 | 9:00
| Serajganj | 234 | 17:00 | 228 | 8:00 | Fenchuganj | 247 | 19:00 | 240 | 9:00
| Baghabari | 243 | 5:00 | 237 | 18:00 | Siddhirganj | 233 | 17:00 | 228 | 11:00
| Barapukuria | 232 | 3:00 | 223 | 18:00 | Maniknagar | 232 | 17:00 | 227 | 10:00
| Bogra | 234 | 5:00 | 224 | 18:00 | Agargaon | 231 | 17:00 | 224 | 11:00
| Rajshahi | 231 | 17:00 | 221 | 18:00 | Barisal | 249 | 17:00 | 240 | 18:00
| Khulna South | 236 | 17:00 | 220 | 8:00 | AKSML | 228 | 17:00 | 206 | 10:00
| Rampura | 231 | 4:00 | 229 | 11:00 | BSRM | 229 | 17:00 | 214 | 10:00
| Haripur | 230 | 21:00 | 227 | 11:00 | Bibiyana | 246 | 17:00 | 239 | 2:00
| Hasnabad | 232 | 20:00 | 228 | 9:00 | Bhulta | 234 | 19:00 | 229 | 17:00
| Shyampur | 230 | 17:00 | 220 | 10:00 | Ashuganj (S) | 237 | 17:00 | 231 | 2:00
| Aminbazar | 231 | 21:00 | 227 | 9:00 | Kaliakoir | 230 | 18:30 | 223 | 10:00
| Tongi | 228 | 19:30 | 223 | 7:00 | GPH | 225 | 18:30 | 205 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 17:00 | 136 | 2:00 | Madanhat | 136 | 0.70833 | 127 | 0.45833
| Munsiganj | 141 | 18:30 | 135 | 4:00 | Hathazari | 136 | 0.8125 | 128 | 0.125
| Sonargaon | 136 | 7:00 | 135 | 1:00 | Khulshi | 134 | 0.77083 | 124 | 0.20833
| Shyampur | 134 | 18:00 | 131 | 10:00 | Halishahar | 135 | 0.83333 | 125 | 0.16667
| Bhulta | 133 | 14:00 | 130 | 11:00 | Baraulia | 135 | 0.75 | 126 | 0.41667
| Madanganj | 136 | 17:00 | 133 | 1:00 | Sikalbaha | 135 | 0.77083 | 126 | 0.625
| Shitalakhya | 140 | 16:00 | 136 | 2:00 | Dohazari | 133 | 0.8125 | 124 | 0.41667
| Rahim steal | 139 | 19:00 | 136 | 10:00 | Cox'sbazar | 124 | 0.70833 | 117 | 0.083333
| Matuail | 140 | 17:00 | 136 | 2:00 | Chandraghona | 136 | 0.875 | 126 | 0.125
| Ghorasal | 140 | 17:00 | 136 | 1:00 | Kaptai | 135 | 0.75 | 130 | 0.41667
| Narsinghdi | 139 | 17:00 | 136 | 9:00 | A. Khaer Stl. | 134 | 0.77083 | 126 | 0.625
| Haripur (SBU) | 139 | 18:30 | 137 | 2:00 | Bakulia | 133 | 0.77083 | 124 | 0.41667
| Ullon | 133 | 3:00 | 130 | 9:00 | Julda | 136 | 0.54167 | 126 | 0.41667
| Hasnabad | 138 | 3:00 | 135 | 12:00 | TK Chemical | 135 | 0.83333 | 127 | 0.45833
| Magbazar | 134 | 6:00 | 130 | 10:00 | Modern Steel | 135 | 0.77083 | 126 | 0.41667
| Maniknagar | 138 | 3:00 | 136 | 10:00 | Shahmirpur | 134 | 0.77083 | 125 | 0.083333
| Bangabhaban | 138 | 3:00 | 136 | 10:00 | Khagrachhari | 134 | 0.83333 | 126 | 0.41667
| Narinda | 138 | 3:00 | 136 | 10:00 | Matarbari | 133 | 0.77083 | 123 | 0.083333
| Dhanmondi | 133 | 3:00 | 130 | 9:00 | Baroiar Hat | 136 | 0.70833 | 126 | 0.41667
| Lalbag | 140 | 23:00 | 124 | 10:00 | Rangamati | 135 | 21:00 | 125 | 10:00
| Madartek | 133 | 6:00 | 129 | 11:00 | Goalpara S/S | 140 | 17:00 | 129 | 18:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 17:00 | 129 | 0.75
| Aftabnagar | 133 | 6:00 | 130 | 11:00 | Noapara | 138 | 17:00 | 125 | 0.75
| Fatuiiah | 136 | 17:00 | 132 | 3:00 | Jessore | 136 | 17:00 | 122 | 0.75
| Mirpur | 130 | 21:00 | 125 | 11:00 | Benapol | 135 | 0.16667 | 123 | 0.75
| Kalyanpur | 131 | 19:30 | 126 | 10:00 | Jhenida | 135 | 4:00 | 119 | 0.75
| Gulshan | 132 | 17:00 | 129 | 11:00 | Bottail | 138 | 0.29167 | 128 | 0.75
| Uttara | 136 | 18:00 | 132 | 10:00 | G.K Project | 141 | 0.20833 | 139 | 0.75
| Uttara New | 130 | 19:30 | 124 | 11:00 | Faridpur | 139 | 0.70833 | 114 | 0.75
| Kamrangirchar | 139 | 17:00 | 135 | 10:00 | Madaripur | 141 | 0.33333 | 134 | 0.83333
| Savar | 130 | 19:30 | 124 | 11:00 | Shariyatpur S/S | 142 | 17:00 | 134 | 0.875
| Bhasantec | 134 | 4:00 | 131 | 10:00 | Gopalganj | 143 | 0.70833 | 136 | 0.79167
| Agargaon | 136 | 17:00 | 132 | 9:00 | Bagerhat | 140 | 16:00 | 126 | 0.75
| Satmosjid | 135 | 17:00 | 131 | 10:00 | Mongla | 138 | 17:00 | 125 | 0.33333
| Tongi | 138 | 21:00 | 134 | 11:00 | Satkhira | 139 | 17:00 | 127 | 8:00
| Kabirpur | 133 | 21:00 | 130 | 16:00 | Gallamari | 141 | 0.70833 | 130 | 0.33333
| Basundhara | 136 | 18:30 | 130 | 21:00 | Magura | 135 | 2:00 | 117 | 0.75
| Manikganj | 140 | 21:00 | 135 | 13:00 | Norail | 135 | 0.70833 | 116 | 0.75
| Joydevpur | 142 | 21:00 | 138 | 13:00 | Chuadanga | 133 | 5:00 | 113 | 0.75
| New Tongi | 138 | 18:30 | 132 | 12:00 | Barisal(N) | 142 | 17:00 | 136 | 18:00
| Kodda | 134 | 18:00 | 128 | 10:00 | Barisal (S) | 140 | 0.70833 | 135 | 0.5
| Dhamrai | 132 | 22:00 | 128 | 10:00 | Patuakhali(S) | 136 | 0.25 | 131 | 0.54167
| Rajendrapur | 140 | 18:00 | 135 | 13:00 | Bhandaria | 139 | 0.25 | 132 | 0.75
| Valuka | 131 | 20:00 | 124 | 8:00 | Ishurdi | 140 | 17:00 | 134 | 18:00
| Tangail | 133 | 19:30 | 129 | 16:00 | Ruppur Paromanobik | 140 | 13:00 | 135 | 18:00
| Mymensing | 133 | 20:00 | 125 | 8:00 | Natore | 139 | 17:00 | 132 | 18:00
| Kishorganj | 132 | 5:00 | 129 | 13:00 | Bogra | 137 | 3:00 | 131 | 18:00
| Netrokona | 132 | 22:00 | 122 | 13:00 | Noagaon | 134 | 5:00 | 126 | 18:00
| Jamalpur | 140 | 22:00 | 123 | 8:00 | Rajshahi | 141 | 17:00 | 134 | 18:00
| Sherpur | 140 | 22:00 | 120 | 8:00 | Rajshahi New | 142 | 17:00 | 135 | 18:00
| Srimongal | 139 | 10:00 | 136 | 13:00 | C.Nawabganj | 141 | 17:00 | 134 | 18:00
| Shahjibazar | 137 | 12:00 | 134 | 3:00 | Amnura | 141 | 17:00 | 134 | 8:00
| Fenchuganj | 138 | 1:00 | 136 | 5:00 | Pabna | 139 | 6:00 | 133 | 18:00
| Khulawara | 138 | 22:00 | 136 | 1:00 | Shahjadpur | 140 | 1:00 | 136 | 18:30
| Sylhet | 136 | 21:00 | 134 | 2:00 | Serajganj | 136 | 17:00 | 132 | 18:00
| Chatak | 136 | 23:00 | 133 | 18:00 | Niyamatpur | 134 | 17:00 | 124 | 8:00
| Sunamganj | 135 | 4:00 | 133 | 18:30 | Joypurhat | 136 | 17:00 | 126 | 18:00
| Biani Bazar | 136 | 5:00 | 134 | 18:00 | Sherpur(Bogura) | 137 | 17:00 | 132 | 18:00
| Comilla(s) | 130 | 2:00 | 128 | 12:00 | Mohastangor | 137 | 17:00 | 127 | 18:00
| Comilla(n) | 142 | 18:30 | 139 | 10:00 | Rangpur | 130 | 17:00 | 117 | 18:00
| Chandpur | 144 | 9:00 | 141 | 15:00 | Lalmonirhat | 132 | 17:00 | 120 | 18:00
| Feni | 138 | 17:00 | 133 | 16:00 | Saidpur | 132 | 5:00 | 115 | 18:00
| Chowmuhani | 136 | 15:00 | 133 | 19:00 | Purbasadipur | 130 | 17:00 | 117 | 18:00
| Ashuganj | 138 | 17:00 | 136 | 10:00 | Thakurgaon | 130 | 20:00 | 114 | 18:00
| Daudkandi | 140 | 17:00 | 137 | 10:00 | Palashbari | 132 | 19:00 | 125 | 8:00
| B.Baria | 134 | 11:00 | 131 | 19:00 | Barapukuria | 132 | 17:00 | 123 | 18:00
| Ramganj | 134 | 15:00 | 131 | 18:00 | Panchagar | 130 | 4:00 | 119 | 11:00
| Chaddagram | 140 | 10:00 | 134 | 2:00 | Joldhaka | 130 | 4:00 | 117 | 18:00
| PHP | 136 | 17:00 | 125 | 11:00 | Kurigram | 129 | 0.25 | 116 | 0.75

## L-Curve
Date | 2020-12-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 64 | 4195 | 1920 | 6115 |  |  |  | QF-LDC-11
0:30 | 53 | 4257.5 | 1913 | 6170.5 | Date: | 2020-12-18
1:00 | 42 | 4320 | 1906 | 6226
1:30 | 110 | 4085.5 | 1927.5 | 6013
2:00 | 178 | 3851 | 1949 | 5800
2:30 | 202.5 | 3789 | 1930.5 | 5719.5 | [5 empty] | Gen. at Eve. Peak | 7888 | 7888 MW (19:30 )
3:00 | 227 | 3727 | 1912 | 5639 | [6 empty] | 19:30
3:30 | 208 | 3723.5 | 1836 | 5559.5 | [5 empty] | Gen. at Day Peak | 5988 | 5988 MW (12:00 )
4:00 | 189 | 3720 | 1760 | 5480 | [6 empty] | 12:00
4:30 | 181.5 | 3674.5 | 1768 | 5442.5 | [5 empty] | Highest Generation | 7888
5:00 | 174 | 3629 | 1776 | 5405 | [6 empty] | 19:30
5:30 | 133 | 3710 | 1755.5 | 5465.5
6:00 | 92 | 3791 | 1735 | 5526
6:30 | 104.5 | 3876.5 | 1643.5 | 5520
7:00 | 117 | 3962 | 1552 | 5514
7:30 | 113.5 | 4047.5 | 1611 | 5658.5
8:00 | 110 | 4133 | 1670 | 5803
8:30 | 85 | 4111.5 | 1661.5 | 5773
9:00 | 60 | 4090 | 1653 | 5743
9:30 | 105 | 4013 | 1681.5 | 5694.5
10:00 | 150 | 3936 | 1710 | 5646
10:30 | 170 | 3944 | 1734.5 | 5678.5
11:00 | 190 | 3952 | 1759 | 5711
11:30 | 190 | 4060 | 1789.5 | 5849.5
12:00 | 190 | 4168 | 1820 | 5988
12:30 | 155 | 4269 | 1865.5 | 6134.5
13:00 | 120 | 4370 | 1911 | 6281
13:30 | 160 | 4102 | 1819 | 5921
14:00 | 200 | 3834 | 1727 | 5561
14:30 | 235 | 3768 | 1706 | 5474
15:00 | 270 | 3702 | 1685 | 5387
15:30 | 290 | 3616.5 | 1711 | 5327.5
16:00 | 310 | 3531 | 1737 | 5268
16:30 | 257 | 3728.5 | 1765 | 5493.5
17:00 | 204 | 3926 | 1793 | 5719
17:30 | 173.5 | 4438 | 2091.5 | 6529.5
18:00 | 143 | 4950 | 2390 | 7340
18:30 | 108 | 5079.5 | 2513 | 7592.5
19:00 | 73 | 5209 | 2636 | 7845
19:30 | 47 | 5202 | 2686 | 7888
20:00 | 47 | 5177 | 2621 | 7798 |  |  |  | Executive Engineer
20:30 | 57 | 5110 | 2631.5 | 7741.5 |  |  |  | Network Operation Division
21:00 | 67 | 5043 | 2642 | 7685
21:30 | 74 | 4970 | 2418.5 | 7388.5
22:00 | 81 | 4897 | 2195 | 7092 |  |  |  |  | Page 6 of 7
22:30 | 45.5 | 4700.5 | 2132 | 6832.5
23:00 | 10 | 4504 | 2069 | 6573
23:30 | 37 | 4349.5 | 1994.5 | 6344
24:00 | 64 | 4195 | 1920 | 6115
7888 MW (19:30 )
5988 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-18 |  | Energy | 154354667
[11 empty] | 2020-12-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3101 | 401 | 1611 | 710 | 517 | 47 | 0 | 0 | 72 | 0
0:30 | 3130 | 407.5 | 1647.5 | 502 | 535.5 | 47 | 0 | 0 | 73 | 0 | Date: | 2020-12-18
1:00 | 3159 | 414 | 1684 | 294 | 554 | 47 | 0 | 0 | 74 | 0
1:30 | 3126 | 414 | 1616.5 | 181 | 555.5 | 47 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 154.3547 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3093 | 414 | 1549 | 68 | 557 | 47 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3081.5 | 414 | 1512 | 47 | 548 | 47 | 0 | 0 | 70 | 0 | [7 empty] | Energy Requirement | 154.3547
3:00 | 3070 | 414 | 1475 | 26 | 539 | 47 | 0 | 0 | 68 | 0
3:30 | 3066.5 | 361 | 1453.5 | 26 | 540.5 | 46 | 0 | 0 | 66 | 0 | [6 empty] | Shortage
4:00 | 3063 | 308 | 1432 | 26 | 542 | 45 | 0 | 0 | 64 | 0
4:30 | 3059.5 | 308 | 1424.5 | 26 | 515.5 | 45 | 0 | 0 | 64 | 0
5:00 | 3056 | 308 | 1417 | 26 | 489 | 45 | 0 | 0 | 64 | 0
5:30 | 3047.5 | 308 | 1464.5 | 47 | 487.5 | 45 | 0 | 0 | 66 | 0
6:00 | 3039 | 308 | 1512 | 68 | 486 | 45 | 0 | 0 | 68 | 0
6:30 | 3018.5 | 308 | 1506 | 141 | 436.5 | 45 | 0 | 0 | 64 | 1 |  |  |  |  | Coal
7:00 | 2998 | 308 | 1500 | 214 | 387 | 45 | 0 | 0 | 60 | 2
7:30 | 3050.5 | 308 | 1542 | 249.5 | 387 | 45 | 0 | 0 | 66 | 10.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3103 | 308 | 1584 | 285 | 387 | 45 | 0 | 0 | 72 | 19
8:30 | 3058 | 355.5 | 1555.5 | 297.5 | 362 | 45 | 4 | 0 | 67 | 28.5
9:00 | 3013 | 403 | 1527 | 310 | 337 | 45 | 8 | 0 | 62 | 38
9:30 | 2939.5 | 403 | 1543.5 | 309 | 336.5 | 45 | 8 | 0 | 62 | 48
10:00 | 2866 | 403 | 1560 | 308 | 336 | 45 | 8 | 0 | 62 | 58
10:30 | 2848 | 403 | 1592 | 320.5 | 336.5 | 45 | 8 | 0 | 64 | 61.5
11:00 | 2830 | 403 | 1624 | 333 | 337 | 45 | 8 | 0 | 66 | 65
11:30 | 2829 | 403.5 | 1666.5 | 420 | 342.5 | 45.5 | 8 | 0 | 66 | 68.5
12:00 | 2828 | 404 | 1709 | 507 | 348 | 46 | 8 | 0 | 66 | 72
12:30 | 2855.5 | 404 | 1738.5 | 564.5 | 378 | 46.5 | 8 | 0 | 70 | 69.5
13:00 | 2883 | 404 | 1768 | 622 | 408 | 47 | 8 | 0 | 74 | 67
13:30 | 2883 | 404 | 1768 | 622 | 408 | 47 | 8 | 0 | 74 | 67
14:00 | 2883 | 404 | 1768 | 622 | 408 | 47 | 8 | 0 | 74 | 67
14:30 | 2830 | 404 | 1604 | 424.5 | 397 | 48 | 4 | 0 | 69 | 53.5
15:00 | 2777 | 404 | 1440 | 227 | 386 | 49 | 0 | 0 | 64 | 40
15:30 | 2934 | 404 | 1322.5 | 165 | 361 | 48.5 | 0 | 0 | 64 | 28.5
16:00 | 3091 | 404 | 1205 | 103 | 336 | 48 | 0 | 0 | 64 | 17
16:30 | 3151 | 404 | 1134 | 281.5 | 336.5 | 47.5 | 58 | 0 | 72 | 9
17:00 | 3211 | 404 | 1063 | 460 | 337 | 47 | 116 | 0 | 80 | 1
17:30 | 3270.5 | 546.5 | 1331 | 767.5 | 351.5 | 45.5 | 129.5 | 0 | 87 | 0.5
18:00 | 3330 | 689 | 1599 | 1075 | 366 | 44 | 143 | 0 | 94 | 0
18:30 | 3314.5 | 687 | 1624 | 1252.5 | 436 | 43.5 | 138 | 0 | 97 | 0
19:00 | 3299 | 685 | 1649 | 1430 | 506 | 43 | 133 | 0 | 100 | 0
19:30 | 3345 | 685 | 1709 | 1341 | 537 | 44 | 129 | 0 | 98 | 0
20:00 | 3272 | 686 | 1673 | 1357 | 537 | 46 | 129 | 0 | 98 | 0
20:30 | 3188 | 685.5 | 1689.5 | 1352.5 | 562 | 46 | 121 | 0 | 97 | 0
21:00 | 3104 | 685 | 1706 | 1348 | 587 | 46 | 113 | 0 | 96 | 0
21:30 | 3097.5 | 543 | 1698.5 | 1267 | 588 | 46 | 56.5 | 0 | 92 | 0
22:00 | 3091 | 401 | 1691 | 1186 | 589 | 46 | 0 | 0 | 88 | 0
22:30 | 3092.5 | 401 | 1672 | 948 | 588.5 | 46.5 | 0 | 0 | 84 | 0
23:00 | 3094 | 401 | 1653 | 710 | 588 | 47 | 0 | 0 | 80 | 0
23:30 | 3097.5 | 401 | 1632 | 710 | 552.5 | 47 | 0 | 0 | 76 | 0 | Max Temp. in Dhaka |  | 24.2° C
24:00 | 3101 | 401 | 1611 | 710 | 517 | 47 | 0 | 0 | 72 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 47 | 47 | 47 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 47 | 48 | 49 | 48 | 47 | 44 |  | 43 | 44 | 46 | 46 | 46 | 47 | 47 | 1136727
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 15 | 17 | 18 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 118800
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 203 | 203 | 203 | 215 | 202 | 203 | 203 | 209 | 217 | 203 | 179 | 178 | 178 | 178 | 188 | 203 | 216 |  | 202 | 214 | 203 | 204 | 200 | 202 | 202 | 4738944
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 44 | 51 |  | 51 | 51 | 51 | 51 |  |  | 0 | 223696
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 21 | 75 |  | 95 | 95 | 95 | 95 | 45 | 15 | 0 | 534436
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 36 | 36 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1154181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [16 empty] | 67 | [8 empty] | 0 | 103000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7205627
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 70 | 70 | 70 |  | 70 | 70 | 85 | 100 | 100 | 100 | 100 | 2325325
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 26 | 26 | 26 | 26 | 5 | 5 | 5 |  | 5 | 5 | 5 | 26 | 26 | 26 | 26 | 455472
33 | Ashuganj 225 MW CCPP | 183 | 185 | 183 | 183 | 193 | 183 | 186 | 187 | 194 | 208 | 200 | 193 | 155 | 170 | 173 | 133 | 136 | 161 |  | 160 | 165 | 173 | 183 | 183 | 183 | 182 | 4359000
34 | Ashuganj 450 MW CCPP(South) | [10 empty] | 10 | 15 | 70 | 45 | 40 | 240 | 250 | 260 |  | 270 | 265 | 215 | 0 |  |  | 0 | 1405000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 20 | 20 | 5 | 5 | 55 | 56 | 56 | 56 | 56 | 56 | 20 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 671040
36 | Chandpur 150 MW CCPP | 49 | 51 | 51 | 51 | 51 | 51 | 50 | 52 | 52 | 51 | 50 | 51 | 45 | 47 | 46 | 52 | 46 | 51 |  | 50 | 51 | 46 | 52 | 51 | 45 | 51 | 1157230
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 349 | 360 | 352 | 351 | 357 | 363 | 353 | 363 | 352 | 364 | 374 | 377 | 380 | 354 | 352 | 358 | 361 | 361 |  | 362 | 375 | 366 | 354 | 349 | 349 | 349 | 8738820
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 350 | 320 | 340 | 300 | 300 | 330 | 360 | 400 | 330 | 330 | 330 | 300 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 8479250
41 | Haripur 360MW CCPP(HPL) | 359 | 359 | 359 | 359 | 308 | 308 | 267 | 267 | 270 | 274 | 309 | 306 | 353 | 286 | 285 | 287 | 248 | 353 |  | 360 | 354 | 353 | 358 | 359 | 359 | 359 | 7644000
42 | RPCL 210MW CCPP | 164 | 163 | 163 | 166 | 163 | 164 | 165 | 164 | 163 | 162 | 160 | 142 | 121 | 120 | 121 | 121 | 140 | 143 |  | 144 | 144 | 144 | 145 | 145 | 148 | 165 | 3501560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 10 | 23 | 35 | 39 | 45 | 40 | 32 | 24 | 10 | 1 | [9 empty] | 257620
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 919440
46 | Shajibazar 330 MW CCPP | 157 | 156 | 158 | 156 | 126 | 127 | 127 | 127 | 128 | 129 | 126 | 128 | 126 | 126 | 127 | 127 | 127 | 126 |  | 127 | 126 | 127 | 128 | 129 | 126 | 126 | 3010000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 20 | 20 | 20 | 20 | 35 | 34 | 34 | 20 | 20 | 20 | 20 | 33 | 20 | 20 | 20 | 20 | 33 |  | 34 | 34 | 34 | 34 | 34 | 35 | 34 | 647040
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 10 | 10 | 10 | 10 | 70 | 74 | 77 | 77 | 77 | 76 | 75 | 75 | 76 | 76 | 10 | 10 | 75 |  | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 1389120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 101 | 95 | 95 | 95 | 95 | 95 | 98 | 127 | 96 | 21 | 21 | 20 | 20 | 77 | 77 | 77 | 102 | 118 |  | 119 | 119 | 120 | 119 | 120 | 120 | 118 | 2106660
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 447000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | [5 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 104528
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 28 | 31 | 31 | 14 | 14 | 31 |  | 34 | 34 | 34 | 34 | 34 | 34 | 5 | 371400
56 | Shahjahanulla 25 MW PP | 8 | [16 empty] | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 97488
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 300 | 300 | 301 | 300 | 300 | 300 | 300 | 300 | 300 | 200 | 196 | 196 | 196 | 197 | 200 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6617700
58 | Nababganj 55 MW PP (Southern power )
59 | Tangail Palli Power Gen 22 MW | 26 | 26 | 26 | 26 | 26 | 25 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 17 | [10 empty] | 0 | 376320
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 378816
61 | Narshingdi 22 MW PP (Doreen) | 16 | [5 empty] | 16 | 16 |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 11 | 11 | 228024
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 406008
63 | Impoprt (Tripura) | 74 | 72 | 68 | 64 | 64 | 68 | 60 | 72 | 62 | 62 | 66 | 66 | 74 | 66 | 64 | 64 | 80 | 94 |  | 100 | 98 | 98 | 96 | 88 | 80 | 72 | 1790400
64 | Malancha, Ctg. EPZ (United) | 19 | 4 | 3 | 3 | 3 | 3 | 4 | 6 | 18 | 4 | 18 | 20 | 20 | 20 | 7 | 9 | 12 | 12 |  | 18 | 18 | 18 | 20 | 20 | 20 | 29 | 377760
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | [10 empty] | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 276084
66 | Feni 11 MW PP (Doreen) | 11 | [15 empty] | 2 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 63360
67 | Jangalia 33MW PP (Summit) | 25 | 8 | 8 | 8 | 8 | 25 | 25 | 21 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 20 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 4839000
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 15 | 15 | 15 | 18 | 18 | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 419020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 25 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 22 |  | 22 | 22 | 22 | 32 | 32 | 32 | 33 | 546480
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 542300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 840400
73 | Ghorashal 108MW PP (Regent) | 101 | 56 | 27 | 27 | 27 | 95 | 99 | 99 | 99 | 101 | 98 | 101 | 102 | 104 | 97 | 25 | 13 | 13 |  | 82 | 91 | 101 | 103 | 101 | 100 | 100 | 1875545
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [9 empty] | 26 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  |  | 0 |  |  |  |  | 0 | 360360
Manikgonj 162MW PP(MPGL)
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 16 |  | 15 | [5 empty] | 0 | 38400
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 32 | 32 |  | 20 | 16 | 16 |  |  |  | 0 | 102720
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 5 | 38 |  | 92 | 95 | 95 | 64 | 48 |  | 0 | 385920
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25200
| Jodiac Power | 54 | 17 |  |  |  | 7 | 27 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 |  | 22 | 35 |  | 35 | 35 | 35 | 35 | 46 | 54 | 54 | 711131
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 7 | 24 |  | 30 | 15 | 15 | 15 |  |  |  | 117528
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 86 |  |  |  |  | 6 | 10 | [14 empty] | 6 | 40 | 40 | 40 | 40 | 286018
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 1 | 7 | 7 | 7 | 7 |  | 4 | 7 | [7 empty] | 0 | 85440
| Meghnaghat 104 MW PP (OPCL) | 35 |  |  |  |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 35 | 17 |  | 30 | 53 |  | 71 | 71 | 71 | 87 | 87 | 86 | 85 | 902400
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 3 | 10 | 30 | [12 empty] | 0 | 34320
92 | Fenchuganj 44MW (Energyprima) | 30 | 5 | 5 | 5 | 5 | 18 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 22 |  | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 786960
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 11 | 47 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 5 | 5 | 35 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 953622
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | 18 | [5 empty] | 1 | 20 | [9 empty] | 20 |  | 36 | 44 | 45 | 46 | 50 | 12 | 12 | 300480
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 53 | 60 | 25 | 14 | [10 empty] | 0 | 175680
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 12223
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 17 |  | 308501
101 | Kushiara 163 MW CCPP (KP) | 110 | 140 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 110 | 110 | 110 | 110 | 163 |  | 130 | 163 | 163 | 163 | 163 | 130 | 130 | 3379745
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12750
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 17 | 17 | 17 | 30 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 688680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 5 | [7 empty] | 0 | 24000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [16 empty] | 6 | 39 |  | 50 | 32 | 32 | 32 | 22 |  | 0 | 190080
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 10 | 30 | 40 | 10 | 70 | 90 | 100 | 70 | 50 | 50 | 50 | 90 |  | 100 | 100 | 100 | 100 | 100 | 60 | 20 | 1150080
116 | Chandpur 200MW (Desh energy) | 34 |  |  |  |  | 7 | 34 | 37 | 51 | 51 | 51 | 51 | 51 | 17 | 17 |  | 15 | 36 |  | 50 | 50 | 52 | 68 | 68 | 68 | 34 | 984960
117 | Ashuganj 150MW PP (Midland) | [11 empty] | 5 | 30 | 10 |  |  | 15 | 58 |  | 100 | 70 | 70 | 70 | 70 | 40 | 0 | 543636
118 | Bibiyana-III 400 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 130 | 124 | 130 | 120 | 120 | 120 | 120 | 120 |  | 122 | 119 | 122 | 123 | 122 | 133 | 120 | 3740000
| Jamalpur 115 MW PP (United) | 24 | 8 | [14 empty] | 35 | 115 |  | 115 | 115 | 115 | 115 | 115 | 75 | 16 | 812400
| Anwara 300 MW PP (United) | [6 empty] | 66 | 102 | 123 | 125 | 16 | 16 | 16 | 16 | 5 |  | 31 | 101 |  | 135 | 141 | 142 | 143 | 142 | 106 | 70 | 1359927
| Juldah unit-2 (Acorn) | [10 empty] | 60 | 90 | 90 | 50 | 30 |  | 30 | 40 |  | 40 | 40 | 40 | 40 | 40 |  | 0 | 528000
| Anlima Energy Ltd. | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4320 | 3851 | 3727 | 3720 | 3629 | 3791 | 3962 | 4133 | 4090 | 3936 | 3952 | 4168 | 4370 | 3834 | 3702 | 3531 | 3926 | 4950 |  | 5209 | 5202 | 5177 | 5043 | 4897 | 4504 | 4195 | 105969782
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 3 | 16 |  | 32 | [5 empty] | 0 | 52800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 35 | 35 | 17 |  |  | 35 | 70 |  | 70 | 70 | 70 | 70 | 70 | 35 | 0 | 541920
130
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 38 | 36 | 36 | 36 | 36 | 36 | 13 | 16 | 11 | 12 | 12 | 12 | 10 | 11 | 35 | 11 | 15 | 35 |  | 36 | 36 | 35 | 17 | 17 | 37 | 36 | 613473
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 12 | 19 |  | 48 | 48 | 48 | 48 | 64 | 48 | 0 | 300672
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 11 | 12 | 12 | 12 | 12 | 12 | 13 | 291690
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 21 | 21 | 20 | 19 | 21 | 17 | 18 | 18 | 16 | 16 | 20 | 19 | 18 | 15 | 15 | 16 | 24 |  | 24 | 25 | 25 | 27 | 26 | 26 | 25 | 483000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [6 empty] | 8 | [19 empty] | 6375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 414 | 414 | 414 | 308 | 308 | 308 | 308 | 308 | 403 | 403 | 403 | 404 | 404 | 403 | 404 | 404 | 404 | 689 |  | 685 | 685 | 686 | 685 | 401 | 401 | 401 | 10412364
147 | Bheramara 410 MW CCPP | 345 | 350 | 345 | 340 | 365 | 350 | 300 | 355 | 320 | 320 | 375 | 365 | 350 | 290 | 295 | 365 | 340 | 390 |  | 345 | 370 | 340 | 340 | 340 | 340 | 345 | 8531424
148 | Payra 1320 MW | 470 | 470 | 450 | 450 | 400 | 400 | 300 | 300 | 250 | 250 | 250 | 260 | 320 | 320 | 300 | 250 | 250 | 280 |  | 420 | 450 | 450 | 500 | 500 | 500 | 430 | 9768000
149
150 | Barapukuria TPP Unit-1 | 84 | 87 | 89 | 92 | 89 | 86 | 87 | 87 | 87 | 86 | 87 | 88 | 88 | 87 | 86 | 86 | 87 | 86 |  | 86 | 87 | 87 | 87 | 89 | 88 | 87 | 2067490
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP | [11 empty] | 30 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 805000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 164 | 161 | 160 | 153 | 152 | 147 | 163 | 157 | 164 | 168 | 170 | 191 | 166 | 157 | 161 | 162 | 167 |  | 164 | 162 | 166 | 160 | 156 | 156 | 156 | 4131382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 383 | 375 | 333 | 385 | 342 | 332 | 383 | 358 | 408 | 397 | 385 | 373 | 295 | 281 | 334 | 265 | 371 |  | 343 | 365 | 320 | 360 | 347 | 323 | 327 | 8508327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 445680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 195210
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 |  |  |  |  | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 40 | 60 |  | 62 | 62 | 62 | 62 |  |  |  | 320570
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 17 | 36 |  | 99 | 111 | 111 | 111 | 70 |  | 0 | 524064
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 37 | 37 |  | 108 | 100 | 106 | 60 |  |  | 0 | 360000
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 3 | 3 | 3 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 25444
178
178