## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:November 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | November 2020 |  | October 2020 |  | November 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11572 | 02-11-2020 | 12759 | 11/10/20 | 10255 | 03/11/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 5330 | 28/11/20 | 6045 | 23/10/20 | 4949 | 11/11/19 | - | -
|  |  | 5:00 |  | 9:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11572 | 02-11-2020 | 12759 | 11-10-2020 | 10255 | 03/11/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9280 | 02-11-2020 | 10723 | 13-10-2020 | 8544.3 | 05/11/19 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11572 | 02/11/20 | 12759 | 11/10/20 | 10255 | 03/11/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9501.5333 |  | 11755.2903 |  | 9029.8667 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 7762.9 |  | 9551.7742 |  | 7277.1833 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 915 | 01/11/2020 | 933 | 28/10/2020 | 935 | 02/11/19 | 956 | 27/3/2019
|  |  | 19:00 |  | 15:00 |  | 19:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 152 | 03/11/2020 | 178 | 14/10/2020 | 160 | 05/11/19 | 194 | 12/06/19
|  |  | 18:00 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3010.001 |  | 3604.3882 |  | 3246.9588 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 92.709 |  | 123.1302 |  | 112.6542
22 | Net Generation of BPDB (MKWH) | 2917.292 |  | 3481.2581 |  | 3134.3046
23 | Net Generation of IPP & RPCL (MKWH) | 1607.0453 |  | 2428.8487 |  | 1256.2848
24 | Net Generation of REB (MKWH) | 122.2164 |  | 145.8563 |  | 113.3873
24 | Net Generation of Rental Power Plant (MKWH) | 280.216 |  | 540.7093 |  | 179.5401
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4926.7697 |  | 6596.6723 |  | 4683.5168 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 3705.2202 |  | 4215.0603 |  | 4207.0156 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 139.7118 |  | 467.3091 |  | 48.4064 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 634.4156 |  | 1436.1631 |  | 303.8485 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 103.6451 |  | 85.0566 |  | 56.3246 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.6869 |  | 6.3227 |  | 7.3823 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 431.7992 |  | 509.8908 |  | 173.1936 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & Tripura) (MKWH) | 536.2305 |  | 765.2903 |  | 471.4251 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 66.6805 |  | 78.8511 |  | 71.3418 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11572 | 02-11-2020 | 19:00
Generation Period
| Dhaka | MW | 4000
| Chattogram | MW | 1093
| Cumilla | MW | 1021
| Mymensingh | MW | 877
| Sylhet | MW | 465
a) | Total supply in East zone | MW | 7456
| Khulna | MW | 1360
| Barisal | MW | 299
| Rajshahi | MW | 1139
| Rangpur | MW | 676
b) | Total supply in West zone | MW | 3474
c) | Total supply in both zone ( a+b) | MW | 10930
Ref: | 27.21.0000.603.16.087.20.346 | Date: 15/12/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:November' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 28/11/20 | 18:00
| b) Ishurdi end | MW | 211 | 18/11/20 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 570 | 18/11/20 | 17:00
| b) Ishurdi end | MW | 132 | 28/11/20 | 18:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.0106
| b) Ishurdi end | MKWH | 78.1916
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 75.8459
| b) Ishurdi end | MKWH | 1.9521
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 80 | 02/11/20 | 19:30
| b)Serajganj end | MW | 550 | 17/11/20 | 12:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 520 | 17/11/20 | 12:00
| b)Sirajganj end | MW | 70 | 02/11/20 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | - | -
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.552
| b)Sirajganj end | MKWH | 163.07
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 159.932
| b)Sirajganj end | MKWH | 3.544
30 | Transmission loss of EWI /NO-2 | % | 1.446
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV Transformer-T2 | 2020-11-02 12:22 | 2020-11-02 12:47 | 0:25 | E/O | Due to Oil leavel low | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T-1, | 2020-11-10 08:32 | 2020-11-10 08:32 | 0:00 | E/O | Due to bursting of Y-phase PT
| 132/33 kV Transformers-T-2, | 2020-11-10 08:32 | 2020-11-10 09:16 | 0:44 | E/O |  | 80 | 58.6667 | Power interruption
| 132/33 kV Transformers-T-4, | 2020-11-10 08:32 | 2020-11-10 12:32 | 4:00 | E/O
Valuka | 132/33 kV Transformers-T-2 | 2020-11-22 16:13 | 2020-11-22 17:02 | 1:28 | E/O | Due to SF6 gas filling at 33 kV side | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1 & T2 | 2020-11-24 17:06 | 2020-11-24 18:32 | 1:26 | T | Due to 33 kV feeder fault | 40 | 57.3333 | Power interruption
Agargaon | 230/132 kV Transformer-T-01 | 2020-11-28 12:08 | 2020-11-28 14:19 | 2:11 | T | Tripped showing master trip relay | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformers-T-1 | 2020-11-29 10:05 | 2020-11-29 10:59 | 0:54 | T | Tripped showing differential relay | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T-3 | 2020-11-30 09:46 | 2020-11-30 12:04 | 2:18 | T | Tripped showing main protection relay | 0 | 0 | No interruption
|  |  | Total : | 13:26 |  | Unserved Energy: |  | 116
Dhaka (South) Grid Circle :
Sonargaon | 132/33 kV Transformers-T-1 & T2 | 2020-11-07 04:08 | 2020-11-07 04:27 | 0:19 | T | Tripped showing PRD relay | 48 | 15.2 | Power interruption
| 132/33 kV Transformer-T1 | 2020-11-20 17:02 | 2020-11-20 17:51 | 0:49 | T | Due to 33 kV feeder fault | 10 | 8.1667 | Power interruption
Haripur | 230/132 kV Transformer-T-02 | 2020-11-25 18:11 | 2020-11-25 18:11 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 | 2020-11-30 04:40 | 2020-11-30 10:23 | 0:28 | T | Tripped showing backup protcetion relay | 0 | 0 | No interruption
|  |  | Total : | 1:36 |  | Unserved Energy: |  | 23.3667
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2020-11-11 23:45 | 2020-11-12 00:03 | 0:18 | T | Due to 33 kV feeder fault | 39 | 11.7 | Power interruption
Hathazari | 230/132 kV Transformer-T2 | 2020-11-27 15:18 | 2020-11-27 15:38 | 1:28 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T-2 | 2020-11-28 10:12 | 2020-11-28 10:28 | 2:28 | E/O | Due to flashing at 33 kV isolator | 60 | 148 | Power interruption
|  |  | Total : | 4:14 |  | Unserved Energy: |  | 159.7
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T2 | 2020-11-09 09:22 | 2020-11-09 12:40 | 3:18 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T4 | 2020-11-10 10:19 | 2020-11-10 11:32 | 1:13 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-11-10 08:01 | 2020-11-10 09:04 | 1:03 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2020-11-10 18:00 | 2020-11-10 18:52 | 0:52 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV Transformers-T1 & T2 | 2020-11-14 07:38 | 2020-11-14 08:16 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-11-17 08:25 | 2020-11-17 16:05 | 1:28 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T4 | 2020-11-21 14:44 | 2020-11-21 15:44 | 1:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T2 | 2020-11-23 09:30 | 2020-11-23 16:26 | 1:28 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 10:50 |  |  |  | 0
Khulna Grid Circle :
Khulna(S) | 132 kV Bus | 2020-11-01 12:57 | 2020-11-01 13:25 | 0:28 | E/O | Due to bursting of 230/132 kV Transformer T3 | 300 | 140 | Power interruption
Bagerhat | 132/33 kV Transformer-T3 | 2020-11-05 06:17 | 2020-11-05 08:49 | 2:32 | E/O | Due to red-hot maintenance | 15 | 38 | Power interruption
Shariatpur | 132/33 kV Transformer-T2 | 2020-11-06 12:53 |  |  | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2020-11-10 08:41 | 2020-11-10 10:19 | 1:38 | E/O | Due to red-hot maintenance | 3 | 4.9 | Power interruption
| 132 kV Bus section(N)-2 | 2020-11-15 07:59 | 2020-11-15 10:15 | 2:16 | E/O | Due to red-hot maintenance | 10 | 22.6667 | Power interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-11-19 22:15 | 2020-11-20 11:29 | 13:14 | E/O | Due to Oil level low | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2020-11-20 16:23 | 2020-11-20 16:54 | 0:31 | T | Tripped showing PRD. relay | 25 | 12.9167 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 | 2020-11-23 07:34 | 2020-11-23 07:40 | 0:06 | T | Tripped showing E/F. relay | 20 | 2 | Power interruption
| 132/33 kV Transformers-T2 | 2020-11-23 07:34 | 2020-11-23 07:44 | 0:10 | T
Goalpara | 132/33 kV Transformers-T5 & T6 | 2020-11-24 17:15 | 2020-11-24 19:05 | 1:50 | T | Tripped showing E/F. relay | 12 | 22 | Power interruption
| 33 kV Bus | 2020-11-25 10:26 | 2020-11-25 11:45 | 1:19 | T | Tripped 33 kV feeder fault | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-11-29 10:03 | 2020-11-29 14:14 | 4:11 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 & 33 kV Bus | 2020-11-29 12:08 | 2020-11-29 12:21 | 0:13 | E/O | Due to red-hot maintenance at 33 kV side | 26 | 5.6333 | Power interruption
|  |  | Total : | 28:28 |  | Unserved Energy: |  | 248.1167
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
HVDC Bheramara | Auxiliary 33/04 Transformer T2 | 2020-11-05 08:04 | 2020-11-05 20:30 | 12:26 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| HVDC Bheramara block-2 33/.04 kV auxiliary Transformer | 2020-11-12 06:15 | 2020-11-12 11:09 | 12:26 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-11-09 11:30 | 2020-11-09 12:01 | 12:26 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-11-23 18:01 | 2020-11-23 20:53 | 2:52 | T | Tripped showing Diff. relay at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 40:10 |  |  |  | 0
Bogura Grid Circle:
Sirajganj | 132/33 kV Transformer-T4 | 2020-11-01 18:13 | 2020-11-01 19:08 | 0:55 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-3 | 2020-11-03 12:30 | 2020-11-03 18:35 | 6:05 | E/O | Due to CB gas pressure low | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-4 | 2020-11-14 11:34 | 2020-11-14 14:23 | 2:49 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 with 33 kV Bus | 2020-11-22 08:45 | 2020-11-22 10:10 | 1:25 | E/O | Due to red-hot maintenance at 33 kV side | 14 | 19.8333 | Power interruption
| 132/33 kV Transformer-T-3 | 2020-11-22 13:09 | 2020-11-22 14:11 | 1:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-2 | 2020-11-25 08:50 | 2020-11-25 09:28 | 0:38 | T | Tripped showing diff.& O/C relay at 33 kV side | 15 | 9.5 | Power interruption
Rajshahi | 132/33 kV Transformer-T-3 with 33 kV Bus | 2020-11-28 16:50 | 2020-11-28 17:17 | 0:27 | E/O | Due to emergency maintenance work | 20 | 9 | Power interruption
Jaldhaka | 132/33 kV Transformer-T-1 | 2020-11-29 11:18 | 2020-11-29 11:57 | 0:39 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 14:00 |  |  |  | 38.3333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 112:44 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Lalbagh 132 kV line | 2020-11-02 11:16 | 2020-11-02 11:30 | 0:14 | T | Tripped showing dist.relay | 80 | 18.6667 | Power interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-05 04:58 | 2020-11-05 05:18 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-11-14 05:48 | 2020-11-14 06:07 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kadda | Kadda-Kabirpur 132 kV line-1 | 2020-11-20 15:15 | 2020-11-20 15:24 | 0:09 | T | Tripped showing dist. main protection relay | 0 | 0 | No interruption
Mymensingh | Mymensingh -Baluka 132 kV line-1 & 2 | 2020-11-24 13:40 | 2020-11-24 14:00 | 0:20 | T | Tripped showing dist.(C-phase) relay | 68 | 22.6667 | Power interruption
|  |  | Total : | 1:22 |  | Unserved Energy: |  | 41.3333
Dhaka (South) Grid Circle :
Rampura | Rampura-Bashundhara 132 kV line-1 | 2020-11-02 13:15 | 2020-11-02 20:12 | 6:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2020-11-09 13:48 | 2020-11-09 13:54 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fatullah | Fatullah-Shyampur 230 kV line-1 | 2020-11-12 06:48 | 2020-11-12 07:05 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-11-15 07:59 | 2020-11-15 08:55 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Fatullah 132 kV line | 2020-11-20 08:45 | 2020-11-20 09:32 | 0:47 | T | Tripped showing O/C. relay | 23 | 18.0167 | Power interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2020-11-25 10:54 | 2020-11-25 14:28 | 3:34 | E/O | Due to gas filling | 0 | 0 | No interruption
|  |  | Total : | 12:37 |  | Unserved Energy: |  | 18.0167
Chittagong Grid Circle :
Hathazari | Hathazari-Baroierhat 132 kV line-1 & 2 | 2020-11-08 20:28 | 2020-11-08 20:50 | 0:22 | T | Tripped showing dist. relay | 22 | 8.0667 | Power interruption
Baroierhat | Baroierhat-Feni 132 kV line-1 | 2020-11-08 20:28 | 2020-11-08 23:23 | 2:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV line | 2020-11-08 20:28 | 2020-11-08 22:55 | 2:27 | T | Tripped showing dist. relay | 6.4 | 15.68 | Power interruption
Madunaghat | Madunaghat-T.K chemical 32 kV line | 2020-11-18 16:26 | 2020-11-18 17:11 | 0:45 | T | Due to Oil leakage | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2020-11-20 12:01 | 2020-11-20 17:02 | 5:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 11:30 |  | Unserved Energy: |  | 23.7467
Cumilla Grid Circle :
Chowmuhani | Chowmuhani-Feni 132 kV line-1 & 2 | 2020-11-08 20:28 | 2020-11-08 21:03 | 0:35 | T | Tripped showing dist. relay | 90 | 39 | Power interruption 20:28 to 20:54
Chaddagram | Chaddagram-Feni 132 kV line-1 & 2 | 2020-11-08 20:28 | 2020-11-08 20:52 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV line | 2020-11-08 20:28 | 2020-11-08 20:28 | 0:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2020-11-10 13:10 | 2020-11-10 13:38 | 0:28 | T | Due to sparking at Cumilla(N) end | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 230 kV line-3 | 2020-11-12 03:19 | 2020-11-12 03:19 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-1 | 2020-11-12 06:05 | 2020-11-12 07:36 | 1:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV line-1 | 2020-11-17 11:02 | 2020-11-17 16:56 | 5:54 | E/O | Due to fire at 132/3 kV Transformer T4 | 200 | 426.6667 | Power interruption 11:02 to 13:10
| Sylhet-Fenchuganj S/S 132 kV line-2 | 2020-11-17 11:02 | 2020-11-17 17:44 | 6:42 | E/O
| Sylhet-Fenchuganj S/S 132 kV line | 2020-11-18 14:46 | 2020-11-18 14:57 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sylhet-Fenchuganj S/S 132 kV line | 2020-11-18 16:02 | 2020-11-18 16:59 | 0:57 | T | Tripped showing SOTF. relay | 0 | 0 | No interruption
| Sylhet-Fenchuganj S/S 132 kV line | 2020-11-18 18:28 | 2020-11-19 19:46 | 25:18 | T |  | 0 | 0 | No interruption
| Sylhet-Fenchuganj S/S 132 kV line | 2020-11-19 19:46 | 2020-11-19 20:04 | 0:18 |  |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2020-11-22 01:45 | 2020-11-23 20:32 | 42:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line | 2020-11-28 05:37 | 2020-11-28 14:28 | 8:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2020-11-29 01:08 | 2020-11-29 01:28 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bibiyana | Bibiyana -Kaliakoir 400 kV line-2 | 2020-11-29 08:21 | 2020-11-29 10:16 | 1:55 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2020-11-30 08:15 | 2020-11-30 11:36 | 3:21 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 99:32 |  | Unserved Energy: |  | 465.6667
Khulna Grid Circle :
Faridpur | Faridpur-Gopalganj 132 kV line-2 | 2020-11-07 11:43 | 2020-11-07 11:54 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:11 |  | Unserved Energy: |  | 0
HVDC Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Palshbari | Palshbari-Mohasthangarth 132 kV line-1 | 2020-11-02 14:55 | 2020-11-02 15:04 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2020-11-19 04:42 | 2020-11-19 20:45 | 16:03 | E/O | Due to bursting of PT | 10 | 160.5 | Power interruption
Palshbari | Palshbari-Rangpur confidence 132 kV line-1 & 2 | 2020-11-19 04:05 | 2020-11-19 04:29 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2020-11-19 04:05 | 2020-11-19 04:45 | 0:40 | T | Tripped showing dist. relay | 70 | 21 | Power interruption 04:05 to 04:23
| Rangpur-Saidpur 132 kV line-1 | 2020-11-19 04:05 | 2020-11-19 04:23 | 0:18 | T | Tripped showing dist. relay
| Rangpur-Barapukuria 132 kV line-1 &2 | 2020-11-19 04:05 | 2020-11-19 04:31 | 0:26 | T |  | 0 | 0 | No interruption
|  |  | Total : | 18:00 |  | Unserved Energy: |  | 181.5
Others :
Ullon | Ullon-Dhanmondi 132 kV line-3 | 2020-11-02 07:40 | 2020-11-02 16:05 | 8:25 | T | Tripped showing interconnection trip | 0 | 0 | No interruption
|  |  | Total : | 8:25 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 151:37 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 230 kV bus-2 | 2020-11-01 06:39 | 2020-11-01 08:10 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-11-01 08:01 | 2020-11-01 17:28 | 9:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2020-11-01 10:59 | 2020-11-01 16:25 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-11-01 09:06 | 2020-11-01 16:25 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-11-01 09:24 | 2020-11-01 16:42 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-11-01 09:10 | 2020-11-01 16:40 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-RPCL 100 MW 132 kV line | 2020-11-01 08:07 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-11-02 08:04 | 2020-11-02 17:12 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2020-11-02 08:44 | 2020-11-02 15:42 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-11-02 09:02 | 2020-11-02 16:30 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-11-02 09:04 | 2020-11-02 16:49 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-11-02 09:15 | 2020-11-02 15:30 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-11-03 09:15 | 2020-11-03 16:39 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2020-11-03 08:33 | 2020-11-03 14:52 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2 | 2020-11-03 10:34 | 2020-11-03 16:29 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-11-03 09:01 | 2020-11-03 16:30 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-11-03 09:20 | 2020-11-03 16:39 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-11-03 07:54 | 2020-11-03 16:44 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-11-04 07:58 | 2020-11-04 07:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2 | 2020-11-04 09:13 | 2020-11-04 15:01 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(new) | 132/33 kV Transformer-T1 | 2020-11-05 09:13 | 2020-11-05 15:01 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-11-05 08:30 | 2020-11-05 15:01 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 | 2020-11-05 08:25 | 2020-11-05 08:58 | 0:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2020-11-06 07:39 | 2020-11-06 16:07 | 8:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-11-07 06:30 | 2020-11-07 07:58 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(new) | 132/33 kV Transformer-T2 | 2020-11-07 09:36 | 2020-11-07 15:36 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2020-11-07 08:19 | 2020-11-07 16:32 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-11-07 09:11 | 2020-11-07 14:48 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-11-07 09:10 | 2020-11-07 17:08 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2020-11-08 07:53 | 2020-11-08 07:53 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-11-08 09:05 | 2020-11-08 16:54 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-11-08 09:34 | 2020-11-08 15:44 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-11-08 09:02 | 2020-11-08 16:32 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-11-08 08:07 | 2020-11-08 15:20 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 |  | 2020-11-08 14:38 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2020-11-09 08:19 | 2020-11-09 15:07 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-11-09 09:02 | 2020-11-09 16:31 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-11-09 09:09 | 2020-11-09 16:32 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-11-09 11:37 | 2020-11-09 13:34 | 1:57 | S/O | Due to delta test | 0 | 0 | No interruption
Savar | 33 kV capacitor bank-1,2 & 3 | 2020-11-10 09:40 | 2020-11-10 16:53 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-11-10 09:22 | 2020-11-10 16:17 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-11-10 09:50 | 2020-11-10 16:35 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-11-10 09:02 | 2020-11-10 12:01 | 2:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 132 kV Bus-2 | 2020-11-11 06:32 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 33 kV capacitor bank-1 & 2 | 2020-11-11 09:27 | 2020-11-11 13:27 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2020-11-11 08:39 | 2020-11-11 17:15 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-11-12 08:50 | 2020-11-12 15:20 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-1 | 2020-11-12 09:57 | 2020-11-12 11:19 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-11-12 11:52 | 2020-11-12 13:34 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132 kV main Bus | 2020-11-13 06:05 | 2020-11-13 12:30 | 6:25 | S/O | Due to D/W work | 82 | 526.1667 | Power interruption
Kaliakoir | 400/230 kV Transformer-T2 | 2020-11-13 06:16 | 2020-11-13 10:35 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2020-11-13 07:54 | 2020-11-13 11:54 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-11-13 08:11 | 2020-11-13 10:31 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-11-13 14:15 | 2020-11-13 17:15 | 3:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1& its Bus | 2020-11-14 08:58 | 2020-11-14 16:36 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T3 & its Bus | 2020-11-14 09:10 | 2020-11-14 17:11 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2020-11-14 09:25 | 2020-11-14 16:16 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV capacitor banks | 2020-11-15 10:24 | 2020-11-15 15:40 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1& its 33 kV Bus | 2020-11-15 08:28 | 2020-11-15 15:40 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-11-15 09:05 | 2020-11-15 17:07 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2020-11-15 09:09 | 2020-11-15 16:18 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV capacitor banks(all) | 2020-11-16 09:24 | 2020-11-16 13:36 | 4:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2020-11-16 08:31 | 2020-11-16 17:03 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2020-11-16 09:06 | 2020-11-16 16:06 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T2 | 2020-11-16 09:54 | 2020-11-16 14:08 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-11-16 14:12 | 2020-11-16 17:10 | 2:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-11-17 08:35 | 2020-11-17 16:38 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T4 | 2020-11-17 08:16 | 2020-11-17 08:16 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-11-17 09:33 | 2020-11-17 14:52 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2020-11-17 09:11 | 2020-11-17 16:16 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T4 | 2020-11-17 10:50 | 2020-11-17 14:23 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-11-17 09:33 | 2020-11-17 19:32 | 9:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2020-11-18 10:58 | 2020-11-18 16:09 | 5:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-MTR1 | 2020-11-18 10:15 | 2020-11-18 12:24 | 2:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-11-18 08:40 | 2020-11-18 13:10 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2020-11-19 10:03 | 2020-11-19 13:40 | 3:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-11-19 08:58 | 2020-11-19 18:58 | 10:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformers-T-1, | 2020-11-20 06:48 | 2020-11-20 07:56 | 1:08 | S/O | Due to buccholz alarm shown | 0 | 0 | No interruption
Tangail | 132 kV main Bus | 2020-11-20 06:09 | 2020-11-20 13:22 | 7:13 | S/O | Due to D/W work | 94 | 678.3667 | Power interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-11-20 11:08 | 2020-11-20 19:52 | 8:44 | S/O | Due to maintenance work | 5 | 43.6667 | Power interruption
Valuka | 132/33 kV Transformer-T1 | 2020-11-21 08:48 | 2020-11-21 17:13 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-11-21 09:28 | 2020-11-21 13:55 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus -Coupler | 2020-11-21 09:10 | 2020-11-21 16:55 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T1 | 2020-11-22 08:50 | 2020-11-22 16:05 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-11-22 09:41 | 2020-11-22 15:35 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-11-22 09:02 | 2020-11-22 15:27 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-11-22 09:40 | 2020-11-22 15:52 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus -B | 2020-11-22 09:58 | 2020-11-22 16:57 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T3 | 2020-11-21 07:50 | 2020-11-21 16:53 | 9:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-11-23 07:30 | 2020-11-23 17:14 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2020-11-23 09:02 | 2020-11-23 16:48 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-11-23 08:45 | 2020-11-23 16:22 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-11-23 09:18 | 2020-11-23 17:05 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformers-T-2 | 2020-11-24 07:51 | 2020-11-24 17:22 | 9:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT3 | 2020-11-24 09:03 | 2020-11-24 12:41 | 3:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-11-24 09:08 | 2020-11-24 16:55 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-11-24 08:38 | 2020-11-24 10:58 | 2:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T2 | 2020-11-24 08:46 | 2020-11-24 11:49 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-11-24 11:51 | 2020-11-24 14:04 | 2:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-2 | 2020-11-24 11:56 | 2020-11-24 13:18 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T-3 | 2020-11-24 15:09 | 2020-11-24 16:31 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-GT3 | 2020-11-25 07:36 | 2020-11-25 17:07 | 9:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-11-25 08:54 | 2020-11-25 13:10 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformer-T-2 | 2020-11-25 09:08 | 2020-11-25 17:37 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T2 | 2020-11-25 08:01 | 2020-11-25 16:23 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T2 | 2020-11-25 09:00 | 2020-11-25 20:04 | 11:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-11-25 08:38 | 2020-11-25 10:58 | 2:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 with Kabirpur line-2 | 2020-11-26 07:36 | 2020-11-26 17:07 | 9:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2020-11-27 09:45 | 2020-11-27 12:15 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2020-11-27 12:54 | 2020-11-27 16:35 | 3:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 with Kabirpur line-2 | 2020-11-28 07:12 | 2020-11-28 13:31 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T5 | 2020-11-28 08:17 | 2020-11-28 12:58 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-11-28 08:31 | 2020-11-28 13:52 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2020-11-29 08:51 | 2020-11-29 17:23 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 | 2020-11-29 13:59 | 2020-11-29 15:05 | 1:06 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Page: 3/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400 kV Bus-1 | 2020-11-29 15:50 | 2020-11-29 17:02 | 1:12 | S/O | Due to disconnect of Kaliakoir-Bibiyana 400 kv line-2 | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-11-29 09:10 | 2020-11-29 13:20 | 4:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 | 2020-11-29 08:58 | 2020-11-29 13:37 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-1 | 2020-11-30 10:02 | 2020-11-30 16:48 | 6:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-11-30 08:53 | 2020-11-30 17:27 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-11-30 09:05 | 2020-11-30 13:20 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 | 2020-11-30 15:06 | 2020-11-30 16:04 | 0:58 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 690:38 |  | Unserved Energy: |  | 1248.2
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T2 | 2020-11-02 07:33 | 2020-11-02 18:01 | 10:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-03 07:45 | 2020-11-03 18:20 | 10:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-03 18:29 | 2020-11-03 21:44 | 3:15 | S/O | Due to Y-phase noise problem | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2020-11-04 07:50 | 2020-11-04 07:50 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2020-11-05 07:45 | 2020-11-05 20:01 | 12:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T01 | 2020-11-06 10:09 | 2020-11-06 11:00 | 0:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T01 | 2020-11-07 08:58 | 2020-11-07 16:53 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T1 | 2020-11-07 09:07 | 2020-11-07 16:40 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-ATR1 | 2020-11-09 08:41 | 2020-11-09 16:12 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-1 | 2020-11-09 08:50 | 2020-11-09 16:25 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-1 | 2020-11-10 08:01 | 2020-11-10 20:23 | 12:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T2 | 2020-11-13 07:42 | 2020-11-13 11:13 | 3:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2020-11-13 07:56 | 2020-11-13 16:58 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-GT1 | 2020-11-14 08:50 | 2020-11-14 08:50 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-1 | 2020-11-14 14:49 | 2020-11-14 16:19 | 1:30 | S/O | Due to loop change | 0 | 0 | No interruption
Haripur P/S | 412 MW Bay | 2020-11-15 10:36 | 2020-11-15 20:23 | 9:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-Tr-2 | 2020-11-15 08:31 | 2020-11-15 20:23 | 11:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T-2 | 2020-11-16 07:19 | 2020-11-16 15:46 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-Tr-2 | 2020-11-16 09:13 | 2020-11-16 18:20 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2020-11-19 07:31 | 2020-11-19 16:03 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-ATr-1 | 2020-11-19 08:37 | 2020-11-19 16:39 | 8:02 | S/O | Due to A/M work | 10 | 80.3333 | Power interruption
Syampur | 230 kV Bus & 132 kV Bus | 2020-11-20 08:45 | 2020-11-20 09:14 | 0:29 | S/O | Due to A/M work | 160 | 77.3333 | Power interruption
Rampura | 132 kV Bus-A | 2020-11-22 08:30 | 2020-11-22 17:49 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2020-11-22 08:21 | 2020-11-22 15:23 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-T01 | 2020-11-22 08:46 | 2020-11-22 16:20 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV Transformer-T01 | 2020-11-23 08:44 | 2020-11-23 21:08 | 12:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Syampur | 132/33 kV Transformer-T1 | 2020-11-24 08:17 | 2020-11-24 13:16 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-2 | 2020-11-24 13:20 | 2020-11-24 13:21 | 0:01 | S/O | Due to checking work | 0 | 0 | No interruption
Syampur | 132/33 kV Transformer-T2 | 2020-11-25 08:18 | 2020-11-25 14:27 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-TR-2 | 2020-11-25 08:34 | 2020-11-25 17:20 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
APR | 230 kV Bus | 2020-11-25 06:41 | 2020-11-25 12:14 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-TR-2 | 2020-11-26 08:19 | 2020-11-26 20:27 | 12:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus-2 | 2020-11-28 07:45 | 2020-11-28 16:28 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-11-29 07:46 | 2020-11-29 16:16 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-2 |  | 2020-11-29 14:29 |  | S/O | After maintenance work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 |  | 2020-11-30 10:23 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 241:48 |  | Unserved Energy: |  | 157.6667
Page: 4/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T1 | 2020-11-06 07:54 | 2020-11-06 14:52 | 6:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T1 | 2020-11-07 08:11 | 2020-11-07 14:40 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2020-11-12 21:21 |  |  | S/O | Due to oil centrifuging | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2020-11-14 08:22 | 2020-11-14 14:28 | 6:06 | S/O | Due to A/M work | 10 | 61 | Power interruption
Sikalbaha | 132 kV Bus-A | 2020-11-15 07:15 | 2020-11-15 09:25 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV Transformer-T1 | 2020-11-20 09:18 | 2020-11-20 10:51 | 1:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2020-11-20 08:16 | 2020-11-20 12:37 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T2 | 2020-11-21 09:57 | 2020-11-21 12:04 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T3 | 2020-11-21 08:23 | 2020-11-21 14:22 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV Transformer-T1 | 2020-11-21 09:18 | 2020-11-21 10:51 | 1:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T03 | 2020-11-22 11:39 | 2020-11-22 15:30 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-11-22 15:33 | 2020-11-22 16:49 | 1:16 | S/O | Due to installation work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-11-23 10:02 | 2020-11-23 11:26 | 1:24 | S/O | Due to meter testing | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-11-24 07:39 | 2020-11-24 13:32 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT04 | 2020-11-24 10:48 | 2020-11-24 11:19 | 0:31 | S/O | Due to CB testing | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-11-25 07:22 | 2020-11-25 15:30 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2020-11-25 10:02 | 2020-11-25 11:40 | 1:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2020-11-27 07:31 | 2020-11-27 13:16 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1 | 2020-11-28 07:01 | 2020-11-28 11:38 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer-T4 | 2020-11-28 09:42 | 2020-11-28 16:43 | 7:01 | S/O | Due to isolator work | 0 | 0 | No interruption
|  |  | Total : | 77:20 |  | Unserved Energy : |  | 61
Cumilla Grid Circle :
Cumilla (S) | 132/33 kV Transformer-T1 | 2020-11-01 10:37 | 2020-11-01 13:26 | 2:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-01 13:29 | 2020-11-01 14:58 | 1:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2020-11-01 13:22 | 2020-11-01 14:25 | 1:03 | S/O | Due to CB maintenance | 5 | 5.25 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-11-02 09:01 | 2020-11-02 13:50 | 4:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2020-11-02 12:22 | 2020-11-02 15:13 | 2:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-11-02 11:37 | 2020-11-02 11:37 | 0:00 | S/O | Due to high temperature | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2020-11-02 15:32 | 2020-11-02 17:08 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T3 | 2020-11-02 16:54 | 2020-11-02 18:48 | 1:54 | S/O | Due to Delta test | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 & T6 | 2020-11-03 09:24 | 2020-11-03 13:25 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2020-11-03 12:56 | 2020-11-03 15:06 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-11-03 10:27 | 2020-11-03 12:54 | 2:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T1 | 2020-11-04 06:25 | 2020-11-04 13:08 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-11-04 08:36 | 2020-11-04 13:02 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2020-11-04 09:14 | 2020-11-04 17:23 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T2 | 2020-11-04 13:40 | 2020-11-04 16:50 | 3:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 |  | 2020-11-04 10:02 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-11-07 07:22 | 2020-11-07 11:21 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T2 | 2020-11-07 09:00 | 2020-11-07 15:51 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2020-11-08 10:54 | 2020-11-08 17:29 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Biyanabazar | 132/33 kV Transformer-T1 |  | 2020-11-08 17:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2020-11-09 06:58 | 2020-11-09 14:12 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2020-11-09 10:50 | 2020-11-09 14:30 | 3:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2020-11-09 08:27 | 2020-11-09 15:27 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-11-09 11:15 | 2020-11-09 11:15 | 0:00 | S/O | Due to Oil centrifuge | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2020-11-10 08:40 | 2020-11-10 15:33 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2020-11-10 10:15 | 2020-11-10 14:45 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2020-11-11 08:52 | 2020-11-11 14:10 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 33 kV full Bus | 2020-11-14 07:18 | 2020-11-14 12:55 | 5:37 | S/O | Due to C/M work | 80 | 449.3333 | Power interruption
Chandpur | 132/33 kV Transformer-T5 | 2020-11-14 09:05 | 2020-11-14 16:25 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Baroirhat | 132/33 kV Transformer-T2 | 2020-11-14 10:18 | 2020-11-14 10:18 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T1 | 2020-11-14 12:31 | 2020-11-14 16:00 | 3:29 | S/O | Due to changing work | 24 | 83.6 | Power interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2020-11-15 09:47 | 2020-11-15 17:22 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Biyanabazar | 132/33 kV Transformer-T2 | 2020-11-16 09:20 | 2020-11-16 17:32 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2020-11-17 08:11 | 2020-11-17 17:13 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2020-11-18 07:05 | 2020-11-18 17:05 | 10:00 | S/O | Due maintenance work at 33 kV side | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2020-11-18 08:05 | 2020-11-18 17:23 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2020-11-19 08:39 | 2020-11-19 17:33 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 |  | 2020-11-19 16:40 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-19 17:23 | 2020-11-19 18:15 | 0:52 | S/O | Due maintenance work at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & 33 kV bus | 2020-11-21 08:16 | 2020-11-21 15:48 | 7:32 | S/O | Due to A/M work by PBS | 19 | 143.1333 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-11-21 09:02 | 2020-11-21 15:48 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T1 | 2020-11-21 08:54 | 2020-11-21 16:39 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-T01 | 2020-11-21 08:56 | 2020-11-21 16:07 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2020-11-21 08:39 | 2020-11-21 18:00 | 9:21 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-11-22 08:51 | 2020-11-22 16:01 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T1 | 2020-11-22 09:05 | 2020-11-22 16:52 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-T01 | 2020-11-22 08:43 | 2020-11-22 13:30 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T02 | 2020-11-22 10:07 | 2020-11-22 14:25 | 4:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T1 | 2020-11-23 09:19 | 2020-11-23 16:53 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-T01 | 2020-11-23 08:42 | 2020-11-23 16:04 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T02 | 2020-11-23 09:07 | 2020-11-23 12:20 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T1A-T1B | 2020-11-24 08:23 | 2020-11-24 16:42 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-11-25 08:37 | 2020-11-25 16:10 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-11-25 12:25 | 2020-11-25 14:47 | 2:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-11-26 08:22 | 2020-11-26 16:34 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-29 08:32 | 2020-11-29 16:45 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 & T3 | 2020-11-30 08:36 | 2020-11-30 15:10 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 291:55 |  | Unserved Energy : |  | 681.3167
Khulna Grid Circle :
Barishal | 230/132 kV Transformer-T1 | 2020-11-01 08:32 | 2020-11-01 17:00 | 8:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-1 | 2020-11-01 08:27 | 2020-11-01 14:07 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2020-11-01 08:55 | 2020-11-01 16:21 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-11-01 08:22 | 2020-11-01 08:22 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 230/132 kV Transformer-T-1 | 2020-11-02 08:42 | 2020-11-02 17:10 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-11-02 09:05 | 2020-11-02 17:27 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T1 | 2020-11-02 08:10 | 2020-11-02 15:18 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-1 | 2020-11-02 08:45 | 2020-11-02 17:58 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-11-03 22:02 | 2020-11-03 22:13 | 0:11 | S/O | Due maintenance work | 15 | 2.75 | Power interruption
Khulna(C) | 132/33 kV Transformer-T1 | 2020-11-03 07:48 | 2020-11-03 17:10 | 9:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 230/132 kV Transformer-T-2 | 2020-11-03 08:21 | 2020-11-03 17:16 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-2 | 2020-11-03 08:45 | 2020-11-03 11:19 | 2:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-1 | 2020-11-03 11:22 | 2020-11-03 16:50 | 5:28 | S/O | Due to high temperature of 132 kV Y-phase isolator | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-11-03 09:36 | 2020-11-03 17:26 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 132/33 kV Transformer-T2 | 2020-11-04 07:32 | 2020-11-04 07:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 230/132 kV Transformer-T-2 | 2020-11-04 08:47 | 2020-11-04 17:01 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T2 | 2020-11-05 07:42 | 2020-11-05 13:16 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 230/132 kV Transformer-T-2 | 2020-11-05 08:28 | 2020-11-05 17:10 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-2 | 2020-11-05 08:28 | 2020-11-05 17:36 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2020-11-07 07:34 | 2020-11-07 14:55 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 132/33 kV Transformer-T3 | 2020-11-07 07:51 | 2020-11-07 11:19 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Mongla | 132/33 kV Transformer-T1 | 2020-11-07 10:02 | 2020-11-07 16:01 | 5:59 | S/O | Due to A/M work | 10 | 59.8333 | Power interruption
Barishal | 230 kV Bus-1 | 2020-11-07 08:48 | 2020-11-07 16:24 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2020-11-08 07:57 | 2020-11-08 15:31 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2020-11-08 08:09 | 2020-11-08 14:32 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-3 | 2020-11-08 08:32 | 2020-11-08 17:07 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2020-11-08 09:12 | 2020-11-08 13:23 | 4:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-11-09 09:55 | 2020-11-09 12:59 | 3:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-11-09 09:02 | 2020-11-09 16:58 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-1 | 2020-11-09 11:44 | 2020-11-09 20:27 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 230 kV Bus-1 | 2020-11-09 08:09 | 2020-11-09 09:29 | 1:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2020-11-09 08:36 | 2020-11-09 17:27 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132 kV Bus coupler | 2020-11-10 09:37 | 2020-11-10 13:45 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Narail | 132/33 kV Transformer-T1 | 2020-11-10 09:01 | 2020-11-10 16:25 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2020-11-10 10:06 | 2020-11-10 12:51 | 2:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-11-10 09:01 | 2020-11-10 17:15 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T5 | 2020-11-12 08:24 | 2020-11-12 16:23 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2020-11-12 09:01 | 2020-11-12 16:52 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132 main Bus | 2020-11-12 08:13 | 2020-11-12 14:13 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-11-12 09:07 | 2020-11-12 15:24 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132 kV Bus coupler | 2020-11-12 09:10 | 2020-11-12 12:30 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-11-14 08:28 | 2020-11-14 16:50 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2020-11-14 08:21 | 2020-11-14 13:10 | 4:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-11-15 08:38 | 2020-11-15 15:53 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2020-11-15 08:20 | 2020-11-15 14:32 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sharaiatpur | 132/33 kV Transformer-T1 | 2020-11-15 08:39 | 2020-11-15 15:59 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2020-11-16 08:50 | 2020-11-16 13:38 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Sharaiatpur | 132/33 kV Transformer-T2 | 2020-11-16 08:13 | 2020-11-16 16:13 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-11-16 08:38 | 2020-11-16 15:53 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2020-11-16 08:20 | 2020-11-16 14:32 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sharaiatpur | 132/33 kV Transformer-T1 | 2020-11-16 08:39 | 2020-11-16 15:59 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-11-16 14:38 | 2020-11-16 16:57 | 2:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2020-11-17 08:01 | 2020-11-17 16:03 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T6 | 2020-11-17 08:05 | 2020-11-17 16:25 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2020-11-17 08:42 | 2020-11-17 14:27 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sharaiatpur | 132/33 kV Transformer-T2 | 2020-11-17 08:22 | 2020-11-17 16:14 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T6 | 2020-11-18 08:01 | 2020-11-18 09:42 | 1:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T4 | 2020-11-18 08:46 | 2020-11-18 14:06 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sharaiatpur | 33 kV Bus | 2020-11-18 08:45 | 2020-11-18 14:59 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2020-11-19 09:07 | 2020-11-19 16:40 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132 kV Bus coupler | 2020-11-19 08:15 | 2020-11-19 08:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T4 | 2020-11-19 08:53 | 2020-11-19 15:33 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-3 | 2020-11-20 10:04 | 2020-11-20 17:38 | 7:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-11-20 11:33 | 2020-11-20 19:11 | 7:38 | S/O | After maintenance work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-A | 2020-11-21 10:15 | 2020-11-21 15:50 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV Bus-A | 2020-11-21 11:07 | 2020-11-21 14:27 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T1 | 2020-11-21 09:23 | 2020-11-21 09:23 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-B | 2020-11-22 08:05 | 2020-11-22 15:48 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV Bus-B | 2020-11-22 08:55 | 2020-11-22 13:48 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-11-22 08:40 | 2020-11-22 15:44 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132 kV mai Bus | 2020-11-22 09:38 | 2020-11-22 11:12 | 1:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-11-23 08:02 | 2020-11-23 15:38 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2020-11-23 10:37 | 2020-11-23 16:41 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-11-24 08:14 | 2020-11-24 14:45 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2020-11-24 08:35 | 2020-11-24 15:49 | 7:14 | S/O | Due to A/M work | 15 | 108.5 | Power interruption
Khulna(S) | 230 kV Bus-2 & Bus coupler | 2020-11-24 10:05 | 2020-11-24 14:02 | 3:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-11-24 13:28 | 2020-11-24 15:38 | 2:10 | S/O | Due to protection test | 0 | 0 | No interruption
Page: 7/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T1 | 2020-11-24 14:51 | 2020-11-24 17:05 | 2:14 | S/O | Due to bushing leakage seal | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-11-25 09:07 | 2020-11-25 13:50 | 4:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2020-11-25 08:35 | 2020-11-25 15:49 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-11-25 08:14 | 2020-11-25 14:45 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-11-26 10:25 | 2020-11-26 16:35 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 33 kV Bus-section-1 & 2 | 2020-11-28 08:16 | 2020-11-28 16:43 | 8:27 | S/O | Due to C/M work | 20 | 96.6667 | Power interruption 08:16 to 13:06
|  |  | Total : | 497:13 |  | Unserved Energy : |  | 267.75
HVDC Grid Circle :
Benapole | 132/33 kV Transformer-T1 | 2020-11-01 07:47 | 2020-11-01 15:30 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-11-01 10:10 | 2020-11-01 13:06 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-11-01 12:20 | 2020-11-01 13:00 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Banapole | 132/33 kV Transformer-T-1 | 2020-11-02 08:05 | 2020-11-02 15:37 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | 132/33 kV Transformer-T1 | 2020-11-02 08:10 | 2020-11-02 17:15 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Benapole | 132/33 kV Transformer-T2 | 2020-11-04 08:02 | 2020-11-04 15:32 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | 132/33 kV Transformer-T3 | 2020-11-04 08:20 | 2020-11-04 15:35 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Banapole | 132/33 kV Transformer-T-2 | 2020-11-05 07:25 | 2020-11-05 07:25 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2020-11-07 07:51 | 2020-11-07 07:51 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2020-11-08 07:57 | 2020-11-08 15:31 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDCBheramara | HVDCBheramara 01 H02 33 kV auxiliary | 2020-11-08 11:22 | 2020-11-08 15:06 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDCBheramara auto Transformer | 2020-11-09 10:13 | 2020-11-09 18:11 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T1 | 2020-11-09 08:29 | 2020-11-09 16:38 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDCBheramara | HVDCBheramara 33/0.415 kV Transformers T1 & T2 | 2020-11-10 09:44 | 2020-11-10 13:39 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2020-11-10 08:31 | 2020-11-10 14:53 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDCBheramara | HVDCBheramara 33/0.415 kV Transformer | 2020-11-11 11:25 | 2020-11-11 16:59 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-11-24 10:16 | 2020-11-24 15:34 | 5:18 | S/O | Due to checking panel borad | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2020-11-26 07:25 | 2020-11-26 07:25 | 0:00 | S/O | Due to bushing problem | 0 | 0 | No interruption
HVDCBheramara | HVDC Bheramara pole-2 | 2020-11-27 07:30 | 2020-11-27 07:30 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 400 kV Bus-2 | 2020-11-29 10:39 | 2020-11-29 16:05 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara 230 kV filter bank-4 | 2020-11-30 10:15 | 2020-11-30 18:04 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-11-30 10:44 | 2020-11-30 15:29 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 109:15 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Naogaon | 132/33 kV Transformer-T-1 | 2020-11-01 08:04 | 2020-11-01 16:05 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-1 | 2020-11-01 08:52 | 2020-11-01 14:16 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-2 | 2020-11-01 16:09 | 2020-11-01 17:34 | 1:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Panchugar | 132/33 kV Transformer-T-2 | 2020-11-02 08:07 | 2020-11-02 16:22 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-1 | 2020-11-02 08:10 | 2020-11-02 15:56 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-1 | 2020-11-02 10:02 | 2020-11-02 14:16 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-01 | 2020-11-03 07:56 | 2020-11-03 15:49 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugar | 132/33 kV Transformer-T-1 | 2020-11-03 08:09 | 2020-11-03 16:31 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-2 | 2020-11-04 08:19 | 2020-11-04 16:01 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-2 | 2020-11-04 08:15 | 2020-11-04 15:15 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-2 | 2020-11-04 10:27 | 2020-11-04 15:43 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-11-04 15:51 | 2020-11-04 17:10 | 1:19 | S/O | Due to relay test | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-3 | 2020-11-05 08:15 | 2020-11-05 12:59 | 4:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-3 | 2020-11-05 08:04 | 2020-11-05 15:55 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-1 | 2020-11-05 13:12 | 2020-11-05 16:13 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-06 | 2020-11-07 08:27 | 2020-11-07 20:33 | 12:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-3 | 2020-11-07 08:22 | 2020-11-07 15:57 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-3 | 2020-11-07 12:32 | 2020-11-07 14:24 | 1:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-6 | 2020-11-08 09:13 | 2020-11-08 15:48 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 8/8 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Joypurhat | 132/33 kV Transformer-T-4 | 2020-11-08 08:18 | 2020-11-08 16:20 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-11-09 08:12 | 2020-11-09 12:27 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-1 | 2020-11-09 08:11 | 2020-11-09 16:18 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T-3 | 2020-11-09 08:42 | 2020-11-09 08:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-1 | 2020-11-10 08:16 | 2020-11-10 17:07 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-1 | 2020-11-10 08:02 | 2020-11-10 16:52 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T-2 | 2020-11-11 10:20 | 2020-11-11 14:20 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Palshbari 132 kV line-1 | 2020-11-11 08:21 | 2020-11-11 16:04 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-2 | 2020-11-11 08:45 | 2020-11-11 16:27 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-2 | 2020-11-11 08:18 | 2020-11-11 17:07 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T-2 |  | 2020-11-11 19:05 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sirajganj | 230 kV bus-2 | 2020-11-12 07:37 | 2020-11-12 17:38 | 10:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-2 | 2020-11-12 08:21 | 2020-11-12 17:31 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-2 | 2020-11-12 08:29 | 2020-11-12 16:17 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 230 kV bus-1 | 2020-11-13 09:35 | 2020-11-13 16:09 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-3 | 2020-11-14 07:37 | 2020-11-14 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-3 | 2020-11-14 08:27 | 2020-11-14 15:47 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV Transformer-T-1 | 2020-11-14 08:26 | 2020-11-14 15:13 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-3 | 2020-11-15 07:58 | 2020-11-15 17:05 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T-5 | 2020-11-15 08:58 | 2020-11-15 16:08 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-3 | 2020-11-15 08:07 | 2020-11-15 16:17 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-3 | 2020-11-16 09:03 | 2020-11-16 12:46 | 3:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-11-16 12:03 | 2020-11-16 12:46 | 0:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-4 | 2020-11-16 08:25 | 2020-11-16 19:56 | 11:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-4 | 2020-11-17 08:08 | 2020-11-17 15:47 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-1 | 2020-11-18 08:29 | 2020-11-18 16:30 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-4 | 2020-11-19 08:18 | 2020-11-19 15:55 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-1 | 2020-11-19 08:40 | 2020-11-19 16:12 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-1 | 2020-11-19 10:36 | 2020-11-19 15:33 | 4:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-1 | 2020-11-20 08:20 | 2020-11-20 10:25 | 2:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 230 kV Bus-2 | 2020-11-20 09:31 | 2020-11-20 14:56 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/32 kV Transformer-T-1 | 2020-11-20 08:45 | 2020-11-20 12:46 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-2 | 2020-11-21 08:18 | 2020-11-21 16:02 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-4 | 2020-11-21 08:37 | 2020-11-21 15:33 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-1 | 2020-11-21 08:16 | 2020-11-21 16:10 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-2 | 2020-11-22 09:09 | 2020-11-22 16:44 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-3 | 2020-11-22 08:13 | 2020-11-22 16:29 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-2 | 2020-11-22 08:20 | 2020-11-22 16:17 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-11-23 08:22 | 2020-11-23 15:40 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2020-11-24 08:09 | 2020-11-24 16:34 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-3 | 2020-11-24 08:22 | 2020-11-24 16:05 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-1 | 2020-11-25 08:18 | 2020-11-25 16:04 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-3 | 2020-11-25 09:41 | 2020-11-25 16:09 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2020-11-25 08:09 | 2020-11-25 16:34 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-3 | 2020-11-25 08:22 | 2020-11-25 16:05 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2020-11-26 08:56 | 2020-11-26 12:57 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-11-28 08:35 | 2020-11-28 15:16 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-1 | 2020-11-30 08:12 | 2020-11-30 17:00 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 437:41 |  | Unserved Energy : |  | 0
Others :
GPH | 230/33/11 kV Transformer- | 2020-11-12 12:36 | 2020-11-12 13:40 | 1:04 | S/O | Due to primary bushing checking | 0 | 0 | No interruption
Modern still Mill | 132/11 kV Transformer | 2020-11-12 16:10 |  |  | S/O | As per directon of high court | 0 | 0 | No interruption
|  |  | Total | 1:04 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2346:54 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-11-01 08:53 | 2020-11-01 19:43 | 10:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-11-02 09:10 | 2020-11-02 17:43 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Metro Rail 132 kV line | 2020-11-02 09:20 | 2020-11-02 15:30 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttra 132 kV line |  | 2020-11-02 16:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line-1 | 2020-11-03 08:38 | 2020-11-03 15:40 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-11-03 09:10 | 2020-11-03 21:26 | 12:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line | 2020-11-03 15:42 | 2020-11-03 16:42 | 1:00 | S/O | Due to relay test | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line-1 | 2020-11-04 08:34 | 2020-11-04 15:25 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | Rajendrapur-Kodda 132 kV line-1 | 2020-11-04 09:35 | 2020-11-04 15:02 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-RPCL 100 MW 132 kV line | 2020-11-04 08:23 | 2020-11-04 16:10 | 7:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 |  | 2020-11-04 17:26 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kadda Summit 300 MW 132 kV line | 2020-11-05 06:46 | 2020-11-05 08:58 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-11-05 08:42 | 2020-11-05 16:26 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2020-11-05 11:19 | 2020-11-05 18:05 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2020-11-06 07:06 | 2020-11-06 07:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail-Kabirpur 132 kV line-1 | 2020-11-06 06:12 | 2020-11-06 19:22 | 13:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2020-11-07 06:02 | 2020-11-07 16:44 | 10:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2020-11-07 08:13 | 2020-11-07 15:26 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-07 08:16 | 2020-11-07 20:43 | 12:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-11-07 06:57 | 2020-11-07 16:18 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2020-11-08 08:28 | 2020-11-08 09:51 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-08 08:51 | 2020-11-08 17:35 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-11-08 09:54 | 2020-11-08 11:23 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-2 | 2020-11-08 12:59 | 2020-11-08 17:24 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2020-11-09 07:23 | 2020-11-09 16:29 | 9:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 & 2 | 2020-11-09 08:18 | 2020-11-09 09:46 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-09 09:07 | 2020-11-09 17:05 | 7:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | Kadda-Joydevpur 132 kV line-1 | 2020-11-09 08:37 | 2020-11-09 18:33 | 9:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Kabirpur 132 kV line-2 | 2020-11-10 06:50 | 2020-11-10 14:59 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-1 | 2020-11-10 08:35 | 2020-11-10 15:58 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-10 09:17 | 2020-11-10 18:40 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-11-10 12:06 | 2020-11-10 17:02 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-11 07:06 | 2020-11-11 17:28 | 10:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-1 | 2020-11-11 09:09 | 2020-11-11 13:22 | 4:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL P/P 132 kV line-2 | 2020-11-11 09:14 | 2020-11-11 10:56 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 | 2020-11-12 08:41 | 2020-11-12 17:21 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-12 08:41 | 2020-11-12 16:51 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-11-13 08:38 | 2020-11-13 16:51 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-1 | 2020-11-14 07:17 | 2020-11-14 16:58 | 9:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-2 | 2020-11-14 08:24 | 2020-11-14 15:03 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-2 | 2020-11-14 09:18 | 2020-11-14 15:14 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-11-14 10:06 | 2020-11-14 14:45 | 4:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-11-14 11:15 | 2020-11-14 16:59 | 5:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-2 | 2020-11-15 09:03 | 2020-11-15 11:51 | 2:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-11-15 10:21 | 2020-11-15 16:44 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-11-15 09:19 | 2020-11-15 16:59 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-11-15 08:21 | 2020-11-15 14:26 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-11-15 09:48 | 2020-11-15 13:59 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-11-16 07:17 | 2020-11-16 18:07 | 10:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-2 | 2020-11-16 10:05 | 2020-11-16 12:15 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-11-16 09:19 | 2020-11-16 16:59 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-2 | 2020-11-16 08:53 | 2020-11-16 17:14 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-1 | 2020-11-16 09:32 | 2020-11-16 17:07 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-11-17 08:33 | 2020-11-17 16:23 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-11-17 08:07 | 2020-11-17 18:29 | 10:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2020-11-17 10:38 | 2020-11-17 16:46 | 6:08 | S/O | Due to protection test | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-11-18 08:46 | 2020-11-18 15:49 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-2 | 2020-11-18 10:01 | 2020-11-18 17:11 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV line-1 | 2020-11-18 12:33 | 2020-11-18 16:54 | 4:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-1 | 2020-11-18 08:24 | 2020-11-18 16:23 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-11-18 10:56 | 2020-11-18 16:50 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2020-11-19 06:49 | 2020-11-19 08:37 | 1:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-1 | 2020-11-19 09:34 | 2020-11-19 17:34 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV line-2 | 2020-11-19 10:24 | 2020-11-19 16:59 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-11-19 10:11 | 2020-11-19 18:55 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-11-19 09:40 | 2020-11-19 17:19 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-11-19 10:12 | 2020-11-19 15:42 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-11-20 08:34 | 2020-11-20 17:32 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-11-21 08:43 | 2020-11-21 15:26 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2020-11-21 11:05 | 2020-11-21 14:37 | 3:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kishoreganj-Mymensingh 132 kV lkine-2 | 2020-11-21 09:59 | 2020-11-21 17:31 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-1 | 2020-11-22 07:35 | 2020-11-22 17:02 | 9:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-11-22 08:53 | 2020-11-22 14:26 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-11-22 09:14 | 2020-11-22 17:01 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Amibazar | Amibazar-Kallyanpur 132 kV line-2 | 2020-11-23 07:13 | 2020-11-23 21:35 | 14:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2020-11-23 07:30 | 2020-11-23 17:14 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-2 | 2020-11-23 10:38 | 2020-11-23 12:01 | 1:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL P/P 132 kV line-1 | 2020-11-23 09:03 | 2020-11-23 16:12 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-11-23 09:53 | 2020-11-23 16:46 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-2 | 2020-11-24 09:32 | 2020-11-24 16:10 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL P/P 132 kV line-1 | 2020-11-24 10:03 | 2020-11-24 12:03 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2020-11-24 08:27 | 2020-11-24 10:14 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Bibiyana 400 kV line-2 | 2020-11-24 11:36 | 2020-11-24 13:19 | 1:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-2 | 2020-11-25 07:18 | 2020-11-25 15:57 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-2 | 2020-11-25 07:45 | 2020-11-25 16:47 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/S 132 kV line | 2020-11-25 09:10 | 2020-11-25 16:00 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-11-25 12:13 | 2020-11-25 14:40 | 2:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-11-26 07:25 | 2020-11-26 07:25 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/S 132 kV line-1 | 2020-11-26 09:47 | 2020-11-26 16:28 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV lkine-2 | 2020-11-26 08:49 | 2020-11-26 17:30 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-11-27 07:21 | 2020-11-27 21:15 | 13:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-2 | 2020-11-27 07:21 | 2020-11-28 07:27 | 24:06 |  |  | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-1 & 2 | 2020-11-28 07:27 | 2020-11-28 20:00 | 12:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 3/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
UMPL | UMPL-Sherpur 132 kV line-1 | 2020-11-28 09:07 | 2020-11-28 16:48 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2020-11-28 09:54 | 2020-11-28 16:41 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj power-Amibazar 132 kV line-1 | 2020-11-28 10:03 | 2020-11-28 17:14 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2020-11-28 08:32 | 2020-11-28 15:37 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL 132 kV line-2 | 2020-11-28 10:10 | 2020-11-28 16:56 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-RPCL 132 kV line-1 | 2020-11-29 07:52 | 2020-11-29 07:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2020-11-29 08:35 | 2020-11-29 15:19 | 6:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2020-11-30 07:34 | 2020-11-30 17:52 | 10:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV line-1 | 2020-11-29 09:05 | 2020-11-29 16:47 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-11-29 09:23 | 2020-11-29 16:28 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 160 MW -aminbazar 132 kV line-1 | 2020-11-29 09:23 | 2020-11-29 16:20 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL 132 kV line-1 | 2020-11-30 08:36 | 2020-11-30 17:22 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2020-11-30 09:30 | 2020-11-30 16:20 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV line-1 | 2020-11-30 08:51 | 2020-11-30 16:29 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-2 | 2020-11-30 09:54 | 2020-11-30 17:47 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2020-11-30 09:23 | 2020-11-30 16:41 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 749:21 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat -Shyampur 132 kV line | 2020-11-01 07:21 | 2020-11-01 07:21 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2020-11-01 08:19 | 2020-11-01 17:08 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Shyampur 230 kV line-1 | 2020-11-02 07:33 | 2020-11-02 16:19 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2020-11-02 07:40 | 2020-11-02 15:48 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
APR | APR-Hasnabad 230 kV line | 2020-11-02 09:00 | 2020-11-02 09:43 | 0:43 | S/O | Due to relay testing | 0 | 0 | No interruption
Meghanghat | Meghanghat-Shyampur 230 kV line-1 | 2020-11-03 09:21 | 2020-11-03 17:01 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2020-11-03 09:09 | 2020-11-03 15:08 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2020-11-04 08:07 | 2020-11-04 14:22 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-11-05 07:28 | 2020-11-05 16:24 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-2 | 2020-11-05 08:54 | 2020-11-05 16:21 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Cumilla(N) 230 kV line-1 | 2020-11-05 08:42 | 2020-11-05 17:13 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2020-11-05 08:27 | 2020-11-05 16:28 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Cumilla(N) 230 kV line-1 | 2020-11-06 10:17 | 2020-11-06 16:42 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghanghat-Shyampur 230 kV line-2 | 2020-11-07 07:17 | 2020-11-07 16:44 | 9:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-11-07 08:14 | 2020-11-07 15:28 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Shyampur 230 kV line-2 | 2020-11-08 07:29 | 2020-11-08 16:10 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghanghat-Shyampur 230 kV line-2 | 2020-11-09 07:29 | 2020-11-09 16:10 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV line-1 | 2020-11-09 08:30 | 2020-11-09 17:01 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-11-10 08:24 | 2020-11-10 17:02 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghoarshal | Ghoarshal-Bhulta 230 kV line-1 | 2020-11-11 07:35 | 2020-11-11 16:49 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2020-11-11 08:44 | 2020-11-11 13:03 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Cumilla(N) 230 kV line-2 | 2020-11-12 09:01 | 2020-11-12 15:03 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghanghat-Cumilla(N) 230 kV line-2 | 2020-11-13 09:15 | 2020-11-13 14:21 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line-2 | 2020-11-14 06:56 | 2020-11-14 15:27 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Cumilla(N) 230 kV line-2 | 2020-11-14 09:04 | 2020-11-14 15:38 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-2 | 2020-11-15 08:28 | 2020-11-15 16:39 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2020-11-15 08:01 | 2020-11-15 18:21 | 10:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2020-11-16 08:49 | 2020-11-16 14:26 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-2 | 2020-11-17 09:31 | 2020-11-17 14:29 | 4:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV line-2 | 2020-11-17 08:24 | 2020-11-17 18:06 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2020-11-17 08:01 | 2020-11-17 15:09 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV line-2 | 2020-11-18 07:27 | 2020-11-18 17:18 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2020-11-18 11:35 | 2020-11-18 11:35 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Page: 4/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Narsingdi | Narsingdi-Ghorashal 132 kV line-2 | 2020-11-19 09:15 | 2020-11-19 15:12 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghanghat 230 kV line-2 | 2020-11-21 11:01 | 2020-11-21 17:35 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghoarshal | Ghoarshal-Ashuganj 132 kV line-1 | 2020-11-21 10:09 | 2020-11-21 18:11 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Dautch Bangla 132 kV line | 2020-11-22 09:28 | 2020-11-22 13:20 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2020-11-23 06:50 | 2020-11-23 18:55 | 12:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-2 | 2020-11-23 09:28 | 2020-11-23 15:09 | 5:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Dautch Bangla 132 kV line | 2020-11-23 10:34 | 2020-11-23 12:58 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-11-24 07:45 | 2020-11-24 17:05 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Madertek 132 kV line-2 | 2020-11-24 07:29 | 2020-11-24 19:36 | 12:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2020-11-25 08:42 | 2020-11-25 15:00 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati P/S 132 kV line | 2020-11-25 08:54 | 2020-11-25 20:28 | 11:34 | S/O | Due to A/M work | 0 | 0 | No interruption
APR | APR -Shyampur-Hasnabad 230 kV line | 2020-11-25 06:41 | 2020-11-25 06:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2020-11-26 10:12 | 2020-11-26 18:27 | 8:15 | S/O | Due to painting work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2020-11-26 10:59 | 2020-11-26 16:57 | 5:58 | S/O |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sikalbaha 132 kV line | 2020-11-27 08:50 | 2020-11-27 15:01 | 6:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2020-11-27 08:59 | 2020-11-27 16:03 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 & 2 | 2020-11-26 08:23 | 2020-11-26 16:19 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2020-11-29 08:32 | 2020-11-29 19:25 | 10:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV line-1 | 2020-11-30 08:45 | 2020-11-30 15:39 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 369:30 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Chandraghona | Chandraghona-Madunaghat 132 kV line | 2020-11-02 07:39 | 2020-11-02 15:54 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona -Madunaghat 132 kV line-2 | 2020-11-03 07:54 | 2020-11-03 14:23 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2020-11-05 07:41 | 2020-11-05 16:18 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | T.K chemical -Sikalbaha 132 kV line | 2020-11-06 08:54 | 2020-11-06 14:51 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2020-11-07 08:18 | 2020-11-07 14:34 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-07 08:37 | 2020-11-07 16:16 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.k compex 132 kV kV line | 2020-11-08 07:42 | 2020-11-08 15:44 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-08 08:45 | 2020-11-08 15:41 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.k compex 132 kV kV line | 2020-11-09 07:44 | 2020-11-09 14:28 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-09 08:42 | 2020-11-09 16:55 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K Chemical 132 kV line | 2020-11-10 08:30 | 2020-11-10 16:14 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-10 08:40 | 2020-11-10 15:43 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-11-11 08:54 | 2020-11-11 16:08 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-11 08:40 | 2020-11-11 16:19 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line-1 | 2020-11-12 09:06 | 2020-11-12 16:22 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-11-12 08:56 | 2020-11-12 16:41 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2020-11-13 07:25 | 2020-11-13 10:57 | 3:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K 132 kV kV line | 2020-11-13 07:25 | 2020-11-13 11:01 | 3:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-11-15 08:40 | 2020-11-15 16:37 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah P/S | Juldah P/S-Juldah S/S 132 kV line | 2020-11-15 09:04 | 2020-11-15 09:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2020-11-15 12:42 | 2020-11-15 14:41 | 1:59 | S/O | Due to TRTU work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-11-16 08:29 | 2020-11-16 16:30 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2020-11-16 08:41 | 2020-11-16 15:55 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-11-17 08:50 | 2020-11-17 13:47 | 4:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2020-11-17 08:23 | 2020-11-17 16:32 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-18 09:24 | 2020-11-18 14:46 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-11-18 08:47 | 2020-11-18 16:01 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-19 09:19 | 2020-11-19 16:01 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-11-19 08:39 | 2020-11-19 15:28 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-21 12:25 | 2020-11-21 16:18 | 3:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-11-21 09:05 | 2020-11-21 15:50 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV line | 2020-11-21 10:13 | 2020-11-21 13:55 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Khulshi 132 kV line-1 | 2020-11-21 14:30 | 2020-11-21 16:30 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 5/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-11-22 08:37 | 2020-11-22 15:49 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-22 08:39 | 2020-11-22 17:09 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-11-23 09:36 | 2020-11-23 16:41 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-23 09:04 | 2020-11-23 16:24 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2020-11-23 10:46 | 2020-11-23 13:14 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV line-2 | 2020-11-23 13:15 | 2020-11-23 16:15 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-1 | 2020-11-23 15:29 | 2020-11-23 17:21 | 1:52 | S/O | Due to meter change | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-11-24 09:47 | 2020-11-24 16:34 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2020-11-24 12:13 | 2020-11-24 13:50 | 1:37 | S/O | Due to CB tming test | 0 | 0 | No interruption
| Hathazari-Hathazari P/S 132 kV line | 2020-11-24 12:51 | 2020-11-24 13:37 | 0:46 | S/O | Due to CB tming test | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-2 | 2020-11-25 09:40 | 2020-11-25 14:49 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2020-11-26 08:35 | 2020-11-26 16:24 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Hathazari 132 kV line-1 | 2020-11-28 08:56 | 2020-11-28 17:00 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Hathazari 132 kV line-1 | 2020-11-29 08:42 | 2020-11-29 17:10 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Hathazari 132 kV line-2 | 2020-11-30 08:46 | 2020-11-30 16:32 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 289:34 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2020-11-01 12:02 | 2020-11-01 18:04 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| AshuganjS/S-Ashuganj(S) 230 kV line-2 | 2020-11-01 12:17 | 2020-11-01 15:47 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Chaddagram | Chaddagram-Cumilla(N) 132 kV line-1 | 2020-11-04 09:57 | 2020-11-04 18:24 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Feni Lanka 132 kV line |  | 2020-11-07 16:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-11-10 14:43 | 2020-11-10 17:00 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-PHP S/S 132 kV line | 2020-11-11 11:10 | 2020-11-11 17:48 | 6:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj 90 MW 132 kV line-2 | 2020-11-16 15:12 | 2020-11-16 16:51 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-11-17 09:37 | 2020-11-17 16:21 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 90 MW P/S 132 kV line | 2020-11-18 12:30 | 2020-11-18 13:47 | 1:17 | S/O | Due to DC supply checking work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-2 | 2020-11-20 11:02 | 2020-11-20 11:52 | 0:50 | S/O | Due to DC system work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-11-22 08:27 | 2020-11-22 16:36 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Desh Energy 132 kV line-1 | 2020-11-24 09:03 | 2020-11-24 19:25 | 10:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandpur-Chandpur P/S 132 kV line-2 | 2020-11-26 09:01 | 2020-11-26 21:57 | 12:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV lkine-1 | 2020-11-28 08:39 | 2020-11-28 14:39 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2020-11-28 09:07 | 2020-11-28 20:07 | 11:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2020-11-29 12:12 | 2020-11-29 12:12 | 0:00 | S/O | Due to load test | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV line-1 | 2020-11-29 08:58 | 2020-11-29 12:59 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur Desh-Ramganj 132 kV line-1 | 2020-11-29 09:11 | 2020-11-29 16:45 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-1 | 2020-11-30 09:34 | 2020-11-30 14:28 | 4:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur Desh-Ramganj 132 kV line-2 | 2020-11-30 10:08 | 2020-11-30 18:42 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 110:54 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goalpara | Goalpara-Bagerhat 132 kV line | 2020-11-01 07:17 | 2020-11-01 21:12 | 13:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Orion Rupsha | Orion Rupsha-Bagerhat 132 kV line | 2020-11-03 06:22 | 2020-11-03 06:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line | 2020-11-06 06:17 | 2020-11-06 06:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Goalpara-Orion Rupsha-Bagerhat 132 kV line | 2020-11-06 06:19 | 2020-11-06 06:19 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2020-11-06 06:07 | 2020-11-14 16:48 | 202:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 230 kV line-1 | 2020-11-11 09:19 | 2020-11-11 09:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2020-11-13 08:24 | 2020-11-13 12:54 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV line-1 & 2 | 2020-11-13 08:09 | 2020-11-13 13:00 | 4:51 | S/O | Due to D/W work | 10 | 48.5 | Power interruption
| Magura-Narail 132 kV line-1 & 2 | 2020-11-14 07:52 | 2020-11-14 12:34 | 4:42 | S/O | Due to D/W work | 10 | 47 | Power interruption
Goalpara | Goalpara-NWPGCL 132 kV line | 2020-11-15 10:45 | 2020-11-15 15:59 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV line-1 | 2020-11-16 06:57 | 2020-11-16 17:06 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna©-NWPGCL 132 kV line-1 | 2020-11-16 06:59 | 2020-11-16 06:59 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
United | United 150 MW-Patuakhali 132 kV line |  | 2020-11-16 01:12 |  |  | New connection | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-HVDC 230 kV line-2 | 2020-11-17 08:07 | 2020-11-17 17:46 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV line-1 | 2020-11-17 08:19 | 2020-11-17 17:29 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Goalpara | Goalpara-NWPGCL 132 kV line-1 | 2020-11-17 08:28 | 2020-11-17 17:27 | 8:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-HVDC 230 kV line-2 | 2020-11-18 08:15 | 2020-11-18 16:30 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Bheramara HVDC 230 kV line-2 | 2020-11-19 08:16 | 2020-11-19 15:46 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-11-20 06:37 | 2020-11-20 11:16 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj (new) | Gopalganj (new)-Madaripur 132 kV line-3 | 2020-11-21 06:56 | 2020-11-21 21:37 | 14:41 | S/O | Due to D/W work | 10 | 146.8333 | Power interruption
Faridpur | Faridpur-Faridpur P/P 132 kV line | 2020-11-23 10:18 | 2020-11-23 14:48 | 4:30 | S/O | Due to replacement work | 0 | 0 | No interruption
Narail | Narail-Magura 132 kV line-1 | 2020-11-27 10:04 | 2020-11-27 15:02 | 4:58 | S/O | Due to L/A problem | 0 | 0 | No interruption
Magura | Magura-Jhenidah 132 kV line-2 | 2020-11-29 08:09 | 2020-11-29 20:33 | 12:24 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 330:47 |  | Unserved Energy: |  | 242.3333
HVDC Grid Circle :
Ishurdi | Ishurdi-Pabna 132 kV line | 2020-11-01 08:21 | 2020-11-01 16:44 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2020-11-01 08:19 | 2020-11-01 17:00 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC shunt reactor 20DF44 | 2020-11-02 09:27 | 2020-11-02 13:46 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC 01H01,02H05 & 33 kV Trasnformer | 2020-11-07 10:57 | 2020-11-07 14:43 | 3:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV line-2 | 2020-11-08 08:34 | 2020-11-08 14:58 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2020-11-09 09:09 | 2020-11-09 12:56 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara-G.K 132 kV line-1 & 2 | 2020-11-13 08:00 | 2020-11-13 13:27 | 5:27 | S/O | Due to A/M work | 22 | 119.9 | Power interruption
HVDC | Bheramara-Khulna (S) 230 kV line-1 | 2020-11-14 08:06 | 2020-11-14 17:24 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC-Bheramara 230 kV line-1 | 2020-11-21 08:25 | 2020-11-21 15:03 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC-NWPGCL 230 kV line-2 | 2020-11-22 08:30 | 2020-11-22 14:36 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC-Ishurdi 230 kV line-2 | 2020-11-23 09:04 | 2020-11-23 17:11 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC-Ishurdi 230 kV line-3 | 2020-11-24 08:43 | 2020-11-24 17:15 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-1 | 2020-11-24 08:10 | 2020-11-24 16:02 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Magura 132 kV line-1 | 2020-11-25 07:52 | 2020-11-25 15:30 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | Bheramara HVDC-Ishurdi 230 kV line-3 | 2020-11-25 09:20 | 2020-11-25 17:14 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC-Ishurdi 230 kV line-4 | 2020-11-26 09:14 | 2020-11-26 19:43 | 10:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-1 | 2020-11-26 08:06 | 2020-11-26 15:55 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bahrampur 400 kV line-1 | 2020-11-27 09:25 | 2020-11-27 17:09 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bahrampur | Bahrampur-HVDC 230 kV line-1 | 2020-11-28 09:48 | 2020-11-28 17:14 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-2 | 2020-11-28 08:05 | 2020-11-28 15:14 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC-Rajshahi 230 kV line-1 | 2020-11-28 09:27 | 2020-11-28 21:20 | 11:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 230 kV line-2 | 2020-11-29 08:30 | 2020-11-29 22:14 | 13:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV line-2 | 2020-11-30 08:23 | 2020-11-30 17:32 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-2 | 2020-11-30 08:10 | 2020-11-30 16:35 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 186:40 |  | Unserved Energy: |  | 119.9
Bogura Grid Circle :
Natore | Natore-Bogura 132 kV line-1 | 2020-11-01 08:20 | 2020-11-01 20:10 | 11:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur confidenance 132 kV line-2 | 2020-11-02 07:12 | 2020-11-02 12:26 | 5:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-1 | 2020-11-02 09:27 | 2020-11-02 17:29 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-1 | 2020-11-03 09:22 | 2020-11-03 16:39 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-2 | 2020-11-04 08:04 | 2020-11-04 16:45 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-2 | 2020-11-05 09:21 | 2020-11-05 17:20 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur -Lalmonirhat 132 kV line | 2020-11-06 08:01 | 2020-11-06 16:13 | 8:12 | S/O | Due to A/M work | 35 | 287 | Power interruption
| Rangpur -Lalmonirhat 132 kV line | 2020-11-07 08:22 | 2020-11-07 16:45 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Natore 132 kV line-2 | 2020-11-07 09:28 | 2020-11-07 17:17 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Barapukuria P/S 230 kV line-2 | 2020-11-07 08:30 | 2020-11-07 17:14 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 7/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Baghabari | Baghabari-Sirajganj 230 kV line-1 | 2020-11-09 07:44 | 2020-11-09 17:22 | 9:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baghabari-Sirajganj 230 kV line-1 | 2020-11-10 07:49 | 2020-11-10 17:37 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Palshbari 132 kV line-2 | 2020-11-10 08:29 | 2020-11-10 16:15 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-2 | 2020-11-11 07:34 | 2020-11-11 17:37 | 10:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Palshbari 132 kV line-2 | 2020-11-12 08:27 | 2020-11-12 15:27 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2020-11-13 08:42 | 2020-11-13 16:20 | 7:38 | S/O | Due to A/M work | 25 | 190.8333 | Power interruption
| Rangpur-Kurigram 132 kV line | 2020-11-14 08:11 | 2020-11-14 15:53 | 7:42 | S/O | Due to A/M work | 25 | 192.5 | Power interruption
Bogura | Bogura -Sirajganj 230 kV line-1 | 2020-11-14 08:02 | 2020-11-14 16:02 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur confidenance 132 kV line-2 | 2020-11-15 08:55 | 2020-11-15 16:06 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 230 kV line-1 | 2020-11-15 08:08 | 2020-11-15 16:08 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur confidenance 132 kV line-2 | 2020-11-16 08:23 | 2020-11-16 15:46 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 230 kV line-1 | 2020-11-16 09:21 | 2020-11-16 14:02 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Rangpur 132 kV line-1 | 2020-11-17 08:33 | 2020-11-17 16:15 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 230 kV line-2 | 2020-11-17 08:10 | 2020-11-17 16:45 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Rangpur 132 kV line-1 | 2020-11-18 08:18 | 2020-11-18 16:26 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 230 kV line-2 | 2020-11-18 08:13 | 2020-11-19 16:28 | 32:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV line-2 | 2020-11-21 09:00 | 2020-11-21 16:58 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2020-11-21 09:14 | 2020-11-21 16:52 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV line-2 | 2020-11-22 08:23 | 2020-11-22 16:27 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangpur-Barapukuria 132 kV line-1 | 2020-11-23 08:50 | 2020-11-23 15:04 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2020-11-23 08:22 | 2020-11-23 17:34 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2020-11-24 08:40 | 2020-11-24 19:04 | 10:24 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line | 2020-11-24 08:18 | 2020-11-24 15:32 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-2 | 2020-11-24 08:17 | 2020-11-24 16:42 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line | 2020-11-25 08:25 | 2020-11-25 16:01 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2020-11-25 08:18 | 2020-11-25 17:23 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-1 | 2020-11-26 08:32 | 2020-11-26 16:40 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV line | 2020-11-27 08:25 | 2020-11-27 15:03 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2020-11-28 08:45 | 2020-11-28 16:23 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-2 | 2020-11-29 08:38 | 2020-11-29 18:02 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-2 | 2020-11-30 08:34 | 2020-11-30 16:38 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 355:23 |  | Unserved Energy: |  | 670.3333
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-1 | 2020-11-28 08:24 | 2020-11-28 17:40 | 9:16 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 9:16 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2401:25 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November' 2020
| Area | Previous Month (October) 2020) |  |  |  | Current Month (November 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 16 | 10 | 114 | 140 | 9 | 5 | 233 | 247
2 | Dhaka (South) Grid Circle. | 17 | 5 | 43 | 65 | 9 | 1 | 53 | 63
3 | Chattogram Grid Circle. | 10 | 1 | 56 | 67 | 6 | 2 | 68 | 75
4 | Cumilla Grid Circle. | 26 | 7 | 33 | 66 | 15 | 11 | 77 | 103
5 | Khulna Grid Circle. | 15 | 7 | 28 | 50 | 6 | 8 | 105 | 119
6 | HVDC Grid Circle | 9 | 4 | 32 | 45 | 1 | 3 | 46 | 50
7 | Bogura Grid Circle. | 15 | 11 | 80 | 106 | 5 | 8 | 109 | 123
8 | Others | 2 |  | 3 | 5 | 1 |  | 3 | 4
9 | Total | 110 | 45 | 389 | 544 | 52 | 38 | 694 | 784
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November' 2020
| Area | Previous Month (October 2020) |  |  |  | Current Month (November 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 56.04 | 273.73 | 427.01 | 756.78 | 98.66 | 58.67 | 1248.2 | 1405.53
2 | Dhaka (South) Grid Circle. | 829.53 | 14.33 | 52.08 | 895.94 | 41.39 |  | 157.67 | 199.06
3 | Chattogram Grid Circle. | 31.75 |  |  | 31.75 | 35.45 | 148 | 61 | 244.45
4 | Cumilla Grid Circle. | 19.5 | 201.97 | 228.93 | 450.4 | 39 | 426.67 | 681.32 | 1146.99
5 | Khulna Grid Circle. | 90.28 | 17 | 878.17 | 985.45 | 36.92 | 211.2 | 510.08 | 758.2
6 | HVDC Grid Circle | 179.27 | 22.6 | 163.13 | 365 |  |  | 119.9 | 119.9
7 | Bogura Grid Circle. | 274.95 | 64.46 | 427.18 | 766.59 | 30.5 | 189.33 | 670.33 | 890.16
8 | Others
9 | Total | 1481.32 | 594.09 | 2176.5 | 4251.91 | 281.92 | 1033.87 | 3448.5 | 4764.29
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 2 | 3 | 5 | - | 1 | 4 | 1364.2
2 | Dhaka (South) | 5031.6 | 2 | 2 | 4 | 2 | 1 | 1 | 181.04
3 | Chattogram | 2042 | 2 | 1 | 3 | 1 | - | 2 | 220.7
4 | Khulna | 2434 | 8 | 4 | 12 | 5 | - | 7 | 515.87
5 | HVDC | 5954.3 | - | - | - | - | - | - | -
6 | Bogura | 3145.6 | 3 |  | 3 | 1 | 1 | 1 | 38.33
7 | Cumilla | 2981 | 4 |  | 4 |  |  | 4 | 681.32
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 3001.46
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.97%
4 | Khulna | 99.86%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 2 | - | - | 41.33
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | - | 1 | - | 18.02
3 | Chattogram | 917 | - | 2 | - | 2 | 1 | - | 1 | 23.75
4 | Khulna | 1238.4 | - | - | 3 | 3 | - | - | 3 | 242.33
5 | HVDC | 1325 | 501 | - | 1 | 1 | - | - | 1 | 119.9
6 | Bogura | 1803.3 | - | 2 | 3 | 5 | 1 | 1 | 3 | 851.83
7 | Cumilla | 1648.16 | - | 2 | - | 2 | 1 | - | 1 | 465.67
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 1762.83
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.98%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.93% | [7 empty] | Information Management Division
7 | Cumilla | 99.74% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-11-18 | 10 | - | 5 | 6hour 38 min | 2 | 02hour 8 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:November' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 0:44 | 80 | 58.6667 | Due to bursting of PT
Kabirpur | 1 | 1:26 | 40 | 57.3333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Aminbazar | 1 | 0:14 | 80 | 18.6667 | Due to tripping of Amibazar-Lalbagh 132 kV line
Mymensingh | 1 | 0:20 | 68 | 22.6667 | Due to tripping of Mymensingh- Baluka 132 kV line-1 & 2
Tangail | 2 | 6:25 | 82 | 526.1667 | Due to S/D of 132 kV Bus
| 1 | 7:13 | 94 | 678.3667
Kishoreganj | 1 | 8:44 | 5 | 43.6667 | Due to S/D of132/33 kV Transformer-T3
Sonargaon | 2 | 0:19 | 48 | 15.2 | Due to tripping of 132/33 kV Transformers-T1 & T2
|  | 0:49 | 10 | 8.1667 | Due to tripping of 132/33 kV Transformer-T1
Haripur | 1 | 0:47 | 23 | 18.0167 | Due to Haripur-Fatulla 132 kV line
Bhulta | 1 | 8:02 | 10 | 80.3333 | Due to S/D of 400/230 kV Transformer-ATr-1
Syampur | 1 | 0:29 | 160 | 77.3333 | Due to S/D of 230 kV & 132 kV Bus
Madunaghat |  | 0:18 | 39 | 11.7 | Due to 33 kV feeder fault
Khulshi | 1 | 2:28 | 60 | 148 | Due to flashing of 33 kV isolator
Hathazari | 1 | 0:22 | 22 | 8.0667 | Due to tripping of Hathazari-Baroierhat 132 kV line-1 & 2
Baroierhat |  | 2:27 | 6.4 | 15.68 | Due to tripping of Baroierhat-PHP 132 kV line
Bakulia | 1 | 6:06 | 10 | 61 | Due to S/D of132/33 kV Transformer-T2
Chowmuhani | 1 | 0:35 | 90 | 39 | Due to tripping of Chowmuhani-Feni 132 kV line-1 & 2
Sylhet | 1 | 2:08 | 200 | 426.6667 | Due to fire incident on 132/33 kV T4 Transformer & tripping of Sylhet-Fenchugan S/S 132 kV line-1 & 2
Chandpur | 1 | 1:03 | 5 | 5.25 | Due to S/D of 132/33 kV Transformer-T2
Sylhet | 1 | 5:37 | 80 | 449.3333 | Due to S/D to S/D of 33 kV full Bus
Cumilla(S) | 1 | 3:29 | 24 | 83.6 | Due to S/D of132/33 kV Transformer-T1
Sylhet |  | 7:32 | 19 | 143.1333 | Due to S/D of132/33 kV Transformer-T2
Khulna(S) | 1 | 0:28 | 300 | 140 | Due to bursting of 230/132 kV Transformer-T3
Bagerhat | 1 | 2:32 | 15 | 38 | Due to red-hot maintenance of 132/33 kV T3 Transformer
Khulna(C) |  | 1:38 | 3 | 4.9
| 2 | 2:16 | 10 | 22.6667 | Due to red-hot maintenance of 132 kV Bus-2
Gopalganj | 1 | 0:31 | 25 | 12.9167 | Due to tripping of 132/33 kV Transformer-T2
Bagerhat | 1 | 0:06 | 20 | 2 | Due to tripping of 132/33 kV Transformer-T1
Goalpara | 1 | 1:50 | 12 | 22 | Due to tripping of 132/33 kV Transformers-T5 & T6
Faridpur | 1 | 0:13 | 26 | 5.6333 | Due to tripping of 132/33 kV Transformer-T1 & 33 kV Bus
Satkhira | 1 | 0:11 | 15 | 2.75 | Due to S/D of132/33 kV Transformer-T2
Mongla | 1 | 5:59 | 10 | 59.8333 | Due to S/D of132/33 kV Transformer-T1
Gallamari |  | 7:14 | 15 | 108.5 | Due to S/D of 132/33 kV Transformer T2
Bagerhat | 1 | 4:50 | 20 | 96.6667 | Due to S/D of 132 kV Bus-1 & 2
Magura | 2 | 4:51 | 10 | 48.5 | Due to S/D of Magura-Narial 132 kV line-1 & 2
|  | 4:42 | 10 | 47 | Due to S/D of Magura-Narial 132 kV line-1 & 2
Gopalganj (new) | 1 | 14:41 | 10 | 146.8333 | Due to S/D of Gopalganj (new)-Madaripur 132 kV line-3
Bheramara | 1 | 5:27 | 22 | 119.9 | Due to S/D Bheramara- G.K 132 kV line-2
Palashbari | 1 | 1:25 | 14 | 19.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Naogaon | 1 | 0:38 | 15 | 9.5 | Due to tripping of 132/33 kV Transformer-T1
Rajshahi | 1 | 0:27 | 20 | 9 | Due to emergency maintenance of 132/33 kV Transformer-T3
Rangpur | 5 | 16:03 | 10 | 160.5 | Due to bursting of PT
|  | 0:18 | 70 | 21 | Due to tripping of Rangpur-Saidpur 132 kV line-1 & 2
|  | 8:12 | 35 | 287 | Due to S/D of Rangpur -Lalmonirhat 132 kV line
|  | 7:38 | 25 | 190.8333 | Due to S/D of Rangpur-Kurigram 132 kV line
|  | 7:42 | 25 | 192.5
| Total Unserved energy : |  |  | 4764.28 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 124 | 2 | 2020-11-01 | 18:00
2 | Munsiganj | 114 | 2 | 2020-11-01 | 20:00
3 | Sonargaon | 80 | 3 | 2020-11-01 | 0:00
4 | Shyampur | 194 | 3 | 2020-11-01 | 12:00
5 | Bhulta | 185 | 1 | 2020-11-01 | 19:00
6 | Madanganj | 63 | 30 | 2020-11-01 | 21:00
7 | Shitalakhya | 116 | 2 | 2020-11-01 | 16:00
8 | Rahim steel | 81 | 22 | 2020-11-01 | 7:00
9 | Matuail | 87 | 3 | 2020-11-01 | 12:00
10 | Ghorasal | 108 | 12 | 2020-11-01 | 18:00
11 | Narsingdi | 139 | 1 | 2020-11-01 | 21:00
12 | Haripur (SBU) | 114 | 28 | 2020-11-01 | 18:30
13 | Ullon | 70 | 2 | 2020-11-01 | 18:00
14 | Hasnabad | 201 | 2 | 2020-11-01 | 18:00
15 | Magbazar | 103 | 3 | 2020-11-01 | 14:00
16 | Maniknagar | 98 | 3 | 2020-11-01 | 12:00
17 | Bangabhaban | 34 | 1 | 2020-11-01 | 13:00
18 | Narinda | 88 | 3 | 2020-11-01 | 18:00
19 | Dhanmondi | 167 | 1 | 2020-11-01 | 13:00
20 | Lalbag | 86 | 1 | 2020-11-01 | 13:00
21 | Madartek | 64 | 2 | 2020-11-01 | 20:00
22 | Dhaka University | - | - | - | -
23 | Aftabnagar | 34 | 23 | 2020-11-01 | 10:00
24 | Fatullah | 41 | 3 | 2020-11-01 | 10:00
25 | Mirpur | 103 | 3 | 2020-11-01 | 18:00
26 | Kalyanpur | 87 | 2 | 2020-11-01 | 18:00
27 | Gulshan | 124 | 2 | 2020-11-01 | 13:00
28 | Uttara | 88 | 3 | 2020-11-01 | 18:00
29 | Uttara(new) | 33 | 3 | 2020-11-01 | 18:00
30 | Kamrangirchar | 88 | 1 | 2020-11-01 | 18:00
31 | Savar | 139 | 3 | 2020-11-01 | 19:00
32 | Bhasantec | 148 | 1 | 2020-11-01 | 18:00
33 | Agargaon | 70 | 1 | 2020-11-01 | 15:00
34 | Satmosjid | 91 | 1 | 2020-11-01 | 15:00
35 | Tongi | 106 | 14 | 2020-11-01 | 11:00
36 | Kabirpur | 246 | 3 | 2020-11-01 | 18:30
37 | Basundhara | 139 | 1 | 2020-11-01 | 13:00
38 | Manikganj | 74 | 2 | 2020-11-01 | 19:30
39 | Joydevpur | 148 | 3 | 2020-11-01 | 18:30
40 | New Tongi | 103 | 1 | 2020-11-01 | 11:00
41 | Kodda | 229 | 12 | 2020-11-01 | 15:00
42 | Dhamrai | 90 | 2 | 2020-11-01 | 18:30
43 | Rajendrapur | 98 | 3 | 2020-11-01 | 18:30
44 | Valuka | 96 | 1 | 2020-11-01 | 18:00
45 | Tangail | 184 | 2 | 2020-11-01 | 19:00
46 | Mymensing | 203 | 2 | 2020-11-01 | 18:00
47 | Kishorganj | 124 | 3 | 2020-11-01 | 22:00
48 | Netrokona | 99 | 2 | 2020-11-01 | 19:00
49 | Jamalpur | 120 | 1 | 2020-11-01 | 21:00
50 | Sherpur | 102 | 3 | 2020-11-01 | 18:30
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
51 | Srimongal | 46 | 3 | 2020-11-01 | 18:00
52 | Shahjibazar | 110 | 3 | 2020-11-01 | 22:00
53 | Fenchuganj | 44 | 3 | 2020-11-01 | 18:30
54 | Kulawara | 43 | 3 | 2020-11-01 | 18:00
55 | Sylhet | 125 | 3 | 2020-11-01 | 18:00
56 | Chatak | 30 | 3 | 2020-11-01 | 19:30
57 | Sunamganj | 41 | 1 | 2020-11-01 | 20:00
58 | Bianibazar | 59 | 2 | 2020-11-01 | 18:30
59 | Cumilla (S) | 152 | 3 | 2020-11-01 | 18:00
60 | Cumilla(N) | 103 | 2 | 2020-11-01 | 20:00
61 | Chandpur | 91 | 2 | 2020-11-01 | 18:30
62 | Feni | 105 | 9 | 2020-11-01 | 19:00
63 | Chowmuhani | 154 | 3 | 2020-11-01 | 19:30
64 | Ashuganj | 54 | 2 | 2020-11-01 | 23:00
65 | Daudkandi | 134 | 2 | 2020-11-01 | 23:00
66 | B.Baria | 146 | 3 | 2020-11-01 | 21:00
67 | Ramganj | 92 | 3 | 2020-11-01 | 19:30
68 | Chaddagram | 32 | 3 | 2020-11-01 | 19:00
69 | PHP | 11 | 1 | 2020-11-01 | 13:00
70 | Madanhat | 60 | 2 | 2020-11-01 | 21:00
71 | Hathazari | 95 | 3 | 2020-11-01 | 18:00
72 | Khulshi | 198 | 3 | 2020-11-01 | 10:00
73 | Halishahar | 142 | 16 | 2020-11-01 | 15:00
74 | Baraulia | 158 | 1 | 2020-11-01 | 11:00
75 | Sikalbaha | 25 | 3 | 2020-11-01 | 18:00
76 | Dohazari | 80 | 5 | 2020-11-01 | 19:00
77 | Cox'sbazar | 99 | 9 | 2020-11-01 | 19:00
78 | Chandraghona | 28 | 2 | 2020-11-01 | 18:00
79 | Kaptai | 4.2 | 4 | 2020-11-01 | 18:00
80 | A. Khaer Stl. | 12 | 29 | 2020-11-01 | 11:00
81 | Bakulia | 97 | 2 | 2020-11-01 | 12:00
82 | Julda | 24 | 17 | 2020-11-01 | 15:00
83 | TK chemical | 27 | 9 | 2020-11-01 | 18:00
84 | Modern Steel | 18 | 30 | 2020-11-01 | 19:30
85 | Shahmirpur | 23 | 28 | 2020-11-01 | 14:00
86 | Khagrachhari | 22 | 3 | 2020-11-01 | 1:00
87 | Matarbari | 34 | 3 | 2020-11-01 | 19:30
88 | Baroiar Hat | 34 | 25 | 2020-11-01 | 18:00
89 | Rangamati | 12 | 2 | 2020-11-01 | 18:30
90 | Abul Khair 230 | 189 | 7 | 2020-11-01 | 9:00
91 | BSRM | 161 | 1 | 2020-11-01 | 4:00
92 | GPH Ispat | 87 | 2 | 2020-11-01 | 18:00
93 | Goalpara | 30 | 2 | 2020-11-01 | 14:00
94 | Central s/s | 90 | 24 | 2020-11-01 | 18:00
95 | Noapara | 54 | 3 | 2020-11-01 | 18:30
96 | Jashore | 108 | 3 | 2020-11-01 | 18:00
97 | Benapol | 48 | 3 | 2020-11-01 | 19:30
98 | Jhenidah | 98 | 2 | 2020-11-01 | 18:30
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
99 | Bottail | 120 | 1 | 2020-11-01 | 18:30
100 | G.K Project | 49 | 1 | 2020-11-01 | 18:30
101 | Faridpur | 170 | 2 | 2020-11-01 | 18:30
102 | Madaripur | 87 | 3 | 2020-11-01 | 20:00
103 | Sariatpur | 65 | 3 | 2020-11-01 | 19:30
104 | Gopalganj | 86 | 1 | 2020-11-01 | 18:00
105 | Bagerhat | 90 | 2 | 2020-11-01 | 20:00
106 | Mongla | 40 | 8 | 2020-11-01 | 18:00
107 | Satkhira | 104 | 3 | 2020-11-01 | 19:30
108 | Gallamari | 47 | 9 | 2020-11-01 | 13:00
109 | Magura | 46 | 1 | 2020-11-01 | 18:00
110 | Norail | 39 | 3 | 2020-11-01 | 18:30
111 | Chuadanga | 85 | 1 | 2020-11-01 | 19:30
112 | Barsal(N) | 39 | 3 | 2020-11-01 | 19:30
113 | Barsal(S) | 90 | 2 | 2020-11-01 | 19:00
114 | Patuakhali | 100 | 2 | 2020-11-01 | 21:00
115 | Bhandaria | 50 | 2 | 2020-11-01 | 21:00
116 | Borhan Uddin | 36 | 3 | 2020-11-01 | 21:00
117 | Ishurdi | 60 | 1 | 2020-11-01 | 21:00
118 | Ruppur Paromanobik | 2 | 1 | 2020-11-01 | 7:00
119 | Natore | 110 | 2 | 2020-11-01 | 18:30
120 | Bogura | 154 | 2 | 2020-11-01 | 19:00
121 | Naogaon | 102 | 2 | 2020-11-01 | 19:30
122 | Rajshahi | 135 | 2 | 2020-11-01 | 19:00
123 | Rajshahi New | 13 | 1 | 2020-11-01 | 19:30
124 | C.Nawabganj | 65 | 2 | 2020-11-01 | 18:30
125 | Amnura | 42 | 1 | 2020-11-01 | 18:30
126 | Pabna | 111 | 1 | 2020-11-01 | 18:30
127 | Shahjadpur | 98 | 2 | 2020-11-01 | 18:30
128 | Serajganj | 97 | 1 | 2020-11-01 | 19:30
129 | Niyamatpur | 50 | 2 | 2020-11-01 | 20:00
130 | Joypurhat | 51 | 1 | 2020-11-01 | 19:30
131 | Sherpur(Bogura) | 46 | 1 | 2020-11-01 | 18:00
132 | Mohastangar | 42 | 1 | 2020-11-01 | 19:00
133 | Rangpur | 139 | 1 | 2020-11-01 | 18:30
134 | Lalmonirhat | 65 | 19 | 2020-11-01 | 18:00
135 | Saidpur | 105 | 2 | 2020-11-01 | 18:00
136 | Purbasadipur | 88 | 1 | 2020-11-01 | 19:00
137 | Thakurgaon | 69 | 2 | 2020-11-01 | 19:00
138 | Palshbari | 103 | 1 | 2020-11-01 | 18:30
139 | Barapukuria | 46 | 1 | 2020-11-01 | 20:00
140 | Panchugar | 46 | 2 | 2020-11-01 | 19:30
141 | Joldhaka | 25 | 19 | 2020-11-01 | 18:00
142 | Kurigram | 52 | 14 | 2020-11-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:November' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 4108 | 03.11.2020 | 18:00
Chattogram | 1220 | 03.11.2020 | 23:00
Khulna | 1360 | 02.11.2020 | 19:00
Rajshahi | 1139 | 02.11.2020 | 19:00
Cumilla | 1034 | 03.11.2020 | 19:30
Mymensingh | 899 | 02.11.2020 | 18:30
Sylhet | 481 | 03.11.2020 | 19:00
Barisal | 309 | 03.11.2020 | 21:00
Rangpur | 689 | 01.11.2020 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 419 | 27 | 2020-11-01 | 18:30 | 369 | 17 | 2020-11-01 | 11:00
2 | Bheramara | 400 | 414 | 13 | 2020-11-01 | 9:00 | 369 | 16 | 2020-11-01 | 22:00
3 | Ashuganj(N) | 400 | 401 | 26 | 2020-11-01 | 4:00 | 356 | 7 | 2020-11-01 | 11:00
4 | Payra | 400 | 423 | 5 | 2020-11-01 | 18:00 | 400 | 9 | 2020-11-01 | 19:30
5 | Kaliakoir | 400 | 412 | 17 | 2020-11-01 | 8:00 | 363 | 24 | 2020-11-01 | 12:00
6 | Bhulta | 400 | 396 | 26 | 2020-11-01 | 19:00 | 353 | 7 | 2020-11-01 | 11:00
7 | Gopalganj | 400 | 426 | 6 | 2020-11-01 | 7:00 | 384 | 2 | 2020-11-01 | 18:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 27 | 2020-11-01 | 1:00 | 222 | 11 | 2020-11-01 | 15:00
2 | Ishurdi | 230 | 241 | 24 | 2020-11-01 | 3:00 | 223 | 12 | 2020-11-01 | 12:00
3 | Ashuganj | 230 | 241 | 26 | 2020-11-01 | 19:00 | 220 | 7 | 2020-11-01 | 11:00
4 | Serajganj | 230 | 235 | 14 | 2020-11-01 | 6:00 | 223 | 23 | 2020-11-01 | 12:00
5 | Baghabari | 230 | 243 | 18 | 2020-11-01 | 2:00 | 226 | 17 | 2020-11-01 | 9:00
6 | Barapukuria | 230 | 237 | 1 | 2020-11-01 | 5:00 | 220 | 2 | 2020-11-01 | 18:00
7 | Bogura | 230 | 232 | 30 | 2020-11-01 | 2:00 | 217 | 16 | 2020-11-01 | 12:00
8 | Rajshahi | 230 | 235 | 17 | 2020-11-01 | 6:00 | 207 | 17 | 2020-11-01 | 17:00
9 | Khulna South | 230 | 245 | 18 | 2020-11-01 | 1:00 | 203 | 18 | 2020-11-01 | 4:00
10 | Rampura | 230 | 234 | 28 | 2020-11-01 | 2:00 | 215 | 4 | 2020-11-01 | 14:00
11 | Haripur | 230 | 233 | 27 | 2020-11-01 | 23:00 | 213 | 7 | 2020-11-01 | 11:00
12 | Hasnabad | 230 | 236 | 27 | 2020-11-01 | 19:00 | 204 | 15 | 2020-11-01 | 12:00
13 | Shyampur | 230 | 234 | 27 | 2020-11-01 | 18:00 | 220 | 1 | 2020-11-01 | 12:00
14 | Aminbazar | 230 | 238 | 27 | 2020-11-01 | 17:00 | 205 | 15 | 2020-11-01 | 12:00
15 | Tongi | 230 | 239 | 27 | 2020-11-01 | 1:00 | 207 | 7 | 2020-11-01 | 15:00
16 | Comilla (N) | 230 | 241 | 27 | 2020-11-01 | 18:30 | 220 | 17 | 2020-11-01 | 11:00
17 | Hathazari | 230 | 230 | 6 | 2020-11-01 | 18:00 | 209 | 26 | 2020-11-01 | 12:00
18 | Megnaghat | 230 | 241 | 17 | 2020-11-01 | 20:00 | 214 | 8 | 2020-11-01 | 23:00
19 | Fenchuganj | 230 | 248 | 27 | 2020-11-01 | 17:00 | 222 | 17 | 2020-11-01 | 10:00
20 | Siddhirganj | 230 | 236 | 27 | 2020-11-01 | 17:00 | 214 | 7 | 2020-11-01 | 11:00
21 | Maniknagar | 230 | 235 | 27 | 2020-11-01 | 18:30 | 209 | 15 | 2020-11-01 | 12:00
22 | Old Airport | 230 | 252 | 17 | 2020-11-01 | 17:00 | 204 | 15 | 2020-11-01 | 12:00
23 | Barisal | 230 | 253 | 4 | 2020-11-01 | 18:00 | 216 | 17 | 2020-11-01 | 10:00
24 | AKSML | 230 | 227 | 24 | 2020-11-01 | 19:30 | 210 | 26 | 2020-11-01 | 12:00
25 | BSRM | 230 | 229 | 6 | 2020-11-01 | 17:00 | 214 | 8 | 2020-11-01 | 3:00
26 | Bibiyana | 230 | 248 | 27 | 2020-11-01 | 18:00 | 222 | 17 | 2020-11-01 | 11:00
27 | Bhulta | 230 | 237 | 28 | 2020-11-01 | 19:00 | 215 | 7 | 2020-11-01 | 17:00
28 | Ashuganj (S) | 230 | 239 | 26 | 2020-11-01 | 19:00 | 219 | 7 | 2020-11-01 | 11:00
29 | Kaliakoir | 230 | 238 | 24 | 2020-11-01 | 3:00 | 206 | 15 | 2020-11-01 | 12:00
30 | GPH | 230 | 239 | 17 | 2020-11-01 | 4:00 | 209 | 26 | 2020-11-01 | 11:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 21 | 2020-11-01 | 0.83333 | 127 | 7 | 2020-11-01 | 0.45833
2 | Munsiganj | 132 | 141 | 21 | 2020-11-01 | 0.75 | 125 | 7 | 2020-11-01 | 0.45833
3 | Sonargaon | 132 | 139 | 27 | 2020-11-01 | 0.75 | 125 | 7 | 2020-11-01 | 0.45833
4 | Shyampur | 132 | 137 | 16 | 2020-11-01 | 0.79167 | 124 | 7 | 2020-11-01 | 0.45833
5 | Bhulta | 132 | 134 | 27 | 2020-11-01 | 0.54167 | 120 | 12 | 2020-11-01 | 0.5
6 | Madanganj | 132 | 140 | 26 | 2020-11-01 | 0.83333 | 124 | 14 | 2020-11-01 | 0.45833
7 | Shitalakhya | 132 | 144 | 24 | 2020-11-01 | 0.041667 | 121 | 7 | 2020-11-01 | 0.45833
8 | Rahim Steal | 132 | 139 | 24 | 2020-11-01 | 0.33333 | 127 | 7 | 2020-11-01 | 0.45833
9 | Matuail | 132 | 140 | 21 | 2020-11-01 | 0.83333 | 127 | 7 | 2020-11-01 | 0.45833
10 | Ghorasal | 132 | 140 | 25 | 2020-11-01 | 0.75 | 130 | 12 | 2020-11-01 | 0.625
11 | Narsinghdi | 132 | 138 | 8 | 2020-11-01 | 0.20833 | 123 | 1 | 2020-11-01 | 0.5
12 | Haripur (SBU) | 132 | 140 | 21 | 2020-11-01 | 0.79167 | 127 | 11 | 2020-11-01 | 0.45833
13 | Ullon | 132 | 136 | 20 | 2020-11-01 | 0.20833 | 115 | 1 | 2020-11-01 | 0.54167
14 | Hasnabad | 132 | 145 | 24 | 2020-11-01 | 0.33333 | 120 | 15 | 2020-11-01 | 0.5
15 | Magbazar | 132 | 136 | 21 | 2020-11-01 | 0.83333 | 122 | 3 | 2020-11-01 | 0.8125
16 | Maniknagar | 132 | 139 | 27 | 2020-11-01 | 0.70833 | 121 | 15 | 2020-11-01 | 0.5
17 | Bangabhaban | 132 | 139 | 27 | 2020-11-01 | 0.70833 | 121 | 15 | 2020-11-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
18 | Narinda | 132 | 139 | 27 | 2020-11-01 | 0.70833 | 121 | 15 | 2020-11-01 | 0.5
19 | Dhanmondi | 132 | 136 | 20 | 2020-11-01 | 0.20833 | 115 | 1 | 2020-11-01 | 0.54167
20 | Lalbag | 132 | 139 | 6 | 2020-11-01 | 0.75 | 119 | 24 | 2020-11-01 | 0.5
21 | Madartek | 132 | 136 | 24 | 2020-11-01 | 0.16667 | 123 | 3 | 2020-11-01 | 0.5
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Aftabnagar | 132 | 138 | 24 | 2020-11-01 | 0.20833 | 125 | 25 | 2020-11-01 | 0.5
24 | Fatullah | 132 | 138 | 16 | 2020-11-01 | 0.83333 | 125 | 7 | 2020-11-01 | 0.5
25 | Mirpur | 132 | 139 | 6 | 2020-11-01 | 0.75 | 120 | 24 | 2020-11-01 | 0.5
26 | Kalyanpur | 132 | 140 | 6 | 2020-11-01 | 0.75 | 121 | 13 | 2020-11-01 | 0.5
27 | Gulshan | 132 | 135 | 6 | 2020-11-01 | 0.75 | 122 | 15 | 2020-11-01 | 0.5
28 | Uttara | 132 | 138 | 6 | 2020-11-01 | 0.75 | 121 | 24 | 2020-11-01 | 0.5
29 | Uttara(New) | 132 | 138 | 6 | 2020-11-01 | 0.77083 | 119 | 24 | 2020-11-01 | 0.5
30 | Kamrangirchar | 132 | 142 | 24 | 2020-11-01 | 0.25 | 118 | 7 | 2020-11-01 | 0.45833
31 | Savar | 132 | 140 | 21 | 2020-11-01 | 0.25 | 120 | 15 | 2020-11-01 | 12;00
32 | Bhasantec | 132 | 139 | 6 | 2020-11-01 | 0.75 | 122 | 15 | 2020-11-01 | 12;00
33 | Agargaon | 132 | 140 | 6 | 2020-11-01 | 0.75 | 124 | 8 | 2020-11-01 | 0.5
34 | Satmosjid | 132 | 140 | 22 | 2020-11-01 | 0.95833 | 123 | 15 | 2020-11-01 | 12;00
35 | Tongi | 132 | 141 | 8 | 2020-11-01 | 0.75 | 129 | 16 | 2020-11-01 | 0.41667
36 | Kabirpur | 132 | 139 | 6 | 2020-11-01 | 0.29167 | 123 | 15 | 2020-11-01 | 0.58333
37 | Basundhara | 132 | 136 | 21 | 2020-11-01 | 0.875 | 123 | 1 | 2020-11-01 | 0.5
38 | Manikganj | 132 | 143 | 8 | 2020-11-01 | 0.75 | 127 | 3 | 2020-11-01 | 0.5
39 | Joydevpur | 132 | 144 | 24 | 2020-11-01 | 0.95833 | 128 | 5 | 2020-11-01 | 0.625
40 | New Tongi | 132 | 141 | 27 | 2020-11-01 | 0.70833 | 127 | 11 | 2020-11-01 | 0.45833
41 | Kodda | 132 | 140 | 8 | 2020-11-01 | 0.75 | 122 | 11 | 2020-11-01 | 0.45833
42 | Dhamrai | 132 | 137 | 6 | 2020-11-01 | 0.875 | 122 | 11 | 2020-11-01 | 0.54167
43 | Rajendrapur | 132 | 139 | 8 | 2020-11-01 | 0.77083 | 120 | 14 | 2020-11-01 | 0.5
44 | Valuka | 132 | 132 | 26 | 2020-11-01 | 0.95833 | 114 | 1 | 2020-11-01 | 0.75
45 | Tangail | 132 | 136 | 6 | 2020-11-01 | 0.91667 | 107 | 6 | 2020-11-01 | 0.54167
46 | Mymensing | 132 | 134 | 20 | 2020-11-01 | 0.375 | 116 | 3 | 2020-11-01 | 0.75
47 | Kishorganj | 132 | 133 | 27 | 2020-11-01 | 0.70833 | 119 | 3 | 2020-11-01 | 0.75
48 | Netrokona | 132 | 132 | 20 | 2020-11-01 | 0.083333 | 111 | 3 | 2020-11-01 | 0.8125
49 | Jamalpur | 132 | 140 | 3 | 2020-11-01 | 0.70833 | 117 | 6 | 2020-11-01 | 0.54167
50 | Sherpur | 132 | 138 | 3 | 2020-11-01 | 0.70833 | 117 | 9 | 2020-11-01 | 0.29167
51 | Srimongal | 132 | 140 | 6 | 2020-11-01 | 0.75 | 132 | 2 | 2020-11-01 | 0.70833
52 | Shahjibazar | 132 | 139 | 18 | 2020-11-01 | 0.33333 | 129 | 3 | 2020-11-01 | 0.8125
53 | Fenchuganj | 132 | 139 | 6 | 2020-11-01 | 0.91667 | 127 | 17 | 2020-11-01 | 0.45833
54 | Khulawara | 132 | 138 | 6 | 2020-11-01 | 0.75 | 132 | 2 | 2020-11-01 | 0.77083
55 | Sylhet | 132 | 137 | 20 | 2020-11-01 | 0.33333 | 128 | 19 | 2020-11-01 | 0.8125
56 | Chattak | 132 | 136 | 29 | 2020-11-01 | 0.083333 | 126 | 19 | 2020-11-01 | 0.8125
57 | Sunamganj | 132 | 135 | 8 | 2020-11-01 | 0.29167 | 126 | 19 | 2020-11-01 | 0.8125
58 | Biani Bazar | 132 | 136 | 16 | 2020-11-01 | 0.29167 | 128 | 2 | 2020-11-01 | 0.77083
59 | Comilla(South) | 132 | 132 | 16 | 2020-11-01 | 0.083333 | 122 | 2 | 2020-11-01 | 0.75
60 | Comilla (North) | 132 | 142 | 24 | 2020-11-01 | 0.77083 | 130 | 7 | 2020-11-01 | 0.45833
61 | Chandpur | 132 | 145 | 28 | 2020-11-01 | 0.41667 | 128 | 3 | 2020-11-01 | 0.83333
62 | Feni | 132 | 140 | 21 | 2020-11-01 | 0.75 | 127 | 7 | 2020-11-01 | 0.625
63 | Chowmuhani | 132 | 139 | 27 | 2020-11-01 | 0.75 | 123 | 23 | 2020-11-01 | 0.29167
64 | Ashuganj | 132 | 138 | 28 | 2020-11-01 | 0.83333 | 130 | 12 | 2020-11-01 | 0.29167
65 | Daudkandi | 132 | 140 | 27 | 2020-11-01 | 0.70833 | 126 | 15 | 2020-11-01 | 0.5
66 | Brahminbaria | 132 | 134 | 20 | 2020-11-01 | 0.375 | 125 | 3 | 2020-11-01 | 0.875
67 | Ramganj | 132 | 135 | 27 | 2020-11-01 | 0.8125 | 116 | 13 | 2020-11-01 | 0.8125
68 | Chaddagram | 132 | 140 | 17 | 2020-11-01 | 0.77083 | 125 | 4 | 2020-11-01 | 0.625
69 | PHP | 132 | 138 | 16 | 2020-11-01 | 0.77083 | 125 | 4 | 2020-11-01 | 0.625
70 | Madanhat | 132 | 139 | 6 | 2020-11-01 | 0.75 | 127 | 26 | 2020-11-01 | 0.45833
71 | Hathazari | 132 | 137 | 6 | 2020-11-01 | 0.75 | 127 | 26 | 2020-11-01 | 0.5
72 | Khulshi | 132 | 136 | 8 | 2020-11-01 | 0.75 | 122 | 26 | 2020-11-01 | 0.5
73 | Halishahar | 132 | 137 | 6 | 2020-11-01 | 0.75 | 123 | 26 | 2020-11-01 | 0.45833
74 | Baraulia | 132 | 137 | 22 | 2020-11-01 | 0.75 | 126 | 8 | 2020-11-01 | 0.25
75 | Sikalbaha | 132 | 139 | 8 | 2020-11-01 | 0.75 | 125 | 26 | 2020-11-01 | 0.45833
76 | Dohazari | 132 | 137 | 8 | 2020-11-01 | 0.75 | 123 | 15 | 2020-11-01 | 0.66667
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
77 | Cox'sbazar | 132 | 129 | 6 | 2020-11-01 | 0.375 | 112 | 24 | 2020-11-01 | 0.77083
78 | Chandraghona | 132 | 137 | 6 | 2020-11-01 | 0.75 | 127 | 26 | 2020-11-01 | 0.45833
79 | Kaptai | 132 | 137 | 6 | 2020-11-01 | 0.75 | 129 | 30 | 2020-11-01 | 0.41667
80 | A. Khaer Stl. | 132 | 135 | 6 | 2020-11-01 | 0.75 | 124 | 26 | 2020-11-01 | 0.5
81 | Bakulia | 132 | 138 | 8 | 2020-11-01 | 0.75 | 123 | 26 | 2020-11-01 | 0.45833
82 | Julda | 132 | 140 | 8 | 2020-11-01 | 0.75 | 123 | 26 | 2020-11-01 | 0.45833
83 | TK Chemical | 132 | 138 | 8 | 2020-11-01 | 0.75 | 125 | 26 | 2020-11-01 | 0.45833
84 | Modern Steel | 132 | 141 | 4 | 2020-11-01 | 0.25 | 122 | 26 | 2020-11-01 | 0.5
85 | Shahmirpur | 132 | 139 | 8 | 2020-11-01 | 0.75 | 124 | 26 | 2020-11-01 | 0.45833
86 | Khagrachhari | 132 | 136 | 6 | 2020-11-01 | 0.77083 | 127 | 26 | 2020-11-01 | 0.45833
87 | Matarbari | 132 | 132 | 9 | 2020-11-01 | 0.33333 | 119 | 11 | 2020-11-01 | 0.54167
88 | Baroiar Hat | 132 | 138 | 16 | 2020-11-01 | 0.79167 | 125 | 7 | 2020-11-01 | 0.45833
89 | Rangamati | 132 | 136 | 6 | 2020-11-01 | 0.75 | 127 | 26 | 2020-11-01 | 0.45833
90 | Goalpara | 132 | 141 | 5 | 2020-11-01 | 0.75 | 107 | 1 | 2020-11-01 | 0.54167
91 | Khulna Central | 132 | 140 | 5 | 2020-11-01 | 0.25 | 106 | 1 | 2020-11-01 | 0.54167
92 | Noapara | 132 | 138 | 5 | 2020-11-01 | 0.25 | 108 | 1 | 2020-11-01 | 0.54167
93 | Jessore | 132 | 137 | 19 | 2020-11-01 | 0.16667 | 104 | 1 | 2020-11-01 | 0.54167
94 | Benapol | 132 | 136 | 13 | 2020-11-01 | 0.125 | 114 | 1 | 2020-11-01 | 0.54167
95 | Jhenida | 132 | 136 | 24 | 2020-11-01 | 0.041667 | 112 | 2 | 2020-11-01 | 0.77083
96 | Bottail | 132 | 138 | 7 | 2020-11-01 | 0.25 | 123 | 2 | 2020-11-01 | 0.75
97 | G.K Project | 132 | 142 | 23 | 2020-11-01 | 0.20833 | 134 | 2 | 2020-11-01 | 0.75
98 | Faridpur | 132 | 139 | 7 | 2020-11-01 | 0.125 | 121 | 2 | 2020-11-01 | 0.75
99 | Madaripur | 132 | 143 | 16 | 2020-11-01 | 0.41667 | 126 | 2 | 2020-11-01 | 0.75
100 | Sariatpur | 132 | 141 | 7 | 2020-11-01 | 0.33333 | 123 | 2 | 2020-11-01 | 0.75
101 | Gopalganj | 132 | 144 | 23 | 2020-11-01 | 0.25 | 125 | 2 | 2020-11-01 | 0.75
102 | Bagerhat | 132 | 140 | 5 | 2020-11-01 | 0.75 | 100 | 1 | 2020-11-01 | 0.54167
103 | Mongla | 132 | 137 | 27 | 2020-11-01 | 0.70833 | 108 | 1 | 2020-11-01 | 0.54167
104 | Satkhira | 132 | 139 | 5 | 2020-11-01 | 0.25 | 120 | 2 | 2020-11-01 | 0.77083
105 | Gallamari | 132 | 142 | 5 | 2020-11-01 | 0.75 | 122 | 17 | 2020-11-01 | 0.70833
106 | Magura | 132 | 135 | 6 | 2020-11-01 | 0.25 | 111 | 2 | 2020-11-01 | 0.77083
107 | Norail | 132 | 134 | 26 | 2020-11-01 | 0.16667 | 109 | 2 | 2020-11-01 | 0.77083
108 | Chuadanga | 132 | 133 | 24 | 2020-11-01 | 0.041667 | 103 | 1 | 2020-11-01 | 0.54167
109 | Barisal(N) | 132 | 143 | 26 | 2020-11-01 | 0.041667 | 126 | 2 | 2020-11-01 | 0.75
110 | Barisal(S) | 132 | 141 | 23 | 2020-11-01 | 0.20833 | 125 | 2 | 2020-11-01 | 0.75
111 | Patuakhali | 132 | 140 | 20 | 2020-11-01 | 0.79167 | 121 | 1 | 2020-11-01 | 0.79167
112 | Bhandaria | 132 | 140 | 16 | 2020-11-01 | 0.375 | 110 | 2 | 2020-11-01 | 0.75
113 | Ishurdi | 132 | 140 | 24 | 2020-11-01 | 0.041667 | 131 | 12 | 2020-11-01 | 0.5
114 | Ruppur paromanobik | 132 | 140 | 24 | 2020-11-01 | 0.083333 | 131 | 3 | 2020-11-01 | 0.75
115 | Natore | 132 | 139 | 5 | 2020-11-01 | 0.125 | 131 | 15 | 2020-11-01 | 0.5
116 | Bogra | 132 | 140 | 20 | 2020-11-01 | 0.16667 | 129 | 15 | 2020-11-01 | 0.5
117 | Noagaon | 132 | 136 | 25 | 2020-11-01 | 0.16667 | 124 | 30 | 2020-11-01 | 0.375
118 | Rajshahi | 132 | 140 | 24 | 2020-11-01 | 0.041667 | 130 | 16 | 2020-11-01 | 0.5
119 | Rajshahi New | 132 | 141 | 7 | 2020-11-01 | 0.25 | 131 | 15 | 2020-11-01 | 0.5
120 | C.Nawabganj | 132 | 139 | 8 | 2020-11-01 | 0.75 | 128 | 2 | 2020-11-01 | 0.5
121 | Amnura | 132 | 140 | 3 | 2020-11-01 | 0.79167 | 129 | 2 | 2020-11-01 | 0.5
122 | Pabna | 132 | 139 | 7 | 2020-11-01 | 0.125 | 124 | 2 | 2020-11-01 | 0.5
123 | Shahjadpur | 132 | 143 | 13 | 2020-11-01 | 0.625 | 134 | 3 | 2020-11-01 | 0.66667
124 | Serajganj | 132 | 136 | 5 | 2020-11-01 | 0.58333 | 125 | 25 | 2020-11-01 | 0.54167
125 | Niyamatpur | 132 | 136 | 28 | 2020-11-01 | 0.20833 | 122 | 30 | 2020-11-01 | 0.33333
126 | Joypurhat | 132 | 138 | 28 | 2020-11-01 | 0.16667 | 124 | 30 | 2020-11-01 | 0.33333
127 | Sherpur(Bogura) | 132 | 140 | 24 | 2020-11-01 | 0.125 | 128 | 25 | 2020-11-01 | 0.25
128 | Mohastangor | 132 | 138 | 19 | 2020-11-01 | 0.16667 | 127 | 19 | 2020-11-01 | 0.5
129 | Rangpur | 132 | 133 | 1 | 2020-11-01 | 0.16667 | 116 | 2 | 2020-11-01 | 0.75
130 | Lalmonirhat | 132 | 132 | 1 | 2020-11-01 | 0.625 | 115 | 2 | 2020-11-01 | 0.75
131 | Saidpur | 132 | 134 | 1 | 2020-11-01 | 0.16667 | 113 | 2 | 2020-11-01 | 0.75
132 | Purbasadipur | 132 | 130 | 1 | 2020-11-01 | 0.20833 | 111 | 2 | 2020-11-01 | 0.75
133 | Thakurgaon | 132 | 130 | 1 | 2020-11-01 | 0.20833 | 112 | 2 | 2020-11-01 | 0.75
134 | Palashbari | 132 | 134 | 9 | 2020-11-01 | 0.58333 | 123 | 2 | 2020-11-01 | 0.75
135 | Barapukuria | 132 | 137 | 1 | 2020-11-01 | 0.20833 | 120 | 2 | 2020-11-01 | 0.75
136 | Panchagar | 132 | 129 | 1 | 2020-11-01 | 0.8125 | 107 | 2 | 2020-11-01 | 0.75
137 | Joldhaka | 132 | 133 | 1 | 2020-11-01 | 0.25 | 113 | 2 | 2020-11-01 | 0.77083
138 | Kurigram | 132 | 131 | 1 | 2020-11-01 | 0.58333 | 113 | 2 | 2020-11-01 | 0.77083
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:November' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 110 | 250
Hasnabad | TR2 | 225 | 100 | 250 | 01.11.2020 | 07:00
| TR3 | 225 | 100 | 260
| TR1 | 225 | 180 | 520
Tongi | TR2 | 225 | 180 | 520 | 02.11.2020 | 18:00
| TR3 | 225 | 180 | 520
Haripur | TR1 | 225 | 105 | 290 | 16.11.2020 | 16:00
| TR2 | 225 | 105 | 290
| TR3 | 225 | 105 | 290
| TR1 | 225 | 173 | 495
Rampura | TR2 | 225 | 173 | 495
| TR3 | 225 | 173 | 495 | 03.11.2020 | 12:00
| TR1 | 225 | 141 | 423
Aminbazar | TR2 | 225 | 141 | 423
| TR3 | 225 | 146 | 438 | 08.11.2020 | 12:00
Maniknagar | TR1 | 300 | 105 | 330
| TR2 | 300 | 105 | 330 | 03.11.2020 | 11:00
Cumilla (N) | TR1 | 225 | 158 | 432
| TR2 | 225 | 157 | 428 | 08.11.2020 | 21:00
Fenchuganj | AT2 | 300 | 234 | 576 | 17.11.2020 | 10:00
| MT1 | 150 | 71 | 200 | 06.11.2020
Hathazari | MT2 | 150 | 71 | 200
| MT3 | 150 | 71 | 200 |  | 17:00
| MT4 | 150 | 71 | 200
| TR1 | 225 | 60 | 160
Ishurdi | TR2 | 225 | 60 | 160
| TR3 | 225 | 60 | 160 | 28.11.2020 | 18:00
Khulna(S) | TR1 | 225 | 111 | 318
| TR2 | 225 | 111 | 318
| TR3 | 300 | 142 | 402 | 02.11.2020 | 19:00
Bogra | TR1 | 225 | 102 | 293
| TR2 | 225 | 102 | 293 | 28.11.2020 | 18:00
| TR3 | 225 | 139 | 386
Baghabari | TR1 | 300 | 117 | 325
| TR2 | 225 | 90 | 240 | 29.11.2020 | 19:30
Barapukuria | TR1 | 225 | 131 | 600 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 138 | 640 | 01.11.2020 | 18:00 | 132 kV current is being provided
| TR6 | 300 | 178 | 835
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:November' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 276 | 459 | 20.11.2020 | 12:30
| TR2(400/230 kV) | 520 | 276 | 459
| TR1(400/132 kV) | 325 | 258 | 427 | 03.11.2020 | 18:30
| TR2(400/132 kV) | 325 | 258 | 427
Bibiyana | ICT1(400/230 kV) | 520 | 97 | 148 | 24.11.2020 | 21:00
| ICT2(400/230kV) | 520 | 97 | 148
Bhulta | ATR1(400/230 kV) | 520 | 210 | 383 | 17.11.2020 | 11:30
| ATR2(400/230kV) | 520 | 210 | 383
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:November' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:November' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-11-20 | 11051 | 11051 | - | - | - | - | - | - | - | - | - | - | - | - | 01-11-20 | 9261 | 9261 | - | - | - | - | - | - | - | - | - | - | - | -
02-11-20 | 11572 | 11572 | - | - | - | - | - | - | - | - | - | - | - | - | 02-11-20 | 9280 | 9280 | - | - | - | - | - | - | - | - | - | - | - | -
03-11-20 | 11427 | 11427 | - | - | - | - | - | - | - | - | - | - | - | - | 03-11-20 | 9250 | 9250 | - | - | - | - | - | - | - | - | - | - | - | -
04-11-20 | 10322 | 10322 | - | - | - | - | - | - | - | - | - | - | - | - | 04-11-20 | 8623 | 8623 | - | - | - | - | - | - | - | - | - | - | - | -
05-11-20 | 9602 | 9602 | - | - | - | - | - | - | - | - | - | - | - | - | 05-11-20 | 8281 | 8281 | - | - | - | - | - | - | - | - | - | - | - | -
06-11-20 | 7975 | 7975 | - | - | - | - | - | - | - | - | - | - | - | - | 06-11-20 | 6269 | 6269 | - | - | - | - | - | - | - | - | - | - | - | -
07-11-20 | 9242 | 9242 | - | - | - | - | - | - | - | - | - | - | - | - | 07-11-20 | 7204 | 7204 | - | - | - | - | - | - | - | - | - | - | - | -
08-11-20 | 9801 | 9801 | - | - | - | - | - | - | - | - | - | - | - | - | 08-11-20 | 8109 | 8109 | - | - | - | - | - | - | - | - | - | - | - | -
09-11-20 | 10008 | 10008 | - | - | - | - | - | - | - | - | - | - | - | - | 09-11-20 | 8288 | 8288 | - | - | - | - | - | - | - | - | - | - | - | -
10-11-20 | 10084 | 10084 | - | - | - | - | - | - | - | - | - | - | - | - | 10-11-20 | 8409 | 8409 | - | - | - | - | - | - | - | - | - | - | - | -
11-11-20 | 9996 | 9996 | - | - | - | - | - | - | - | - | - | - | - | - | 11-11-20 | 8245 | 8245 | - | - | - | - | - | - | - | - | - | - | - | -
12-11-20 | 10193 | 10193 | - | - | - | - | - | - | - | - | - | - | - | - | 12-11-20 | 8484 | 8484 | - | - | - | - | - | - | - | - | - | - | - | -
13-11-20 | 8915 | 8915 | - | - | - | - | - | - | - | - | - | - | - | - | 13-11-20 | 6891 | 6891 | - | - | - | - | - | - | - | - | - | - | - | -
14-11-20 | 9822 | 9822 | - | - | - | - | - | - | - | - | - | - | - | - | 14-11-20 | 7632 | 7632 | - | - | - | - | - | - | - | - | - | - | - | -
15-11-20 | 9729 | 9729 | - | - | - | - | - | - | - | - | - | - | - | - | 15-11-20 | 8157 | 8157 | - | - | - | - | - | - | - | - | - | - | - | -
16-11-20 | 9719 | 9719 | - | - | - | - | - | - | - | - | - | - | - | - | 16-11-20 | 8109 | 8109 | - | - | - | - | - | - | - | - | - | - | - | -
17-11-20 | 9633 | 9633 | - | - | - | - | - | - | - | - | - | - | - | - | 17-11-20 | 7960 | 7960 | - | - | - | - | - | - | - | - | - | - | - | -
18-11-20 | 9429 | 9429 | - | - | - | - | - | - | - | - | - | - | - | - | 18-11-20 | 7952 | 7952 | - | - | - | - | - | - | - | - | - | - | - | -
19-11-20 | 9294 | 9294 | - | - | - | - | - | - | - | - | - | - | - | - | 19-11-20 | 7892 | 7892 | - | - | - | - | - | - | - | - | - | - | - | -
20-11-20 | 8454 | 8454 | - | - | - | - | - | - | - | - | - | - | - | - | 20-11-20 | 6631 | 6631 | - | - | - | - | - | - | - | - | - | - | - | -
21-11-20 | 9321 | 9321 | - | - | - | - | - | - | - | - | - | - | - | - | 21-11-20 | 7373 | 7373 | - | - | - | - | - | - | - | - | - | - | - | -
22-11-20 | 8989 | 8989 | - | - | - | - | - | - | - | - | - | - | - | - | 22-11-20 | 7488 | 7488 | - | - | - | - | - | - | - | - | - | - | - | -
23-11-20 | 8867 | 8867 | - | - | - | - | - | - | - | - | - | - | - | - | 23-11-20 | 7154 | 7154 | - | - | - | - | - | - | - | - | - | - | - | -
24-11-20 | 8762 | 8762 | - | - | - | - | - | - | - | - | - | - | - | - | 24-11-20 | 7246 | 7246 | - | - | - | - | - | - | - | - | - | - | - | -
25-11-20 | 8900 | 8900 | - | - | - | - | - | - | - | - | - | - | - | - | 25-11-20 | 7387 | 7387 | - | - | - | - | - | - | - | - | - | - | - | -
26-11-20 | 8926 | 8926 | - | - | - | - | - | - | - | - | - | - | - | - | 26-11-20 | 7437 | 7437 | - | - | - | - | - | - | - | - | - | - | - | -
27-11-20 | 7828 | 7828 | - | - | - | - | - | - | - | - | - | - | - | - | 27-11-20 | 6082 | 6082 | - | - | - | - | - | - | - | - | - | - | - | -
28-11-20 | 9056 | 9056 | - | - | - | - | - | - | - | - | - | - | - | - | 28-11-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-11-20 | 9055 | 9055 | - | - | - | - | - | - | - | - | - | - | - | - | 29-11-20 | 7473 | 7473 | - | - | - | - | - | - | - | - | - | - | - | -
30-11-20 | 9074 | 9074 | - | - | - | - | - | - | - | - | - | - | - | - | 30-11-20 | 7479 | 7479 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:November' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11572 | 02-11-2020 | 19:00
2 | Maximum Day Peak Genaration | MW | 9280 | 02-11-2020 | 12:00
3 | Maximum Evening Peak Demand | MW | 11572 | 02/11/20 | 19:00
4 | Minimum Generation | MW | 5330 | 28/11/20 | 5:00
5 | Average of the daily evening peak Genaration | MW | 9501.5333
6 | Average of the daily day peak Genaration | MW | 7762.9
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5555.7092
12 | Total Generation by BPDB | MKWH | 3010.001 | % of total Gen. | 54.18%
13 | Total Generation by IPP | MKWH | 1492.9816 | '' | 26.87%
14 | A) Total Generation by RPCL | MKWH | 114.0637 | '' | 2.053%
| B) Total Generation by REB | MKWH | 122.2164 | " | 2.2%
| C) Total Generation by RENTAL | MKWH | 280.216 | " | 5.044%
| D) Total Imported from India (BIPTC) | MKWH | 468.1607 | " | 8.427%
| E) Total Imported from Tripura, India (A.C) | MKWH | 68.0698 | " | 1.225%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3705.2202 | % of total Gen. | 66.69%
| B) Oil | MKWH | 774.1274 | '' | 13.93%
| C) Hydro | MKWH | 103.6451 | '' | 1.866%
| D) Solar | MKWH | 4.6869 | '' | 0.08436%
| E) Coal | MKWH | 431.7992 | '' | 7.772%
| F) BIPTC (Import from India) | MKWH | 468.1607 | '' | 8.427%
| G) A.C (Import from Tripura, India) | MKWH | 68.0698 | '' | 1.225%
16 | Maximun of the daily total Generation . | MKWH | 228.5896 | 02-11-2020
17 | Monthly Load factor | % | 66.6805
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 14501.2736
| A) Gas | M.Taka | 4268.4241
| B) Liquid fuel | M.Taka | 5319.5064
| C) Coal | M.Taka | 2015.2003
| D) BIPTC (Import from India) | M.Taka | 2387.6197
| E) Tripura(Import from India) | M.Taka | 510.5232
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 612.8178 | 03/11/2020
| A) Gas | M.Taka | 162.9341 | 02/11/2020
| B) Liquid fuel | M.Taka | 376.5599 | 03/11/2020
| C) Coal | M.Taka | 85.4249 | 01/11/2020
| D) BIPTC (Import from India) | M.Taka | 111.9218 | 01-11-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.7383
| B) Excluding Hydro & Solar | Taka/KWHR | 2.7924
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/2020 | 06:00
b) | Actual | FT (MSL) | 100.51 | 30/11/2020 | 06:00
22 | Peak Genaration of November 2019 | MW | 10255 | 03/11/19 | 19:00
23 | Peak Demand of November 2019 | MW | 10255 | 03/11/19 | 19:00
24 | Maximum peak Generation recorded upto 30/11/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/11/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/11/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.