## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-22 | Tuesday
|  |  | Date (day): | 2020-12-22 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11428.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12764 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-21 | 2020-12-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 44 | 44 | 44 |  | 126 | Machine problem
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 106 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 382 | 346 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 282 | 255 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 48 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 74 | 86 | 86 | 86 |  | 14 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 37 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 58 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 126 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1952 | 2906 | 3384 | 3674 | 1361 | 858
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 40 | 40 | 40 | 190 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 236 | 163 | 215 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 70 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 27 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 91 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 108 | 161 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 55 | 90 | 90 | 90 |  | 10 | Engine problem
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 14 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 648 | 934 | 1437 | 1432 | 700 | 114
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 130 | 120 | 120 | 120
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 183 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 165 | 0 | 0 | 0 |  | 360 | Under maint.
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 | 22 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 5 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 130 | 142 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 55 | 50 | 60 | 60
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 85 | 120 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 102 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1067 | 922 | 1371 | 1631 | 478 | 741
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 107 | 115 | 115 | 87 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 0
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 285 | 382 | 596.6 | 545 | 87 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 0 | 0 | 0 |  | 163 | Under maint.
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 127 | 120 | 150 | 150 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 51 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 50 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 73 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 197 | 170 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 120 | 270 | 250 | 300
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 410 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1157 | 869 | 961 | 1041 | 178 | 616
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 552 | 788 | 559 | 799
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 265 | 130 | 310 | 320 | 90 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 53 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 907 | 1126 | 1309 | 1895 | 90 | 88
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 12 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 300 | 540 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 13 | 35 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 339 | 688 | 865 | 925 | 0 | 202
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 13 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 9 | 150 | 150 | 70 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 130 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 420 | 372 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 53 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 663 | 834 | 1296 | 1420 | 461 | 225
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 85 | 88 | 88 | 88
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 90 | 201 | 209 | 201 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7108 | 8862 | 11428.6 | 12764 | 3355 | 3243
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6800.0027 | 8478 | 10933.3865 | 12210.9221
| A. |  | 2020-12-21 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 8862 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5558 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8862 | MW
| 3 | Day peak Generation : |  |  | 7108 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8478 | MW
| 4 | Evening peak Generation : |  |  | 8862 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 168.0802 | MKWHr | By Solar | 0.43153 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 99.7335 | MKWHr |  | By Oil: | 39.599 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.3932 | MKWHr |  | By Hydro: | 0.99802 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3355 | MW | Dhaka | 3004 | 3004 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3243 | MW | Chittagong | 958 | 958 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6598 | MW | Khulna | 1070 | 1070 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 757.3 | MMCFD |  |  | Rajshahi | 880 | 880 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 106651685.162 | ii) Oil : | Taka | 319275490.8 | Comilla | 745 | 745 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 57846212 | Total | Taka | 483773387.962 | Mymensingh | 707 | 707 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.748 | MKWHr. | Sylhet | 309 | 309 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -65 | MW (E to W) at | 19:30 | hrs | Barisal | 240 | 240 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -120 | MW at | 1:00 | hrs | Rangpur | 565 | 565 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 24.9° C |  |  | Total | 8478 | 8478 |  | 0
| B. |  | 2020-12-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 24.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12764 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
| 4 | Reserve(Generation end) |  |  |  | 3764 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 170.6975 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5505 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.0415 | MKWHr. | ii) HVDC Flow at Peak Time |  | 788 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8835 | MKWHr. | iii) Maximum HVDC Flow : |  | 790 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.84 |  | (b) Today: | 98.81 |  | (c) Rule Curve: |  | 104.2
.

## YesterdayGen
2020-12-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 10 | 0 | 300 | 12 | 0 | 359 | 291 |  | 0 | 185 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 16 | 35 | 0 | 150 | 0 | 0 | 50 | 192 | 45 | 50 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 70 | 109 | 0 | 20 | 0 | 0 | 20 | 14 | 10 | 163 | 126 | 18 | 75 | 0 | 170 | 18 | 0 | 0 | 0 | 12 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 80 | 180 | 24 | 0 | 0 | 0 | 105 | 54 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 0 | 0 | 103 |  | 412 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 37 | 0 | 0 |  | 4498 | 1677 | 6175 | 2913 | 412 | 1421 | 837 | 487 | 35 | 0 | 70 | 0 | 0 | 98.84
2:00 | 0 | 0 | 10 | 0 | 300 | 12 | 0 | 350 | 315 |  | 0 | 225 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 16 | 36 | 0 | 150 | 0 | 0 | 45 | 200 | 45 | 45 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 66 | 111 | 0 | 20 | 0 | 0 | 20 | 14 | 10 | 163 | 126 | 18 | 76 | 0 | 189 | 18 | 0 | 0 | 0 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 80 | 181 | 24 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 0 | 0 | 300 | 18 | 0 | 0 | 0 | 103 |  | 410 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 34 | 0 | 0 |  | 4293 | 1592 | 5885 | 2929 | 410 | 1422 | 556 | 467 | 35 | 0 | 66 | 0 | 0 | 98.84
3:00 | 0 | 0 | 10 | 0 | 300 | 12 | 0 | 361 | 344 |  | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 0 | 50 | 203 | 45 | 52 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 66 | 109 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 127 | 18 | 76 | 0 | 189 | 19 | 0 | 0 | 0 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 80 | 185 | 8 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 0 | 300 | 34 | 0 | 0 | 0 | 103 |  | 410 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 35 | 0 | 0 |  | 4094 | 1648 | 5742 | 2965 | 410 | 1468 | 351 | 447 | 35 | 0 | 66 | 0 | 0 | 98.84
4:00 | 0 | 0 | 10 | 0 | 300 | 12 | 0 | 352 | 352 |  | 0 | 225 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 0 | 50 | 193 | 45 | 50 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 64 | 110 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 127 | 18 | 76 | 0 | 188 | 19 | 0 | 0 | 0 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 180 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 300 | 34 | 0 | 0 | 0 | 103 |  | 316 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 36 | 0 | 0 |  | 4038 | 1550 | 5588 | 2959 | 316 | 1450 | 315 | 449 | 35 | 0 | 64 | 0 | 0 | 98.84
5:00 | 0 | 0 | 10 | 0 | 300 | 12 | 0 | 355 | 353 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 0 | 50 | 189 | 45 | 52 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 62 | 109 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 128 | 18 | 74 | 0 | 188 | 19 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 180 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 103 |  | 316 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 36 | 0 | 0 |  | 3966 | 1592 | 5558 | 2969 | 316 | 1477 | 251 | 448 | 35 | 0 | 62 | 0 | 0 | 98.84
6:00 | 0 | 0 | 12 | 0 | 300 | 12 | 0 | 383 | 353 |  | 0 | 225 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 0 | 45 | 185 | 64 | 52 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 58 | 109 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 126 | 18 | 74 | 0 | 189 | 19 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 90 | 180 | 2 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 103 |  | 316 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 36 | 0 | 0 |  | 4057 | 1640 | 5697 | 3027 | 316 | 1503 | 309 | 449 | 35 | 0 | 58 | 0 | 0 | 98.84
7:00 | 0 | 0 | 11 | 0 | 300 | 51 | 0 | 370 | 353 |  | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 38 | 0 | 150 | 0 | 0 | 50 | 166 | 64 | 51 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 56 | 110 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 124 | 20 | 74 | 0 | 188 | 19 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 50 | 100 | 180 | 35 | 0 | 0 | 0 | 33 | 54 | 0 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 103 |  | 410 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 130 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 15 | 0 | 0 |  | 4251 | 1800 | 6051 | 3050 | 410 | 1543 | 477 | 479 | 35 | 0 | 56 | 1 | 0 | 98.83
8:00 | 0 | 0 | 12 | 0 | 300 | 51 | 0 | 387 | 330 |  | 0 | 225 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 63 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 40 | 16 | 9 | 0 | 130 | 0 | 0 | 50 | 157 | 73 | 50 | 23 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 16 | 62 | 110 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 126 | 20 | 74 | 0 | 189 | 19 | 0 | 0 | 0 | 12 | 2 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 6 | 100 | 58 | 115 | 181 | 78 | 0 | 0 | 0 | 80 | 54 | 0 | 0 | 0 | 30 | 300 | 27 | 5 | 0 | 0 | 103 |  | 504 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 195 | 0 | 395 | 0 | 0 | 21 | 0 | 0 | 0 | 1 | 0 | 430 | 12 | 0 | 0 |  | 4524 | 1974 | 6498 | 3091 | 504 | 1462 | 815 | 517 | 35 | 0 | 62 | 12 | 0 | 98.83
9:00 | 0 | 0 | 0 | 0 | 300 | 54 | 0 | 356 | 303 |  | 0 | 225 | 0 | 57 | 0 | 13 | 0 | 0 | 0 | 7 | 0 | 48 | 74 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 7 | 0 | 130 | 0 | 0 | 80 | 180 | 73 | 51 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 16 | 62 | 110 | 0 | 20 | 0 | 0 | 20 | 11 | 10 | 130 | 127 | 20 | 74 | 0 | 189 | 19 | 0 | 0 | 0 | 16 | 2 | 0 | 70 | 0 | 0 | 0 | 0 | 32 | 11 | 50 | 75 | 132 | 180 | 115 | 0 | 0 | 1 | 155 | 54 | 0 | 0 | 0 | 30 | 300 | 75 | 13 | 0 | 0 | 0 |  | 504 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 204 | 0 | 387 | 90 | 0 | 89 | 0 | 0 | 0 | 2 | 0 | 320 | 17 | 0 | 0 |  | 4772 | 2026 | 6798 | 3044 | 504 | 1402 | 1271 | 405 | 35 | 48 | 62 | 27 | 0 | 98.83
10:00 | 0 | 0 | 0 | 0 | 300 | 95 | 0 | 354 | 274 |  | 0 | 225 | 0 | 80 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 48 | 75 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 16 | 7 | 0 | 130 | 0 | 0 | 115 | 198 | 73 | 49 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 16 | 72 | 109 | 0 | 20 | 1 | 0 | 30 | 11 | 10 | 110 | 129 | 20 | 70 | 0 | 165 | 19 | 0 | 0 | 0 | 14 | 2 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 15 | 30 | 85 | 130 | 120 | 115 | 0 | 0 | 3 | 107 | 54 | 0 | 0 | 0 | 30 | 400 | 90 | 36 | 0 | 0 | 0 |  | 552 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 192 | 0 | 328 | 90 | 0 | 109 | 0 | 0 | 0 | 4 | 0 | 300 | 28 | 0 | 0 |  | 4857 | 2021 | 6878 | 3089 | 552 | 1337 | 1298 | 388 | 35 | 48 | 72 | 59 | 0 | 98.83
11:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 366 | 274 |  | 0 | 225 | 0 | 94 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 48 | 75 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 7 | 0 | 130 | 0 | 0 | 125 | 200 | 73 | 50 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 16 | 74 | 105 | 0 | 20 | 2 | 0 | 30 | 11 | 10 | 110 | 129 | 20 | 70 | 0 | 150 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 17 | 30 | 85 | 130 | 120 | 115 | 0 | 0 | 4 | 107 | 54 | 0 | 0 | 0 | 30 | 420 | 90 | 42 | 0 | 17 | 0 |  | 552 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 140 | 0 | 355 | 90 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 300 | 29 | 0 | 0 |  | 4937 | 1954 | 6891 | 3060 | 552 | 1373 | 1293 | 386 | 35 | 48 | 74 | 70 | 0 | 98.83
12:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 382 | 282 |  | 0 | 225 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 48 | 74 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 236 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 130 | 0 | 0 | 165 | 197 | 73 | 55 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 16 | 78 | 102 | 0 | 20 | 2 | 0 | 30 | 11 | 10 | 163 | 127 | 31 | 71 | 0 | 150 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 17 | 70 | 85 | 130 | 120 | 115 | 0 | 0 | 4 | 108 | 54 | 0 | 0 | 0 | 55 | 410 | 90 | 46 | 0 | 14 | 0 |  | 552 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 140 | 0 | 420 | 90 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 300 | 13 | 0 | 0 |  | 5109 | 1999 | 7108 | 3112 | 552 | 1483 | 1341 | 385 | 35 | 48 | 78 | 74 | 0 | 98.83
13:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 354 | 282 |  | 0 | 225 | 0 | 100 | 0 | 42 | 0 | 0 | 0 | 40 | 0 | 48 | 75 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 24 | 17 | 33 | 0 | 0 | 30 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 10 | 0 | 130 | 0 | 0 | 220 | 166 | 45 | 44 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 16 | 86 | 103 | 12 | 20 | 2 | 0 | 30 | 14 | 10 | 110 | 126 | 32 | 72 | 0 | 130 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 152 | 0 | 0 | 0 | 0 | 68 | 16 | 100 | 121 | 135 | 120 | 115 | 0 | 0 | 4 | 87 | 54 | 0 | 0 | 0 | 50 | 415 | 90 | 43 | 0 | 0 | 0 |  | 552 | 0 | 245 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 168 | 0 | 309 | 90 | 0 | 108 | 0 | 35 | 0 | 4 | 25 | 300 | 16 | 0 | 0 |  | 5232 | 2031 | 7263 | 3062 | 552 | 1304 | 1690 | 387 | 65 | 48 | 86 | 69 | 7263 | 98.83
14:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 346 | 242 |  | 0 | 225 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 48 | 82 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 24 | 17 | 33 | 0 | 0 | 31 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 80 | 0 | 0 | 380 | 158 | 16 | 44 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 14 | 86 | 85 | 32 | 20 | 1 | 0 | 30 | 14 | 10 | 110 | 126 | 32 | 72 | 0 | 130 | 18 | 0 | 0 | 0 | 6 | 2 | 0 | 200 | 0 | 0 | 0 | 0 | 111 | 13 | 50 | 140 | 130 | 120 | 115 | 0 | 0 | 3 | 87 | 54 | 0 | 0 | 0 | 20 | 406 | 90 | 36 | 0 | 0 | 0 |  | 552 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 232 | 70 | 0 | 111 | 0 | 35 | 0 | 4 | 35 | 300 | 14 | 0 | 0 |  | 5245 | 1866 | 7111 | 2996 | 552 | 1157 | 1758 | 391 | 66 | 48 | 86 | 57 | 0 | 98.83
15:00 | 0 | 43 | 0 | 0 | 300 | 105 | 0 | 354 | 263 |  | 0 | 225 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 16 | 0 | 48 | 67 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 24 | 17 | 33 | 0 | 0 | 30 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 4 | 0 | 80 | 0 | 0 | 0 | 222 | 8 | 45 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 14 | 82 | 89 | 32 | 20 | 1 | 0 | 30 | 14 | 10 | 0 | 125 | 32 | 72 | 0 | 136 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 170 | 37 | 0 | 0 | 0 | 64 | 10 | 100 | 120 | 100 | 120 | 115 | 0 | 0 | 2 | 101 | 54 | 0 | 0 | 0 | 40 | 0 | 90 | 26 | 0 | 0 | 0 |  | 552 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 397 | 70 | 0 | 80 | 0 | 0 | 0 | 3 | 35 | 300 | 35 | 0 | 0 |  | 4399 | 2010 | 6409 | 2359 | 552 | 1236 | 1637 | 388 | 65 | 48 | 82 | 42 | 0 | 98.83
16:00 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 344 | 262 |  | 0 | 225 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 50 | 24 | 82 | 82 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 17 | 33 | 20 | 0 | 32 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 50 | 16 | 5 | 0 | 110 | 0 | 0 | 0 | 183 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 82 | 89 | 32 | 20 | 0 | 0 | 30 | 11 | 10 | 0 | 124 | 32 | 72 | 0 | 129 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 200 | 33 | 0 | 0 | 0 | 100 | 5 | 100 | 120 | 100 | 135 | 115 | 15 | 0 | 1 | 105 | 54 | 0 | 0 | 0 | 80 | 0 | 90 | 10 | 0 | 20 | 0 |  | 552 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 13 | 0 | 130 | 0 | 338 | 53 | 0 | 110 | 0 | 70 | 0 | 2 | 35 | 300 | 25 | 0 | 0 |  | 4683 | 2028 | 6711 | 2350 | 552 | 1165 | 2007 | 388 | 67 | 82 | 82 | 18 | 0 | 98.82
17:00 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 370 | 253 |  | 0 | 225 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 60 | 40 | 82 | 85 | 0 | 0 | 0 | 54 | 55 | 25 | 16 | 25 | 28 | 17 | 33 | 28 | 0 | 32 | 50 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 24 | 50 | 16 | 9 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 45 | 23 | 5 | 0 | 30 | 0 | 0 | 1 | 18 | 11 | 25 | 21 | 90 | 104 | 32 | 20 | 0 | 0 | 30 | 14 | 10 | 0 | 124 | 33 | 50 | 0 | 143 | 18 | 0 | 0 | 0 | 0 | 2 | 0 | 230 | 12 | 0 | 0 | 0 | 124 | 0 | 100 | 120 | 103 | 135 | 115 | 36 | 0 | 0 | 158 | 54 | 0 | 0 | 0 | 80 | 0 | 90 | 1 | 0 | 0 | 0 |  | 552 | 0 | 195 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 13 | 0 | 130 | 0 | 389 | 53 | 0 | 111 | 0 | 82 | 0 | 1 | 35 | 320 | 15 | 0 | 0 |  | 4903 | 2095 | 6998 | 2446 | 552 | 1163 | 2173 | 408 | 82 | 82 | 90 | 2 | 0 | 98.82
18:00 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 365 | 255 |  | 0 | 225 | 0 | 100 | 26 | 55 | 0 | 0 | 0 | 90 | 40 | 133 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 20 | 17 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 4 | 163 | 0 | 0 | 0 |  | 0 | 0 | 96 | 20 | 61 | 50 | 16 | 15 | 0 | 150 | 0 | 0 | 0 | 185 | 8 | 50 | 23 | 5 | 0 | 38 | 0 | 0 | 30 | 18 | 11 | 25 | 21 | 104 | 106 | 68 | 20 | 0 | 0 | 30 | 14 | 10 | 0 | 125 | 33 | 70 | 0 | 196 | 18 | 0 | 0 | 0 | 16 | 7 | 0 | 280 | 56 | 0 | 19 | 0 | 138 | 0 | 100 | 120 | 123 | 270 | 115 | 75 | 0 | 0 | 158 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | 0 |  | 790 | 0 | 180 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 72 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 12 | 0 | 130 | 0 | 419 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 90 | 530 | 16 | 0 | 0 |  | 5756 | 2889 | 8645 | 2631 | 790 | 1235 | 2947 | 616 | 43 | 279 | 104 | 0 | 0 | 98.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 351 | 254 |  | 0 | 225 | 0 | 100 | 48 | 55 | 0 | 0 | 0 | 100 | 7 | 133 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 33 | 17 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 14 | 163 | 0 | 0 | 0 |  | 0 | 0 | 102 | 64 | 89 | 50 | 16 | 21 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 45 | 23 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 104 | 106 | 90 | 20 | 0 | 0 | 30 | 51 | 40 | 0 | 120 | 33 | 70 | 0 | 197 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 270 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 120 | 123 | 270 | 115 | 105 | 0 | 0 | 158 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 126 | 0 | 0 |  | 788 | 0 | 135 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 96 | 0 | 0 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 12 | 0 | 130 | 0 | 329 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 540 | 34 | 0 | 0 |  | 5966 | 2871 | 8837 | 2548 | 788 | 1249 | 3184 | 628 | 40 | 296 | 104 | 0 | 0 | 98.82
19:30 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 346 | 255 |  | 0 | 225 | 0 | 100 | 48 | 55 | 0 | 0 | 0 | 100 | 0 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 37 | 16 | 25 | 33 | 17 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 102 | 40 | 91 | 50 | 16 | 27 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 102 | 107 | 90 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 120 | 33 | 73 | 0 | 197 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 120 | 142 | 270 | 115 | 105 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 126 | 0 | 0 |  | 788 | 0 | 130 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 80 | 0 | 0 | 0 | 13 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 130 | 0 | 372 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 540 | 35 | 0 | 0 |  | 6013 | 2849 | 8862 | 2546 | 788 | 1313 | 3127 | 628 | 40 | 318 | 102 | 0 | 0 | 0
20:00 | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 347 | 255 |  | 0 | 225 | 0 | 100 | 48 | 55 | 0 | 0 | 0 | 100 | 0 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 37 | 16 | 25 | 33 | 17 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 92 | 50 | 16 | 28 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 45 | 23 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 102 | 106 | 90 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 122 | 34 | 73 | 0 | 197 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 120 | 140 | 270 | 115 | 105 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 72 | 0 | 0 |  | 790 | 0 | 135 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 80 | 0 | 0 | 0 | 25 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 130 | 0 | 331 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 540 | 17 | 0 | 0 |  | 5918 | 2810 | 8728 | 2549 | 790 | 1256 | 3033 | 628 | 40 | 330 | 102 | 0 | 0 | 98.82
21:00 | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 357 | 255 |  | 0 | 225 | 0 | 94 | 48 | 55 | 0 | 0 | 0 | 100 | 0 | 100 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 33 | 17 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 90 | 0 | 57 | 50 | 16 | 30 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 45 | 23 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 25 | 21 | 98 | 108 | 90 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 114 | 34 | 73 | 0 | 183 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 32 | 0 | 149 | 0 | 100 | 120 | 143 | 281 | 115 | 72 | 0 | 0 | 178 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 37 | 0 | 0 |  | 790 | 0 | 120 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 28 | 80 | 0 | 0 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 12 | 0 | 129 | 0 | 325 | 70 | 0 | 111 | 0 | 70 | 0 | 0 | 113 | 560 | 15 | 0 | 0 |  | 5681 | 2757 | 8438 | 2502 | 790 | 1255 | 2846 | 648 | 40 | 259 | 98 | 0 | 0 | 98.82
22:00 | 0 | 0 | 0 | 0 | 300 | 106 | 0 | 348 | 260 |  | 0 | 225 | 0 | 69 | 48 | 15 | 0 | 0 | 0 | 100 | 0 | 48 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 16 | 30 | 0 | 120 | 0 | 0 | 0 | 193 | 8 | 45 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 25 | 21 | 90 | 108 | 83 | 20 | 0 | 0 | 30 | 53 | 50 | 0 | 156 | 33 | 73 | 0 | 183 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 137 | 0 | 100 | 120 | 147 | 281 | 115 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 |  | 788 | 0 | 115 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 377 | 70 | 0 | 111 | 0 | 11 | 0 | 0 | 70 | 560 | 17 | 0 | 0 |  | 5236 | 2486 | 7722 | 2441 | 788 | 1315 | 2292 | 648 | 40 | 108 | 90 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 349 | 270 |  | 0 | 225 | 0 | 55 | 48 | 15 | 0 | 0 | 0 | 100 | 0 | 32 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 16 | 34 | 0 | 80 | 0 | 0 | 0 | 183 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 25 | 21 | 82 | 111 | 91 | 20 | 0 | 0 | 30 | 53 | 50 | 0 | 157 | 34 | 73 | 0 | 128 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 120 | 148 | 280 | 115 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 |  | 600 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 12 | 0 | 0 | 0 | 290 | 70 | 0 | 111 | 0 | 0 | 0 | 0 | 70 | 500 | 30 | 0 | 0 |  | 5087 | 2142 | 7229 | 2412 | 600 | 1252 | 2189 | 588 | 40 | 66 | 82 | 0 | 0 | 0
24:00 | 0 | 38 | 0 | 0 | 300 | 102 | 0 | 357 | 290 |  | 0 | 225 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 6 | 86 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 35 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 46 | 23 | 19 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 76 | 116 | 24 | 20 | 0 | 0 | 30 | 53 | 50 | 0 | 158 | 34 | 73 | 0 | 143 | 19 | 0 | 0 | 0 | 16 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 72 | 0 | 100 | 100 | 143 | 260 | 115 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 |  | 412 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 12 | 0 | 0 | 0 | 310 | 35 | 0 | 111 | 0 | 0 | 0 | 0 | 35 | 450 | 36 | 0 | 0 |  | 4882 | 1849 | 6731 | 2547 | 412 | 1310 | 1802 | 538 | 40 | 6 | 76 | 0 | 0 | 0
KWH | 0 | 300900 | 90580 | 0 | 7038545 | 1694681 | 0 | 8751100 | 6908000 |  | 0 | 4621100 | 0 | 1733760 | 303912 | 603441 | 0 | 0 | 0 | 984000 | 147600 | 1126560 | 1862551 | 0 | 0 | 0 | 1175760 | 934592 | 165192 | 296856 | 600000 | 688680 | 404700 | 816100 | 254820 | 0 | 198022 | 800000 | 0 | 0 | 24285 | 4464096 | 0 | 0 | 0 |  | 0 | 0 | 483262 | 117720 | 357120 | 926880 | 294000 | 582720 | 0 | 3107030 | 0 | 0 | 1623000 | 4528000 | 903272 | 1152210 | 513720 | 492960 | 0 | 1203240 | 0 | 0 | 189782 | 458280 | 237960 | 604500 | 487410 | 1883520 | 2473760 | 707520 | 432108 | 9200 | 0 | 618720 | 510000 | 518472 | 1958972 | 2915000 | 626496 | 1728000 | 0 | 4137070 | 439000 | 0 | 0 | 0 | 314808 | 122500 | 0 | 3540326 | 166794 | 0 | 187200 | 0 | 1515312 | 112590 | 1639680 | 2280960 | 2830254 | 4518000 | 2060400 | 443268 | 0 | 23426 | 2501564 | 1300737 | 0 | 0 | 0 | 1060800 | 4970600 | 1674240 | 255460 | 326880 | 53945 | 918000 |  | 13041454 | 0 | 4967424 | 0 | 669120 | 0 | 0 | 0 | 0 | 0 | 168000 | 0 | 424900 | 479424 | 0 | 0 | 0 | 36192 | 0 | 229216 | 16100 | 0 | 0 | 66240 | 0 | 501600 | 0 | 214146 | 2097600 | 0 | 0 | 0 | 0 | 0 | 0 | 394073 | 0 | 300806 | 0 | 3397945 | 0 | 8819454 | 1104960 | 0 | 1698624 | 0 | 644160 | 0 | 30854 | 805824 | 10295600 | 647972 | 0 | 0 |  | 117028481 | 51051688 | 168080169 | 67917317 | 13041454 | 31816149 | 37723747 | 12393200 | 998022 | 1875230 | 1883520 | 431530 | 0
Fuel Cost | 0 | 445332 | 132246.8 | 0 | 7812784.95 | 2236978.92 | 0 | 8838611 | 7115240 |  | 0 | 5036999 | 0 | 13159238.4 | 2093953.68 | 5105110.86 | 0 | 0 | 0 | 7409520 | 1346112 | 11085350.4 | 17172720.22 | 0 | 0 | 0 | 8583048 | 7224396.16 | 1628793.12 | 222642 | 450000 | 0 | 0 | 0 | 2464109.4 | 0 | 53465.94 | 216000 | 0 | 0 | 225607.65 | 4865864.64 | 0 | 0 | 0 |  | 0 | 0 | 4687641.4 | 1124226 | 3106944 | 7340889.6 | 370440 | 1730678.4 | 0 | 4598404.4 | 0 | 0 | 1623000 | 4165760 | 1165220.88 | 1325041.5 | 580503.6 | 690144 | 0 | 2057540.4 | 0 | 0 | 1812418.1 | 582015.6 | 178470 | 1057875 | 365557.5 | 14126400 | 2622185.6 | 6424281.6 | 548777.16 | 146648 | 0 | 989952 | 907800 | 808816.32 | 2233228.08 | 3031600 | 1234197.12 | 3300480 | 0 | 7157131.1 | 961410 | 0 | 0 | 0 | 236106 | 93100 | 0 | 26764864.56 | 2832162.12 | 0 | 973440 | 0 | 14910670.08 | 1316177.1 | 13363392 | 24748416 | 19953290.7 | 4201740 | 18790848 | 4188882.6 | 0 | 0 | 18911823.84 | 11329419.27 | 0 | 0 | 0 | 7064928 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75118775.04 | 0 | 5215795.2 | 0 | 5259283.2 | 0 | 0 | 0 | 0 | 0 | 1750560 | 0 | 658595 | 4679178.24 | 0 | 0 | 0 | 356129.28 | 0 | 2028561.6 | 123970 | 0 | 0 | 641865.6 | 0 | 963072 | 0 | 162108.522 | 12648528 | 0 | 0 | 0 | 0 | 0 | 0 | 520176.36 | 0 | 451209 | 0 | 3975595.65 | 0 | 8731259.46 | 11535782.4 | 0 | 16119941.76 | 0 | 4998681.6 | 0 | 340936.7 | 5955039.36 | 45197684 | 0 | 0 | 0 |  | 367659062.77 | 207432727.972 | 575091790.742 | 68564423.702 | 75118775.04 | 38087261.46 | 301117808.12 | 57846212 | 269465.94 | 18157682.68 | 14126400 | 1803761.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 382 | 282 |  | 0 | 225 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 48 | 74 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 17 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 236 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 130 | 0 | 0 | 165 | 197 | 73 | 55 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 16 | 78 | 102 | 0 | 20 | 2 | 0 | 30 | 11 | 10 | 163 | 127 | 31 | 71 | 0 | 150 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 17 | 70 | 85 | 130 | 120 | 115 | 0 | 0 | 4 | 108 | 54 | 0 | 0 | 0 | 55 | 410 | 90 | 46 | 0 | 14 | 0 |  | 552 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 140 | 0 | 420 | 90 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 300 | 13 | 0 | 0 |  | 7108 | DayPeak
Yesterday Evening Peak | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 346 | 255 | 0 | 0 | 225 | 0 | 100 | 48 | 55 | 0 | 0 | 0 | 100 | 0 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 37 | 16 | 25 | 33 | 17 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 91 | 50 | 16 | 27 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 102 | 107 | 90 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 120 | 33 | 73 | 0 | 197 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 120 | 142 | 270 | 115 | 105 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 126 | 0 | 0 |  | 788 | 0 | 130 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 80 | 0 | 0 | 0 | 13 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 12 | 0 | 130 | 0 | 372 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 540 | 35 | 0 | 0 |  | 8862 | EvPeak
Forecast for Evening | 0 | 44 | 0 | 0 | 300 | 108 | 0 | 412 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 86 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 0 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 20 | 0 | 120 | 0 | 0 | 0 | 221 | 8 | 60 | 23 | 55 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 25 | 21 | 148 | 115 | 95 | 20 | 0 | 0 | 30 | 51 | 44 | 0 | 150 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 90 | 0 | 90 | 0 | 0 |  | 100 |  | 799 | 16 | 320 | 0 | 115 | 220 | 0 | 0 | 30 | 65 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 44 | 0 | 0 | 300 | 108 | 0 | 412 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 86 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 0 | 40 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 10 | 0 | 120 | 0 | 0 | 0 | 221 | 8 | 60 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 20 | 139 | 115 | 95 | 20 | 1.6 | 0 | 30 | 51 | 44 | 0 | 150 | 33 | 86 | 0 | 170 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 250 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 90 | 0 | 90 | 50 | 0 |  | 100 |  | 559 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 30 | 65 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 95 | 0 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 44 | 0 | 0 | 300 | 101 | 0 | 364 | 335 | 0 | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 25 | 30 | 17 |  | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 8 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 45 | 20 | 55 | 0 | 40 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 66 | 144 | 30 | 20 | 0 | 0 | 30 | 48 | 33 | 0 | 157 | 34 | 76 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 33 | 4 | 100 | 17 | 133 | 310 | 115 | 0 | 0 | 1 | 141 | 54 | 0 | 0 | 16 | 90 | 0 | 53 | 11 | 0 | 0 | 0 | 0 | 506 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 12 | 0 | 0 | 0 | 300 | 90 | 0 | 93 | 0 | 70 | 0 | 1 | 25 | 290 | 37 | 0 | 0 | 0
199
| Minimum Generation |  | 5558 | 5:00
| Highest Generation |  | 8862 | 19:30
| Day Peak Generation |  | 7108 | 12:00
| Evening Peak Generation |  | 8862 | 19:30
| HVDC Max Flow |  | 790 | 18:00
| HVDC EvPeak Flow |  | 788 | 19:30
| Load factor L.F |  | 79.03%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7108 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5505 | MW
Evening Peak Generation : |  | 8862 | MW Hour : | 19:30 | Available Max Generation : |  | 12764 | MW
E.P. Demand (at gen end) : |  | 8862 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8862 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3764 | MW
Total Gen. (MKWH) : |  | 168.0802 | System Load Factor : | 79.03% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -120 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-22
Actual : | 98.81 | Ft.(MSL) , | Rule curve : | 104.2 | Ft.( MSL )
Gas Consumed : | Total = | 757.3 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106651685.162
: |  | Coal : | 57846212 | Oil : | 319275490.8 | Total : | 483773387.962
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3215.4514 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1088.1209 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 973.9739 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 879.7316 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 795.186 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 641.6736 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 365.6262 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.3945 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 494.8578 |  |  | 0 | 0%
Total | 0 |  | 8620.016 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71 &100 MW | 11) Fenchugonj CCPP Phase-2
|  |  |  | 3) Ghorasal Unit-1,2,4 | 12) Kushiara-163 MW
|  |  |  | 4) Shahjibazar 330 MW GT-2 | 13) Bibiyana south-400 MW.
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,3 CCPP
9) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Halishahar-Khulsi 132 kV Ckt-1 was under shut down from 08:50 to 17:06 for A/M.
b) GPH-BSRM 230 kV Ckt was under shut down from 08:31 to 16:20 for A/M.
c) Kaliakoir-Dhamrai 132 kV Ckt-1 was under shut down from 08:54 to 18:36 for A/M.
d) Jamalpur-UMPL 132 kV Ckt-2 was under shut down from 09:16 to 17:03 for A/M.
e) UMPL-Sherpur 132 kV Ckt-2 was under shut down from 09:10 to 17:16 for A/M.
f) Dohazari-Sikalbaha 132 kV Ckt-1 was under shut down from 12:39 to 16:43 for D/W.
g) Ashuganj-Kishorganj 132 kV Ckt-2 was under shut down from 12:56 to 16:38 for D/W.
h) Madanganj-Munshiganj 132 kV Ckt-1 was under shut down from 09:34 to 12:26 for A/M.
i) Madanganj-Munshiganj 132 kV Ckt-2 was under shut down from 12:36 to 16:39 for A/M.
j) Ghorasal-Joydevpur 132 kV Ckt-2 was under shut down from 08:37 to 18:54 for D/W.
k) Saidpur-Jaldhaka 132 kV Ckt-1 was under shut down from 08:49 to 16:36 for A/M.
l) Barapukuria-Bogura 230 kV Ckt-1 was under shut down from 08:32 to 16:50 for A/M.
m) Purbasadipur-Thakurgaon 132 kV Ckt-2 was under shut down from 10:14 to 17:04 for A/M.
n) Natore-Rajshahi 132 kV Ckt-1 was under shut down from 08:19 to 16:46 for A/M.
o) Faridpur-Gopalganj 132 kV Ckt-2 was under shut down from 08:54 to 16:40 for A/M.
p) Baghabari-Ishurdi 230 kV Ckt-1 was under shut down from 08:16 to 20:19 for A/M.
q) Mymensing 132/33 kV T-1 transformer was under shut down from 09:18 to 16:55 for A/M.
r) Hasnabad 230 kV Bus-1 was under shut down from 08:36 to 17:11 for A/M.
s) Uttara 3rd phase 132/33 kV T-2 transformer was under shut down from 10:43 to 14:22 for A/M.
t) Savar 132/33 kV T-3 transformer was under shut down from 08:51 to 17:46 for A/M.
u) Bhandaria 132/33 kV T-1 transformer was under shut down from 08:04 to 17:02 for A/M.
v) Ghorasal #4 was shut down at 12:00 due to maintenance work.
w) Shahjibazar-100 MW tripped at 08:57 due to vacuum failure of mineral lube oil tank.
y) Ashuganj(S)-360 MW tripped at 14:40 showing acceleration monitor.
z) Bibiyana south-400 MW tripped at 14:28 showing gen. protection.
aa) Kushiara-163 MW tripped at 14:35 due to high voltage.
ab) Sirajganj #2 CCPP GT & ST were synchronized at 15:58 & 20:00 respectively.
ac) Sirajganj #3 CCPP ST & GT were shut down at 21:37 & 21:56 respectively.
ad) Ishurdi 230/132 kV T-02 transformer was shut down at 20:30 due to 132 kV CB problem.
ae) After maintenance Ghorasal #3 was synchronized at 23:20.
af) HVDC 400 kV block-2 filter 10CF24 tripped at 06:05(22/12/20).
ag) HVDC Pole-2 is blocked due to 10CF24 trip.
ah) Dohazari-Cox's bazar 132 kV Ckt-1 is under shut down since 07:43(22/12/20) for A/M.
ai) Faridpur-Gopalganj 132 kV Ckt-2 is under shut down since 07:42(22/12/20) for A/M.
aj) Ishurdi-Ghorasal 230 kV Ckt-1 is under shut down since 07:53(22/12/20) for A/M.
ak) Rampura-Bhulta 132 kV Ckt-1 is under shut down since 07:52(22/12/20) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 44 | 300900 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 90580 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7038545
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 106 | 1694681
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8751100 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 255 | 6908000 | Frequency Control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4621100 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1733760
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 303912 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 603441
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 86 | 1862551 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 296856 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 984000
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 147600 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1175760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1126560
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 934592
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 37 | 165192 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1288680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 404700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 254820
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3540326
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 166794 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1515312
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 443268
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1674240 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 326880
| Dhaka area Total |  |  |  | 6057 | 2906 | 49170250
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 24285 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 112590
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 926880
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 998022 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 163 | 4464096 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 483262
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 117720 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1639680
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 294000 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 582720
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 357120 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23426
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 161 | 2501564 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300737
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1060800 | Engine problem
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 53945
| Chattogram area Total |  |  |  | 2266 | 934 | 14940847
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 3107030
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4528000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 1623000 | Tripped at 14:40
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 513720 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 492960 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 903272 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1203240
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2830254
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1152210 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 2280960 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 458280
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1883520
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 604500 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 189782 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 487410
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve.
| Cumilla Area Total |  |  |  | 2980 | 922 | 22496098
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2473760 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 432108
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 707520
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 187200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2060400 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 255460
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 687 | 382 | 6125648
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 618720 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 1958972 | Tripped at 14:35
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 120 | 2915000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 510000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 518472
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 122500
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 626496 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1728000 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 918000 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 197 | 4137070
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 439000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 314808 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 270 | 4518000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 4970600 | Tripped at 14:28
| Sylhet Area Total |  |  |  | 1988 | 869 | 24295638
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 788 | 13041454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 669120
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 130 | 4967424 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 168000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 1104960 | Low demand
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1126 | 19950958
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 479424 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 424900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 300806 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 540 | 10295600 | Line O/L
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 35 | 647972 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1054 | 688 | 12148702
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 13 | 36192 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 16100 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 9 | 394073 | Machine problem
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3397945 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 8819454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 501600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214146
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 66240 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 53 | 229216 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1698624
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 805824
| Rajshahi Area Total |  |  |  | 2183 | 834 | 16179414
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 88 | 2097600
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 644160
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30854
| Rangpur Area Total |  |  |  | 605 | 201 | 2772614
| Total |  |  |  | 20104 | 8862 | 168080169
| Eastern Grid Total |  |  |  | 13978 | 6013 | 117028481
| Western Grid Total |  |  |  | 6126 | 2849 | 51051688
| National Grid Total |  |  |  | 20104 | 8862 | 168080169
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-21
| (a) ENTIRE EASTERN GRID : |  | 5723 | MW | (b) ENTIRE WESTERN GRID : |  | 2755 | MW
| i) Dhaka area |  | 3004 | MW | i) Khulna area |  | 1070 | MW
| ii) Chittagong area |  | 958 | MW | ii) Rajshahi area |  | 880 | MW
| iii) Comilla area |  | 745 | MW | iii) Barisal area |  | 240 | MW
| iv) Mymensingh area |  | 707 | MW | iv) Rangpur area |  | 565 | MW
| v) Sylhet area |  | 309 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8478 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 100 | 10:00 | Jamalpur | 87 | 19:30 | Benapol | 36 | 18:00
| Munsiganj | 84 | 19:30 | Sherpur | 80 | 18:00 | Jhenida | 82 | 18:00
| Sonargaon | 50 | 19:30 | Srimongal | 23 | 18:00 | Bottail | 114 | 18:00
| Shyampur | 156 | 9:00 | Shahjibazar | 80 | 18:30 | G.K Project | 38 | 18:30
| Bhulta | 158 | 18:30 | Fenchuganj | 24 | 18:00 | Faridpur | 134 | 18:30
| Madanganj | 48 | 19:30 | Kulawara | 31 | 18:30 | Madaripur | 64 | 19:30
| Shitalakhya | 100 | 17:00 | Sylhet | 75 | 18:00 | Sariatpur | 42 | 20:00
| Rahim steel | 6 | 9:00 | Chatak | 23 | 18:00 | Gopalganj | 59 | 18:30
| Matuail | 54 | 0:00 | Sunamganj | 26 | 18:30 | Bagerhat | 78 | 19:30
| Ghorasal | 58 | 18:00 | Biani Bazar | 41 | 18:00 | Mongla | 38 | 9:00
| Narsingdi | 121 | 21:00 | Comilla (S) | 104 | 18:00 | Satkhira | 76 | 19:00
| Haripur (SBU) | 100 | 12:00 | Comilla(N) | 55 | 20:00 | Gallamari | 19 | 13:00
| Ullon | 38 | 13:00 | Chandpur | 62 | 19:30 | Magura | 40 | 18:30
| Hasnabad | 125 | 18:00 | Feni | 75 | 18:30 | Norail | 24 | 18:00
| Magbazar | 65 | 14:00 | Chowmuhani | 118 | 19:00 | Chuadanga | 61 | 19:00
| Maniknagar | 62 | 11:00 | Ashuganj | 39 | 19:00 | Barisal(N) | 28 | 18:30
| Bangabhaban | 18 | 13:00 | Daudkandi | 104 | 19:30 | Barisal (S) | 70 | 18:30
| Narinda | 68 | 12:00 | B.Baria | 90 | 18:00 | Patuakhali | 81 | 21:00
| Dhanmondi | 90 | 13:00 | Ramganj | 72 | 19:00 | Bhandaria | 41 | 20:00
| Lalbag | 68 | 17:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 19:30
| Madartek | 43 | 18:00 | PHP | 11 | 18:30 | Ishurdi | 49 | 19:00
| Dhaka University |  |  | Madunaghat | 42 | 19:30 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 65 | 0.75 | Natore | 83 | 0.75
| Fatullah | 29 | 11:00 | Khulshi | 169 | 13:00 | Bogra | 126 | 18:30
| Mirpur | 70 | 18:00 | Halishahar | 86 | 18:30 | Noagaon | 80 | 18:30
| Kalyanpur | 57 | 18:00 | Baraulia | 132 | 3:00 | Rajshahi | 101 | 19:30
| Gulshan | 66 | 18:00 | Sikalbaha | 20 | 18:30 | Rajshahi New | 8 | 18:00
| Uttara | 85 | 12:00 | Dohazari | 58 | 18:30 | C.Nawabganj | 52 | 20:00
| Uttara New | 22 | 18:00 | Cox'sbazar | 71 | 18:30 | Amnura | 30 | 18:30
| Kamrangirchar | 75 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 80 | 19:00
| Savar | 131 | 18:00 | Kaptai | 16 | 13:00 | Shahjadpur | 75 | 18:30
| Bhasantec | 94 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 67 | 18:30
| Agargaon | 43 | 13:00 | Bakulia | 71 | 18:30 | Niyamatpur | 40 | 18:00
| Satmosjid | 64 | 0.54167 | Julda | 20 | 0.5 | Joypurhat | 46 | 0.75
| Tongi | 59 | 8:00 | TK chemical | 20.7 | 19:00 | Sherpur(Bogura) | 42 | 18:00
| Kabirpur | 154 | 16:00 | Modern Steel | 0 | 1:00 | Mohastangor | 34 | 18:30
| Basundhara | 93 | 18:30 | Shahmirpur | 18.6 | 18:00 | Rangpur | 102 | 18:00
| Manikganj | 44 | 19:30 | Khagrachhari | 20 | 18:30 | Lalmonirhat | 49 | 18:30
| Joydevpur | 98 | 19:00 | Matarbari | 27 | 20:00 | Saidpur | 77 | 19:30
| New Tongi | 100 | 11:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 88 | 18:30
| Kodda | 185 | 19:00 | Rangamati | 8 | 12:00 | Thakurgaon | 62 | 18:00
| Dhamrai | 68 | 18:00 | Abul Khair 230 | 135 | 5:00 | Palashbari | 83 | 19:30
| Rajendrapur | 72 | 19:00 | BSRM | 150 | 16:00 | Barapukuria | 41 | 19:00
| Valuka | 76 | 18:00 | GPH Ispat | 78 | 18:30 | Panchagar | 43 | 18:30
| Tangail | 142 | 18:00 | Goalpara | 17 | 13:00 | Joldhaka | 19 | 18:00
| Mymensing | 159 | 18:30 | Central s/s | 78 | 18:00 | Kurigram | 43 | 18:30
| Kishorganj | 82 | 20:00 | Noapara | 49 | 19:00
| Netrokona | 92 | 19:00 | Jessore | 81 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 430 | 20:00 | 409 | 20:00 | Kaliakoir | 396 | 0.58333 | 366 | 0.5
| Bheramara | 405 | 16:00 | 393 | 11:00 | Bhulta | 386 | 24:00 | 369 | 0.5
| Ashuganj(N) | 389 | 24:00 | 376 | 12:00 | Gopalganj | 418 | 0.58333 | 397 | 0.875
| Payra | 420 | 21:00 | 406 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 232 | 8:00 | Comilla (N) | 240 | 23:00 | 232 | 12:00
| Ishurdi | 239 | 4:00 | 231 | 8:00 | Hathazari | 227 | 21:00 | 213 | 11:00
| Ashuganj | 240 | 14:00 | 235 | 12:00 | Megnaghat | 238 | 16:00 | 222 | 12:00
| Serajganj | 235 | 24:00 | 228 | 8:00 | Fenchuganj | 250 | 24:00 | 242 | 19:30
| Baghabari | 242 | 5:00 | 237 | 12:00 | Siddhirganj | 234 | 21:00 | 225 | 12:00
| Barapukuria | 233 | 17:00 | 224 | 8:00 | Maniknagar | 232 | 24:00 | 223 | 12:00
| Bogra | 235 | 23:00 | 226 | 7:00 | Agargaon | 234 | 15:00 | 219 | 12:00
| Rajshahi | 233 | 6:00 | 219 | 8:00 | Barisal | 250 | 23:00 | 241 | 21:00
| Khulna South | 237 | 15:00 | 219 | 8:00 | AKSML | 229 | 19:00 | 213 | 12:00
| Rampura | 232 | 23:00 | 228 | 11:00 | BSRM | 231 | 20:00 | 217 | 11:00
| Haripur | 233 | 24:00 | 224 | 11:00 | Bibiyana | 251 | 24:00 | 239 | 19:30
| Hasnabad | 235 | 23:00 | 226 | 11:00 | Bhulta | 236 | 19:00 | 223 | 17:00
| Shyampur | 232 | 21:00 | 220 | 12:00 | Ashuganj (S) | 238 | 23:00 | 231 | 12:00
| Aminbazar | 235 | 24:00 | 222 | 12:00 | Kaliakoir | 235 | 24:00 | 220 | 12:00
| Tongi | 234 | 23:00 | 217 | 11:00 | GPH | 229 | 24:00 | 211 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 21:00 | 134 | 12:00 | Madanhat | 140 | 0.83333 | 130 | 0.41667
| Munsiganj | 142 | 18:30 | 133 | 12:00 | Hathazari | 139 | 0.875 | 128 | 0.45833
| Sonargaon | 139 | 18:30 | 135 | 3:00 | Khulshi | 136 | 0.875 | 126 | 0.45833
| Shyampur | 135 | 19:30 | 128 | 12:00 | Halishahar | 139 | 0.77083 | 127 | 0.45833
| Bhulta | 134 | 18:00 | 128 | 12:00 | Baraulia | 140 | 0.95833 | 128 | 0.41667
| Madanganj | 140 | 18:30 | 132 | 12:00 | Sikalbaha | 140 | 0.79167 | 128 | 0.5
| Shitalakhya | 142 | 18:30 | 133 | 12:00 | Dohazari | 137 | 0.875 | 126 | 0.5
| Rahim steal | 140 | 19:30 | 135 | 11:00 | Cox'sbazar | 130 | 0.83333 | 118 | 0.54167
| Matuail | 140 | 21:00 | 134 | 12:00 | Chandraghona | 139 | 0.77083 | 130 | 0.45833
| Ghorasal | 140 | 1:00 | 138 | 16:00 | Kaptai | 137 | 0.875 | 127 | 0.5
| Narsinghdi | 138 | 17:00 | 134 | 12:00 | A. Khaer Stl. | 137 | 0.83333 | 127 | 0.41667
| Haripur (SBU) | 140 | 21:00 | 134 | 12:00 | Bakulia | 138 | 0.77083 | 127 | 0.45833
| Ullon | 132 | 1:00 | 127 | 10:00 | Julda | 140 | 0.79167 | 128 | 0.45833
| Hasnabad | 140 | 1:00 | 132 | 15:00 | TK Chemical | 140 | 0.79167 | 130 | 0.16667
| Magbazar | 132 | 4:00 | 125 | 12:00 | Modern Steel | 137 | 0.83333 | 128 | 0.41667
| Maniknagar | 139 | 23:00 | 133 | 12:00 | Shahmirpur | 139 | 0.77083 | 128 | 0.45833
| Bangabhaban | 139 | 23:00 | 133 | 12:00 | Khagrachhari | 137 | 0.77083 | 128 | 0.5
| Narinda | 139 | 23:00 | 133 | 12:00 | Matarbari | 132 | 0.83333 | 121 | 0.45833
| Dhanmondi | 132 | 1:00 | 127 | 10:00 | Baroiar Hat | 138 | 0.75 | 132 | 0.5
| Lalbag | 129 | 23:00 | 119 | 12:00 | Rangamati | 138 | 23:00 | 129 | 11:00
| Madartek | 133 | 24:00 | 124 | 12:00 | Goalpara S/S | 140 | 20:00 | 128 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 140 | 15:00 | 129 | 0.33333
| Aftabnagar | 132 | 22:00 | 126 | 11:00 | Noapara | 138 | 15:00 | 124 | 0.33333
| Fatuiiah | 136 | 18:30 | 129 | 12:00 | Jessore | 134 | 3:00 | 124 | 0.33333
| Mirpur | 131 | 1:00 | 121 | 12:00 | Benapol | 136 | 0.625 | 124 | 0.33333
| Kalyanpur | 132 | 24:00 | 122 | 12:00 | Jhenida | 134 | 1:00 | 125 | 0.33333
| Gulshan | 132 | 24:00 | 124 | 12:00 | Bottail | 137 | 0.16667 | 131 | 0.75
| Uttara | 131 | 24:00 | 121 | 12:00 | G.K Project | 141 | 0.20833 | 138 | 0.33333
| Uttara New | 130 | 24:00 | 119 | 12:00 | Faridpur | 137 | 0.125 | 131 | 0.77083
| Kamrangirchar | 141 | 24:00 | 133 | 12:00 | Madaripur | 141 | 0.625 | 135 | 0.875
| Savar | 131 | 20:00 | 119 | 12:00 | Shariyatpur S/S | 140 | 10:00 | 129 | 0.45833
| Bhasantec | 137 | 24:00 | 127 | 12:00 | Gopalganj | 142 | 0.16667 | 134 | 0.75
| Agargaon | 138 | 24:00 | 128 | 12:00 | Bagerhat | 139 | 16:00 | 125 | 0.33333
| Satmosjid | 137 | 24:00 | 128 | 12:00 | Mongla | 137 | 15:00 | 124 | 0.33333
| Tongi | 142 | 23:00 | 132 | 11:00 | Satkhira | 140 | 15:00 | 128 | 8:00
| Kabirpur | 136 | 24:00 | 125 | 11:00 | Gallamari | 140 | 0.875 | 129 | 0.33333
| Basundhara | 136 | 11:00 | 128 | 13:00 | Magura | 135 | 1:00 | 125 | 0.33333
| Manikganj | 146 | 21:00 | 134 | 11:00 | Norail | 135 | 0.20833 | 123 | 0.54167
| Joydevpur | 143 | 20:00 | 137 | 12:00 | Chuadanga | 133 | 3:00 | 123 | 0.33333
| New Tongi | 141 | 21:00 | 130 | 12:00 | Barisal(N) | 141 | 5:00 | 137 | 12:00
| Kodda | 143 | 21:00 | 136 | 13:00 | Barisal (S) | 140 | 0.625 | 136 | 0.5
| Dhamrai | 135 | 23:00 | 132 | 12:00 | Patuakhali(S) | 138 | 0.41667 | 134 | 0.54167
| Rajendrapur | 140 | 20:00 | 132 | 12:00 | Bhandaria | 139 | 0.20833 | 134 | 0.875
| Valuka | 131 | 21:00 | 124 | 12:00 | Ishurdi | 139 | 2:00 | 133 | 8:00
| Tangail | 132 | 2:00 | 126 | 12:00 | Ruppur Paromanobik | 138 | 1:00 | 134 | 8:00
| Mymensing | 132 | 22:00 | 126 | 12:00 | Natore | 139 | 4:00 | 132 | 12:00
| Kishorganj | 133 | 3:00 | 127 | 18:00 | Bogra | 138 | 4:00 | 131 | 8:00
| Netrokona | 133 | 23:00 | 126 | 11:00 | Noagaon | 134 | 3:00 | 126 | 18:00
| Jamalpur | 141 | 19:00 | 128 | 1:00 | Rajshahi | 140 | 2:00 | 134 | 8:00
| Sherpur | 139 | 21:00 | 125 | 3:00 | Rajshahi New | 142 | 4:00 | 134 | 8:00
| Srimongal | 140 | 24:00 | 137 | 18:30 | C.Nawabganj | 141 | 3:00 | 134 | 8:00
| Shahjibazar | 137 | 15:00 | 134 | 18:00 | Amnura | 140 | 15:00 | 132 | 12:00
| Fenchuganj | 139 | 10:00 | 136 | 6:00 | Pabna | 139 | 3:00 | 133 | 8:00
| Khulawara | 138 | 5:00 | 136 | 19:30 | Shahjadpur | 141 | 7:00 | 135 | 11:00
| Sylhet | 137 | 1:00 | 135 | 12:00 | Serajganj | 135 | 1:00 | 131 | 12:00
| Chatak | 136 | 1:00 | 134 | 18:00 | Niyamatpur | 134 | 2:00 | 125 | 12:00
| Sunamganj | 136 | 1:00 | 134 | 18:00 | Joypurhat | 136 | 2:00 | 125 | 12:00
| Biani Bazar | 137 | 1:00 | 133 | 18:00 | Sherpur(Bogura) | 138 | 14:00 | 131 | 8:00
| Comilla(s) | 130 | 3:00 | 125 | 13:00 | Mohastangor | 137 | 4:00 | 130 | 12:00
| Comilla(n) | 144 | 18:30 | 138 |  | Rangpur | 132 | 17:00 | 120 | 8:00
| Chandpur | 145 | 18:00 | 143 | 10:00 | Lalmonirhat | 130 | 16:00 | 120 | 8:00
| Feni | 140 | 20:00 | 134 | 12:00 | Saidpur | 132 | 17:00 | 119 | 8:00
| Chowmuhani | 138 | 19:00 | 135 | 8:00 | Purbasadipur | 130 | 4:00 | 117 | 9:00
| Ashuganj | 138 | 21:00 | 136 | 12:00 | Thakurgaon | 128 | 16:00 | 117 | 8:00
| Daudkandi | 141 | 21:00 | 135 | 12:00 | Palashbari | 133 | 2:00 | 125 | 12:00
| B.Baria | 134 | 16:00 | 131 | 14:00 | Barapukuria | 133 | 17:00 | 124 | 8:00
| Ramganj | 136 | 17:00 | 134 | 21:00 | Panchagar | 128 | 20:00 | 118 | 12:00
| Chaddagram | 140 | 19:00 | 138 | 9:00 | Joldhaka | 131 | 16:00 | 120 | 9:00
| PHP | 139 | 21:00 | 132 | 12:00 | Kurigram | 130 | 0.66667 | 118 | 0.375

## L-Curve
Date | 2020-12-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 67 | 4882 | 1849 | 6731 |  |  |  | QF-LDC-11
0:30 | 93.5 | 4690 | 1763 | 6453 | Date: | 2020-12-21
1:00 | 120 | 4498 | 1677 | 6175
1:30 | 103 | 4395.5 | 1634.5 | 6030
2:00 | 86 | 4293 | 1592 | 5885
2:30 | 85 | 4193.5 | 1620 | 5813.5 | [5 empty] | Gen. at Eve. Peak | 8862 | 8862 MW (19:30 )
3:00 | 84 | 4094 | 1648 | 5742 | [6 empty] | 19:30
3:30 | 77 | 4066 | 1599 | 5665 | [5 empty] | Gen. at Day Peak | 7108 | 7108 MW (12:00 )
4:00 | 70 | 4038 | 1550 | 5588 | [6 empty] | 12:00
4:30 | 65 | 4002 | 1571 | 5573 | [5 empty] | Highest Generation | 8862
5:00 | 60 | 3966 | 1592 | 5558 | [6 empty] | 19:30
5:30 | 36.5 | 4011.5 | 1616 | 5627.5
6:00 | 13 | 4057 | 1640 | 5697
6:30 | 29 | 4154 | 1720 | 5874
7:00 | 45 | 4251 | 1800 | 6051
7:30 | 52.5 | 4387.5 | 1887 | 6274.5
8:00 | 60 | 4524 | 1974 | 6498
8:30 | 50 | 4648 | 2000 | 6648
9:00 | 40 | 4772 | 2026 | 6798
9:30 | 80 | 4814.5 | 2023.5 | 6838
10:00 | 120 | 4857 | 2021 | 6878
10:30 | 100 | 4897 | 1987.5 | 6884.5
11:00 | 80 | 4937 | 1954 | 6891
11:30 | 60 | 5023 | 1976.5 | 6999.5
12:00 | 40 | 5109 | 1999 | 7108
12:30 | 55 | 5170.5 | 2015 | 7185.5
13:00 | 70 | 5232 | 2031 | 7263
13:30 | 80 | 5238.5 | 1948.5 | 7187
14:00 | 90 | 5245 | 1866 | 7111
14:30 | 245 | 4822 | 1938 | 6760
15:00 | 400 | 4399 | 2010 | 6409
15:30 | 320 | 4541 | 2019 | 6560
16:00 | 240 | 4683 | 2028 | 6711
16:30 | 210 | 4793 | 2061.5 | 6854.5
17:00 | 180 | 4903 | 2095 | 6998
17:30 | 105 | 5329.5 | 2492 | 7821.5
18:00 | 30 | 5756 | 2889 | 8645
18:30 | 34 | 5861 | 2880 | 8741
19:00 | 38 | 5966 | 2871 | 8837
19:30 | 65 | 6013 | 2849 | 8862
20:00 | 94 | 5918 | 2810 | 8728 |  |  |  | Executive Engineer
20:30 | 70 | 5799.5 | 2783.5 | 8583 |  |  |  | Network Operation Division
21:00 | 46 | 5681 | 2757 | 8438
21:30 | 65.5 | 5458.5 | 2621.5 | 8080
22:00 | 85 | 5236 | 2486 | 7722 |  |  |  |  | Page 6 of 7
22:30 | 69.5 | 5161.5 | 2314 | 7475.5
23:00 | 54 | 5087 | 2142 | 7229
23:30 | 60.5 | 4984.5 | 1995.5 | 6980
24:00 | 67 | 4882 | 1849 | 6731
8862 MW (19:30 )
7108 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-21 |  | Energy | 168080169
[11 empty] | 2020-12-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2547 | 412 | 1310 | 2189 | 538 | 40 | 6 | 0 | 76 | 0
0:30 | 2730 | 412 | 1365.5 | 1513 | 512.5 | 37.5 | 3 | 0 | 73 | 0 | Date: | 2020-12-21
1:00 | 2913 | 412 | 1421 | 837 | 487 | 35 | 0 | 0 | 70 | 0
1:30 | 2921 | 411 | 1421.5 | 696.5 | 477 | 35 | 0 | 0 | 68 | 0 | [7 empty] | Total Energy | 168.0802 | Total Energy Gen 168.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 168.080 MKWHr
2:00 | 2929 | 410 | 1422 | 556 | 467 | 35 | 0 | 0 | 66 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2947 | 410 | 1445 | 453.5 | 457 | 35 | 0 | 0 | 66 | 0 | [7 empty] | Energy Requirement | 168.0802
3:00 | 2965 | 410 | 1468 | 351 | 447 | 35 | 0 | 0 | 66 | 0
3:30 | 2962 | 363 | 1459 | 333 | 448 | 35 | 0 | 0 | 65 | 0 | [6 empty] | Shortage
4:00 | 2959 | 316 | 1450 | 315 | 449 | 35 | 0 | 0 | 64 | 0
4:30 | 2964 | 316 | 1463.5 | 283 | 448.5 | 35 | 0 | 0 | 63 | 0
5:00 | 2969 | 316 | 1477 | 251 | 448 | 35 | 0 | 0 | 62 | 0
5:30 | 2998 | 316 | 1490 | 280 | 448.5 | 35 | 0 | 0 | 60 | 0
6:00 | 3027 | 316 | 1503 | 309 | 449 | 35 | 0 | 0 | 58 | 0
6:30 | 3038.5 | 363 | 1523 | 393 | 464 | 35 | 0 | 0 | 57 | 0.5 |  |  |  |  | Coal
7:00 | 3050 | 410 | 1543 | 477 | 479 | 35 | 0 | 0 | 56 | 1
7:30 | 3070.5 | 457 | 1502.5 | 646 | 498 | 35 | 0 | 0 | 59 | 6.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3091 | 504 | 1462 | 815 | 517 | 35 | 0 | 0 | 62 | 12
8:30 | 3067.5 | 504 | 1432 | 1043 | 461 | 35 | 24 | 0 | 62 | 19.5
9:00 | 3044 | 504 | 1402 | 1271 | 405 | 35 | 48 | 0 | 62 | 27
9:30 | 3066.5 | 528 | 1369.5 | 1284.5 | 396.5 | 35 | 48 | 0 | 67 | 43
10:00 | 3089 | 552 | 1337 | 1298 | 388 | 35 | 48 | 0 | 72 | 59
10:30 | 3074.5 | 552 | 1355 | 1295.5 | 387 | 35 | 48 | 0 | 73 | 64.5
11:00 | 3060 | 552 | 1373 | 1293 | 386 | 35 | 48 | 0 | 74 | 70
11:30 | 3086 | 552 | 1428 | 1317 | 385.5 | 35 | 48 | 0 | 76 | 72
12:00 | 3112 | 552 | 1483 | 1341 | 385 | 35 | 48 | 0 | 78 | 74
12:30 | 3087 | 552 | 1393.5 | 1515.5 | 386 | 50 | 48 | 0 | 82 | 71.5
13:00 | 3062 | 552 | 1304 | 1690 | 387 | 65 | 48 | 0 | 86 | 69
13:30 | 3062 | 552 | 1304 | 1690 | 387 | 65 | 48 | 0 | 86 | 69
14:00 | 3062 | 552 | 1304 | 1690 | 387 | 65 | 48 | 0 | 86 | 69
14:30 | 2710.5 | 552 | 1270 | 1663.5 | 387.5 | 65 | 48 | 0 | 84 | 55.5
15:00 | 2359 | 552 | 1236 | 1637 | 388 | 65 | 48 | 0 | 82 | 42
15:30 | 2354.5 | 552 | 1200.5 | 1822 | 388 | 66 | 65 | 0 | 82 | 30
16:00 | 2350 | 552 | 1165 | 2007 | 388 | 67 | 82 | 0 | 82 | 18
16:30 | 2398 | 552 | 1164 | 2090 | 398 | 74.5 | 82 | 0 | 86 | 10
17:00 | 2446 | 552 | 1163 | 2173 | 408 | 82 | 82 | 0 | 90 | 2
17:30 | 2538.5 | 671 | 1199 | 2560 | 512 | 62.5 | 180.5 | 0 | 97 | 1
18:00 | 2631 | 790 | 1235 | 2947 | 616 | 43 | 279 | 0 | 104 | 0
18:30 | 2589.5 | 789 | 1242 | 3065.5 | 622 | 41.5 | 287.5 | 0 | 104 | 0
19:00 | 2548 | 788 | 1249 | 3184 | 628 | 40 | 296 | 0 | 104 | 0
19:30 | 2546 | 788 | 1313 | 3127 | 628 | 40 | 318 | 0 | 102 | 0
20:00 | 2549 | 790 | 1256 | 3033 | 628 | 40 | 330 | 0 | 102 | 0
20:30 | 2525.5 | 790 | 1255.5 | 2939.5 | 638 | 40 | 294.5 | 0 | 100 | 0
21:00 | 2502 | 790 | 1255 | 2846 | 648 | 40 | 259 | 0 | 98 | 0
21:30 | 2471.5 | 789 | 1285 | 2569 | 648 | 40 | 183.5 | 0 | 94 | 0
22:00 | 2441 | 788 | 1315 | 2292 | 648 | 40 | 108 | 0 | 90 | 0
22:30 | 2426.5 | 694 | 1283.5 | 2240.5 | 618 | 40 | 87 | 0 | 86 | 0
23:00 | 2412 | 600 | 1252 | 2189 | 588 | 40 | 66 | 0 | 82 | 0
23:30 | 2479.5 | 506 | 1281 | 2189 | 563 | 40 | 36 | 0 | 79 | 0 | Max Temp. in Dhaka |  | 24.9° C
24:00 | 2547 | 412 | 1310 | 2189 | 538 | 40 | 6 | 0 | 76 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 168.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 168.080 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [12 empty] | 30 | 31 | 30 | 32 | 32 | 43 | [8 empty] | 198022
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 0 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 800000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 4 |  | 14 | [6 empty] | 24285
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 15 | 17 | 17 | 16 | 13 | 10 | 5 | 0 | [9 empty] | 112590
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 202 | 202 | 205 | 219 | 202 | 223 | 202 | 222 | 236 | 203 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 162 | 163 | 4464096
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 0 | [6 empty] | 96 |  | 102 | 102 | 102 | 90 | 34 | 34 |  | 483262
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [6 empty] | 7 | 70 | 95 | 95 | 95 | 152 | 200 | 170 | 200 | 230 | 280 |  | 270 | 300 | 300 | 300 | 300 | 300 | 300 | 3540326
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 64 | 64 | 73 | 73 | 73 | 73 | 73 | 45 | 16 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 903272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | [14 empty] | 43 | 44 | 44 | 44 |  | 44 | 44 | 44 |  |  |  | 38 | 300900
22 | Ghorasal Repowered CCPP Unit-4 | 10 | 10 | 10 | 10 | 10 | 12 | 11 | 12 | [18 empty] | 90580
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7038545
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 110 | 150 | 150 |  | 120 | 120 | 120 | 120 | 120 | 80 | 120 | 3107030
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 513720
33 | Ashuganj 225 MW CCPP | 192 | 200 | 203 | 193 | 189 | 185 | 166 | 157 | 180 | 198 | 200 | 197 | 166 | 158 | 222 | 183 | 183 | 185 |  | 183 | 183 | 183 | 183 | 193 | 183 | 183 | 4528000
34 | Ashuganj 450 MW CCPP(South) | 50 | 45 | 50 | 50 | 50 | 45 | 50 | 50 | 80 | 115 | 125 | 165 | 220 | 380 | [12 empty] | 1623000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 492960
36 | Chandpur 150 MW CCPP | 50 | 45 | 52 | 50 | 52 | 52 | 51 | 50 | 51 | 49 | 50 | 55 | 44 | 44 | 45 | 50 | 45 | 50 |  | 45 | 50 | 45 | 45 | 45 | 50 | 46 | 1152210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 359 | 350 | 361 | 352 | 355 | 383 | 370 | 387 | 356 | 354 | 366 | 382 | 354 | 346 | 354 | 344 | 370 | 365 |  | 351 | 346 | 347 | 357 | 348 | 349 | 357 | 8751100
40 | Meghnaghat 450 MW CCPP(MPL) | 185 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4621100
41 | Haripur 360MW CCPP(HPL) | 291 | 315 | 344 | 352 | 353 | 353 | 353 | 330 | 303 | 274 | 274 | 282 | 282 | 242 | 263 | 262 | 253 | 255 |  | 254 | 255 | 255 | 255 | 260 | 270 | 290 | 6908000
42 | RPCL 210MW CCPP | 109 | 111 | 109 | 110 | 109 | 109 | 110 | 110 | 110 | 109 | 105 | 102 | 103 | 85 | 89 | 89 | 104 | 106 |  | 106 | 107 | 106 | 108 | 108 | 111 | 116 | 2473760
43 | Sutiakhali 50 MW Solar PP | [7 empty] | 5 | 13 | 36 | 42 | 46 | 43 | 36 | 26 | 10 | 1 | [9 empty] | 255460
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 618720
46 | Shajibazar 330 MW CCPP | 126 | 126 | 127 | 127 | 128 | 126 | 124 | 126 | 127 | 129 | 129 | 127 | 126 | 126 | 125 | 124 | 124 | 125 |  | 120 | 120 | 122 | 114 | 156 | 157 | 158 | 2915000
47 | Shahjibazar GTPP Unit- 8 & 9 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 31 | 32 | 32 | 32 | 32 | 33 | 33 |  | 33 | 33 | 34 | 34 | 33 | 34 | 34 | 626496
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 76 | 76 | 76 | 74 | 74 | 74 | 74 | 74 | 70 | 70 | 71 | 72 | 72 | 72 | 72 | 50 | 70 |  | 70 | 73 | 73 | 73 | 73 | 73 | 73 | 1728000
| Shahjibazar 100 MW GTPP | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | [18 empty] | 918000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 170 | 189 | 189 | 188 | 188 | 189 | 188 | 189 | 189 | 165 | 150 | 150 | 130 | 130 | 136 | 129 | 143 | 196 |  | 197 | 197 | 197 | 183 | 183 | 128 | 143 | 4137070
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 439000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 7 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 122500
55 | Fenchugonj 51 MW PP (Barakatullah) | 14 | 14 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 11 | 14 | 14 |  | 51 | 51 | 51 | 51 | 53 | 53 | 53 | 510000
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 16 | 14 | 14 | 14 | 14 | 6 |  |  |  | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 314808
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 400 | 420 | 410 | 415 | 406 | [12 empty] | 4970600
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 25 | 35 |  | 35 | 37 | 37 | 35 |  |  |  | 165192
59 | Tangail Palli Power Gen 22 MW
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [5 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 294000
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 296856
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 432108
63 | Impoprt (Tripura) | 70 | 66 | 66 | 64 | 62 | 58 | 56 | 62 | 62 | 72 | 74 | 78 | 86 | 86 | 82 | 82 | 90 | 104 |  | 104 | 102 | 102 | 98 | 90 | 82 | 76 | 1883520
64 | Malancha, Ctg. EPZ (United) | 35 | 36 | 38 | 38 | 38 | 38 | 38 | 9 | 7 | 7 | 7 | 5 | 10 | 8 | 4 | 5 | 9 | 15 |  | 21 | 27 | 28 | 30 | 30 | 34 | 35 | 582720
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 458280
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237960
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 18 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 487410
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 33 | 33 | 32 | 20 | 24 | 24 | 24 | 32 | 28 | 20 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 688680
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 404700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816100
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 51 | 51 | 54 | 95 | 101 | 101 | 101 | 104 | 105 | 106 | 106 | 106 |  | 106 | 106 | 106 | 105 | 106 | 105 | 102 | 1694681
| Feni Lanka Power | [26 empty] | 0
Chowmuhani 113 MW
| Manikgonj 162MW PP(MPGL) | [17 empty] | 90 |  | 126 | 126 | 72 | 37 |  |  |  | 326880
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 1 | 7 | 7 | 7 | 7 | 40 | 50 | 16 | 50 | 60 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 984000
78 | Gazipur 52 MW PP | [15 empty] | 20 | 28 | 49 |  | 51 | 51 | 51 | 51 |  |  |  | 254820
79 | Kodda 150MW PP | [8 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 82 | 133 |  | 133 | 150 | 150 | 100 | 48 | 32 | 6 | 1126560
80 | Jamalpur 95 MW PP(Powerpac) | [12 empty] | 12 | 32 | 32 | 32 | 32 | 68 |  | 90 | 90 | 90 | 90 | 83 | 91 | 24 | 707520
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 30 |  | 43 | 43 | 43 | 25 | 8 | 8 |  | 189782
| Gazipur 100 MW PP | [15 empty] | 15 | 36 | 75 |  | 105 | 105 | 105 | 72 |  |  |  | 443268
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23426
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300737
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [17 empty] | 26 |  | 48 | 48 | 48 | 48 | 48 | 48 |  | 303912
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 86 | 85 | 50 | 50 | 50 | 50 | 50 | 63 | 74 | 75 | 75 | 74 | 75 | 82 | 67 | 82 | 85 | 86 |  | 86 | 86 | 86 | 85 | 85 | 85 | 86 | 1862551
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 100 | 68 | 32 | 30 |  | 2 | 16 | 30 | 57 | 80 | 94 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 94 | 69 | 55 | 50 | 1733760
| Meghnaghat 104 MW PP (OPCL) | 90 | 18 | 34 | 34 |  |  | 16 | 27 | 75 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1674240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 20 | 10 | 20 |  | 64 | 40 | [5 empty] | 117720
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 518472
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 30 | 38 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1203240
94 | Gagnagar 102 MW PP (Digital Power) | [15 empty] | 24 | 40 | 40 |  | 7 | [6 empty] | 147600
95 | Patenga 50MW PP (Baraka) | 31 | 31 |  |  |  |  | 22 | 40 | 44 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 926880
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 24 | 61 |  | 89 | 91 | 92 | 57 |  |  |  | 357120
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 13 | 15 | 15 | 15 | 42 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 15 | 15 |  | 603441
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 934592
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 163 | 110 | 110 | [12 empty] | 1958972
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 17 | 17 | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1175760
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 37 | 33 | 12 | 56 | [8 empty] | 166794
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 19 |  | 50 | 50 | 50 | 32 |  |  |  | 187200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 2 | 32 | 32 | 30 | 30 | 68 | 111 | 64 | 100 | 124 | 138 |  | 149 | 149 | 149 | 149 | 137 | 100 | 72 | 1515312
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 40 | 10 |  |  | 10 | 30 | 100 | 50 | 30 | 30 | 70 | 100 | 50 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1639680
116 | Chandpur 200MW (Desh energy) | 68 | 50 | 50 | 50 | 50 | 50 | 50 | 58 | 75 | 85 | 85 | 85 | 121 | 140 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 2280960
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 80 | 80 | 80 | 90 | 100 | 115 | 132 | 130 | 130 | 130 | 135 | 130 | 100 | 100 | 103 | 123 |  | 123 | 142 | 140 | 143 | 147 | 148 | 143 | 2830254
118 | Bibiyana-III 400 MW CCPP | 180 | 181 | 185 | 180 | 180 | 180 | 180 | 181 | 180 | 120 | 120 | 120 | 120 | 120 | 120 | 135 | 135 | 270 |  | 270 | 270 | 270 | 281 | 281 | 280 | 260 | 4518000
| Jamalpur 115 MW PP (United) | 24 | 24 | 8 |  |  | 2 | 35 | 78 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2060400
| Anwara 300 MW PP (United) | 105 | 52 | 16 |  |  | 16 | 33 | 80 | 155 | 107 | 107 | 108 | 87 | 87 | 101 | 105 | 158 | 158 |  | 158 | 161 | 162 | 178 | 180 | 180 | 160 | 2501564
| Juldah unit-2 (Acorn) | [7 empty] | 30 | 30 | 30 | 30 | 55 | 50 | 20 | 40 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1060800
| Anlima Energy Ltd. | [10 empty] | 17 | 14 |  |  |  | 20 | [10 empty] | 53945
120 | Eastern Zone Total | 4498 | 4293 | 4094 | 4038 | 3966 | 4057 | 4251 | 4524 | 4772 | 4857 | 4937 | 5109 | 5232 | 5245 | 4399 | 4683 | 4903 | 5756 |  | 5966 | 6013 | 5918 | 5681 | 5236 | 5087 | 4882 | 117028481
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [12 empty] | 32 | 32 | 32 | 32 | 32 | 100 |  | 115 | 115 | 115 | 115 | 66 | 16 |  | 669120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 53 | 53 | 53 |  | 53 | 53 | 53 | 70 | 70 | 70 | 35 | 1104960
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 37 | 34 | 35 | 36 | 36 | 36 | 15 | 12 | 17 | 28 | 29 | 13 | 16 | 14 | 35 | 25 | 15 | 16 |  | 34 | 35 | 17 | 15 | 17 | 30 | 36 | 647972
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 3 | 72 |  | 96 | 80 | 80 | 80 | 64 | 64 | 16 | 479424
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 300806
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 20 | 19 | 18 | 18 | 20 | 18 | 17 | 16 | 12 | 12 | 13 | 14 | 14 | 12 | 12 | 14 | 20 |  | 21 | 21 | 22 | 28 | 26 | 25 | 25 | 424900
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 33 | 16 | 40 |  | 40 | 40 | 40 | 8 |  |  |  | 168000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 412 | 410 | 410 | 316 | 316 | 316 | 410 | 504 | 504 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 790 |  | 788 | 788 | 790 | 790 | 788 | 600 | 412 | 13041454
147 | Bheramara 410 MW CCPP | 140 | 145 | 170 | 190 | 205 | 245 | 280 | 270 | 270 | 275 | 270 | 265 | 245 | 200 | 230 | 200 | 195 | 180 |  | 135 | 130 | 135 | 120 | 115 | 145 | 165 | 4967424
148 | Payra 1320 MW | 400 | 380 | 360 | 360 | 360 | 360 | 390 | 430 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 530 |  | 540 | 540 | 540 | 560 | 560 | 500 | 450 | 10295600
149
150 | Barapukuria TPP Unit-1 | 87 | 87 | 87 | 89 | 88 | 89 | 89 | 87 | 85 | 88 | 86 | 85 | 87 | 91 | 88 | 88 | 88 | 86 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2097600
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 8 | 13 | 25 | 16 |  |  |  | 36192
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [15 empty] | 5 | 16 | 7 |  | 7 | 9 | 9 | 21 | 52 | 89 | 122 | 394073
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 195 | 204 | 192 | 140 | 140 | 168 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 129 |  |  |  | 3397945
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 406 | 347 | 398 | 372 | 400 | 405 | 430 | 395 | 387 | 328 | 355 | 420 | 309 | 232 | 397 | 338 | 389 | 419 |  | 329 | 372 | 331 | 325 | 377 | 290 | 310 | 8819454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 501600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 10 | 10 | 11 | 11 | 11 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 214146
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 | [8 empty] | 16100
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 25 |  | 52 | [6 empty] | 66240
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 50 |  | 53 | 53 | 53 | 53 | 26 |  |  | 229216
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 21 | 89 | 109 | 70 | 70 | 108 | 111 | 80 | 110 | 111 | 111 |  | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 1698624
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 25 | 35 | 35 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 70 | 70 | 35 | 805824
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 35 | 35 |  | 70 | 82 | 113 |  | 113 | 113 | 113 | 70 | 11 |  |  | 644160
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30854
178
178