## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-23 | Wednesday
|  |  | Date (day): | 2020-12-23 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11795.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13091 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-22 | 2020-12-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 44 | 43 | 44 | 44 |  | 126 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 105 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 360 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 283 | 273 | 260 | 260 |  |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 shut down for Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 67 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 20 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 22 | 70 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 24 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 84 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 24 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 66 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 147 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2140 | 2573 | 3283 | 3573 | 1361 | 859
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 2 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 164 | 163 | 160 | 160 | 65 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 22 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 79 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 161 | 216 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 97 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 33 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 711 | 890 | 1392 | 1377 | 765 | 104
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 130 | 150 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 183 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 20 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 56 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 137 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 46 | 50 | 50 |  |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 28 | 100 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 102 | 139 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 16 | 18 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 835 | 1039 | 1613 | 1873 | 595 | 381
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 101 | 106 | 115 | 115 | 87 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 64 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 0
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 293 | 395 | 596.6 | 545 | 87 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 40 | 163 | 163 |  | 163 | Under maint.
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 158 | 158 | 158 | 178 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 74 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 202 | 170 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 280 | 270 | 270 | 300
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 854 | 951 | 1152 | 1212 | 178 | 616
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 552 | 788 | 559 | 799
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 |  | 29 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 65 | 65 |  | 44 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 255 | 320 | 320 | 90 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 958 | 1272 | 1319 | 1895 | 90 | 88
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 27 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 10 | 95 | 95
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 310 | 570 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 36 | 15 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 374 | 686 | 865 | 925 | 0 | 202
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 147 | 139 | 220 | 220 |  |  | FGMO
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 372 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 35 | 35 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 763 | 855 | 1366 | 1490 | 391 | 225
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 87 | 86 | 88 | 88
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 161 | 199 | 209 | 201 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7089 | 8860 | 11795.6 | 13091 | 3467 | 2874
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6800.1593 | 8499 | 11314.9892 | 12557.6082
| A. |  | 2020-12-22 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 8860 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5505 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8860 | MW
| 3 | Day peak Generation : |  |  | 7089 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8499 | MW
| 4 | Evening peak Generation : |  |  | 8860 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 160.9476 | MKWHr | By Solar | 0.437 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 90.2102 | MKWHr |  | By Oil: | 42.4774 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.1333 | MKWHr |  | By Hydro: | 1.0558 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3467 | MW | Dhaka | 3076 | 3076 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2874 | MW | Chittagong | 887 | 887 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6341 | MW | Khulna | 1086 | 1086 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 796.34 | MMCFD |  |  | Rajshahi | 879 | 879 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 105258350.09 | ii) Oil : | Taka | 337189786.59 | Comilla | 730 | 730 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 56639215.65 | Total | Taka | 499087352.33 | Mymensingh | 687 | 687 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.5665 | MKWHr. | Sylhet | 320 | 320 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 40 | MW (E to W) at | 19:00 | hrs | Barisal | 231 | 231 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -182 | MW at | 1:00 | hrs | Rangpur | 603 | 603 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.4° C |  |  | Total | 8499 | 8499 |  | 0
| B. |  | 2020-12-23 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13091 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4091 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 163.4908 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5555 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.8051 | MKWHr. | ii) HVDC Flow at Peak Time |  | 788 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8288 | MKWHr. | iii) Maximum HVDC Flow : |  | 790 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.81 |  | (b) Today: | 98.76 |  | (c) Rule Curve: |  | 103.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 43 | 0 | 0 | 300 | 102 | 0 | 351 | 314 |  | 0 | 225 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 85 | 0 | 0 | 0 | 35 | 55 | 0 | 16 | 25 | 33 | 15 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 36 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 45 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 70 | 159 | 0 | 20 | 0 | 0 | 30 | 53 | 50 | 0 | 158 | 34 | 74 | 0 | 143 | 18 | 0 | 0 | 0 | 14 | 8 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 142 | 260 | 85 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 0 |  | 412 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 12 | 0 | 0 | 0 | 295 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 380 | 27 | 0 | 0 |  | 4580 | 1639 | 6219 | 2601 | 412 | 1341 | 1288 | 467 | 40 | 0 | 70 | 0 | 0 | 98.81
2:00 | 0 | 42 | 0 | 0 | 300 | 102 | 0 | 355 | 287 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 36 | 0 | 120 | 0 | 0 | 0 | 203 | 8 | 50 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 68 | 161 | 0 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 157 | 34 | 74 | 0 | 143 | 18 | 0 | 0 | 0 | 13 | 5 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 142 | 300 | 55 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 0 | 50 | 0 | 83 | 0 | 0 | 0 | 0 |  | 412 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 12 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 |  | 4193 | 1628 | 5821 | 2691 | 412 | 1376 | 797 | 437 | 40 | 0 | 68 | 0 | 0 | 98.81
3:00 | 0 | 43 | 0 | 0 | 300 | 102 | 0 | 357 | 294 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 37 | 0 | 120 | 0 | 0 | 0 | 183 | 8 | 50 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 64 | 167 | 0 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 156 | 34 | 74 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 100 | 310 | 55 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 30 | 0 | 51 | 0 | 0 | 0 | 0 |  | 412 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 12 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 42 | 0 | 0 |  | 4071 | 1606 | 5677 | 2722 | 412 | 1344 | 657 | 438 | 40 | 0 | 64 | 0 | 0 | 98.81
4:00 | 0 | 43 | 0 | 0 | 300 | 102 | 0 | 376 | 335 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 38 | 0 | 120 | 0 | 0 | 0 | 188 | 8 | 44 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 25 | 21 | 62 | 146 | 0 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 156 | 34 | 75 | 0 | 145 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 100 | 303 | 35 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 10 | 0 | 17 | 0 | 0 | 0 | 0 |  | 316 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 12 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 36 | 0 | 0 |  | 3952 | 1553 | 5505 | 2696 | 316 | 1420 | 553 | 418 | 40 | 0 | 62 | 0 | 0 | 98.81
5:00 | 0 | 42 | 0 | 0 | 300 | 102 | 0 | 359 | 331 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 38 | 0 | 120 | 0 | 0 | 0 | 197 | 8 | 55 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 62 | 145 | 0 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 157 | 34 | 10 | 0 | 136 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 108 | 310 | 35 | 0 | 0 | 0 | 50 | 54 | 0 | 0 | 0 | 10 | 0 | 17 | 0 | 0 | 0 | 0 |  | 316 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 36 | 0 | 0 |  | 3989 | 1567 | 5556 | 2718 | 316 | 1355 | 648 | 417 | 40 | 0 | 62 | 0 | 0 | 98.81
6:00 | 0 | 42 | 0 | 0 | 300 | 102 | 0 | 371 | 331 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 31 | 55 | 0 | 16 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 38 | 0 | 135 | 0 | 0 | 0 | 200 | 8 | 50 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 68 | 147 | 0 | 20 | 0 | 0 | 30 | 51 | 50 | 0 | 158 | 34 | 10 | 0 | 136 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 127 | 309 | 55 | 0 | 0 | 0 | 102 | 54 | 0 | 0 | 0 | 20 | 0 | 17 | 0 | 0 | 0 | 0 |  | 316 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 0 | 355 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 310 | 37 | 0 | 0 |  | 4202 | 1597 | 5799 | 2791 | 316 | 1367 | 818 | 399 | 40 | 0 | 68 | 0 | 0 | 98.81
7:00 | 0 | 43 | 0 | 0 | 300 | 102 | 0 | 363 | 315 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 0 | 16 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 34 | 0 | 150 | 0 | 0 | 0 | 189 | 8 | 50 | 20 | 55 | 0 | 30 | 0 | 0 | 0 | 18 | 0 | 25 | 18 | 68 | 166 | 2 | 20 | 0 | 0 | 30 | 14 | 10 | 0 | 156 | 34 | 10 | 0 | 136 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 265 | 0 | 0 | 0 | 0 | 1 | 0 | 100 | 17 | 128 | 300 | 115 | 0 | 0 | 0 | 139 | 54 | 0 | 0 | 0 | 50 | 0 | 35 | 1 | 0 | 0 | 0 |  | 406 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 0 | 335 | 17 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 300 | 37 | 0 | 0 |  | 4289 | 1733 | 6022 | 2811 | 406 | 1228 | 1080 | 388 | 40 | 0 | 68 | 1 | 0 | 98.81
8:00 | 0 | 44 | 0 | 0 | 300 | 101 | 0 | 364 | 335 |  | 0 | 225 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 25 | 30 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 8 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 45 | 20 | 55 | 0 | 40 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 66 | 144 | 30 | 20 | 0 | 0 | 30 | 48 | 33 | 0 | 157 | 34 | 76 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 33 | 4 | 100 | 17 | 133 | 310 | 115 | 0 | 0 | 1 | 141 | 54 | 0 | 0 | 16 | 90 | 0 | 53 | 11 | 0 | 0 | 0 |  | 506 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 12 | 0 | 0 | 0 | 300 | 90 | 0 | 93 | 0 | 70 | 0 | 1 | 25 | 290 | 37 | 0 | 0 |  | 4638 | 2026 | 6664 | 2827 | 506 | 1313 | 1517 | 378 | 40 | 0 | 66 | 17 | 0 | 98.81
9:00 | 0 | 44 | 0 | 0 | 300 | 101 | 0 | 378 | 281 |  | 0 | 225 | 0 | 7 | 12 | 12 | 0 | 0 | 0 | 50 | 0 | 32 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 16 | 6 | 0 | 100 | 0 | 0 | 0 | 225 | 8 | 72 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 64 | 122 | 50 | 20 | 1 | 0 | 30 | 48 | 47 | 0 | 158 | 33 | 75 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 2 | 0 | 300 | 0 | 0 | 0 | 0 | 65 | 10 | 100 | 17 | 138 | 307 | 115 | 0 | 0 | 2 | 159 | 54 | 0 | 0 | 16 | 90 | 0 | 70 | 26 | 0 | 0 | 0 |  | 506 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 12 | 0 | 0 | 0 | 353 | 90 | 0 | 111 | 0 | 70 | 0 | 2 | 35 | 280 | 13 | 0 | 0 |  | 4808 | 2101 | 6909 | 2859 | 506 | 1309 | 1690 | 368 | 40 | 32 | 64 | 41 | 0 | 98.8
10:00 | 0 | 44 | 0 | 0 | 300 | 101 | 0 | 362 | 261 |  | 0 | 225 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 50 | 0 | 80 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 22 | 17 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 14 | 5 | 0 | 130 | 0 | 0 | 0 | 183 | 8 | 46 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 64 | 105 | 50 | 20 | 2 | 0 | 30 | 48 | 47 | 0 | 158 | 32 | 72 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 2 | 0 | 300 | 0 | 0 | 0 | 0 | 66 | 14 | 100 | 17 | 142 | 309 | 75 | 0 | 0 | 3 | 160 | 54 | 0 | 0 | 16 | 90 | 0 | 70 | 37 | 0 | 0 | 0 |  | 530 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 10 | 0 | 0 | 0 | 286 | 90 | 0 | 111 | 0 | 70 | 0 | 3 | 35 | 310 | 15 | 0 | 0 |  | 4738 | 2073 | 6811 | 2749 | 530 | 1218 | 1662 | 397 | 40 | 92 | 64 | 59 | 0 | 98.8
11:00 | 0 | 44 | 0 | 0 | 300 | 102 | 0 | 349 | 262 |  | 0 | 225 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 50 | 0 | 100 | 10 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 22 | 17 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 14 | 4 | 0 | 130 | 0 | 0 | 0 | 183 | 8 | 50 | 23 | 55 | 0 | 40 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 68 | 106 | 50 | 20 | 2 | 0 | 30 | 48 | 46 | 0 | 159 | 32 | 72 | 0 | 163 | 18 | 0 | 0 | 0 | 13 | 2 | 0 | 300 | 0 | 0 | 0 | 0 | 65 | 16 | 100 | 17 | 132 | 281 | 75 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 16 | 90 | 0 | 70 | 42 | 0 | 8 | 0 |  | 531 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 10 | 0 | 0 | 0 | 283 | 90 | 0 | 111 | 0 | 70 | 0 | 4 | 35 | 300 | 15 | 0 | 0 |  | 4729 | 2078 | 6807 | 2712 | 531 | 1206 | 1660 | 387 | 40 | 135 | 68 | 68 | 0 | 98.8
12:00 | 0 | 44 | 0 | 0 | 300 | 102 | 0 | 362 | 283 |  | 0 | 225 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 50 | 0 | 100 | 22 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 24 | 17 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 4 | 0 | 130 | 0 | 0 | 0 | 206 | 8 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 68 | 101 | 50 | 20 | 2 | 0 | 30 | 45 | 46 | 0 | 154 | 31 | 71 | 0 | 163 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 300 | 0 | 0 | 0 | 0 | 66 | 17 | 100 | 28 | 128 | 280 | 75 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 16 | 90 | 0 | 70 | 45 | 0 | 33 | 0 |  | 552 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 402 | 90 | 0 | 111 | 0 | 70 | 0 | 4 | 35 | 310 | 36 | 0 | 0 |  | 4833 | 2256 | 7089 | 2743 | 552 | 1378 | 1704 | 397 | 40 | 135 | 68 | 72 | 0 | 98.8
13:00 | 0 | 44 | 0 | 0 | 300 | 101 | 0 | 382 | 282 |  | 0 | 225 | 0 | 19 | 15 | 30 | 0 | 0 | 0 | 60 | 0 | 100 | 62 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 23 | 17 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 14 | 8 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 45 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 70 | 103 | 64 | 20 | 2 | 0 | 30 | 48 | 46 | 0 | 158 | 32 | 73 | 0 | 202 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 245 | 0 | 0 | 0 | 0 | 72 | 16 | 100 | 73 | 130 | 270 | 98 | 0 | 0 | 4 | 162 | 54 | 0 | 0 | 16 | 92 | 0 | 84 | 40 | 0 | 30 | 0 |  | 456 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 10 | 0 | 0 | 0 | 334 | 90 | 0 | 111 | 0 | 65 | 0 | 5 | 50 | 330 | 35 | 0 | 0 |  | 5015 | 2162 | 7177 | 2801 | 456 | 1316 | 1876 | 416 | 40 | 135 | 70 | 67 | 7177 | 98.8
14:00 | 0 | 44 | 0 | 0 | 300 | 102 | 0 | 352 | 282 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 70 | 0 | 84 | 70 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 25 | 23 | 17 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 51 | 16 | 8 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 49 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 72 | 103 | 24 | 20 | 1 | 0 | 30 | 50 | 46 | 0 | 157 | 31 | 73 | 0 | 202 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 195 | 0 | 0 | 0 | 0 | 78 | 14 | 100 | 100 | 132 | 251 | 115 | 0 | 0 | 3 | 162 | 54 | 0 | 0 | 16 | 70 | 0 | 90 | 21 | 0 | 0 | 0 |  | 457 | 0 | 280 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 10 | 0 | 0 | 0 | 328 | 53 | 0 | 111 | 0 | 37 | 0 | 4 | 35 | 340 | 14 | 0 | 0 |  | 4974 | 2020 | 6994 | 2725 | 457 | 1293 | 1787 | 428 | 70 | 119 | 72 | 43 | 0 | 98.8
15:00 | 0 | 46 | 0 | 0 | 300 | 102 | 0 | 351 | 251 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 50 | 0 | 84 | 70 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 23 | 17 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 5 | 0 | 150 | 0 | 0 | 0 | 184 | 8 | 50 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 74 | 103 | 24 | 20 | 1 | 0 | 30 | 48 | 46 | 0 | 158 | 32 | 72 | 0 | 202 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 65 | 10 | 70 | 100 | 133 | 250 | 115 | 0 | 0 | 2 | 162 | 54 | 0 | 0 | 16 | 50 | 0 | 90 | 22 | 0 | 0 | 0 |  | 552 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 10 | 0 | 0 | 0 | 299 | 53 | 0 | 111 | 0 | 10 | 0 | 3 | 35 | 340 | 15 | 0 | 0 |  | 4788 | 2007 | 6795 | 2658 | 552 | 1228 | 1627 | 430 | 70 | 118 | 74 | 38 | 0 | 98.79
16:00 | 0 | 44 | 0 | 0 | 300 | 99 | 0 | 367 | 273 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 24 | 0 | 48 | 70 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 23 | 17 | 25 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 5 | 0 | 150 | 0 | 0 | 0 | 200 | 8 | 50 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 25 | 21 | 74 | 103 | 24 | 20 | 0 | 0 | 30 | 47 | 49 | 0 | 161 | 31 | 70 | 0 | 202 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 64 | 5 | 70 | 100 | 133 | 290 | 115 | 0 | 0 | 1 | 167 | 54 | 0 | 0 | 16 | 50 | 0 | 90 | 9 | 0 | 9 | 0 |  | 552 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 358 | 53 | 0 | 111 | 0 | 0 | 0 | 2 | 0 | 340 | 36 | 0 | 0 |  | 4776 | 2028 | 6804 | 2762 | 552 | 1328 | 1487 | 426 | 76 | 82 | 74 | 17 | 0 | 98.79
17:00 | 0 | 43 | 0 | 0 | 300 | 102 | 0 | 369 | 273 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 40 | 55 | 9 | 16 | 25 | 23 | 17 | 25 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 7 | 50 | 16 | 6 | 0 | 150 | 0 | 0 | 0 | 183 | 8 | 46 | 23 | 56 | 0 | 51 | 0 | 0 | 5 | 18 | 11 | 25 | 21 | 80 | 105 | 40 | 20 | 0 | 0 | 30 | 49 | 49 | 0 | 158 | 33 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 95 | 0 | 0 | 12 | 0 | 72 | 0 | 100 | 100 | 135 | 240 | 115 | 0 | 0 | 0 | 211 | 38 | 0 | 17 | 16 | 70 | 0 | 90 | 1 | 30 | 20 | 0 |  | 552 | 0 | 260 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 288 | 0 | 0 | 111 | 0 | 55 | 0 | 0 | 20 | 420 | 43 | 0 | 0 |  | 4941 | 2184 | 7125 | 2712 | 552 | 1276 | 1838 | 507 | 41 | 118 | 80 | 1 | 0 | 98.79
18:00 | 0 | 43 | 0 | 0 | 300 | 105 | 0 | 389 | 273 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 24 | 17 | 33 | 5 | 0 | 41 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 50 | 50 | 16 | 12 | 0 | 150 | 0 | 0 | 20 | 200 | 8 | 50 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 20 | 11 | 25 | 21 | 90 | 104 | 70 | 20 | 0 | 0 | 30 | 50 | 49 | 0 | 156 | 32 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 5 | 0 | 185 | 186 | 0 | 52 | 0 | 115 | 0 | 100 | 100 | 133 | 300 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 34 | 16 | 96 | 0 | 90 | 0 | 110 | 0 | 0 |  | 790 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 10 | 0 | 0 | 0 | 418 | 70 | 0 | 111 | 0 | 109 | 0 | 0 | 70 | 480 | 15 | 0 | 0 |  | 5775 | 2884 | 8659 | 2865 | 790 | 1396 | 2740 | 567 | 41 | 170 | 90 | 0 | 0 | 98.79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 43 | 0 | 0 | 300 | 105 | 0 | 360 | 273 |  | 0 | 225 | 0 | 67 | 20 | 55 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 24 | 17 | 33 | 24 | 0 | 40 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 79 | 50 | 16 | 22 | 0 | 150 | 0 | 0 | 20 | 183 | 8 | 46 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 20 | 11 | 25 | 21 | 102 | 106 | 90 | 20 | 0 | 0 | 30 | 53 | 49 | 40 | 158 | 33 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 270 | 0 | 0 | 64 | 0 | 149 | 0 | 100 | 100 | 137 | 270 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 34 | 18 | 97 | 0 | 90 | 0 | 147 | 0 | 0 |  | 788 | 0 | 255 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 10 | 0 | 0 | 0 | 372 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 570 | 15 | 0 | 0 |  | 5848 | 3012 | 8860 | 2762 | 788 | 1402 | 2940 | 656 | 40 | 170 | 102 | 0 | 0 | 98.78
19:30 | 0 | 44 | 0 | 0 | 300 | 105 | 0 | 365 | 273 |  | 0 | 225 | 0 | 100 | 49 | 40 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 24 | 17 | 33 | 24 | 0 | 41 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 93 | 50 | 16 | 25 | 0 | 150 | 0 | 0 | 20 | 204 | 8 | 50 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 25 | 21 | 102 | 105 | 89 | 20 | 0 | 0 | 30 | 53 | 49 | 70 | 156 | 32 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 64 | 0 | 149 | 0 | 100 | 100 | 140 | 230 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 19 | 97 | 0 | 90 | 0 | 95 | 0 | 0 |  | 790 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 10 | 0 | 0 | 0 | 339 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 570 | 22 | 0 | 0 |  | 5879 | 2893 | 8772 | 2737 | 790 | 1410 | 2870 | 652 | 41 | 170 | 102 | 0 | 0 | 0
20:00 | 0 | 44 | 0 | 0 | 300 | 105 | 0 | 367 | 251 |  | 0 | 225 | 0 | 100 | 48 | 40 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 33 | 17 | 33 | 24 | 0 | 41 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 93 | 50 | 16 | 30 | 0 | 150 | 0 | 0 | 20 | 195 | 8 | 50 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 25 | 21 | 102 | 106 | 89 | 20 | 0 | 0 | 30 | 53 | 50 | 70 | 158 | 33 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 64 | 0 | 149 | 0 | 100 | 100 | 140 | 270 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 19 | 98 | 0 | 90 | 0 | 36 | 0 | 0 |  | 788 | 0 | 230 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 11 | 0 | 0 | 0 | 336 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 570 | 35 | 0 | 0 |  | 5850 | 2881 | 8731 | 2785 | 788 | 1405 | 2786 | 654 | 41 | 170 | 102 | 0 | 0 | 98.78
21:00 | 0 | 44 | 0 | 0 | 300 | 105 | 0 | 363 | 254 |  | 0 | 225 | 0 | 100 | 48 | 40 | 0 | 0 | 0 | 24 | 0 | 80 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 16 | 32 | 0 | 150 | 0 | 0 | 20 | 183 | 8 | 47 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 25 | 21 | 98 | 107 | 89 | 20 | 0 | 0 | 30 | 53 | 50 | 70 | 158 | 34 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 32 | 0 | 131 | 0 | 100 | 100 | 142 | 290 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 0 | 98 | 0 | 90 | 0 | 0 | 0 | 0 |  | 788 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 10 | 0 | 0 | 0 | 305 | 90 | 0 | 111 | 0 | 100 | 0 | 0 | 113 | 550 | 36 | 0 | 0 |  | 5622 | 2805 | 8427 | 2786 | 788 | 1378 | 2539 | 632 | 40 | 166 | 98 | 0 | 0 | 98.78
22:00 | 0 | 43 | 0 | 0 | 300 | 105 | 0 | 349 | 253 |  | 0 | 225 | 0 | 100 | 48 | 40 | 0 | 0 | 0 | 20 | 0 | 48 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 16 | 34 | 0 | 150 | 0 | 0 | 40 | 183 | 8 | 46 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 25 | 21 | 90 | 108 | 64 | 20 | 0 | 0 | 30 | 53 | 50 | 70 | 152 | 34 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 200 | 0 | 0 | 0 | 0 | 115 | 0 | 100 | 100 | 142 | 250 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 0 | 100 | 0 | 85 | 0 | 0 | 0 | 0 |  | 790 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 10 | 0 | 0 | 0 | 283 | 90 | 0 | 111 | 0 | 20 | 0 | 0 | 35 | 500 | 34 | 0 | 0 |  | 5345 | 2498 | 7843 | 2736 | 790 | 1355 | 2134 | 581 | 40 | 117 | 90 | 0 | 0 | 98.78
23:00 | 0 | 42 | 0 | 0 | 300 | 105 | 0 | 357 | 253 |  | 0 | 225 | 0 | 100 | 48 | 40 | 0 | 0 | 0 | 0 | 0 | 48 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 16 | 40 | 0 | 150 | 0 | 0 | 70 | 187 | 8 | 46 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 82 | 108 | 64 | 20 | 0 | 0 | 30 | 53 | 50 | 80 | 158 | 33 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 100 | 143 | 251 | 115 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 0 | 0 | 0 |  | 602 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 388 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 440 | 36 | 0 | 0 |  | 5095 | 2219 | 7314 | 2791 | 602 | 1475 | 1686 | 523 | 38 | 117 | 82 | 0 | 0 | 98.78
24:00 | 0 | 45 | 0 | 0 | 300 | 105 | 0 | 350 | 254 |  | 0 | 225 | 0 | 100 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 31 | 16 | 42 | 0 | 150 | 0 | 0 | 95 | 183 | 8 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 76 | 109 | 8 | 20 | 0 | 0 | 30 | 50 | 50 | 110 | 156 | 34 | 74 | 0 | 202 | 19 | 0 | 0 | 0 | 16 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 0 | 100 | 85 | 143 | 250 | 115 | 0 | 0 | 0 | 161 | 36 | 0 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 |  | 412 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 10 | 0 | 0 | 0 | 320 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 440 | 36 | 0 | 0 |  | 4831 | 1891 | 6722 | 2812 | 412 | 1436 | 1384 | 522 | 38 | 42 | 76 | 0 | 0 | 98.78
KWH | 0 | 1211500 | 0 | 0 | 7360473 | 2411863 | 0 | 8826880 | 6796000 |  | 0 | 4745350 | 0 | 979200 | 431448 | 615408 | 0 | 0 | 0 | 691200 | 31104 | 1132800 | 1156888 | 0 | 0 | 0 | 783720 | 1332823 | 247709 | 275076 | 600000 | 638820 | 411700 | 780200 | 63744 | 0 | 427811 | 628000 | 0 | 0 | 3124 | 3819690 | 0 | 0 | 0 |  | 0 | 0 | 285352 | 0 | 254400 | 816480 | 371856 | 593280 | 0 | 3334615 | 0 | 0 | 261000 | 4636000 | 217454 | 1180720 | 481608 | 1345920 | 0 | 1197406 | 0 | 0 | 183874 | 454176 | 228240 | 619600 | 493530 | 1828800 | 2849520 | 927360 | 431064 | 10450 | 0 | 721920 | 1167600 | 1128528 | 385772 | 3607000 | 793824 | 1563840 | 0 | 4235150 | 435000 | 0 | 0 | 0 | 356448 | 128500 | 0 | 5580216 | 148147 | 0 | 244800 | 0 | 1389456 | 109080 | 2146560 | 1395360 | 3228363 | 6805000 | 2359200 | 0 | 0 | 24840 | 3633164 | 1253959 | 0 | 64980 | 421680 | 1701120 | 0 | 1706880 | 262240 | 285120 | 106636 | 0 |  | 12805091 | 0 | 6422112 | 0 | 690240 | 0 | 0 | 0 | 0 | 0 | 52125 | 0 | 451500 | 370272 | 0 | 0 | 0 | 0 | 0 | 470664 | 0 | 0 | 0 | 31680 | 0 | 511680 | 0 | 210060 | 2057455 | 0 | 0 | 0 | 0 | 0 | 0 | 3731191 | 0 | 272738 | 0 | 0 | 0 | 0 | 1371840 | 0 | 2012064 | 0 | 956160 | 0 | 30391 | 920064 | 10075800 | 708818 | 0 | 0 |  | 116795619 | 44151945 | 160947564 | 66712473 | 12805091 | 23497749 | 40588568 | 12133255 | 1055811 | 1888816 | 1828800 | 437001 | 0
Fuel Cost | 0 | 1793020 | 0 | 0 | 8170125.03 | 3183659.16 | 0 | 8915148.8 | 6999880 |  | 0 | 5172431.5 | 0 | 7432128 | 2972676.72 | 5206351.68 | 0 | 0 | 0 | 5204736 | 1596948.48 | 11146752 | 10666507.36 | 0 | 0 | 0 | 5721156 | 10302721.79 | 2442410.74 | 206307 | 450000 | 0 | 0 | 0 | 616404.48 | 0 | 115508.97 | 169560 | 0 | 0 | 29021.96 | 4163462.1 | 0 | 0 | 0 |  | 0 | 0 | 2767914.4 | 0 | 2213280 | 6466521.6 | 468538.56 | 1762041.6 | 0 | 4935230.2 | 0 | 0 | 261000 | 4265120 | 280515.66 | 1357828 | 544217.04 | 1884288 | 0 | 2047564.26 | 0 | 0 | 1755996.7 | 576803.52 | 171180 | 1084300 | 370147.5 | 13716000 | 3020491.2 | 8420428.8 | 547451.28 | 166573 | 0 | 1155072 | 2078328 | 1760503.68 | 439780.08 | 3751280 | 1563833.28 | 2986934.4 | 0 | 7326809.5 | 952650 | 0 | 0 | 0 | 267336 | 97660 | 0 | 42186432.96 | 2515536.06 | 0 | 1272960 | 0 | 13672247.04 | 1275145.2 | 17494464 | 15139656 | 22759959.15 | 6328650 | 21515904 | 0 | 0 | 0 | 27466719.84 | 10921982.89 | 0 | 648500.4 | 3613797.6 | 11329459.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 73757324.16 | 0 | 6743217.6 | 0 | 5425286.4 | 0 | 0 | 0 | 0 | 0 | 543142.5 | 0 | 699825 | 3613854.72 | 0 | 0 | 0 | 0 | 0 | 4165376.4 | 0 | 0 | 0 | 306979.2 | 0 | 982425.6 | 0 | 159015.42 | 12406453.65 | 0 | 0 | 0 | 0 | 0 | 0 | 4925172.12 | 0 | 409107 | 0 | 0 | 0 | 0 | 14322009.6 | 0 | 19094487.36 | 0 | 7419801.6 | 0 | 335820.55 | 6799272.96 | 44232762 | 0 | 0 | 0 |  | 382281950.37 | 206341333.84 | 588623284.21 | 74571066.15 | 73757324.16 | 30687283.94 | 319109743.79 | 56639215.65 | 285068.97 | 18080042.8 | 13716000 | 1777538.75 | 0
Yesterday Day Peak | 0 | 44 | 0 | 0 | 300 | 102 | 0 | 362 | 283 |  | 0 | 225 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 50 | 0 | 100 | 22 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 24 | 17 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 4 | 0 | 130 | 0 | 0 | 0 | 206 | 8 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 18 | 68 | 101 | 50 | 20 | 2 | 0 | 30 | 45 | 46 | 0 | 154 | 31 | 71 | 0 | 163 | 18 | 0 | 0 | 0 | 14 | 2 | 0 | 300 | 0 | 0 | 0 | 0 | 66 | 17 | 100 | 28 | 128 | 280 | 75 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 16 | 90 | 0 | 70 | 45 | 0 | 33 | 0 |  | 552 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 402 | 90 | 0 | 111 | 0 | 70 | 0 | 4 | 35 | 310 | 36 | 0 | 0 |  | 7089 | DayPeak
Yesterday Evening Peak | 0 | 43 | 0 | 0 | 300 | 105 | 0 | 360 | 273 | 0 | 0 | 225 | 0 | 67 | 20 | 55 | 0 | 0 | 0 | 24 | 7 | 84 | 70 | 0 | 0 | 0 | 54 | 55 | 36 | 16 | 25 | 24 | 17 | 33 | 24 | 0 | 40 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 79 | 50 | 16 | 22 | 0 | 150 | 0 | 0 | 20 | 183 | 8 | 46 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 20 | 11 | 25 | 21 | 102 | 106 | 90 | 20 | 0 | 0 | 30 | 53 | 49 | 40 | 158 | 33 | 74 | 0 | 202 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 270 | 0 | 0 | 64 | 0 | 149 | 0 | 100 | 100 | 137 | 270 | 115 | 0 | 0 | 0 | 216 | 54 | 0 | 34 | 18 | 97 | 0 | 90 | 0 | 147 | 0 | 0 |  | 788 | 0 | 255 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 10 | 0 | 0 | 0 | 372 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 570 | 15 | 0 | 0 |  | 8860 | EvPeak
Forecast for Evening | 0 | 44 | 0 | 0 | 300 | 108 | 0 | 412 | 260 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 40 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 20 | 0 | 80 | 0 | 0 | 360 | 221 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 25 | 21 | 148 | 115 | 95 | 20 | 0 | 0 | 30 | 51 | 44 | 163 | 158 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 0 |  | 100 |  | 799 | 16 | 320 | 0 | 115 | 220 | 0 | 0 | 30 | 65 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 44 | 0 | 0 | 300 | 108 | 0 | 412 | 260 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 40 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 10 | 0 | 80 | 0 | 0 | 360 | 221 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 20 | 139 | 115 | 95 | 20 | 1.6 | 0 | 30 | 51 | 44 | 163 | 158 | 33 | 86 | 0 | 170 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 270 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 0 |  | 100 |  | 559 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 30 | 65 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 0 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 44 | 0 | 0 | 300 | 106 | 0 | 365 | 256 | 0 | 0 | 225 | 0 | 21 | 0 | 15 | 0 | 0 | 0 | 1 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 55 | 0 | 13 | 25 | 27 | 0 |  | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 16 | 10 | 0 | 80 | 0 | 0 | 360 | 170 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 1 | 21 | 0 | 33 | 18 | 60 | 109 | 0 | 20 | 1 | 0 | 30 | 51 | 50 | 130 | 158 | 34 | 73 | 0 | 163 | 19 | 0 | 0 | 0 | 13 | 2 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 100 | 50 | 107 | 260 | 46 | 0 | 0 | 0 | 155 | 54 | 0 | 0 | 0 | 70 | 0 | 90 | 10 | 0 | 0 | 0 | 0 | 458 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 10 | 0 | 0 | 0 | 345 | 90 | 0 | 69 | 0 | 0 | 0 | 1 | 0 | 450 | 34 | 0 | 0 | 0
199
| Minimum Generation |  | 5505 | 4:00
| Highest Generation |  | 8860 | 19:00
| Day Peak Generation |  | 7089 | 12:00
| Evening Peak Generation |  | 8860 | 19:00
| HVDC Max Flow |  | 790 | 18:00
| HVDC EvPeak Flow |  | 788 | 19:00
| Load factor L.F |  | 75.69%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7089 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5555 | MW
Evening Peak Generation : |  | 8860 | MW Hour : | 19:00 | Available Max Generation : |  | 13091 | MW
E.P. Demand (at gen end) : |  | 8860 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8860 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4091 | MW
Total Gen. (MKWH) : |  | 160.9476 | System Load Factor : | 75.69% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -182 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-23
Actual : | 98.76 | Ft.(MSL) , | Rule curve : | 103.9 | Ft.( MSL )
Gas Consumed : | Total = | 796.34 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 105258350.09
: |  | Coal : | 56639215.65 | Oil : | 337189786.59 | Total : | 499087352.33
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3223.7653 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1091.0083 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 976.5717 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 882.0828 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 797.3086 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 643.3866 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 366.5064 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.8335 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 496.1793 |  |  | 0 | 0%
Total | 0 |  | 8642.6426 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
|  |  |  | 2) Baghabari-71 &100 MW | 11) Fenchugonj CCPP Phase-2
3) Ghorasal Unit-1,2,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,3 CCPP
9) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Halishahar-Khulsi 132 kV Ckt-1 was under shut down from 09:05 to 14:39 for A/M.
b) Savar 132/33 kV T-3 transformer was under shut down from 09:27 to 16:45 for A/M.
c) Daudkandi-Sonargaon 132 kV Ckt-1 was under shut down from 10:15 to 12:39 for A/M.
d) Daudkandi-Sonargaon 132 kV Ckt-2 was under shut down from 12:40 to 14:54 for A/M.
e) Ghorasal-Ashuganj 132 kV Ckt-2 was under shut down from 10:05 to 20:18 for A/M.
f) Kaliakoir-Dhamrai 132 kV Ckt-1 was under shut down from 09:33 to 15:01 for A/M.
g) Mymensing 132/33 kV T-2 transformer was under shut down from 09:25 to 17:15 for A/M.
h) Jamalpur-UMPL 132 kV Ckt-2 was under shut down from 09:27 to 16:52 for A/M.
i) UMPL-Sherpur 132 kV Ckt-2 was under shut down from 09:08 to 16:44 for A/M.
j) Hasnabad 132/33 kV T-3 transformer was under shut down from 08:06 to 21:11 for A/M.
k) Dohazari-Sikalbaha 132 kV Ckt-1 was under shut down from 08:20 to 16:56 for A/M.
l) Shahjibazar 132/33 kV T-4 transformer was under shut down from 08:34 to 16:17 for A/M.
m) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 10:56 to 16:41 for D/W.
n) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 08:34 to 10:45 for D/W.
o) BSRM 230 kV Bus-1 was under shut down from 09:34 to 20:05 for D/W.
p) Munshiganj 33 kV Bus-1 was under shut down from 08:37 to 15:00 for A/M. |  |  |  |  | About 25 MW power interruption occurred under Munshiganj S/S area
from 08:37 to 15:00.
q) Dohazari-100 MW PP 132 kV Ckt was under shut down from 08:35 to 16:04 A/M.
r) Saidpur-Jaldhaka 132 kV Ckt-2 was under shut down from 08:41 to 16:29 for A/M.
s) Bogura-Barapukuria 230 kV Ckt-2 was under shut down from 08:22 to 16:12 for A/M.
t) Natore-Rajshahi 132 kV Ckt-2 was under shut down from 08:01 to 16:53 for A/M.
u) Mirpur-Aminbazar 132 kV Ckt-2 was under shut down from 09:34 to 17:53 for protection work.
v) Haripur 132 kV Main Bus was under shut down from 12:50 to 15:58 for R/H maint. Work at
Bus coupler breaker.
w) Kaptai unit-3 synchronized at 13:13.
x) Matarbari-Cox's Bazar 132 kV Ckt was switched on at 10:36.
y) After maint. Work HVDC Bheramara pole-2 de-blocked at 11:21.
z) Aminbazar-Agargaon 239 kV Ckt-1 was under shut down from 13:56 to 17:01 for loop refixing
at Aminbazar end.
aa) Kulaura 132/33 kV T-2 transformer was under shut down from 14:00 to 20:21 for protection test.
ab) GPH-BSRM 230 kV Ckt was under shut down from 08:46 to 15:42 for A/M.
ac) Ullon-Dhanmondi 132 kV Ckt-3 was under shut down from 09:57 to 15:15 for A/M.
ad) BSRM 230 kV Bus-2 was shut down at 20:42 for D/W.
ae) Ashuganj(S) GT was synchronized at 17:11.
af) Kushiara CCPP GT was synchronized at 18:35.
ag) Ullon-Dhanmondi 132 kV Ckt-2 was under shut down from 15:50 to 17:12 for A/M.
ah) Shyampur 132/33 kV T-2 transformer was under shut down from 21:10 to 22:53for R/H maint. work.
ai) Ghorashal-Ishurdi 230 kV Ckt-2 was shut down at 07:29(23/12/2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 43 | 1211500 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7360473
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2411863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8826880 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 273 | 6796000 | Frequency Control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4745350 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 67 | 979200 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 20 | 431448 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 615408
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 70 | 1156888 | High Voltage.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 275076 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 691200 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 31104 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 783720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 84 | 1132800 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1332823
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 36 | 247709 | High Voltage.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1238820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 780200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 24 | 63744 | High Voltage.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 5580216 | High Voltage.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 148147 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1389456
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1706880 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 147 | 285120
| Dhaka area Total |  |  |  | 6057 | 2573 | 50633725
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 2 | 3124 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 109080
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 816480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1055811 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 163 | 3819690 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 285352 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2146560
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 371856 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 593280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 79 | 254400 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24840
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 216 | 3633164 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1253959
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 97 | 1701120 | Engine problem
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 106636
| Chattogram area Total |  |  |  | 2266 | 890 | 16175352
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 3334615
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4636000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 20 | 261000 | Synchronized at 17:11.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 481608 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1345920 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1197406
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3228363
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 46 | 1180720 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1395360 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 454176
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1828800 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 619600 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 183874 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 493530
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 64980 | High Voltage.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 421680 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1039 | 21573326
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2849520 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 431064
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 927360
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10450
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 64 | 244800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2359200 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 262240
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 687 | 395 | 7084634
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721920 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 40 | 385772 | Synchronized at 18:35.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3607000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1167600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1128528
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 128500
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 793824 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1563840 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 4235150
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 435000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 356448 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 270 | 6805000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | under maint.
| Sylhet Area Total |  |  |  | 1988 | 951 | 21328582
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 788 | 12805091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 690240
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 255 | 6422112 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 52125 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1371840 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1272 | 21341408
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 370272 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 451500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 272738 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 10075800 | Line O/L
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 15 | 708818 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1054 | 686 | 11879128
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 139 | 3731191 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 0 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210060
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 31680
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 35 | 470664 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 2012064
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 920064
| Rajshahi Area Total |  |  |  | 2183 | 855 | 7887403
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 86 | 2057455
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 956160
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30391
| Rangpur Area Total |  |  |  | 605 | 199 | 3044006
| Total |  |  |  | 20104 | 8860 | 160947564
| Eastern Grid Total |  |  |  | 13978 | 5848 | 116795619
| Western Grid Total |  |  |  | 6126 | 3012 | 44151945
| National Grid Total |  |  |  | 20104 | 8860 | 160947564
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-22
| (a) ENTIRE EASTERN GRID : |  | 5700 | MW | (b) ENTIRE WESTERN GRID : |  | 2799 | MW
| i) Dhaka area |  | 3076 | MW | i) Khulna area |  | 1086 | MW
| ii) Chittagong area |  | 887 | MW | ii) Rajshahi area |  | 879 | MW
| iii) Comilla area |  | 730 | MW | iii) Barisal area |  | 231 | MW
| iv) Mymensingh area |  | 687 | MW | iv) Rangpur area |  | 603 | MW
| v) Sylhet area |  | 320 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8499 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 102 | 12:00 | Jamalpur | 89 | 18:30 | Benapol | 36 | 18:00
| Munsiganj | 82 | 21:00 | Sherpur | 88 | 18:00 | Jhenida | 82 | 18:00
| Sonargaon | 54 | 19:30 | Srimongal | 26 | 18:00 | Bottail | 98 | 18:00
| Shyampur | 162 | 10:00 | Shahjibazar | 83 | 18:00 | G.K Project | 35 | 18:00
| Bhulta | 162 | 20:00 | Fenchuganj | 27 | 18:00 | Faridpur | 132 | 18:30
| Madanganj | 53 | 19:30 | Kulawara | 29 | 19:30 | Madaripur | 63 | 21:00
| Shitalakhya | 97 | 10:00 | Sylhet | 73 | 19:00 | Sariatpur | 40 | 19:30
| Rahim steel | 6 | 9:00 | Chatak | 22 | 18:00 | Gopalganj | 59 | 18:30
| Matuail | 60 | 9:00 | Sunamganj | 27 | 19:00 | Bagerhat | 85 | 18:00
| Ghorasal | 66 | 19:00 | Biani Bazar | 38 | 18:00 | Mongla | 36 | 14:00
| Narsingdi | 125 | 18:30 | Comilla (S) | 104 | 18:30 | Satkhira | 75 | 19:00
| Haripur (SBU) | 102 | 18:30 | Comilla(N) | 57 | 19:30 | Gallamari | 21 | 13:00
| Ullon | 38 | 18:00 | Chandpur | 62 | 19:00 | Magura | 38 | 18:00
| Hasnabad | 128 | 19:00 | Feni | 73 | 18:00 | Norail | 24 | 19:00
| Magbazar | 61 | 18:30 | Chowmuhani | 118 | 19:00 | Chuadanga | 63 | 18:00
| Maniknagar | 62 | 12:00 | Ashuganj | 40 | 12:00 | Barisal(N) | 30 | 19:30
| Bangabhaban | 20 | 13:00 | Daudkandi | 100 | 19:00 | Barisal (S) | 68 | 19:00
| Narinda | 70 | 19:00 | B.Baria | 94 | 19:30 | Patuakhali | 79 | 20:00
| Dhanmondi | 82 | 13:00 | Ramganj | 72 | 19:00 | Bhandaria | 40 | 19:30
| Lalbag | 70 | 13:00 | Chaddagram | 32 | 17:00 | Borhan Uddin | 26 | 19:30
| Madartek | 44 | 18:00 | PHP | 10 | 17:00 | Ishurdi | 46 | 18:30
| Dhaka University | 0 | #NUM! | Madunaghat | 46 | 19:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 66 | 0.77083 | Natore | 81 | 0.75
| Fatullah | 29 | 10:00 | Khulshi | 152 | 11:00 | Bogra | 120 | 19:00
| Mirpur | 69 | 18:00 | Halishahar | 91 | 19:00 | Noagaon | 77 | 19:00
| Kalyanpur | 57 | 18:00 | Baraulia | 145 | 12:00 | Rajshahi | 96 | 20:00
| Gulshan | 72 | 11:00 | Sikalbaha | 19 | 18:30 | Rajshahi New | 8 | 20:00
| Uttara | 67 | 18:00 | Dohazari | 60 | 18:30 | C.Nawabganj | 51 | 20:00
| Uttara New | 23 | 18:00 | Cox'sbazar | 73 | 18:00 | Amnura | 30 | 19:30
| Kamrangirchar | 75 | 18:00 | Chandraghona | 22 | 18:00 | Pabna | 79 | 18:30
| Savar | 125 | 18:00 | Kaptai | 3.8 | 18:00 | Shahjadpur | 79 | 19:00
| Bhasantec | 96 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 66 | 19:30
| Agargaon | 42 | 18:00 | Bakulia | 69 | 13:00 | Niyamatpur | 44 | 19:00
| Satmosjid | 66 | 0.54167 | Julda | 21 | 0.041667 | Joypurhat | 46 | 0.75
| Tongi | 55 | 11:00 | TK chemical | 20 | 20:00 | Sherpur(Bogura) | 38 | 19:00
| Kabirpur | 159 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 34 | 18:30
| Basundhara | 104 | 18:00 | Shahmirpur | 22 | 18:00 | Rangpur | 115 | 18:30
| Manikganj | 44 | 19:00 | Khagrachhari | 20 | 1:00 | Lalmonirhat | 48 | 18:00
| Joydevpur | 97 | 18:00 | Matarbari | 22 | 18:00 | Saidpur | 89 | 18:00
| New Tongi | 94 | 9:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 85 | 18:30
| Kodda | 186 | 19:00 | Rangamati | 8 | 18:00 | Thakurgaon | 64 | 18:00
| Dhamrai | 68 | 18:00 | Abul Khair 230 | 157 | 12:00 | Palashbari | 88 | 18:30
| Rajendrapur | 72 | 18:30 | BSRM | 145 | 12:00 | Barapukuria | 39 | 18:30
| Valuka | 80 | 18:30 | GPH Ispat | 64 | 4:00 | Panchagar | 44 | 18:30
| Tangail | 120 | 22:00 | Goalpara | 17 | 13:00 | Joldhaka | 19 | 19:00
| Mymensing | 156 | 18:00 | Central s/s | 80 | 18:30 | Kurigram | 40 | 19:00
| Kishorganj | 82 | 19:00 | Noapara | 46 | 18:00
| Netrokona | 85 | 18:30 | Jessore | 78 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 6:00 | 406 | 17:00 | Kaliakoir | 394 | 0.16667 | 288 | 24:00
| Bheramara | 404 | 5:00 | 392 | 10:00 | Bhulta | 387 | 0.041667 | 374 | 0.5
| Ashuganj(N) | 390 | 6:00 | 378 | 12:00 | Gopalganj | 418 | 0.45833 | 393 | 0.77083
| Payra | 420 | 1:00 | 405 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 2:00 | 236 | 1:00 | Comilla (N) | 240 | 24:00 | 234 | 12:00
| Ishurdi | 241 | 1:00 | 230 | 19:30 | Hathazari | 228 | 18:30 | 216 | 16:00
| Ashuganj | 240 | 1:00 | 235 | 15:00 | Megnaghat | 238 | 7:00 | 224 | 16:00
| Serajganj | 234 | 1:00 | 229 | 18:00 | Fenchuganj | 245 | 6:00 | 238 | 18:30
| Baghabari | 244 | 14:00 | 238 | 18:00 | Siddhirganj | 235 | 1:00 | 227 | 15:00
| Barapukuria | 232 | 1:00 | 225 | 16:00 | Maniknagar | 233 | 1:00 | 225 | 12:00
| Bogra | 237 | 1:00 | 227 | 18:00 | Agargaon | 234 | 5:00 | 224 | 12:00
| Rajshahi | 234 | 23:00 | 221 | 18:00 | Barisal | 249 | 22:00 | 238 | 19:30
| Khulna South | 238 | 6:00 | 226 | 18:00 | AKSML | 231 | 1:00 | 217 | 12:00
| Rampura | 232 | 1:00 | 228 | 16:00 | BSRM | 231 | 24:00 | 220 | 12:00
| Haripur | 232 | 1:00 | 225 | 12:00 | Bibiyana | 245 | 1:00 | 239 | 17:00
| Hasnabad | 236 | 1:00 | 225 | 12:00 | Bhulta | 234 | 19:00 | 227 | 17:00
| Shyampur | 233 | 1:00 | 220 | 12:00 | Ashuganj (S) | 237 | 3:00 | 232 | 12:00
| Aminbazar | 235 | 1:00 | 225 | 15:00 | Kaliakoir | 234 | 1:00 | 221 | 16:00
| Tongi | 232 | 4:00 | 223 | 15:00 | GPH | 228 | 1:00 | 215 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 1:00 | 135 | 12:00 | Madanhat | 141 | 0 | 132 | 0.5
| Munsiganj | 140 | 1:00 | 134 | 12:00 | Hathazari | 139 | 0.77083 | 133 | 0.5
| Sonargaon | 138 | 1:00 | 134 | 11:00 | Khulshi | 136 | 0.77083 | 130 | 0.5
| Shyampur | 136 | 1:00 | 130 | 12:00 | Halishahar | 138 | 0.79167 | 131 | 0.5
| Bhulta | 133 | 1:00 | 129 | 12:00 | Baraulia | 138 | 0.041667 | 132 | 0.5
| Madanganj | 136 | 1:00 | 133 | 10:00 | Sikalbaha | 137 | 0.29167 | 132 | 0.16667
| Shitalakhya | 142 | 18:30 | 133 | 12:00 | Dohazari | 136 | 0 | 127 | 0.5
| Rahim steal | 139 | 1:00 | 136 | 11:00 | Cox'sbazar | 129 | 0.041667 | 117 | 0.5
| Matuail | 139 | 1:00 | 135 | 12:00 | Chandraghona | 139 | 0.33333 | 132 | 0.5
| Ghorasal | 140 | 1:00 | 140 | 1:00 | Kaptai | 137 | 0.75 | 132 | 0.20833
| Narsinghdi | 138 | 1:00 | 134 | 12:00 | A. Khaer Stl. | 136 | 0.041667 | 131 | 0.5
| Haripur (SBU) | 140 | 1:00 | 135 | 12:00 | Bakulia | 137 | 0.79167 | 130 | 0.5
| Ullon | 132 | 1:00 | 128 | 11:00 | Julda | 138 | 0.75 | 131 | 0.041667
| Hasnabad | 140 | 18:00 | 135 | 9:00 | TK Chemical | 137 | 0.75 | 132 | 0.45833
| Magbazar | 133 | 4:00 | 127 | 12:00 | Modern Steel | 138 | 0.041667 | 131 | 0.45833
| Maniknagar | 139 | 1:00 | 135 | 12:00 | Shahmirpur | 138 | 0.79167 | 132 | 0.5
| Bangabhaban | 139 | 1:00 | 135 | 12:00 | Khagrachhari | 136 | 0.041667 | 131 | 0.5
| Narinda | 139 | 1:00 | 135 | 12:00 | Matarbari | 131 | 0.29167 | 117 | 0.75
| Dhanmondi | 132 | 1:00 | 128 | 11:00 | Baroiar Hat | 139 | 0.33333 | 134 | 0.5
| Lalbag | 130 | 1:00 | 122 | 12:00 | Rangamati | 137 | 1:00 | 133 | 12:00
| Madartek | 133 | 1:00 | 126 | 16:00 | Goalpara S/S | 139 | 13:00 | 134 | 16:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 13:00 | 134 | 0.66667
| Aftabnagar | 133 | 1:00 | 127 | 12:00 | Noapara | 137 | 4:00 | 132 | 0.29167
| Fatuiiah | 136 | 1:00 | 131 | 11:00 | Jessore | 134 | 10:00 | 127 | 0.75
| Mirpur | 133 | 6:00 | 123 | 12:00 | Benapol | 136 | 0.16667 | 128 | 0.75
| Kalyanpur | 131 | 6:00 | 125 | 12:00 | Jhenida | 135 | 4:00 | 124 | 0.75
| Gulshan | 132 | 6:00 | 126 | 12:00 | Bottail | 137 | 0.125 | 130 | 0.75
| Uttara | 130 | 6:00 | 123 | 12:00 | G.K Project | 141 | 0.20833 | 137 | 0.75
| Uttara New | 138 | 6:00 | 131 | 1:00 | Faridpur | 137 | 0.16667 | 130 | 0.75
| Kamrangirchar | 141 | 1:00 | 133 | 1:00 | Madaripur | 140 | 0.25 | 132 | 0.77083
| Savar | 132 | 1:00 | 123 | 12:00 | Shariyatpur S/S | 141 | 3:00 | 131 | 0.77083
| Bhasantec | 137 | 1:00 | 130 | 12:00 | Gopalganj | 143 | 0.16667 | 130 | 0.77083
| Agargaon | 138 | 1:00 | 130 | 12:00 | Bagerhat | 138 | 6:00 | 130 | 0.75
| Satmosjid | 138 | 1:00 | 131 | 12:00 | Mongla | 136 | 3:00 | 131 | 0.66667
| Tongi | 141 | 18:00 | 136 | 15:00 | Satkhira | 139 | 4:00 | 131 | 20:00
| Kabirpur | 136 | 1:00 | 128 | 16:00 | Gallamari | 140 | 0.041667 | 134 | 0.75
| Basundhara | 141 | 8:00 | 133 | 16:00 | Magura | 135 | 1:00 | 124 | 0.8125
| Manikganj | 143 | 18:00 | 140 | 15:00 | Norail | 134 | 0.20833 | 123 | 0.75
| Joydevpur | 143 | 10:00 | 138 | 16:00 | Chuadanga | 133 | 5:00 | 120 | 0.75
| New Tongi | 140 | 1:00 | 134 | 15:00 | Barisal(N) | 142 | 4:00 | 134 | 19:30
| Kodda | 140 | 13:00 | 133 | 17:00 | Barisal (S) | 140 | 0.20833 | 133 | 0.8125
| Dhamrai | 135 | 1:00 | 127 | 15:00 | Patuakhali(S) | 138 | 0.20833 | 130 | 0.77083
| Rajendrapur | 139 | 18:30 | 135 | 16:00 | Bhandaria | 139 | 0.29167 | 130 | 0.8125
| Valuka | 133 | 6:00 | 125 | 16:00 | Ishurdi | 140 | 1:00 | 135 | 18:00
| Tangail | 136 | 6:00 | 127 | 16:00 | Ruppur Paromanobik | 139 | 3:00 | 135 | 18:30
| Mymensing | 135 | 6:00 | 128 | 16:00 | Natore | 139 | 1:00 | 133 | 18:00
| Kishorganj | 135 | 5:00 | 128 | 18:30 | Bogra | 139 | 1:00 | 134 | 18:00
| Netrokona | 135 | 7:00 | 125 | 18:30 | Noagaon | 134 | 3:00 | 128 | 18:00
| Jamalpur | 140 | 10:00 | 130 | 5:00 | Rajshahi | 141 | 6:00 | 134 | 18:00
| Sherpur | 139 | 21:00 | 130 | 5:00 | Rajshahi New | 142 | 14:00 | 135 | 18:00
| Srimongal | 140 | 1:00 | 137 | 11:00 | C.Nawabganj | 140 | 1:00 | 135 | 20:00
| Shahjibazar | 137 | 1:00 | 134 | 16:00 | Amnura | 141 | 14:00 | 135 | 19:30
| Fenchuganj | 138 | 1:00 | 136 | 9:00 | Pabna | 140 | 6:00 | 133 | 20:00
| Khulawara | 138 | 1:00 | 135 | 17:00 | Shahjadpur | 141 | 4:00 | 139 | 18:00
| Sylhet | 137 | 1:00 | 134 | 13:00 | Serajganj | 136 | 2:00 | 132 | 18:00
| Chatak | 136 | 4:00 | 133 | 18:00 | Niyamatpur | 135 | 3:00 | 126 | 12:00
| Sunamganj | 136 | 1:00 | 134 | 12:00 | Joypurhat | 136 | 1:00 | 129 | 18:00
| Biani Bazar | 137 | 3:00 | 133 | 18:00 | Sherpur(Bogura) | 139 | 1:00 | 133 | 18:00
| Comilla(s) | 132 | 5:00 | 127 | 18:00 | Mohastangor | 138 | 1:00 | 130 | 18:00
| Comilla(n) | 143 | 18:00 | 140 | 11:00 | Rangpur | 130 | 2:00 | 121 | 18:00
| Chandpur | 144 | 23:00 | 142 | 15:00 | Lalmonirhat | 130 | 3:00 | 120 | 18:00
| Feni | 140 | 6:00 | 136 | 16:00 | Saidpur | 132 | 4:00 | 118 | 18:00
| Chowmuhani | 139 | 14:00 | 134 | 22:00 | Purbasadipur | 129 | 1:00 | 115 | 18:00
| Ashuganj | 140 | 6:00 | 136 | 15:00 | Thakurgaon | 132 | 2:00 | 115 | 18:00
| Daudkandi | 140 | 7:00 | 136 | 12:00 | Palashbari | 133 | 1:00 | 126 | 15:00
| B.Baria | 135 | 7:00 | 131 | 16:00 | Barapukuria | 132 | 1:00 | 125 | 18:00
| Ramganj | 138 | 20:00 | 133 | 9:00 | Panchagar | 130 | 3:00 | 113 | 18:00
| Chaddagram | 140 | 19:00 | 137 | 12:00 | Joldhaka | 131 | 6:00 | 117 | 18:00
| PHP | 140 | 6:00 | 134 | 12:00 | Kurigram | 129 | 0.041667 | 120 | 0.75

## L-Curve
Date | 2020-12-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 68 | 4831 | 1891 | 6722 |  |  |  | QF-LDC-11
0:30 | 125 | 4705.5 | 1765 | 6470.5 | Date: | 2020-12-22
1:00 | 182 | 4580 | 1639 | 6219
1:30 | 167 | 4386.5 | 1633.5 | 6020
2:00 | 152 | 4193 | 1628 | 5821
2:30 | 121 | 4132 | 1617 | 5749 | [5 empty] | Gen. at Eve. Peak | 8860 | 9500 MW (19:30 )
3:00 | 90 | 4071 | 1606 | 5677 | [6 empty] | 19:00
3:30 | 61 | 4011.5 | 1579.5 | 5591 | [5 empty] | Gen. at Day Peak | 7089 | 7952.5 MW (12:00 )
4:00 | 32 | 3952 | 1553 | 5505 | [6 empty] | 12:00
4:30 | 39.5 | 3970.5 | 1560 | 5530.5 | [5 empty] | Highest Generation | 8860
5:00 | 47 | 3989 | 1567 | 5556 | [6 empty] | 19:00
5:30 | 73.5 | 4095.5 | 1582 | 5677.5
6:00 | 100 | 4202 | 1597 | 5799
6:30 | 97.5 | 4245.5 | 1665 | 5910.5
7:00 | 95 | 4289 | 1733 | 6022
7:30 | 117.5 | 4463.5 | 1879.5 | 6343
8:00 | 140 | 4638 | 2026 | 6664
8:30 | 75 | 4723 | 2063.5 | 6786.5
9:00 | 10 | 4808 | 2101 | 6909
9:30 | 45 | 4773 | 2087 | 6860
10:00 | 80 | 4738 | 2073 | 6811
10:30 | 140 | 4733.5 | 2075.5 | 6809
11:00 | 200 | 4729 | 2078 | 6807
11:30 | 225 | 4781 | 2167 | 6948
12:00 | 250 | 4833 | 2256 | 7089
12:30 | 145 | 4924 | 2209 | 7133
13:00 | 40 | 5015 | 2162 | 7177
13:30 | 55 | 4994.5 | 2091 | 7085.5
14:00 | 70 | 4974 | 2020 | 6994
14:30 | 145 | 4881 | 2013.5 | 6894.5
15:00 | 220 | 4788 | 2007 | 6795
15:30 | 200 | 4782 | 2017.5 | 6799.5
16:00 | 180 | 4776 | 2028 | 6804
16:30 | 230 | 4858.5 | 2106 | 6964.5
17:00 | 280 | 4941 | 2184 | 7125
17:30 | 160 | 5358 | 2534 | 7892
18:00 | 40 | 5775 | 2884 | 8659
18:30 | 40 | 5811.5 | 2948 | 8759.5
19:00 | 40 | 5848 | 3012 | 8860
19:30 | 10 | 5879 | 2893 | 8772
20:00 | 10 | 5850 | 2881 | 8731 |  |  |  | Executive Engineer
20:30 | 34 | 5736 | 2843 | 8579 |  |  |  | Network Operation Division
21:00 | 58 | 5622 | 2805 | 8427
21:30 | 62.5 | 5483.5 | 2651.5 | 8135
22:00 | 67 | 5345 | 2498 | 7843 |  |  |  |  | Page 6 of 7
22:30 | 58.5 | 5220 | 2358.5 | 7578.5
23:00 | 50 | 5095 | 2219 | 7314
23:30 | 59 | 4963 | 2055 | 7018
24:00 | 68 | 4831 | 1891 | 6722
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-22 |  | Energy | 160947564
[11 empty] | 2020-12-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2812 | 412 | 1436 | 1686 | 522 | 38 | 42 | 0 | 76 | 0
0:30 | 2706.5 | 412 | 1388.5 | 1487 | 494.5 | 39 | 21 | 0 | 73 | 0 | Date: | 2020-12-22
1:00 | 2601 | 412 | 1341 | 1288 | 467 | 40 | 0 | 0 | 70 | 0
1:30 | 2646 | 412 | 1358.5 | 1042.5 | 452 | 40 | 0 | 0 | 69 | 0 | [7 empty] | Total Energy | 160.9476 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2691 | 412 | 1376 | 797 | 437 | 40 | 0 | 0 | 68 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2706.5 | 412 | 1360 | 727 | 437.5 | 40 | 0 | 0 | 66 | 0 | [7 empty] | Energy Requirement | 160.9476
3:00 | 2722 | 412 | 1344 | 657 | 438 | 40 | 0 | 0 | 64 | 0
3:30 | 2709 | 364 | 1382 | 605 | 428 | 40 | 0 | 0 | 63 | 0 | [6 empty] | Shortage
4:00 | 2696 | 316 | 1420 | 553 | 418 | 40 | 0 | 0 | 62 | 0
4:30 | 2707 | 316 | 1387.5 | 600.5 | 417.5 | 40 | 0 | 0 | 62 | 0
5:00 | 2718 | 316 | 1355 | 648 | 417 | 40 | 0 | 0 | 62 | 0
5:30 | 2754.5 | 316 | 1361 | 733 | 408 | 40 | 0 | 0 | 65 | 0
6:00 | 2791 | 316 | 1367 | 818 | 399 | 40 | 0 | 0 | 68 | 0
6:30 | 2801 | 361 | 1297.5 | 949 | 393.5 | 40 | 0 | 0 | 68 | 0.5 |  |  |  |  | Coal
7:00 | 2811 | 406 | 1228 | 1080 | 388 | 40 | 0 | 0 | 68 | 1
7:30 | 2819 | 456 | 1270.5 | 1298.5 | 383 | 40 | 0 | 0 | 67 | 9 |  |  |  | Oil |  |  |  | ,
8:00 | 2827 | 506 | 1313 | 1517 | 378 | 40 | 0 | 0 | 66 | 17
8:30 | 2843 | 506 | 1311 | 1603.5 | 373 | 40 | 16 | 0 | 65 | 29
9:00 | 2859 | 506 | 1309 | 1690 | 368 | 40 | 32 | 0 | 64 | 41
9:30 | 2804 | 518 | 1263.5 | 1676 | 382.5 | 40 | 62 | 0 | 64 | 50
10:00 | 2749 | 530 | 1218 | 1662 | 397 | 40 | 92 | 0 | 64 | 59
10:30 | 2730.5 | 530.5 | 1212 | 1661 | 392 | 40 | 113.5 | 0 | 66 | 63.5
11:00 | 2712 | 531 | 1206 | 1660 | 387 | 40 | 135 | 0 | 68 | 68
11:30 | 2727.5 | 541.5 | 1292 | 1682 | 392 | 40 | 135 | 0 | 68 | 70
12:00 | 2743 | 552 | 1378 | 1704 | 397 | 40 | 135 | 0 | 68 | 72
12:30 | 2772 | 504 | 1347 | 1790 | 406.5 | 40 | 135 | 0 | 69 | 69.5
13:00 | 2801 | 456 | 1316 | 1876 | 416 | 40 | 135 | 0 | 70 | 67
13:30 | 2801 | 456 | 1316 | 1876 | 416 | 40 | 135 | 0 | 70 | 67
14:00 | 2801 | 456 | 1316 | 1876 | 416 | 40 | 135 | 0 | 70 | 67
14:30 | 2729.5 | 504 | 1272 | 1751.5 | 423 | 55 | 126.5 | 0 | 72 | 52.5
15:00 | 2658 | 552 | 1228 | 1627 | 430 | 70 | 118 | 0 | 74 | 38
15:30 | 2710 | 552 | 1278 | 1557 | 428 | 73 | 100 | 0 | 74 | 27.5
16:00 | 2762 | 552 | 1328 | 1487 | 426 | 76 | 82 | 0 | 74 | 17
16:30 | 2737 | 552 | 1302 | 1662.5 | 466.5 | 58.5 | 100 | 0 | 77 | 9
17:00 | 2712 | 552 | 1276 | 1838 | 507 | 41 | 118 | 0 | 80 | 1
17:30 | 2788.5 | 671 | 1336 | 2289 | 537 | 41 | 144 | 0 | 85 | 0.5
18:00 | 2865 | 790 | 1396 | 2740 | 567 | 41 | 170 | 0 | 90 | 0
18:30 | 2813.5 | 789 | 1399 | 2840 | 611.5 | 40.5 | 170 | 0 | 96 | 0
19:00 | 2762 | 788 | 1402 | 2940 | 656 | 40 | 170 | 0 | 102 | 0
19:30 | 2737 | 790 | 1410 | 2870 | 652 | 41 | 170 | 0 | 102 | 0
20:00 | 2785 | 788 | 1405 | 2786 | 654 | 41 | 170 | 0 | 102 | 0
20:30 | 2785.5 | 788 | 1391.5 | 2662.5 | 643 | 40.5 | 168 | 0 | 100 | 0
21:00 | 2786 | 788 | 1378 | 2539 | 632 | 40 | 166 | 0 | 98 | 0
21:30 | 2761 | 789 | 1366.5 | 2336.5 | 606.5 | 40 | 141.5 | 0 | 94 | 0
22:00 | 2736 | 790 | 1355 | 2134 | 581 | 40 | 117 | 0 | 90 | 0
22:30 | 2763.5 | 696 | 1415 | 1910 | 552 | 39 | 117 | 0 | 86 | 0
23:00 | 2791 | 602 | 1475 | 1686 | 523 | 38 | 117 | 0 | 82 | 0
23:30 | 2801.5 | 507 | 1455.5 | 1686 | 522.5 | 38 | 79.5 | 0 | 79 | 0 | Max Temp. in Dhaka |  | 25.4° C
24:00 | 2812 | 412 | 1436 | 1686 | 522 | 38 | 42 | 0 | 76 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [13 empty] | 35 | 35 | 41 | 41 | 41 |  | 40 | 41 | 41 | 40 | 40 | 38 | 38 | 427811
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | [10 empty] | 628000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 2 | [6 empty] | 3124
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 4 | 10 | 14 | 16 | 17 | 16 | 14 | 10 | 5 | 0 | [9 empty] | 109080
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 162 | 162 | 162 | 162 | 162 | 164 | 162 | 163 | 163 | 163 | 164 | 164 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 162 | 3819690
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 285352
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 250 | 210 | 210 | 210 | 210 | 210 | 265 | 300 | 300 | 300 | 300 | 300 | 245 | 195 | 145 | 95 | 95 | 185 |  | 270 | 300 | 300 | 300 | 200 | 95 | 95 | 5580216
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 43 | 42 | 43 | 40 | 43 | 42 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 46 | 44 | 43 | 43 |  | 43 | 44 | 44 | 44 | 43 | 42 | 45 | 1211500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7360473
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 120 | 135 | 150 | 150 | 100 | 130 | 130 | 130 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3334615
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 481608
33 | Ashuganj 225 MW CCPP | 183 | 203 | 183 | 188 | 197 | 200 | 189 | 183 | 225 | 183 | 183 | 206 | 183 | 183 | 184 | 200 | 183 | 200 |  | 183 | 204 | 195 | 183 | 183 | 187 | 183 | 4636000
34 | Ashuganj 450 MW CCPP(South) | [17 empty] | 20 |  | 20 | 20 | 20 | 20 | 40 | 70 | 95 | 261000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 1345920
36 | Chandpur 150 MW CCPP | 45 | 50 | 50 | 44 | 55 | 50 | 50 | 45 | 72 | 46 | 50 | 50 | 45 | 49 | 50 | 50 | 46 | 50 |  | 46 | 50 | 50 | 47 | 46 | 46 | 50 | 1180720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 355 | 357 | 376 | 359 | 371 | 363 | 364 | 378 | 362 | 349 | 362 | 382 | 352 | 351 | 367 | 369 | 389 |  | 360 | 365 | 367 | 363 | 349 | 357 | 350 | 8826880
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4745350
41 | Haripur 360MW CCPP(HPL) | 314 | 287 | 294 | 335 | 331 | 331 | 315 | 335 | 281 | 261 | 262 | 283 | 282 | 282 | 251 | 273 | 273 | 273 |  | 273 | 273 | 251 | 254 | 253 | 253 | 254 | 6796000
42 | RPCL 210MW CCPP | 159 | 161 | 167 | 146 | 145 | 147 | 166 | 144 | 122 | 105 | 106 | 101 | 103 | 103 | 103 | 103 | 105 | 104 |  | 106 | 105 | 106 | 107 | 108 | 108 | 109 | 2849520
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 11 | 26 | 37 | 42 | 45 | 40 | 21 | 22 | 9 | 1 | [9 empty] | 262240
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 721920
46 | Shajibazar 330 MW CCPP | 158 | 157 | 156 | 156 | 157 | 158 | 156 | 157 | 158 | 158 | 159 | 154 | 158 | 157 | 158 | 161 | 158 | 156 |  | 158 | 156 | 158 | 158 | 152 | 158 | 156 | 3607000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 32 | 32 | 31 | 32 | 31 | 32 | 31 | 33 | 32 |  | 33 | 32 | 33 | 34 | 34 | 33 | 34 | 793824
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 75 | 10 | 10 | 10 | 76 | 75 | 72 | 72 | 71 | 73 | 73 | 72 | 70 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1563840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 143 | 143 | 163 | 145 | 136 | 136 | 136 | 163 | 163 | 163 | 163 | 163 | 202 | 202 | 202 | 202 | 202 | 202 |  | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 4235150
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 435000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 0 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 128500
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 51 | 51 | 51 | 51 | 51 | 14 | 48 | 48 | 48 | 48 | 45 | 48 | 50 | 48 | 47 | 49 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 1167600
56 | Shahjahanulla 25 MW PP | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 356448
57 | Bibiana-II 341 MW CCPP (Summit)
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 9 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 |  | 247709
59 | Tangail Palli Power Gen 22 MW
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 371856
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 |  |  | 16 | 16 |  |  |  | 16 | 16 | 16 | 19 |  | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 275076
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431064
63 | Impoprt (Tripura) | 70 | 68 | 64 | 62 | 62 | 68 | 68 | 66 | 64 | 64 | 68 | 68 | 70 | 72 | 74 | 74 | 80 | 90 |  | 102 | 102 | 102 | 98 | 90 | 82 | 76 | 1828800
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 37 | 38 | 38 | 38 | 34 | 8 | 6 | 5 | 4 | 4 | 8 | 8 | 5 | 5 | 6 | 12 |  | 22 | 25 | 30 | 32 | 34 | 40 | 42 | 593280
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 454176
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 |  | 11 | 11 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228240
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 619600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493530
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 30 | 33 | 22 | 22 | 24 | 23 | 23 | 23 | 23 | 23 | 24 |  | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 638820
71 | Maona 33 MW PP(Summit) | 15 | 17 | 17 | 17 | 17 | 15 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 780200
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 101 | 101 | 101 | 102 | 102 | 101 | 102 | 102 | 99 | 102 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2411863
| Feni Lanka Power | [16 empty] | 17 | 34 |  | 34 | [6 empty] | 64980
| Chowmuhani 113 MW | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 18 | 19 | 19 |  |  |  |  | 421680
| Manikgonj 162MW PP(MPGL) | [16 empty] | 30 | 110 |  | 147 | 95 | 36 |  |  |  |  | 285120
77 | Siddhirganj 100 PP(Dutch Bangla) | 70 | [6 empty] | 20 | 50 | 50 | 50 | 50 | 60 | 70 | 50 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 20 |  |  | 691200
78 | Gazipur 52 MW PP | [17 empty] | 5 |  | 24 | 24 | 24 |  |  |  |  | 63744
79 | Kodda 150MW PP | [8 empty] | 32 | 80 | 100 | 100 | 100 | 84 | 84 | 48 | 84 | 84 |  | 84 | 84 | 84 | 80 | 48 | 48 | 0 | 1132800
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 2 | 30 | 50 | 50 | 50 | 50 | 64 | 24 | 24 | 24 | 40 | 70 |  | 90 | 89 | 89 | 89 | 64 | 64 | 8 | 927360
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 5 | 34 |  | 34 | 34 | 34 | 34 | 34 |  |  | 183874
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24840
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 1253959
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [8 empty] | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 20 | 49 | 48 | 48 | 48 | 48 | 15 | 431448
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 85 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 62 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1156888
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 29 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 19 | 50 | 50 | 50 | 50 | 50 |  | 67 | 100 | 100 | 100 | 100 | 100 | 100 | 979200
| Meghnaghat 104 MW PP (OPCL) | 90 | 83 | 51 | 17 | 17 | 17 | 35 | 53 | 70 | 70 | 70 | 70 | 84 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 85 | 77 | 70 | 1706880
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 33 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 49 | 49 | 49 |  | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 1128528
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 30 | 40 | 51 | 51 | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1197406
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 7 | 7 |  | 7 | 7 | 7 |  |  |  |  | 31104
95 | Patenga 50MW PP (Baraka) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 31 | 31 | 31 | 30 | 33 | 51 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 31 | 816480
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [5 empty] | 7 | 50 |  | 79 | 93 | 93 |  |  |  |  | 254400
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 12 | 15 | 15 | 15 | 30 | 55 | 55 | 55 | 55 | 55 |  | 55 | 40 | 40 | 40 | 40 | 40 | 25 | 615408
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1332823
101 | Kushiara 163 MW CCPP (KP) | [19 empty] | 40 | 70 | 70 | 70 | 70 | 80 | 110 | 385772
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 10450
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 31 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 783720
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 186 | [8 empty] | 148147
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 12 | 52 |  | 64 | 64 | 64 | 32 |  |  |  | 244800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 1 | 33 | 65 | 66 | 65 | 66 | 72 | 78 | 65 | 64 | 72 | 115 |  | 149 | 149 | 149 | 131 | 115 | 32 | 15 | 1389456
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 50 | 40 | 10 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2146560
116 | Chandpur 200MW (Desh energy) |  |  |  |  | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 73 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 85 | 1395360
117 | Ashuganj 150MW PP (Midland) | 142 | 142 | 100 | 100 | 108 | 127 | 128 | 133 | 138 | 142 | 132 | 128 | 130 | 132 | 133 | 133 | 135 | 133 |  | 137 | 140 | 140 | 142 | 142 | 143 | 143 | 3228363
118 | Bibiyana-III 400 MW CCPP | 260 | 300 | 310 | 303 | 310 | 309 | 300 | 310 | 307 | 309 | 281 | 280 | 270 | 251 | 250 | 290 | 240 | 300 |  | 270 | 230 | 270 | 290 | 250 | 251 | 250 | 6805000
| Jamalpur 115 MW PP (United) | 85 | 55 | 55 | 35 | 35 | 55 | 115 | 115 | 115 | 75 | 75 | 75 | 98 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2359200
| Anwara 300 MW PP (United) | 161 | 52 | 16 | 16 | 50 | 102 | 139 | 141 | 159 | 160 | 161 | 161 | 162 | 162 | 162 | 167 | 211 | 216 |  | 216 | 216 | 216 | 216 | 216 | 162 | 161 | 3633164
| Juldah unit-2 (Acorn) | 50 | 50 | 30 | 10 | 10 | 20 | 50 | 90 | 90 | 90 | 90 | 90 | 92 | 70 | 50 | 50 | 70 | 96 |  | 97 | 97 | 98 | 98 | 100 | 100 | 50 | 1701120
| Anlima Energy Ltd. | [10 empty] | 8 | 33 | 30 |  |  | 9 | 20 | [9 empty] | 106636
120 | Eastern Zone Total | 4580 | 4193 | 4071 | 3949 | 3990 | 4202 | 4289 | 4638 | 4808 | 4738 | 4729 | 4833 | 5015 | 4974 | 4788 | 4776 | 4941 | 5775 |  | 5848 | 5879 | 5850 | 5622 | 5345 | 5095 | 4831 | 116795619
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 5 | 16 | 16 | 16 | 16 | 49 | 32 | 32 |  | 56 | 115 |  | 115 | 115 | 90 | 83 | 32 |  |  | 690240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | [5 empty] | 17 | 90 | 90 | 90 | 90 | 90 | 90 | 53 | 53 | 53 |  | 70 |  | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 1371840
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 27 | 36 | 42 | 36 | 36 | 37 | 37 | 37 | 13 | 15 | 15 | 36 | 35 | 14 | 15 | 36 | 43 | 15 |  | 15 | 22 | 35 | 36 | 34 | 36 | 36 | 708818
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 48 | 64 |  | 64 | 64 | 64 | 64 | 48 | 16 | 16 | 370272
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 11 | 10 | 10 | 10 | 10 | 272738
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 15 | 15 | 14 | 20 | 19 | 13 | 12 | 12 | 14 | 18 | 18 | 18 | 18 | 19 | 20 | 28 |  | 27 | 28 | 28 | 27 | 27 | 25 | 25 | 451500
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 24 |  | 24 | [6 empty] | 52125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 412 | 412 | 412 | 316 | 316 | 316 | 406 | 506 | 506 | 530 | 531 | 552 | 456 | 457 | 552 | 552 | 552 | 790 |  | 788 | 790 | 788 | 788 | 790 | 602 | 412 | 12805091
147 | Bheramara 410 MW CCPP | 180 | 208 | 220 | 230 | 245 | 280 | 305 | 310 | 325 | 310 | 300 | 300 | 300 | 280 | 230 | 250 | 260 | 270 |  | 255 | 230 | 230 | 230 | 230 | 230 | 230 | 6422112
148 | Payra 1320 MW | 380 | 350 | 350 | 330 | 330 | 310 | 300 | 290 | 280 | 310 | 300 | 310 | 330 | 340 | 340 | 340 | 420 | 480 |  | 570 | 570 | 570 | 550 | 500 | 440 | 440 | 10075800
149
150 | Barapukuria TPP Unit-1 | 87 | 87 | 88 | 88 | 87 | 89 | 88 | 88 | 88 | 87 | 87 | 87 | 86 | 88 | 90 | 86 | 87 | 87 |  | 86 | 82 | 84 | 82 | 81 | 83 | 82 | 2057455
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 130 | 130 | 135 | 154 | 150 | 150 | 149 | 156 | 158 | 146 | 144 | 147 | 155 | 145 | 145 | 147 | 147 | 155 |  | 139 | 148 | 150 | 148 | 139 | 147 | 143 | 3731191
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 295 | 350 | 305 | 345 | 350 | 355 | 335 | 300 | 353 | 286 | 283 | 402 | 334 | 328 | 299 | 358 | 288 | 418 |  | 372 | 339 | 336 | 305 | 283 | 388 | 320
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 511680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 210060
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 52 | [6 empty] | 31680
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 12 | 35 | 35 | 35 | 35 | 34 | 34 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 8 | 470664
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 |  |  |  |  | 1 | 38 | 93 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 |  | 111 | 111 | 111 | 111 | 111 | 70 | 70 | 2012064
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 25 | 35 | 35 | 35 | 35 | 50 | 35 | 35 |  | 20 | 70 |  | 113 | 113 | 113 | 113 | 35 | 35 |  | 920064
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 70 | 70 | 70 | 70 | 70 | 65 | 37 | 10 |  | 55 | 109 |  | 113 | 113 | 113 | 100 | 20 |  |  | 956160
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 30391
178
178