## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-25 | Friday
|  |  | Date (day): | 2020-12-25 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11934.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13198 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-24 | 2020-12-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 77 | 93 | 93 | 80 |  | 90 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 280 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 361 | 386 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 261 | 242 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 shut down for Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 75 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 2 | 64 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 8 | 46 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 69 | 86 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 8 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 59 | 51 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 24 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 111 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 71 | 100 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 100 | 160
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1845 | 2556 | 3486 | 3823 | 1421 | 809
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 49 | 49 | 49 | 181 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 162 | 162 | 160 | 160 | 65 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 19 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 25 | 25 | 35
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 51 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 216 | 253 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 60 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 20 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 742 | 935 | 1416 | 1401 | 756 | 104
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 15 | 80 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 129 | 129
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 290 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 23 | 23 | 22 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 53 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 41 | 16 | 16 | 40 | 155 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 142 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 50 | 50 | 113 |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 68 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 104 | 140 | 149
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 25 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 24 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 34 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 35 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1076 | 1207 | 1653 | 1946 | 424 | 594
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 106 | 115 | 115 | 87 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 83 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 24 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 0
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 295 | 348 | 596.6 | 545 | 87 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 20 | 30 | 30
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 32 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 140 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 155 | 158 | 158 | 172 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 14 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 47 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 32 | 32 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 74 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 215 | 176 | 215 | 215
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 219 | 270 | 300 | 300
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 25 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1014 | 1027 | 1257 | 1257 | 172 | 383
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 564 | 801 | 421 | 709
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 120 | 300 | 300 | 110 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 882 | 1060 | 1171 | 1695 | 110 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 64 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 26 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 10 | 10 | 10 | 85 |  | Gas shortage
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 420 | 540 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 19 | 36 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 485 | 676 | 780 | 840 | 85 | 202
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 8 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 129 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 35 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 356 | 380 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 52 | 77 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 47 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 60 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 658 | 841 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 75 | 88 | 88
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 51 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 132 | 188 | 209 | 201 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7129 | 8838 | 11934.6 | 13198 | 3656 | 2579
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6763.5964 | 8385 | 11322.8809 | 12521.5241
| A. |  | 2020-12-24 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 8838 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5510 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8838 | MW
| 3 | Day peak Generation : |  |  | 7129 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8385 | MW
| 4 | Evening peak Generation : |  |  | 8838 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 169.8728 | MKWHr | By Solar | 0.40784 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 100.3441 | MKWHr |  | By Oil: | 39.0737 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6779 | MKWHr |  | By Hydro: | 1.1619 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3656 | MW | Dhaka | 2998 | 2998 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2579 | MW | Chittagong | 887 | 887 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6235 | MW | Khulna | 1044 | 1044 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 819.31 | MMCFD |  |  | Rajshahi | 867 | 867 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 114751116.986 | ii) Oil : | Taka | 312496694.84 | Comilla | 744 | 744 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 63041713.54 | Total | Taka | 490289525.366 | Mymensingh | 710 | 710 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.631 | MKWHr. | Sylhet | 309 | 309 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -115 | MW (E to W) at | 19:00 | hrs | Barisal | 232 | 232 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -266 | MW at | 24:00 | hrs | Rangpur | 594 | 594 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.0° C |  |  | Total | 8385 | 8385 |  | 0
| B. |  | 2020-12-25 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 25.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13198 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6200 | MW
| 4 | Reserve(Generation end) |  |  |  | 5098 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 155.6879 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5614 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.2815 | MKWHr. | ii) HVDC Flow at Peak Time |  | 801 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9258 | MKWHr. | iii) Maximum HVDC Flow : |  | 801 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.7 |  | (b) Today: | 98.62 |  | (c) Rule Curve: |  | 103.7
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 349 | 262 |  | 0 | 225 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 41 | 0 | 80 | 0 | 0 | 355 | 187 | 8 | 49 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 74 | 105 | 0 | 20 | 0 | 0 | 30 | 11 | 30 | 110 | 156 | 34 | 75 | 0 | 183 | 18 | 0 | 0 | 0 | 15 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 250 | 24 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 |  | 422 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 332 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 38 | 0 | 0 |  | 4353 | 1858 | 6211 | 2966 | 422 | 1294 | 821 | 589 | 45 | 0 | 74 | 0 | 0 | 98.71
2:00 | 0 | 43 | 0 | 0 | 310 | 51 | 0 | 379 | 268 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 42 | 0 | 80 | 0 | 0 | 355 | 195 | 8 | 50 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 72 | 108 | 0 | 20 | 0 | 0 | 30 | 11 | 30 | 130 | 157 | 34 | 75 | 0 | 169 | 18 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 270 | 24 | 0 | 0 | 0 | 53 | 54 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 420 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 337 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 38 | 0 | 0 |  | 4143 | 1815 | 5958 | 3007 | 420 | 1325 | 520 | 569 | 45 | 0 | 72 | 0 | 0 | 98.71
3:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 358 | 267 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 42 | 0 | 80 | 0 | 0 | 355 | 175 | 8 | 50 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 70 | 108 | 0 | 20 | 0 | 0 | 30 | 11 | 30 | 110 | 157 | 34 | 76 | 0 | 169 | 19 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 251 | 24 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 |  | 420 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 36 | 0 | 0 |  | 3967 | 1744 | 5711 | 2959 | 420 | 1273 | 406 | 538 | 45 | 0 | 70 | 0 | 0 | 98.71
4:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 386 | 279 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 0 | 355 | 190 | 8 | 50 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 68 | 106 | 0 | 20 | 0 | 0 | 30 | 11 | 30 | 130 | 158 | 34 | 76 | 0 | 169 | 19 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 290 | 24 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 |  | 326 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 36 | 0 | 0 |  | 3934 | 1659 | 5593 | 3040 | 326 | 1332 | 243 | 537 | 47 | 0 | 68 | 0 | 0 | 98.7
5:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 359 | 277 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 0 | 355 | 175 | 8 | 50 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 68 | 109 | 0 | 20 | 0 | 0 | 30 | 11 | 30 | 130 | 158 | 34 | 76 | 0 | 169 | 19 | 0 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 290 | 24 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 326 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 36 | 0 | 0 |  | 3875 | 1635 | 5510 | 3007 | 326 | 1315 | 229 | 518 | 47 | 0 | 68 | 0 | 0 | 98.7
6:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 390 | 279 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 0 | 355 | 138 | 8 | 45 | 20 | 34 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 66 | 108 | 0 | 20 | 0 | 0 | 30 | 11 | 38 | 130 | 155 | 34 | 76 | 0 | 220 | 19 | 0 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 50 | 0 | 0 | 83 | 0 | 0 | 0 | 133 | 54 | 0 | 26 | 0 | 20 | 0 | 34 | 0 | 0 | 0 | 0 |  | 338 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 383 | 31 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 420 | 37 | 0 | 0 |  | 3938 | 1724 | 5662 | 2754 | 338 | 1413 | 547 | 497 | 47 | 0 | 66 | 0 | 0 | 98.7
7:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 351 | 248 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 0 | 17 | 35 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 42 | 0 | 150 | 0 | 0 | 320 | 0 | 8 | 46 | 23 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 33 | 108 | 0 | 20 | 0 | 0 | 30 | 50 | 50 | 130 | 157 | 34 | 73 | 0 | 216 | 19 | 0 | 0 | 0 | 14 | 2 | 0 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 90 | 34 | 38 | 0 | 115 | 0 | 0 | 0 | 210 | 54 | 0 | 70 | 0 | 90 | 0 | 34 | 1 | 35 | 0 | 0 |  | 420 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 246 | 35 | 0 | 88 | 0 | 50 | 0 | 0 | 0 | 420 | 37 | 0 | 0 |  | 4247 | 1856 | 6103 | 2624 | 420 | 1308 | 1139 | 497 | 49 | 32 | 33 | 1 | 0 | 98.7
8:00 | 0 | 44 | 0 | 0 | 310 | 51 | 0 | 366 | 287 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 37 | 19 | 16 | 0 | 150 | 0 | 0 | 305 | 0 | 8 | 50 | 23 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 12 | 62 | 109 | 0 | 20 | 0 | 0 | 30 | 50 | 50 | 130 | 157 | 33 | 74 | 0 | 215 | 19 | 0 | 0 | 0 | 14 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 75 | 4 | 100 | 17 | 50 | 130 | 115 | 0 | 0 | 1 | 210 | 54 | 0 | 70 | 0 | 100 | 0 | 47 | 14 | 35 | 0 | 0 |  | 516 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 0 | 325 | 35 | 0 | 110 | 0 | 50 | 0 | 1 | 0 | 420 | 36 | 0 | 0 |  | 4584 | 2064 | 6648 | 2762 | 516 | 1398 | 1312 | 497 | 49 | 32 | 62 | 20 | 0 | 98.69
9:00 | 0 | 43 | 0 | 0 | 330 | 51 | 0 | 362 | 288 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 48 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 8 | 0 | 150 | 0 | 0 | 305 | 0 | 8 | 45 | 23 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 54 | 106 | 0 | 20 | 1 | 0 | 30 | 50 | 50 | 130 | 158 | 33 | 74 | 0 | 215 | 19 | 0 | 0 | 0 | 14 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 105 | 11 | 100 | 17 | 50 | 170 | 115 | 0 | 0 | 2 | 216 | 54 | 0 | 70 | 0 | 100 | 0 | 53 | 30 | 35 | 0 | 0 |  | 516 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 10 | 0 | 0 | 0 | 388 | 35 | 0 | 111 | 0 | 50 | 0 | 2 | 0 | 420 | 36 | 0 | 0 |  | 4700 | 2196 | 6896 | 2872 | 516 | 1458 | 1366 | 496 | 48 | 40 | 54 | 46 | 0 | 98.69
10:00 | 0 | 44 | 0 | 0 | 330 | 52 | 0 | 356 | 288 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 46 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 34 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 8 | 0 | 150 | 0 | 0 | 305 | 0 | 8 | 50 | 23 | 49 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 72 | 98 | 0 | 20 | 2 | 0 | 20 | 48 | 50 | 130 | 156 | 33 | 73 | 0 | 215 | 19 | 0 | 0 | 0 | 8 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 104 | 14 | 100 | 0 | 50 | 220 | 115 | 0 | 0 | 3 | 216 | 54 | 0 | 114 | 0 | 100 | 0 | 53 | 33 | 35 | 8 | 0 |  | 562 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 10 | 0 | 0 | 0 | 351 | 35 | 0 | 111 | 0 | 51 | 0 | 4 | 0 | 420 | 36 | 0 | 0 |  | 4749 | 2179 | 6928 | 2837 | 562 | 1419 | 1399 | 496 | 47 | 40 | 72 | 56 | 0 | 98.68
11:00 | 0 | 45 | 0 | 0 | 330 | 52 | 0 | 381 | 271 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 55 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 34 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 29 | 17 | 5 | 0 | 150 | 0 | 0 | 355 | 0 | 26 | 46 | 26 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 76 | 130 | 0 | 20 | 2 | 0 | 20 | 48 | 50 | 163 | 156 | 32 | 72 | 0 | 215 | 18 | 0 | 0 | 0 | 8 | 2 | 0 | 45 | 0 | 0 | 0 | 0 | 78 | 17 | 100 | 0 | 67 | 220 | 115 | 0 | 0 | 4 | 216 | 54 | 0 | 114 | 0 | 50 | 0 | 53 | 27 | 0 | 18 | 0 |  | 563 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 10 | 0 | 0 | 0 | 350 | 53 | 0 | 35 | 0 | 51 | 0 | 5 | 0 | 420 | 36 | 0 | 0 |  | 4780 | 2110 | 6890 | 2875 | 563 | 1450 | 1282 | 496 | 46 | 47 | 76 | 55 | 0 | 98.68
12:00 | 0 | 77 | 0 | 0 | 330 | 12 | 0 | 361 | 261 |  | 0 | 225 | 0 | 7 | 2 | 8 | 0 | 0 | 0 | 8 | 0 | 32 | 69 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 34 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 5 | 15 | 150 | 0 | 0 | 360 | 0 | 41 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 78 | 105 | 8 | 20 | 2 | 0 | 20 | 50 | 50 | 163 | 160 | 32 | 73 | 0 | 215 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 71 | 17 | 100 | 0 | 118 | 219 | 115 | 0 | 0 | 5 | 216 | 54 | 0 | 114 | 0 | 50 | 0 | 53 | 45 | 0 | 20 | 0 |  | 564 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 10 | 0 | 0 | 0 | 356 | 53 | 0 | 47 | 0 | 51 | 0 | 5 | 0 | 420 | 19 | 0 | 0 |  | 4972 | 2157 | 7129 | 2885 | 564 | 1412 | 1490 | 496 | 46 | 84 | 78 | 74 | 0 | 98.68
13:00 | 0 | 93 | 0 | 0 | 330 | 12 | 0 | 354 | 262 |  | 0 | 225 | 0 | 16 | 15 | 22 | 0 | 0 | 0 | 32 | 0 | 32 | 80 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 34 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 8 | 25 | 125 | 0 | 0 | 330 | 0 | 41 | 46 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 78 | 105 | 24 | 20 | 1 | 0 | 20 | 47 | 10 | 130 | 157 | 32 | 70 | 0 | 216 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 70 | 11 | 100 | 0 | 120 | 220 | 115 | 0 | 0 | 3 | 216 | 54 | 0 | 114 | 0 | 50 | 30 | 72 | 27 | 0 | 20 | 0 |  | 564 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 10 | 0 | 0 | 0 | 337 | 70 | 0 | 70 | 0 | 49 | 0 | 5 | 0 | 420 | 12 | 0 | 0 |  | 5059 | 2155 | 7214 | 2849 | 564 | 1312 | 1739 | 496 | 46 | 83 | 78 | 47 | 7214 | 98.67
14:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 368 | 248 |  | 0 | 225 | 0 | 16 | 15 | 30 | 0 | 0 | 0 | 32 | 0 | 32 | 85 | 0 | 0 | 0 | 54 | 55 | 17 | 13 | 25 | 20 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 6 | 65 | 110 | 0 | 0 | 260 | 0 | 16 | 46 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 80 | 104 | 24 | 20 | 1 | 0 | 20 | 14 | 10 | 110 | 158 | 32 | 30 | 0 | 184 | 18 | 0 | 0 | 0 | 14 | 5 | 0 | 195 | 0 | 0 | 0 | 0 | 36 | 15 | 100 | 0 | 137 | 220 | 115 | 0 | 0 | 3 | 216 | 54 | 0 | 114 | 0 | 50 | 50 | 72 | 41 | 0 | 0 | 0 |  | 564 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 10 | 0 | 0 | 0 | 275 | 70 | 0 | 70 | 0 | 49 | 0 | 4 | 0 | 420 | 14 | 0 | 0 |  | 4846 | 2090 | 6936 | 2756 | 564 | 1117 | 1728 | 496 | 47 | 84 | 80 | 64 | 0 | 98.67
15:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 369 | 243 |  | 0 | 225 | 0 | 16 | 15 | 30 | 0 | 0 | 0 | 32 | 0 | 32 | 72 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 26 | 17 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 6 | 70 | 110 | 0 | 0 | 270 | 0 | 16 | 46 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 104 | 24 | 20 | 1 | 0 | 20 | 14 | 10 | 140 | 156 | 32 | 30 | 0 | 151 | 18 | 0 | 0 | 0 | 14 | 8 | 0 | 195 | 0 | 0 | 0 | 0 | 34 | 10 | 100 | 0 | 137 | 200 | 115 | 0 | 0 | 2 | 216 | 54 | 0 | 114 | 0 | 50 | 50 | 72 | 13 | 0 | 20 | 0 |  | 564 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 0 | 6 | 0 | 295 | 70 | 0 | 70 | 0 | 49 | 0 | 3 | 0 | 390 | 37 | 0 | 0 |  | 4800 | 2051 | 6851 | 2670 | 564 | 1180 | 1733 | 466 | 47 | 84 | 78 | 29 | 0 | 98.67
16:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 358 | 243 |  | 0 | 225 | 0 | 16 | 15 | 30 | 0 | 0 | 0 | 32 | 0 | 32 | 81 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 26 | 17 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 8 | 70 | 110 | 0 | 0 | 270 | 0 | 16 | 51 | 23 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 74 | 103 | 24 | 20 | 0 | 0 | 22 | 14 | 10 | 140 | 156 | 31 | 30 | 0 | 150 | 18 | 0 | 0 | 0 | 14 | 8 | 0 | 195 | 0 | 0 | 0 | 0 | 34 | 5 | 100 | 0 | 137 | 220 | 115 | 0 | 0 | 1 | 216 | 54 | 0 | 114 | 0 | 50 | 50 | 72 | 5 | 0 | 17 | 0 |  | 564 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 10 | 0 | 28 | 0 | 310 | 70 | 0 | 70 | 0 | 50 | 0 | 1 | 0 | 400 | 35 | 0 | 0 |  | 4804 | 2039 | 6843 | 2689 | 564 | 1196 | 1700 | 476 | 48 | 84 | 74 | 12 | 0 | 98.66
17:00 | 0 | 94 | 0 | 0 | 280 | 12 | 0 | 375 | 243 |  | 0 | 225 | 0 | 19 | 15 | 30 | 0 | 0 | 0 | 35 | 7 | 133 | 78 | 0 | 0 | 0 | 54 | 55 | 22 | 16 | 25 | 26 | 17 | 25 | 2 | 0 | 48 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 0 | 0 | 2 | 0 | 23 | 50 | 19 | 11 | 75 | 110 | 0 | 0 | 270 | 0 | 16 | 46 | 26 | 53 | 0 | 51 | 0 | 0 | 1 | 18 | 0 | 33 | 22 | 86 | 105 | 26 | 20 | 0 | 10 | 22 | 16 | 10 | 163 | 158 | 32 | 30 | 0 | 127 | 18 | 0 | 0 | 0 | 14 | 8 | 0 | 202 | 0 | 0 | 7 | 0 | 50 | 0 | 100 | 20 | 142 | 220 | 115 | 0 | 0 | 0 | 248 | 54 | 0 | 88 | 0 | 60 | 50 | 90 | 1 | 3 | 15 | 0 |  | 564 | 0 | 135 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 5 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 10 | 0 | 35 | 0 | 201 | 80 | 0 | 73 | 0 | 83 | 0 | 0 | 20 | 420 | 20 | 0 | 0 |  | 5133 | 2019 | 7152 | 2729 | 564 | 1100 | 1928 | 496 | 48 | 200 | 86 | 1 | 0 | 98.66
18:00 | 0 | 94 | 0 | 0 | 280 | 12 | 0 | 339 | 242 |  | 0 | 225 | 0 | 65 | 45 | 44 | 0 | 0 | 0 | 90 | 7 | 150 | 84 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 20 | 17 | 33 | 24 | 0 | 48 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 102 | 10 | 51 | 50 | 19 | 15 | 80 | 110 | 0 | 0 | 275 | 0 | 16 | 51 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 0 | 33 | 22 | 106 | 103 | 67 | 20 | 0 | 20 | 32 | 14 | 25 | 110 | 156 | 32 | 74 | 0 | 161 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 286 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 56 | 142 | 260 | 115 | 0 | 0 | 0 | 254 | 54 | 0 | 52 | 35 | 60 | 50 | 104 | 0 | 17 | 10 | 0 |  | 800 | 0 | 130 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 64 | 0 | 0 | 0 | 8 | 0 | 85 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 10 | 0 | 35 | 0 | 390 | 90 | 0 | 110 | 0 | 113 | 0 | 0 | 35 | 440 | 34 | 0 | 0 |  | 5839 | 2662 | 8501 | 2785 | 800 | 1318 | 2583 | 516 | 48 | 345 | 106 | 0 | 0 | 98.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 386 | 242 |  | 0 | 225 | 0 | 75 | 64 | 46 | 0 | 0 | 0 | 100 | 7 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 26 | 17 | 33 | 24 | 0 | 49 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 102 | 10 | 51 | 50 | 19 | 25 | 80 | 150 | 0 | 0 | 290 | 0 | 16 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 104 | 106 | 83 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 155 | 32 | 74 | 0 | 176 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 68 | 142 | 270 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 34 | 35 | 60 | 25 | 104 | 0 | 17 | 0 | 0 |  | 801 | 0 | 120 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 8 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 10 | 0 | 35 | 0 | 380 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 60 | 540 | 36 | 0 | 0 |  | 6073 | 2765 | 8838 | 2894 | 801 | 1373 | 2665 | 615 | 49 | 337 | 104 | 0 | 0 | 98.65
19:30 | 0 | 94 | 0 | 0 | 280 | 12 | 0 | 362 | 242 |  | 0 | 225 | 0 | 75 | 64 | 46 | 0 | 0 | 0 | 100 | 7 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 26 | 17 | 33 | 24 | 0 | 49 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 102 | 10 | 51 | 50 | 19 | 28 | 80 | 150 | 0 | 0 | 290 | 0 | 16 | 51 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 104 | 106 | 90 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 157 | 32 | 74 | 0 | 176 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 68 | 142 | 270 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 34 | 38 | 60 | 25 | 104 | 0 | 17 | 0 | 0 |  | 801 | 0 | 100 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 10 | 0 | 35 | 0 | 367 | 90 | 0 | 93 | 0 | 113 | 0 | 0 | 70 | 550 | 36 | 0 | 0 |  | 6070 | 2727 | 8797 | 2858 | 801 | 1363 | 2667 | 626 | 49 | 329 | 104 | 0 | 0 | 98.65
20:00 | 0 | 94 | 0 | 0 | 280 | 12 | 0 | 360 | 242 |  | 0 | 225 | 0 | 75 | 64 | 46 | 0 | 0 | 0 | 100 | 7 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 33 | 17 | 33 | 24 | 0 | 49 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 51 | 50 | 19 | 30 | 80 | 150 | 0 | 0 | 290 | 0 | 16 | 44 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 104 | 107 | 90 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 158 | 33 | 75 | 0 | 176 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 68 | 142 | 270 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 17 | 35 | 60 | 25 | 104 | 0 | 17 | 0 | 0 |  | 801 | 0 | 85 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 10 | 0 | 39 | 0 | 366 | 90 | 0 | 105 | 0 | 75 | 0 | 0 | 70 | 550 | 36 | 0 | 0 |  | 6044 | 2679 | 8723 | 2847 | 801 | 1365 | 2602 | 624 | 49 | 331 | 104 | 0 | 0 | 98.65
21:00 | 0 | 94 | 0 | 0 | 280 | 12 | 0 | 370 | 243 |  | 0 | 225 | 0 | 75 | 30 | 46 | 0 | 0 | 0 | 100 | 0 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 33 | 17 | 33 | 24 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 50 | 19 | 32 | 80 | 135 | 0 | 0 | 290 | 0 | 16 | 45 | 23 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 100 | 107 | 90 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 158 | 33 | 75 | 0 | 176 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 68 | 142 | 270 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 35 | 60 | 50 | 104 | 0 | 0 | 0 | 0 |  | 801 | 0 | 65 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 10 | 0 | 72 | 0 | 357 | 90 | 0 | 100 | 0 | 34 | 0 | 0 | 70 | 550 | 36 | 0 | 0 |  | 5897 | 2605 | 8502 | 2843 | 801 | 1359 | 2430 | 627 | 47 | 295 | 100 | 0 | 0 | 98.65
22:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 358 | 244 |  | 0 | 225 | 0 | 41 | 30 | 46 | 0 | 0 | 0 | 100 | 0 | 115 | 84 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 11 | 0 | 0 | 50 | 19 | 37 | 80 | 120 | 0 | 0 | 290 | 0 | 16 | 51 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 94 | 108 | 72 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 156 | 34 | 75 | 0 | 138 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 0 | 0 | 8 | 0 | 70 | 0 | 100 | 68 | 142 | 250 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 35 | 60 | 50 | 104 | 0 | 0 | 0 | 0 |  | 801 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 111 | 0 | 316 | 90 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 520 | 36 | 0 | 0 |  | 5619 | 2287 | 7906 | 2727 | 801 | 1324 | 2115 | 597 | 45 | 203 | 94 | 0 | 0 | 98.65
23:00 | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 355 | 244 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 37 | 19 | 41 | 80 | 120 | 0 | 0 | 260 | 0 | 16 | 51 | 23 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 88 | 107 | 66 | 20 | 0 | 30 | 32 | 11 | 47 | 110 | 156 | 33 | 40 | 0 | 136 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 245 | 0 | 0 | 8 | 0 | 28 | 0 | 100 | 68 | 142 | 251 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 35 | 60 | 50 | 104 | 0 | 0 | 0 | 0 |  | 612 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 126 | 0 | 316 | 90 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 520 | 36 | 0 | 0 |  | 5227 | 2102 | 7329 | 2735 | 612 | 1259 | 1850 | 597 | 45 | 143 | 88 | 0 | 0 | 98.64
24:00 | 0 | 93 | 0 | 0 | 310 | 12 | 0 | 357 | 274 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 48 | 84 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 37 | 19 | 41 | 110 | 140 | 0 | 0 | 260 | 0 | 16 | 51 | 26 | 53 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 80 | 107 | 16 | 20 | 0 | 30 | 32 | 14 | 50 | 163 | 156 | 34 | 75 | 0 | 137 | 20 | 0 | 0 | 0 | 15 | 11 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 142 | 251 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 60 | 50 | 104 | 0 | 0 | 0 | 0 |  | 422 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 129 | 0 | 301 | 70 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 420 | 36 | 0 | 0 |  | 5155 | 1770 | 6925 | 2861 | 422 | 1359 | 1614 | 496 | 45 | 48 | 80 | 0 | 0 | 98.64
KWH | 0 | 1817500 | 0 | 0 | 7203091 | 745409 | 0 | 8873980 | 6238000 |  | 0 | 4724500 | 0 | 513600 | 345240 | 409843 | 0 | 0 | 0 | 872640 | 37440 | 1289280 | 1779051 | 0 | 0 | 0 | 1050120 | 1014917 | 289121 | 257832 | 600000 | 671220 | 411800 | 805900 | 123684 | 0 | 1161949 | 0 | 0 | 0 | 0 | 3820977 | 0 | 0 | 0 |  | 0 | 0 | 396757 | 22080 | 191040 | 921600 | 445536 | 594240 | 860082 | 2849760 | 0 | 0 | 7597000 | 1186000 | 384727 | 1157600 | 556776 | 1010880 | 0 | 1224706 | 0 | 0 | 168250 | 326736 | 167580 | 617000 | 524810 | 1925760 | 2487080 | 663360 | 432540 | 10350 | 175000 | 654960 | 550800 | 933984 | 3419263 | 3598000 | 781920 | 1600320 | 0 | 4328920 | 441000 | 0 | 0 | 0 | 346008 | 136000 | 0 | 3389780 | 0 | 0 | 151200 | 0 | 1186560 | 109215 | 1939200 | 1025280 | 2117672 | 5221000 | 2371200 | 0 | 0 | 23160 | 4453636 | 1301725 | 0 | 1252860 | 268800 | 1190400 | 505200 | 1857600 | 235610 | 182880 | 124200 | 0 |  | 13281456 | 0 | 4769280 | 0 | 224640 | 0 | 0 | 0 | 0 | 0 | 329625 | 0 | 483700 | 547584 | 0 | 0 | 0 | 19226 | 0 | 806992 | 0 | 0 | 0 | 23040 | 0 | 516000 | 0 | 165438 | 1826618 | 0 | 0 | 0 | 0 | 0 | 0 | 3221464 | 0 | 251427 | 0 | 708745 | 0 | 8132000 | 1351680 | 0 | 1649760 | 0 | 927360 | 0 | 29500 | 292800 | 11851300 | 810440 | 0 | 0 |  | 117652697 | 52220075 | 169872772 | 68723735 | 13281456 | 31620396 | 36561468 | 13677918 | 1161949 | 2512255 | 1925760 | 407835 | 0
Fuel Cost | 0 | 2689900 | 0 | 0 | 7995431.01 | 983939.88 | 0 | 8962719.8 | 6425140 |  | 0 | 5149705 | 0 | 3898224 | 2378703.6 | 3467271.78 | 0 | 0 | 0 | 6570979.2 | 341452.8 | 12686515.2 | 16402850.22 | 0 | 0 | 0 | 7665876 | 7845308.41 | 2850733.06 | 193374 | 450000 | 0 | 0 | 0 | 1196024.28 | 0 | 313726.23 | 0 | 0 | 0 | 0 | 4164864.93 | 0 | 0 | 0 |  | 0 | 0 | 3848542.9 | 210864 | 1662048 | 7299072 | 561375.36 | 1764892.8 | 1272921.36 | 4217644.8 | 0 | 0 | 7597000 | 1091120 | 496297.83 | 1331240 | 629156.88 | 1415232 | 0 | 2094247.26 | 0 | 0 | 1606787.5 | 414954.72 | 125685 | 1079750 | 393607.5 | 14443200 | 2636304.8 | 6023308.8 | 549325.8 | 164979 | 287000 | 1047936 | 980424 | 1457015.04 | 3897959.82 | 3741920 | 1540382.4 | 3056611.2 | 0 | 7489031.6 | 965790 | 0 | 0 | 0 | 259506 | 103360 | 0 | 25626736.8 | 0 | 0 | 786240 | 0 | 11675750.4 | 1276723.35 | 15804480 | 11124288 | 14929587.6 | 4855530 | 21625344 | 0 | 0 | 0 | 33669488.16 | 11338024.75 | 0 | 12503542.8 | 2303616 | 7928064 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76501186.56 | 0 | 5007744 | 0 | 1765670.4 | 0 | 0 | 0 | 0 | 0 | 3434692.5 | 0 | 749735 | 5344419.84 | 0 | 0 | 0 | 189183.84 | 0 | 7141879.2 | 0 | 0 | 0 | 223257.6 | 0 | 990720 | 0 | 125236.566 | 11014506.54 | 0 | 0 | 0 | 0 | 0 | 0 | 4252332.48 | 0 | 377140.5 | 0 | 829231.65 | 0 | 8050680 | 14111539.2 | 0 | 15656222.4 | 0 | 7196313.6 | 0 | 325975 | 2163792 | 52027207 | 0 | 0 | 0 |  | 365836649.63 | 217478665.876 | 583315315.506 | 76861376.656 | 76501186.56 | 37889740.33 | 288630573.7 | 63041713.54 | 313726.23 | 23866121.14 | 14443200 | 1767677.35 | 0
Yesterday Day Peak | 0 | 77 | 0 | 0 | 330 | 12 | 0 | 361 | 261 |  | 0 | 225 | 0 | 7 | 2 | 8 | 0 | 0 | 0 | 8 | 0 | 32 | 69 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 34 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 5 | 15 | 150 | 0 | 0 | 360 | 0 | 41 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 78 | 105 | 8 | 20 | 2 | 0 | 20 | 50 | 50 | 163 | 160 | 32 | 73 | 0 | 215 | 18 | 0 | 0 | 0 | 14 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 71 | 17 | 100 | 0 | 118 | 219 | 115 | 0 | 0 | 5 | 216 | 54 | 0 | 114 | 0 | 50 | 0 | 53 | 45 | 0 | 20 | 0 |  | 564 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 10 | 0 | 0 | 0 | 356 | 53 | 0 | 47 | 0 | 51 | 0 | 5 | 0 | 420 | 19 | 0 | 0 |  | 7129 | DayPeak
Yesterday Evening Peak | 0 | 93 | 0 | 0 | 280 | 12 | 0 | 386 | 242 | 0 | 0 | 225 | 0 | 75 | 64 | 46 | 0 | 0 | 0 | 100 | 7 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 26 | 17 | 33 | 24 | 0 | 49 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 10 | 51 | 50 | 19 | 25 | 80 | 150 | 0 | 0 | 290 | 0 | 16 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 18 | 11 | 33 | 22 | 104 | 106 | 83 | 20 | 0 | 20 | 32 | 14 | 47 | 140 | 155 | 32 | 74 | 0 | 176 | 18 | 0 | 0 | 0 | 16 | 8 | 0 | 300 | 0 | 0 | 24 | 0 | 100 | 0 | 100 | 68 | 142 | 270 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 34 | 35 | 60 | 25 | 104 | 0 | 17 | 0 | 0 |  | 801 | 0 | 120 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 64 | 0 | 0 | 0 | 8 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 10 | 0 | 35 | 0 | 380 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 60 | 540 | 36 | 0 | 0 |  | 8838 | EvPeak
Forecast for Evening | 0 | 80 | 0 | 0 | 300 | 108 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 49 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 35 | 135 | 129 | 0 | 0 | 360 | 0 | 40 | 50 | 23 | 55 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 22 | 149 | 115 | 95 | 20 | 0 | 30 | 30 | 51 | 44 | 163 | 158 | 33 | 86 | 0 | 215 | 20 | 0 | 0 | 0 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 160 |  | 100 |  | 709 | 16 | 300 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 93 | 0 | 0 | 300 | 108 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 16 | 25 | 33 | 17 | 33 | 52 | 0 | 49 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 16 | 25 | 135 | 129 | 0 | 0 | 360 | 0 | 16 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 20 | 140 | 115 | 95 | 20 | 1.6 | 30 | 30 | 51 | 44 | 163 | 158 | 33 | 86 | 0 | 215 | 20 | 0 | 0 | 0 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 300 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 |  | 104 | 50 | 100 |  | 100 |  | 421 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 92 | 0 | 0 | 310 | 12 | 0 | 370 | 333 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 28 | 17 |  | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 19 | 40 | 80 | 100 | 0 | 0 | 260 | 0 | 16 | 50 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 25 | 15 | 46 | 167 | 0 | 20 | 1 | 30 | 32 | 8 | 5 | 130 | 158 | 20 | 20 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 34 | 60 | 285 | 65 | 0 | 0 | 1 | 160 | 54 | 0 | 0 | 0 | 10 | 50 | 70 | 11 | 0 | 0 | 0 | 0 | 416 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 189 | 0 | 316 | 30 | 0 | 53 | 0 | 0 | 0 | 1 | 0 | 350 | 36 | 0 | 0 | 0
199
| Minimum Generation |  | 5510 | 5:00
| Highest Generation |  | 8838 | 19:00
| Day Peak Generation |  | 7129 | 12:00
| Evening Peak Generation |  | 8838 | 19:00
| HVDC Max Flow |  | 801 | 19:00
| HVDC EvPeak Flow |  | 801 | 19:00
| Load factor L.F |  | 80.09%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-25
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7129 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5614 | MW
Evening Peak Generation : |  | 8838 | MW Hour : | 19:00 | Available Max Generation : |  | 13198 | MW
E.P. Demand (at gen end) : |  | 8838 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8100 | MW
Maximum Generation : |  | 8838 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5098 | MW
Total Gen. (MKWH) : |  | 169.8728 | System Load Factor : | 80.09% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -266 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-25
Actual : | 98.62 | Ft.(MSL) , | Rule curve : | 103.7 | Ft.( MSL )
Gas Consumed : | Total = | 819.31 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 114751116.986
: |  | Coal : | 63041713.54 | Oil : | 312496694.84 | Total : | 490289525.366
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2876.2633 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 970.319 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 867.9892 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 783.8099 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 708.5887 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 571.7864 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 329.7132 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 147.4842 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 440.9422 |  |  | 0 | 0%
Total | 0 |  | 7696.8961 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Ashuganj(N)-450 MW
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Halishahar-Rampur-Khulshi 132 kV Ckt-2 was under shut down from 09:17 to 15:13 for A/M.
b) Aminbazar 230/132 kV T03 transformer was under shut down from 09:07 to 17:33 for A/M.
c) UMPL-Sherpur 132 kV Ckt-2 was under shut down from 08:57 to 16:44 for A/M.
d) UMPL-Jamalpur 132 kV Ckt-2 was under shut down from 09:26 to 16:57 for A/M.
e) Siddhirganj-Ullon 132 kV Ckt-1 was under shut down from 10:09 to 15:23 for A/M.
f) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 11:13 to 15:32 for A/M.
g) Saidpur-Jaldhaka 132 kV Ckt-2 was under shut down from 09:55 to 14:15 for A/M.
h) Bogura-Barapukuria 230 kV Ckt-2 was under shut down from 09:04 to 17:28 for A/M.
i) Bhandaria 132/33 kV T2 transformer was under shut down from 08:18 to 15:47 for A/M.
j) Gopalganj(New)-Madaripur 132 kV Ckt-1 was under shut down from 08:57 to 16:43 for A/M.
k) Noapara-Jashore 132 kV Ckt-1 was under shut down from 08:57 to 14:37 for A/M.
l) Baghabari 230/132 kV T02 transformer was under shut down from 08:22 to 20:16 for A/M.
m) Rajshahi-HVDC 230 kV Ckt-2 was under shut down from 09:26 to 15:51 for D/W.
n) Polashbari 132/33 kV T1 and its 33 kV Bus were under shut down from 08:10 to 10:30 for C/M. |  |  |  |  | About 15 MW power interruption occurred under Polashbari S/S area
from 08:10 to 10:30.
o) Bogura 230 kV Bus-1 was under shut down from 11:38 to 13:11 for C/M.
p) Kodda 132/33 kV T3 transformer was under shut down from 09:05 to 17:11 for A/M.
q) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 08:35 to 17:29 for A/M.
r) Chowmuhoni 132/33 kV T1 transformer was under shut down from 08:36 to 17:43 for A/M.
s) Savar 132/33 kV T3 transformer was under shut down from 09:15 to 17:14 for A/M.
t) Chandpur 132/33 kV T2 transformer was under shut down from 08:50 to 16:22 for A/M.
u) Bibiyana South GT was synchronized at 12:08 for testing.
v) Ashuganj Unit-3 was synchronized at 11:44.
w) Sirajganj Unit-3 GT & ST were synchronized at 13:56 & 19:37 respectively.
x) Ullon-Haripur 132 kV Ckt was under shut down from 15:31 to 17:52 for A/M.
y) Jashore-Jhenaidah 132 kV Ckt-2 was switched on at 16:48.
z) Rajshahi ATR-1 was under shut down from 15:51 to 16:44 for SAS work.
aa) Shahmirpur-Sikalbaha 132 kV Ckt-01 was shut down at 07:44(25/12/2020) for D/W.
ab) Dohazari-Sikalbaha 132 kV Ckt-01 was shut down at 07:37(25/12/2020) for D/W.
ac) Bagerhat 132/33 kV T3 transformer was shut down at 07:17(25/12/2020) for C/M.
ad) Shahjibazar 132/33 kV T4 transformer tripped at 22:32 from HT side and was switched on at 22:41. |  |  |  |  | About 47 MW power interruption occurred under Shahjibazar S/S area
from 22:32 to 22:41.
ae) Bhangura 132 kV Grid S/S Bus was energized at 22:34 from Baghabari and was shut down
at 00:09(25/12/2020).
af) Bhangura 132/33 kV T1 & T2 transformers were charged at 22:39 & 22:42 respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 93 | 1817500 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 7203091 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 745409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 386 | 8873980 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 242 | 6238000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4724500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 75 | 513600 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 345240 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 46 | 409843 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 86 | 1779051 | High Voltage.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 257832 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 872640
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 37440 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1050120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1289280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1014917
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 289121 | High Voltage.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1271220 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 24 | 123684 | High Voltage.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3389780
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 100 | 1186560 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1857600
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 182880 | High Voltage.
| Dhaka area Total |  |  |  | 6057 | 2556 | 46690988
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 109215
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 921600
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 49 | 1161949 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 162 | 3820977 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 396757
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 22080 | High Voltage.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1939200
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 445536
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 594240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 191040 | High Voltage.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 253 | 4453636 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1301725
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 1190400 | High Voltage.
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 124200
| Chattogram area Total |  |  |  | 2266 | 935 | 16695715
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 860082 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 2849760
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 1186000 | Under maint
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7597000 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 556776 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1010880
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 384727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1224706
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2117672
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1157600 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 1025280 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 326736 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 1925760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 617000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 24 | 168250 | High Voltage.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 524810
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1252860 | High Voltage.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 35 | 268800 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1207 | 25222279
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2487080 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 432540
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 83 | 663360 | High Voltage.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10350
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 24 | 151200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2371200 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 235610
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 687 | 348 | 6351340
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 175000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 654960 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3419263 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 155 | 3598000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 14 | 550800 | High Voltage.
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 933984
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 136000 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 781920 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1600320 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 176 | 4328920
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 441000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 346008 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 270 | 5221000 | Gas shortage
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 25 | 505200
| Sylhet Area Total |  |  |  | 1988 | 1027 | 22692375
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 801 | 13281456
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 224640 | High Voltage.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 120 | 4769280 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 329625 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1351680 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1060 | 19956681
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 547584 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 483700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 251427 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 540 | 11851300 | Line O/L
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 810440 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1054 | 676 | 13944451
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 8 | 19226 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 129 | 3221464 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 35 | 708745 | ST synchronized process
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 8132000 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 516000
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 165438
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 23040 | High Voltage.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 77 | 806992 | High Voltage.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1649760
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 60 | 292800 | High Voltage.
| Rajshahi Area Total |  |  |  | 2183 | 841 | 15535465
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1826618
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 927360
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29500
| Rangpur Area Total |  |  |  | 605 | 188 | 2783478
| Total |  |  |  | 20104 | 8838 | 169872772
| Eastern Grid Total |  |  |  | 13978 | 6073 | 117652697
| Western Grid Total |  |  |  | 6126 | 2765 | 52220075
| National Grid Total |  |  |  | 20104 | 8838 | 169872772
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-24
| (a) ENTIRE EASTERN GRID : |  | 5648 | MW | (b) ENTIRE WESTERN GRID : |  | 2737 | MW
| i) Dhaka area |  | 2998 | MW | i) Khulna area |  | 1044 | MW
| ii) Chittagong area |  | 887 | MW | ii) Rajshahi area |  | 867 | MW
| iii) Comilla area |  | 744 | MW | iii) Barisal area |  | 232 | MW
| iv) Mymensingh area |  | 710 | MW | iv) Rangpur area |  | 594 | MW
| v) Sylhet area |  | 309 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8385 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 94 | 10:00 | Jamalpur | 82 | 18:30 | Benapol | 36 | 19:30
| Munsiganj | 80 | 19:30 | Sherpur | 86 | 21:00 | Jhenida | 92 | 18:30
| Sonargaon | 62 | 18:00 | Srimongal | 35 | 9:00 | Bottail | 98 | 18:00
| Shyampur | 152 | 0:00 | Shahjibazar | 78 | 21:00 | G.K Project | 35 | 18:00
| Bhulta | 155 | 19:00 | Fenchuganj | 26 | 19:00 | Faridpur | 132 | 20:00
| Madanganj | 55 | 22:00 | Kulawara | 31 | 18:00 | Madaripur | 60 | 21:00
| Shitalakhya | 93 | 15:00 | Sylhet | 78 | 19:30 | Sariatpur | 40 | 19:30
| Rahim steel | 17 | 12:00 | Chatak | 20 | 18:00 | Gopalganj | 57 | 18:00
| Matuail | 54 | 10:00 | Sunamganj | 27 | 19:00 | Bagerhat | 82 | 18:30
| Ghorasal | 66 | 18:00 | Biani Bazar | 34 | 18:00 | Mongla | 38 | 18:30
| Narsingdi | 123 | 22:00 | Comilla (S) | 106 | 18:00 | Satkhira | 74 | 19:00
| Haripur (SBU) | 93 | 15:00 | Comilla(N) | 71 | 19:30 | Gallamari | 16 | 13:00
| Ullon | 40 | 17:00 | Chandpur | 64 | 19:30 | Magura | 40 | 18:00
| Hasnabad | 134 | 18:30 | Feni | 76 | 18:00 | Norail | 24 | 18:00
| Magbazar | 63 | 12:00 | Chowmuhani | 122 | 19:00 | Chuadanga | 61 | 18:30
| Maniknagar | 64 | 12:00 | Ashuganj | 38 | 19:00 | Barisal(N) | 28 | 18:30
| Bangabhaban | 19 | 12:00 | Daudkandi | 92 | 19:00 | Barisal (S) | 68 | 18:00
| Narinda | 74 | 18:00 | B.Baria | 94 | 19:00 | Patuakhali | 77 | 20:00
| Dhanmondi | 93 | 13:00 | Ramganj | 62 | 20:00 | Bhandaria | 40 | 18:30
| Lalbag | 70 | 13:00 | Chaddagram | 28 | 12:00 | Borhan Uddin | 25 | 19:30
| Madartek | 44 | 21:00 | PHP | 9 | 19:00 | Ishurdi | 48 | 18:30
| Dhaka University |  |  | Madunaghat | 43 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.5 | Hathazari | 70 | 0.77083 | Natore | 82 | 0.77083
| Fatullah | 41 | 9:00 | Khulshi | 157 | 18:30 | Bogra | 118 | 18:30
| Mirpur | 68 | 18:00 | Halishahar | 91 | 19:30 | Noagaon | 77 | 20:00
| Kalyanpur | 51 | 18:00 | Baraulia | 144 | 15:00 | Rajshahi | 97 | 20:00
| Gulshan | 70 | 13:00 | Sikalbaha | 20 | 18:00 | Rajshahi New | 8 | 18:00
| Uttara | 62 | 18:00 | Dohazari | 56 | 19:00 | C.Nawabganj | 52 | 19:30
| Uttara New | 23 | 18:00 | Cox'sbazar | 72 | 18:00 | Amnura | 30 | 18:00
| Kamrangirchar | 69 | 14:00 | Chandraghona | 18 | 19:00 | Pabna | 80 | 19:00
| Savar | 111 | 12:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 74 | 19:00
| Bhasantec | 96 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 63 | 9:00
| Agargaon | 44 | 13:00 | Bakulia | 72 | 13:00 | Niyamatpur | 41 | 19:00
| Satmosjid | 67 | 0.58333 | Julda | 18 | 0.041667 | Joypurhat | 44 | 0.77083
| Tongi | 72 | 18:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 39 | 18:00
| Kabirpur | 162 | 16:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:00
| Basundhara | 97 | 13:00 | Shahmirpur | 19 | 18:00 | Rangpur | 105 | 18:30
| Manikganj | 48 | 19:00 | Khagrachhari | 20 | 7:00 | Lalmonirhat | 45 | 18:30
| Joydevpur | 110 | 18:30 | Matarbari | 24.5 | 19:00 | Saidpur | 79 | 18:00
| New Tongi | 94 | 12:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 84 | 18:00
| Kodda | 188 | 18:00 | Rangamati | 8 | 12:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 66 | 19:00 | Abul Khair 230 | 162 | 7:00 | Palashbari | 94 | 18:00
| Rajendrapur | 74 | 18:30 | BSRM | 144 | 1:00 | Barapukuria | 40 | 19:30
| Valuka | 90 | 18:30 | GPH Ispat | 88 | 6:00 | Panchagar | 41 | 18:30
| Tangail | 144 | 18:00 | Goalpara | 17 | 13:00 | Joldhaka | 25 | 18:30
| Mymensing | 144 | 19:00 | Central s/s | 78 | 19:30 | Kurigram | 40 | 18:30
| Kishorganj | 92 | 20:00 | Noapara | 47 | 18:30
| Netrokona | 92 | 18:00 | Jessore | 76 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 24:00 | 406 | 11:00 | Kaliakoir | 390 | 0.25 | 370 | 0.45833
| Bheramara | 412 | 24:00 | 395 | 10:00 | Bhulta | 384 | 0.29167 | 369 | 0.5
| Ashuganj(N) | 386 | 24:00 | 374 | 16:00 | Gopalganj | 412 | 0.54167 | 395 | 0.8125
| Payra | 416 | 22:00 | 405 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 7:00 | 234 | 1:00 | Comilla (N) | 239 | 21:00 | 231 | 11:00
| Ishurdi | 239 | 5:00 | 227 | 18:00 | Hathazari | 227 | 6:00 | 218 | 12:00
| Ashuganj | 240 | 6:00 | 231 | 11:00 | Megnaghat | 235 | 7:00 | 230 | 11:00
| Serajganj | 234 | 7:00 | 227 | 12:00 | Fenchuganj | 245 | 6:00 | 241 | 13:00
| Baghabari | 245 | 5:00 | 237 | 21:00 | Siddhirganj | 233 | 7:00 | 224 | 11:00
| Barapukuria | 234 | 4:00 | 224 | 12:00 | Maniknagar | 231 | 7:00 | 224 | 10:00
| Bogra | 236 | 6:00 | 224 | 11:00 | Agargaon | 231 | 5:00 | 221 | 12:00
| Rajshahi | 232 | 6:00 | 220 | 13:00 | Barisal | 247 | 7:00 | 239 | 19:00
| Khulna South | 237 | 6:00 | 218 | 18:00 | AKSML | 227 | 7:00 | 210 | 3:00
| Rampura | 231 | 1:00 | 227 | 11:00 | BSRM | 230 | 7:00 | 217 | 2:00
| Haripur | 230 | 21:00 | 224 | 10:00 | Bibiyana | 245 | 20:00 | 239 | 19:00
| Hasnabad | 231 | 1:00 | 220 | 10:00 | Bhulta | 233 | 19:00 | 224 | 17:00
| Shyampur | 231 | 22:00 | 220 | 11:00 | Ashuganj (S) | 236 | 7:00 | 229 | 11:00
| Aminbazar | 232 | 24:00 | 222 | 11:00 | Kaliakoir | 230 | 23:00 | 217 | 12:00
| Tongi | 228 | 19:30 | 220 | 10:00 | GPH | 228 | 23:00 | 220 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 20:00 | 134 | 11:00 | Madanhat | 138 | 0.125 | 133 | 0.41667
| Munsiganj | 140 | 18:30 | 135 | 10:00 | Hathazari | 138 | 0.25 | 132 | 0.5
| Sonargaon | 138 | 21:00 | 133 | 11:00 | Khulshi | 135 | 0.041667 | 131 | 0.20833
| Shyampur | 135 | 21:00 | 122 | 2:00 | Halishahar | 138 | 0.29167 | 133 | 0.16667
| Bhulta | 133 | 20:00 | 129 | 10:00 | Baraulia | 139 | 0.25 | 130 | 0.33333
| Madanganj | 138 | 19:30 | 133 | 12:00 | Sikalbaha | 139 | 0.29167 | 132 | 0.083333
| Shitalakhya | 142 | 20:00 | 133 | 11:00 | Dohazari | 135 | 0.79167 | 121 | 0.41667
| Rahim steal | 140 | 20:00 | 134 | 10:00 | Cox'sbazar | 126 | 0.375 | 116 | 0.75
| Matuail | 140 | 20:00 | 134 | 11:00 | Chandraghona | 138 | 0.25 | 131 | 0.16667
| Ghorasal | 140 | 1:00 | 136 | 10:00 | Kaptai | 136 | 0.66667 | 135 | 0.041667
| Narsinghdi | 138 | 6:00 | 133 | 10:00 | A. Khaer Stl. | 137 | 0.41667 | 132 | 0.625
| Haripur (SBU) | 140 | 20:00 | 135 | 10:00 | Bakulia | 136 | 0.16667 | 132 | 0.45833
| Ullon | 132 | 4:00 | 127 | 9:00 | Julda | 137 | 0.041667 | 133 | 0.45833
| Hasnabad | 139 | 1:00 | 135 | 9:00 | TK Chemical | 137 | 0.041667 | 131 | 0.29167
| Magbazar | 132 | 3:00 | 125 | 12:00 | Modern Steel | 138 | 0.125 | 132 | 0.5
| Maniknagar | 139 | 7:00 | 134 | 10:00 | Shahmirpur | 139 | 0.29167 | 133 | 0.45833
| Bangabhaban | 139 | 7:00 | 134 | 10:00 | Khagrachhari | 138 | 0.29167 | 131 | 0.16667
| Narinda | 139 | 7:00 | 134 | 10:00 | Matarbari | 126 | 0.29167 | 119 | 0.75
| Dhanmondi | 132 | 4:00 | 127 | 9:00 | Baroiar Hat | 137 | 0.79167 | 134 | 0.29167
| Lalbag | 129 | 7:00 | 119 | 12:00 | Rangamati | 136 | 9:00 | 133 | 1:00
| Madartek | 131 | 3:00 | 126 | 11:00 | Goalpara S/S | 140 | 17:00 | 128 | 18:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 140 | 6:00 | 128 | 0.75
| Aftabnagar | 132 | 6:00 | 126 | 10:00 | Noapara | 139 | 6:00 | 126 | 0.75
| Fatuiiah | 136 | 22:00 | 129 | 10:00 | Jessore | 136 | 6:00 | 123 | 0.75
| Mirpur | 131 | 4:00 | 123 | 11:00 | Benapol | 137 | 0.25 | 124 | 0.75
| Kalyanpur | 130 | 6:00 | 123 | 11:00 | Jhenida | 136 | 6:00 | 121 | 0.75
| Gulshan | 130 | 6:00 | 125 | 12:00 | Bottail | 137 | 0.125 | 129 | 0.75
| Uttara | 129 | 1:00 | 121 | 11:00 | G.K Project | 141 | 0.125 | 135 | 0.77083
| Uttara New | 136 | 6:00 | 130 | 11:00 | Faridpur | 137 | 0.29167 | 130 | 0.75
| Kamrangirchar | 140 | 7:00 | 135 | 12:00 | Madaripur | 138 | 0.625 | 132 | 0.79167
| Savar | 129 | 7:00 | 120 | 12:00 | Shariyatpur S/S | 140 | 6:00 | 132 | 0.79167
| Bhasantec | 136 | 7:00 | 128 | 12:00 | Gopalganj | 140 | 0.20833 | 131 | 0.8125
| Agargaon | 136 | 7:00 | 130 | 12:00 | Bagerhat | 140 | 6:00 | 123 | 0.75
| Satmosjid | 135 | 7:00 | 129 | 12:00 | Mongla | 136 | 6:00 | 127 | 0.75
| Tongi | 139 | 21:00 | 133 | 17:00 | Satkhira | 139 | 6:00 | 127 | 18:00
| Kabirpur | 133 | 0:00 | 125 | 10:00 | Gallamari | 141 | 0.25 | 129 | 0.75
| Basundhara | 137 | 21:00 | 126 | 18:00 | Magura | 135 | 2:00 | 121 | 0.75
| Manikganj | 142 | 21:00 | 134 | 16:00 | Norail | 135 | 0.29167 | 119 | 0.75
| Joydevpur | 142 | 6:00 | 134 | 16:00 | Chuadanga | 134 | 4:00 | 118 | 0.75
| New Tongi | 139 | 21:00 | 131 | 16:00 | Barisal(N) | 141 | 5:00 | 135 | 19:00
| Kodda | 138 | 21:00 | 127 | 16:00 | Barisal (S) | 14 | 0.625 | 135 | 0.45833
| Dhamrai | 132 | 23:00 | 125 | 12:00 | Patuakhali(S) | 136 | 0.20833 | 131 | 0.75
| Rajendrapur | 139 | 22:00 | 131 | 17:00 | Bhandaria | 138 | 0.25 | 131 | 0.79167
| Valuka | 131 | 5:00 | 119 | 18:00 | Ishurdi | 139 | 6:00 | 134 | 11:00
| Tangail | 133 | 4:00 | 126 | 18:00 | Ruppur Paromanobik | 139 | 5:00 | 134 | 18:00
| Mymensing | 132 | 6:00 | 122 | 18:00 | Natore | 139 | 7:00 | 132 | 11:00
| Kishorganj | 134 | 5:00 | 121 | 18:30 | Bogra | 138 | 5:00 | 131 | 11:00
| Netrokona | 132 | 5:00 | 117 | 18:00 | Noagaon | 134 | 3:00 | 126 | 11:00
| Jamalpur | 138 | 11:00 | 122 | 1:00 | Rajshahi | 140 | 2:00 | 134 | 11:00
| Sherpur | 137 | 11:00 | 122 | 1:00 | Rajshahi New | 142 | 5:00 | 135 | 10:00
| Srimongal | 138 | 1:00 | 135 | 18:30 | C.Nawabganj | 140 | 1:00 | 132 | 10:00
| Shahjibazar | 137 | 6:00 | 130 | 19:00 | Amnura | 139 | 15:00 | 132 | 10:00
| Fenchuganj | 139 | 7:00 | 135 | 18:00 | Pabna | 138 | 3:00 | 132 | 12:00
| Khulawara | 138 | 7:00 | 135 | 19:30 | Shahjadpur | 140 | 1:00 | 136 | 11:00
| Sylhet | 137 | 5:00 | 134 | 18:30 | Serajganj | 136 | 2:00 | 130 | 10:00
| Chatak | 136 | 1:00 | 133 | 18:30 | Niyamatpur | 134 | 6:00 | 124 | 10:00
| Sunamganj | 135 | 1:00 | 133 | 18:30 | Joypurhat | 136 | 4:00 | 125 | 11:00
| Biani Bazar | 137 | 4:00 | 133 | 18:00 | Sherpur(Bogura) | 138 | 7:00 | 131 | 12:00
| Comilla(s) | 132 | 6:00 | 126 | 18:00 | Mohastangor | 137 | 7:00 | 128 | 11:00
| Comilla(n) | 143 | 22:00 | 139 | 12:00 | Rangpur | 132 | 7:00 | 121 | 18:00
| Chandpur | 144 | 6:00 | 140 | 11:00 | Lalmonirhat | 131 | 7:00 | 120 | 18:30
| Feni | 140 | 7:00 | 137 | 12:00 | Saidpur | 131 | 4:00 | 120 | 13:00
| Chowmuhani | 140 | 10:00 | 134 | 18:00 | Purbasadipur | 130 | 7:00 | 116 | 18:00
| Ashuganj | 140 | 7:00 | 131 | 18:00 | Thakurgaon | 130 | 6:00 | 116 | 18:00
| Daudkandi | 140 | 20:00 | 135 | 11:00 | Palashbari | 135 | 7:00 | 125 | 18:00
| B.Baria | 132 | 7:00 | 125 | 18:00 | Barapukuria | 134 | 4:00 | 124 | 12:0
| Ramganj | 138 | 8:00 | 134 | 13:00 | Panchagar | 130 | 7:00 | 116 | 18:00
| Chaddagram | 142 | 6:00 | 138 | 3:00 | Joldhaka | 131 | 5:00 | 116 | 18:0
| PHP | 140 | 7:00 | 134 | 2:00 | Kurigram | 128 | 0.20833 | 119 | 0.75

## L-Curve
Date | 2020-12-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 266 | 5155 | 1770 | 6925 |  |  |  | QF-LDC-11
0:30 | 142 | 4754 | 1814 | 6568 | Date: | 2020-12-24
1:00 | 18 | 4353 | 1858 | 6211
1:30 | 49 | 4248 | 1836.5 | 6084.5
2:00 | 80 | 4143 | 1815 | 5958
2:30 | 81.5 | 4055 | 1779.5 | 5834.5 | [5 empty] | Gen. at Eve. Peak | 8838 | 8838 MW (19:00 )
3:00 | 83 | 3967 | 1744 | 5711 | [6 empty] | 19:00
3:30 | 46.5 | 3950.5 | 1701.5 | 5652 | [5 empty] | Gen. at Day Peak | 7129 | 7129 MW (12:00 )
4:00 | 10 | 3934 | 1659 | 5593 | [6 empty] | 12:00
4:30 | 32 | 3904.5 | 1647 | 5551.5 | [5 empty] | Highest Generation | 8838
5:00 | 54 | 3875 | 1635 | 5510 | [6 empty] | 19:00
5:30 | 62 | 3906.5 | 1679.5 | 5586
6:00 | 70 | 3938 | 1724 | 5662
6:30 | 38 | 4092.5 | 1790 | 5882.5
7:00 | 6 | 4247 | 1856 | 6103
7:30 | 15.5 | 4415.5 | 1960 | 6375.5
8:00 | 25 | 4584 | 2064 | 6648
8:30 | 75 | 4642 | 2130 | 6772
9:00 | 125 | 4700 | 2196 | 6896
9:30 | 181 | 4724.5 | 2187.5 | 6912
10:00 | 237 | 4749 | 2179 | 6928
10:30 | 190 | 4764.5 | 2144.5 | 6909
11:00 | 143 | 4780 | 2110 | 6890
11:30 | 151.5 | 4876 | 2133.5 | 7009.5
12:00 | 160 | 4972 | 2157 | 7129
12:30 | 105 | 5015.5 | 2156 | 7171.5
13:00 | 50 | 5059 | 2155 | 7214
13:30 | 30 | 4952.5 | 2122.5 | 7075
14:00 | 10 | 4846 | 2090 | 6936
14:30 | 13 | 4823 | 2070.5 | 6893.5
15:00 | 16 | 4800 | 2051 | 6851
15:30 | 20.5 | 4802 | 2045 | 6847
16:00 | 25 | 4804 | 2039 | 6843
16:30 | 48.5 | 4968.5 | 2029 | 6997.5
17:00 | 72 | 5133 | 2019 | 7152
17:30 | 83 | 5486 | 2340.5 | 7826.5
18:00 | 94 | 5839 | 2662 | 8501
18:30 | 104.5 | 5956 | 2713.5 | 8669.5
19:00 | 115 | 6073 | 2765 | 8838
19:30 | 137 | 6070 | 2727 | 8797
20:00 | 118 | 6044 | 2679 | 8723 |  |  |  | Executive Engineer
20:30 | 118 | 5970.5 | 2642 | 8612.5 |  |  |  | Network Operation Division
21:00 | 118 | 5897 | 2605 | 8502
21:30 | 118.5 | 5758 | 2446 | 8204
22:00 | 119 | 5619 | 2287 | 7906 |  |  |  |  | Page 6 of 7
22:30 | 106.5 | 5423 | 2194.5 | 7617.5
23:00 | 94 | 5227 | 2102 | 7329
23:30 | 180 | 5191 | 1936 | 7127
24:00 | 266 | 5155 | 1770 | 6925
8838 MW (19:00 )
7129 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-24 |  | Energy | 169872772
[11 empty] | 2020-12-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2861 | 422 | 1359 | 1850 | 496 | 45 | 48 | 0 | 80 | 0
0:30 | 2913.5 | 422 | 1326.5 | 1335.5 | 542.5 | 45 | 24 | 0 | 77 | 0 | Date: | 2020-12-24
1:00 | 2966 | 422 | 1294 | 821 | 589 | 45 | 0 | 0 | 74 | 0
1:30 | 2986.5 | 421 | 1309.5 | 670.5 | 579 | 45 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 169.8728 | Total Energy Gen 169.873 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.873 MKWHr
2:00 | 3007 | 420 | 1325 | 520 | 569 | 45 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2983 | 420 | 1299 | 463 | 553.5 | 45 | 0 | 0 | 71 | 0 | [7 empty] | Energy Requirement | 169.8728
3:00 | 2959 | 420 | 1273 | 406 | 538 | 45 | 0 | 0 | 70 | 0
3:30 | 2999.5 | 373 | 1302.5 | 324.5 | 537.5 | 46 | 0 | 0 | 69 | 0 | [6 empty] | Shortage
4:00 | 3040 | 326 | 1332 | 243 | 537 | 47 | 0 | 0 | 68 | 0
4:30 | 3023.5 | 326 | 1323.5 | 236 | 527.5 | 47 | 0 | 0 | 68 | 0
5:00 | 3007 | 326 | 1315 | 229 | 518 | 47 | 0 | 0 | 68 | 0
5:30 | 2880.5 | 332 | 1364 | 388 | 507.5 | 47 | 0 | 0 | 67 | 0
6:00 | 2754 | 338 | 1413 | 547 | 497 | 47 | 0 | 0 | 66 | 0
6:30 | 2689 | 379 | 1360.5 | 843 | 497 | 48 | 16 | 0 | 49.5 | 0.5 |  |  |  |  | Coal
7:00 | 2624 | 420 | 1308 | 1139 | 497 | 49 | 32 | 0 | 33 | 1
7:30 | 2693 | 468 | 1353 | 1225.5 | 497 | 49 | 32 | 0 | 47.5 | 10.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2762 | 516 | 1398 | 1312 | 497 | 49 | 32 | 0 | 62 | 20
8:30 | 2817 | 516 | 1428 | 1339 | 496.5 | 48.5 | 36 | 0 | 58 | 33
9:00 | 2872 | 516 | 1458 | 1366 | 496 | 48 | 40 | 0 | 54 | 46
9:30 | 2854.5 | 539 | 1438.5 | 1382.5 | 496 | 47.5 | 40 | 0 | 63 | 51
10:00 | 2837 | 562 | 1419 | 1399 | 496 | 47 | 40 | 0 | 72 | 56
10:30 | 2856 | 562.5 | 1434.5 | 1340.5 | 496 | 46.5 | 43.5 | 0 | 74 | 55.5
11:00 | 2875 | 563 | 1450 | 1282 | 496 | 46 | 47 | 0 | 76 | 55
11:30 | 2880 | 563.5 | 1431 | 1386 | 496 | 46 | 65.5 | 0 | 77 | 64.5
12:00 | 2885 | 564 | 1412 | 1490 | 496 | 46 | 84 | 0 | 78 | 74
12:30 | 2867 | 564 | 1362 | 1614.5 | 496 | 46 | 83.5 | 0 | 78 | 60.5
13:00 | 2849 | 564 | 1312 | 1739 | 496 | 46 | 83 | 0 | 78 | 47
13:30 | 2849 | 564 | 1312 | 1739 | 496 | 46 | 83 | 0 | 78 | 47
14:00 | 2849 | 564 | 1312 | 1739 | 496 | 46 | 83 | 0 | 78 | 47
14:30 | 2759.5 | 564 | 1246 | 1736 | 481 | 46.5 | 83.5 | 0 | 78 | 38
15:00 | 2670 | 564 | 1180 | 1733 | 466 | 47 | 84 | 0 | 78 | 29
15:30 | 2679.5 | 564 | 1188 | 1716.5 | 471 | 47.5 | 84 | 0 | 76 | 20.5
16:00 | 2689 | 564 | 1196 | 1700 | 476 | 48 | 84 | 0 | 74 | 12
16:30 | 2709 | 564 | 1148 | 1814 | 486 | 48 | 142 | 0 | 80 | 6.5
17:00 | 2729 | 564 | 1100 | 1928 | 496 | 48 | 200 | 0 | 86 | 1
17:30 | 2757 | 682 | 1209 | 2255.5 | 506 | 48 | 272.5 | 0 | 96 | 0.5
18:00 | 2785 | 800 | 1318 | 2583 | 516 | 48 | 345 | 0 | 106 | 0
18:30 | 2839.5 | 800.5 | 1345.5 | 2624 | 565.5 | 48.5 | 341 | 0 | 105 | 0
19:00 | 2894 | 801 | 1373 | 2665 | 615 | 49 | 337 | 0 | 104 | 0
19:30 | 2858 | 801 | 1363 | 2667 | 626 | 49 | 329 | 0 | 104 | 0
20:00 | 2847 | 801 | 1365 | 2602 | 624 | 49 | 331 | 0 | 104 | 0
20:30 | 2845 | 801 | 1362 | 2516 | 625.5 | 48 | 313 | 0 | 102 | 0
21:00 | 2843 | 801 | 1359 | 2430 | 627 | 47 | 295 | 0 | 100 | 0
21:30 | 2785 | 801 | 1341.5 | 2272.5 | 612 | 46 | 249 | 0 | 97 | 0
22:00 | 2727 | 801 | 1324 | 2115 | 597 | 45 | 203 | 0 | 94 | 0
22:30 | 2731 | 706.5 | 1291.5 | 1982.5 | 597 | 45 | 173 | 0 | 91 | 0
23:00 | 2735 | 612 | 1259 | 1850 | 597 | 45 | 143 | 0 | 88 | 0
23:30 | 2798 | 517 | 1309 | 1850 | 546.5 | 45 | 95.5 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 27.0° C
24:00 | 2861 | 422 | 1359 | 1850 | 496 | 45 | 48 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 169.873 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.873 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 45 | 47 | 47 | 47 | 49 | 49 | 48 | 47 | 46 | 46 | 46 | 47 | 47 | 48 | 48 | 48 |  | 49 | 49 | 49 | 47 | 45 | 45 | 45 | 1161949
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 4 | 11 | 14 | 17 | 17 | 11 | 15 | 10 | 5 | 0 | [9 empty] | 109215
6 | Sikalbaha 225MW CCPP (Gas) | 162 | 163 | 163 | 163 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 161 | 164 |  | 162 | 163 | 164 | 162 | 163 | 163 | 163 | 3820977
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 2 | 102 |  | 102 | 102 | 102 | 68 | 11 |  | 0 | 396757
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [5 empty] | 24 | 45 | 45 | 45 | 45 | 111 | 182 | 195 | 195 | 195 | 202 | 286 |  | 300 | 300 | 300 | 300 | 300 | 245 | 195 | 3389780
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 41 | 41 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 44 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 44 | 45 | 77 | 93 | 93 | 93 | 93 | 94 | 94 |  | 93 | 94 | 94 | 94 | 93 | 93 | 93 | 1817500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 330 | 330 | 330 | 330 | 330 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 310 | 7203091
26
28 | Ashuganj TPP Unit- 3 | [11 empty] | 15 | 25 | 65 | 70 | 70 | 75 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 860082
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 150 | 150 | 150 | 150 | 150 | 150 | 125 | 110 | 110 | 110 | 110 | 110 |  | 150 | 150 | 150 | 135 | 120 | 120 | 140 | 2849760
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 23 | 26 | 26 |  | 26 | 26 | 26 | 23 | 26 | 23 | 26 | 556776
33 | Ashuganj 225 MW CCPP | 187 | 195 | 175 | 190 | 175 | 138 | [19 empty] | 0 | 1186000
34 | Ashuganj 450 MW CCPP(South) | 355 | 355 | 355 | 355 | 355 | 355 | 320 | 305 | 305 | 305 | 355 | 360 | 330 | 260 | 270 | 270 | 270 | 275 |  | 290 | 290 | 290 | 290 | 290 | 260 | 260 | 7597000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 34 | 51 | 51 | 50 | 49 | 50 | 54 | 54 | 54 | 52 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1010880
36 | Chandpur 150 MW CCPP | 49 | 50 | 50 | 50 | 50 | 45 | 46 | 50 | 45 | 50 | 46 | 51 | 46 | 46 | 46 | 51 | 46 | 51 |  | 50 | 51 | 44 | 45 | 51 | 51 | 51 | 1157600
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 349 | 379 | 358 | 386 | 359 | 390 | 351 | 366 | 362 | 356 | 381 | 361 | 354 | 368 | 369 | 358 | 375 | 339 |  | 386 | 362 | 360 | 370 | 358 | 355 | 357 | 8873980
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4724500
41 | Haripur 360MW CCPP(HPL) | 262 | 268 | 267 | 279 | 277 | 279 | 248 | 287 | 288 | 288 | 271 | 261 | 262 | 248 | 243 | 243 | 243 | 242 |  | 242 | 242 | 242 | 243 | 244 | 244 | 274 | 6238000
42 | RPCL 210MW CCPP | 105 | 108 | 108 | 106 | 109 | 108 | 108 | 109 | 106 | 98 | 130 | 105 | 105 | 104 | 104 | 103 | 105 | 103 |  | 106 | 106 | 107 | 107 | 108 | 107 | 107 | 2487080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 14 | 30 | 33 | 27 | 45 | 27 | 41 | 13 | 5 | 1 | [9 empty] | 235610
44 | Fenchugonj CCPP Phase-1 | [16 empty] | 10 | 20 |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 175000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 654960
46 | Shajibazar 330 MW CCPP | 156 | 157 | 157 | 158 | 158 | 155 | 157 | 157 | 158 | 156 | 156 | 160 | 157 | 158 | 156 | 156 | 158 | 156 |  | 155 | 157 | 158 | 158 | 156 | 156 | 156 | 3598000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 32 |  | 32 | 32 | 33 | 33 | 34 | 33 | 34 | 781920
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 76 | 76 | 76 | 76 | 73 | 74 | 74 | 73 | 72 | 73 | 70 | 30 | 30 | 30 | 30 | 74 |  | 74 | 74 | 75 | 75 | 75 | 40 | 75 | 1600320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 183 | 169 | 169 | 169 | 169 | 220 | 216 | 215 | 215 | 215 | 215 | 215 | 216 | 184 | 151 | 150 | 127 | 161 |  | 176 | 176 | 176 | 176 | 138 | 136 | 137 | 4328920
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 441000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 2 | 2 | 2 |  |  |  | 2 |  |  | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 136000
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 50 | 50 | 50 | 48 | 48 | 50 | 47 | 14 | 14 | 14 | 16 | 14 |  | 14 | 14 | 14 | 14 | 14 | 11 | 14 | 550800
56 | Shahjahanulla 25 MW PP | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 8 | 8 | 14 | 14 | 14 | 14 | 14 | 14 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 346008
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | [12 empty] | 30 | 50 | 50 | 50 | 50 | 50 |  | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 505200
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 | 17 | 17 | 22 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 289121
59 | Tangail Palli Power Gen 22 MW
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 19 | 19 | 17 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 445536
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 13 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 16 | 257832
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 432540
63 | Impoprt (Tripura) | 74 | 72 | 70 | 68 | 68 | 66 | 33 | 62 | 54 | 72 | 76 | 78 | 78 | 80 | 78 | 74 | 86 | 106 |  | 104 | 104 | 104 | 100 | 94 | 88 | 80 | 1925760
64 | Malancha, Ctg. EPZ (United) | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 16 | 8 | 8 | 5 | 5 | 8 | 6 | 6 | 8 | 11 | 15 |  | 25 | 28 | 30 | 32 | 37 | 41 | 41 | 594240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | [7 empty] | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 326736
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [10 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 167580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [6 empty] | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 617000
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 12 | 18 | 18 | 18 | 18 | 22 | 22 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 34 | 34 | 34 | 34 | 20 | 26 | 26 | 26 | 20 |  | 26 | 26 | 33 | 33 | 32 | 32 | 32 | 671220
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805900
73 | Ghorashal 108MW PP (Regent) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 745409
| Feni Lanka Power | [5 empty] | 26 | 70 | 70 | 70 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 88 | 52 |  | 34 | 34 | 17 |  |  |  | 0 | 1252860
| Chowmuhani 113 MW | [17 empty] | 35 |  | 35 | 38 | 35 | 35 | 35 | 35 | 0 | 268800
| Manikgonj 162MW PP(MPGL) | [6 empty] | 35 | 35 | 35 | 35 | [6 empty] | 3 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 182880
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 0 | 8 | 32 | 32 | 32 | 32 | 35 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 872640
78 | Gazipur 52 MW PP | [16 empty] | 2 | 24 |  | 24 | 24 | 24 | 24 |  |  | 0 | 123684
79 | Kodda 150MW PP | [6 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 133 | 150 |  | 150 | 150 | 150 | 150 | 115 | 100 | 48 | 1289280
80 | Jamalpur 95 MW PP(Powerpac) | [11 empty] | 8 | 24 | 24 | 24 | 24 | 26 | 67 |  | 83 | 90 | 90 | 90 | 72 | 66 | 16 | 663360
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 168250
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 3 | 3 | 2 | 1 | [10 empty] | 23160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1301725
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [11 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 45 |  | 64 | 64 | 64 | 30 | 30 |  | 0 | 345240
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 85 | 85 | 85 | 50 | 50 | 50 | 50 | 50 | 48 | 46 | 55 | 69 | 80 | 85 | 72 | 81 | 78 | 84 |  | 86 | 86 | 85 | 85 | 84 | 85 | 84 | 1779051
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 48 | [9 empty] | 0 | 7 | 16 | 16 | 16 | 16 | 19 | 65 |  | 75 | 75 | 75 | 75 | 41 |  | 0 | 513600
| Meghnaghat 104 MW PP (OPCL) | 104 | 90 | 81 | 48 | 34 | 34 | 34 | 47 | 53 | 53 | 53 | 53 | 72 | 72 | 72 | 72 | 90 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1857600
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 10 | 10 |  |  |  |  | 0 | 22080
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 25 |  | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 933984
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 1224706
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 7 | 7 |  | 7 | 7 | 7 |  |  |  | 0 | 37440
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 |  |  |  | 25 | 37 | 50 | 50 | 29 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 37 | 37 | 921600
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 23 | 51 |  | 51 | 51 | 51 |  |  |  | 0 | 191040
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 8 | 22 | 30 | 30 | 30 | 30 | 44 |  | 46 | 46 | 46 | 46 | 46 |  |  | 409843
100 | Manikganj 55 MW PP (Northern) | 17 | [5 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1014917
101 | Kushiara 163 MW CCPP (KP) | 110 | 130 | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 110 | 140 | 140 | 163 | 110 |  | 140 | 140 | 140 | 140 | 140 | 110 | 163 | 3419263
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 10350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1050120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 7 | 24 |  | 24 | 24 | 24 | 24 | 8 | 8 | 0 | 151200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 5 | 75 | 105 | 104 | 78 | 71 | 70 | 36 | 34 | 34 | 50 | 100 |  | 100 | 100 | 100 | 100 | 70 | 28 | 0 | 1186560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 |  |  |  |  | 46 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1939200
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 50 | 50 | 50 | 50 | 34 | 17 | 17 | [7 empty] | 20 | 56 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1025280
117 | Ashuganj 150MW PP (Midland) | [6 empty] | 38 | 50 | 50 | 50 | 67 | 118 | 120 | 137 | 137 | 137 | 142 | 142 |  | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 2117672
118 | Bibiyana-III 400 MW CCPP | 250 | 270 | 251 | 290 | 290 |  |  | 130 | 170 | 220 | 220 | 219 | 220 | 220 | 200 | 220 | 220 | 260 |  | 270 | 270 | 270 | 270 | 250 | 251 | 251 | 5221000
| Jamalpur 115 MW PP (United) | 24 | 24 | 24 | 24 | 24 | 83 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2371200
| Anwara 300 MW PP (United) | 162 | 53 | 16 |  |  | 133 | 210 | 210 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 248 | 254 |  | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 4453636
| Juldah unit-2 (Acorn) | [5 empty] | 20 | 90 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1190400
| Anlima Energy Ltd. | [9 empty] | 8 | 18 | 20 | 20 |  | 20 | 17 | 15 | 10 | [7 empty] | 0 | 124200
120 | Eastern Zone Total | 4353 | 4143 | 3967 | 3934 | 3875 | 3938 | 4247 | 4584 | 4700 | 4749 | 4780 | 4972 | 5059 | 4846 | 4800 | 4804 | 5133 | 5839 |  | 6073 | 6070 | 6044 | 5897 | 5619 | 5227 | 5155 | 117652697
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 29 | 49 |  | 49 | 49 | 49 | 49 |  |  | 0 | 224640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 35 | 17 |  |  | 31 | 35 | 35 | 35 | 35 | 53 | 53 | 70 | 70 | 70 | 70 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 1351680
130
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 38 | 38 | 36 | 36 | 36 | 37 | 37 | 36 | 36 | 36 | 36 | 19 | 12 | 14 | 37 | 35 | 20 | 34 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 810440
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 16 | 32 | 32 | 32 | 32 | 32 | 64 |  | 64 | 64 | 64 | 64 | 32 | 32 | 16 | 547584
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251427
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 20 | 20 | 16 | 14 | 12 | 17 | 18 | 19 | 20 | 21 | 20 | 17 | 17 | 17 | 25 |  | 26 | 26 | 26 | 26 | 26 | 25 | 24 | 483700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [6 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | [10 empty] | 0 | 329625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 422 | 420 | 420 | 326 | 326 | 338 | 420 | 516 | 516 | 562 | 563 | 564 | 564 | 564 | 564 | 564 | 564 | 800 |  | 801 | 801 | 801 | 801 | 801 | 612 | 422 | 13281456
147 | Bheramara 410 MW CCPP | 220 | 230 | 240 | 240 | 250 | 255 | 265 | 275 | 260 | 250 | 230 | 225 | 205 | 200 | 180 | 165 | 135 | 130 |  | 120 | 100 | 85 | 65 | 65 | 90 | 125 | 4769280
148 | Payra 1320 MW | 510 | 490 | 460 | 460 | 440 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 390 | 400 | 420 | 440 |  | 540 | 550 | 550 | 550 | 520 | 520 | 420 | 11851300
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 78 | 77 | 78 | 77 | 77 | 77 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 75 | 76 | 74 | 77 | 77 | 77 | 76 | 1826618
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 5 | 8 |  | 8 | [6 empty] | 19226
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 147 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 200 | 180 | 180 | 170 | 160 | 161 | 130 | 129 | 126 | 127 |  | 129 | 129 | 127 | 94 |  |  | 0 | 3221464
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [13 empty] | 0 | 6 | 28 | 35 | 35 |  | 35 | 35 | 39 | 72 | 111 | 126 | 129 | 708745
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 332 | 337 | 307 | 336 | 321 | 383 | 246 | 325 | 388 | 351 | 350 | 356 | 337 | 275 | 295 | 310 | 201 | 390 |  | 380 | 367 | 366 | 357 | 316 | 316 | 301 | 8132000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 516000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 165438
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 |  |  |  |  | 0 | 23040
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 8 | 8 | 15 | 52 | 51 | 52 | 52 | 52 | 60 | 85 |  | 77 | 77 | 79 | 77 | 77 | 43 | 0 | 806992
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 3 | 88 | 110 | 111 | 111 | 35 | 47 | 70 | 70 | 70 | 70 | 73 | 110 |  | 111 | 93 | 105 | 100 | 93 | 95 | 111 | 1649760
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 20 | 35 |  | 60 | 70 | 70 | 70 |  |  | 0 | 292800
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 50 | 50 | 50 | 51 | 51 | 51 | 49 | 49 | 49 | 50 | 83 | 113 |  | 113 | 113 | 75 | 34 |  |  | 0 | 927360
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 2 | 4 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 29500
178
178