## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-28 | Monday
|  |  | Date (day): | 2020-12-28 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12322.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13586 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-27 | 2020-12-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 92 | 73 | 94 | 94 |  | 76 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 11 | 12 | 12 | 12 | 98 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 354 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 285 | 340 | 340 | 20 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 40 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 82 | 92 | 85 | 92 |  | 8 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 36 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 51 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 79 | 281 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 101 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 100 | 160
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1943 | 2546 | 3434 | 3791 | 1414 | 785
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 49 | 49 | 181 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 164 | 163 | 160 | 160 | 65 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 17 | 15 | 15
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 57 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 161 | 251 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 36 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 611 | 889 | 1409 | 1384 | 756 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 140 | 100 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 130 | 120 | 130 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 330 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 53 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 143 | 142 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 81 | 50 | 50 | 50 | 113 |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 120 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 102 | 110 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 35 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 22 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1130 | 1234 | 1609 | 1917 | 453 | 594
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 86 | 90 | 120 | 120 | 82 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 9 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 70 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 273 | 385 | 601.6 | 572 | 82 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 20 | 30 | 30
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 32 | 32 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 149 | 150 | 155 | 155 | 175 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 2 | 53 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 2 | 43 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 32 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 72 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 122 | 182 | 200 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 285 | 320 | 320
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 421 | 0 | 300 | 300
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1147 | 897 | 1559 | 1559 | 175 | 442
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 570 | 805 | 580 | 821
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 180 | 270 | 270 | 140 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 910 | 1115 | 1300 | 1777 | 140 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 21 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 10 | 10 | 10 | 85 |  | Gas shortage
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 300 | 500 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 15 | 35 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 53 | 55 | 55 | 55
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 392 | 701 | 835 | 895 | 85 | 202
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 150 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 400 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 35 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 62 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 15 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 718 | 900 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 88 | 88
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 40 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 107 | 176 | 209 | 201 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7231 | 8843 | 12322.6 | 13586 | 3706 | 2611
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6855.6716 | 8384 | 11682.9898 | 12880.8124
| A. |  | 2020-12-27 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 8843 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5545 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8843 | MW
| 3 | Day peak Generation : |  |  | 7231 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8384 | MW
| 4 | Evening peak Generation : |  |  | 8843 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 169.683 | MKWHr | By Solar | 0.41582 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 105.4874 | MKWHr |  | By Oil: | 34.6399 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.5262 | MKWHr |  | By Hydro: | 1.1035 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3706 | MW | Dhaka | 3033 | 3033 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2611 | MW | Chittagong | 858 | 858 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6317 | MW | Khulna | 1079 | 1079 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 807.73 | MMCFD |  |  | Rajshahi | 861 | 861 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 114085973.068 | ii) Oil : | Taka | 266425339.87 | Comilla | 719 | 719 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 57442582.54 | Total | Taka | 437953895.478 | Mymensingh | 696 | 696 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.3245 | MKWHr. | Sylhet | 301 | 301 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -58 | MW (E to W) at | 19:00 | hrs | Barisal | 240 | 240 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -103 | MW at | 24:00 | hrs | Rangpur | 597 | 597 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.0° C |  |  | Total | 8384 | 8384 |  | 0
| B. |  | 2020-12-28 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 24.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13586 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7400 | MW
| 4 | Reserve(Generation end) |  |  |  | 4586 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 172.6956 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5588 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.5527 | MKWHr. | ii) HVDC Flow at Peak Time |  | 805 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9574 | MKWHr. | iii) Maximum HVDC Flow : |  | 806 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.46 |  | (b) Today: | 98.38 |  | (c) Rule Curve: |  | 103.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 95 | 0 | 0 | 330 | 12 | 0 | 438 | 323 |  | 0 | 225 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 80 | 80 | 0 | 0 | 290 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 76 | 110 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 153 | 34 | 75 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 65 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 0 | 0 | 330 | 104 | 0 | 0 | 0 | 0 |  | 428 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 36 | 0 | 0 |  | 4438 | 1821 | 6259 | 3010 | 428 | 1548 | 579 | 573 | 45 | 0 | 76 | 0 | 0 | 98.47
2:00 | 0 | 95 | 0 | 0 | 330 | 12 | 0 | 435 | 327 |  | 0 | 225 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 80 | 80 | 0 | 0 | 290 | 0 | 8 | 52 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 74 | 110 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 153 | 34 | 75 | 0 | 128 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 0 | 33 | 41 | 0 | 0 | 0 | 0 | 330 | 40 | 0 | 0 | 0 | 0 |  | 427 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 4151 | 1787 | 5938 | 2982 | 427 | 1588 | 311 | 512 | 44 | 0 | 74 | 0 | 0 | 98.47
3:00 | 0 | 94 | 0 | 0 | 330 | 12 | 0 | 434 | 355 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 80 | 80 | 0 | 0 | 290 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 74 | 108 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 154 | 34 | 75 | 0 | 128 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 16 | 36 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 |  | 428 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 0 |  | 3955 | 1744 | 5699 | 2978 | 428 | 1616 | 97 | 463 | 43 | 0 | 74 | 0 | 0 | 98.47
4:00 | 0 | 94 | 0 | 0 | 330 | 12 | 0 | 437 | 354 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 80 | 80 | 0 | 0 | 290 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 72 | 108 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 152 | 34 | 76 | 0 | 129 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 16 | 36 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 |  | 334 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 0 |  | 3949 | 1645 | 5594 | 2998 | 334 | 1586 | 97 | 463 | 44 | 0 | 72 | 0 | 0 | 98.46
5:00 | 0 | 94 | 0 | 0 | 330 | 12 | 0 | 384 | 352 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 80 | 0 | 0 | 295 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 72 | 108 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 153 | 34 | 77 | 0 | 128 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 34 | 36 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 |  | 334 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 37 | 0 | 0 |  | 3896 | 1649 | 5545 | 2959 | 334 | 1570 | 103 | 462 | 45 | 0 | 72 | 0 | 0 | 98.46
6:00 | 0 | 94 | 0 | 0 | 330 | 12 | 0 | 399 | 353 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 80 | 0 | 0 | 300 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 70 | 108 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 150 | 34 | 77 | 0 | 128 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 19 | 0 | 0 | 0 | 102 | 38 | 0 | 0 | 0 | 0 | 330 | 16 | 0 | 0 | 0 | 0 |  | 333 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 36 | 0 | 0 |  | 4037 | 1687 | 5724 | 2976 | 333 | 1600 | 227 | 472 | 46 | 0 | 70 | 0 | 0 | 98.46
7:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 441 | 284 |  | 0 | 225 | 0 | 19 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 80 | 0 | 0 | 300 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 68 | 109 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 150 | 33 | 77 | 0 | 128 | 0 | 0 | 0 | 265 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 52 | 11 | 0 | 55 | 0 | 0 | 0 | 120 | 54 | 0 | 0 | 0 | 0 | 330 | 53 | 1 | 0 | 0 | 0 |  | 427 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 | 0 |  | 4152 | 1885 | 6037 | 3013 | 427 | 1535 | 433 | 512 | 47 | 0 | 68 | 2 | 0 | 98.45
8:00 | 0 | 93 | 0 | 0 | 300 | 12 | 0 | 436 | 284 |  | 0 | 225 | 0 | 24 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 72 | 111 | 0 | 20 | 0 | 30 | 32 | 8 | 5 | 0 | 150 | 33 | 77 | 0 | 128 | 0 | 0 | 0 | 255 | 0 | 11 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 7 | 80 | 64 | 40 | 0 | 85 | 0 | 0 | 1 | 175 | 54 | 0 | 0 | 0 | 20 | 330 | 87 | 9 | 0 | 0 | 0 |  | 522 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 433 | 70 | 0 | 28 | 0 | 0 | 0 | 1 | 0 | 450 | 13 | 0 | 0 |  | 4511 | 2060 | 6571 | 3093 | 522 | 1487 | 819 | 513 | 47 | 0 | 72 | 18 | 0 | 98.45
9:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 435 | 315 |  | 0 | 225 | 0 | 44 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 10 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 47 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 68 | 109 | 4 | 20 | 1 | 30 | 32 | 8 | 5 | 0 | 151 | 33 | 77 | 0 | 128 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 12 | 100 | 68 | 107 | 0 | 115 | 0 | 0 | 1 | 212 | 54 | 0 | 0 | 0 | 50 | 330 | 104 | 23 | 0 | 0 | 0 |  | 523 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 340 | 90 | 0 | 89 | 0 | 5 | 0 | 2 | 0 | 470 | 15 | 0 | 0 |  | 4887 | 2062 | 6949 | 3074 | 523 | 1435 | 1232 | 533 | 45 | 0 | 68 | 39 | 0 | 98.45
10:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 403 | 280 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 46 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 72 | 89 | 8 | 20 | 1 | 20 | 32 | 8 | 5 | 0 | 152 | 20 | 71 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 68 | 125 | 0 | 115 | 0 | 0 | 3 | 197 | 54 | 0 | 0 | 0 | 20 | 330 | 104 | 33 | 0 | 22 | 0 |  | 570 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 345 | 90 | 0 | 110 | 0 | 39 | 0 | 4 | 0 | 430 | 34 | 0 | 0 |  | 4816 | 2150 | 6966 | 2999 | 570 | 1418 | 1309 | 493 | 47 | 0 | 72 | 58 | 0 | 98.44
11:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 370 | 280 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 26 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 46 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 74 | 90 | 8 | 20 | 2 | 20 | 32 | 8 | 5 | 0 | 150 | 20 | 73 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 69 | 0 | 0 | 0 | 0 | 15 | 18 | 100 | 68 | 135 | 0 | 115 | 0 | 0 | 4 | 180 | 54 | 0 | 0 | 0 | 20 | 407 | 104 | 40 | 0 | 41 | 0 |  | 570 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 313 | 90 | 0 | 111 | 0 | 36 | 0 | 4 | 0 | 390 | 32 | 0 | 18 |  | 4956 | 2085 | 7041 | 3028 | 570 | 1386 | 1415 | 453 | 47 | 0 | 74 | 68 | 0 | 98.44
12:00 | 0 | 92 | 0 | 0 | 300 | 11 | 0 | 362 | 300 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 0 | 7 | 0 | 82 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 26 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 81 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 78 | 86 | 9 | 20 | 2 | 20 | 32 | 2 | 2 | 0 | 149 | 32 | 72 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 30 | 18 | 100 | 68 | 143 | 0 | 115 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 0 | 20 | 421 | 104 | 41 | 0 | 36 | 0 |  | 570 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 419 | 90 | 0 | 111 | 0 | 40 | 0 | 4 | 15 | 300 | 15 | 0 | 53 |  | 5104 | 2127 | 7231 | 3049 | 570 | 1508 | 1548 | 363 | 46 | 0 | 78 | 69 | 0 | 98.44
13:00 | 0 | 93 | 0 | 0 | 300 | 12 | 0 | 412 | 295 |  | 0 | 225 | 0 | 50 | 15 | 55 | 0 | 0 | 0 | 20 | 16 | 16 | 86 | 0 | 0 | 0 | 54 | 55 | 25 | 19 | 25 | 16 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 125 | 100 | 0 | 0 | 300 | 0 | 8 | 46 | 26 | 54 | 0 | 51 | 0 | 0 | 9 | 21 | 11 | 33 | 16 | 80 | 80 | 51 | 20 | 2 | 20 | 32 | 2 | 2 | 0 | 150 | 32 | 72 | 0 | 122 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 60 | 17 | 100 | 85 | 143 | 0 | 115 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 0 | 40 | 414 | 104 | 42 | 0 | 35 | 0 |  | 569 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 385 | 90 | 0 | 111 | 0 | 41 | 0 | 4 | 35 | 320 | 14 | 0 | 55 |  | 5276 | 2126 | 7402 | 3017 | 569 | 1466 | 1756 | 383 | 46 | 16 | 80 | 69 | 7402 | 98.43
14:00 | 0 | 93 | 0 | 0 | 300 | 12 | 0 | 386 | 295 |  | 0 | 225 | 0 | 50 | 15 | 30 | 0 | 0 | 0 | 7 | 7 | 0 | 87 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 18 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 100 | 100 | 0 | 0 | 300 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 16 | 76 | 77 | 64 | 20 | 1 | 20 | 32 | 2 | 2 | 0 | 156 | 31 | 72 | 0 | 122 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 32 | 15 | 100 | 85 | 143 | 0 | 115 | 0 | 0 | 3 | 160 | 54 | 0 | 0 | 0 | 20 | 412 | 104 | 25 | 0 | 32 | 0 |  | 570 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 365 | 90 | 0 | 70 | 0 | 41 | 0 | 3 | 0 | 350 | 35 | 0 | 55 |  | 5094 | 2062 | 7156 | 2946 | 570 | 1450 | 1608 | 413 | 46 | 0 | 76 | 47 | 0 | 98.43
15:00 | 0 | 73 | 0 | 0 | 300 | 12 | 0 | 347 | 295 |  | 0 | 225 | 0 | 35 | 8 | 30 | 0 | 0 | 0 | 0 | 7 | 0 | 64 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 100 | 0 | 0 | 300 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 22 | 74 | 77 | 32 | 20 | 1 | 20 | 32 | 2 | 2 | 0 | 152 | 31 | 73 | 0 | 122 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 0 | 100 | 89 | 80 | 0 | 95 | 0 | 0 | 2 | 142 | 54 | 0 | 0 | 0 | 20 | 412 | 104 | 20 | 0 | 27 | 0 |  | 569 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 420 | 70 | 0 | 70 | 0 | 41 | 0 | 2 | 0 | 360 | 35 | 0 | 55 |  | 4784 | 2081 | 6865 | 2867 | 569 | 1511 | 1350 | 424 | 45 | 0 | 74 | 25 | 0 | 98.43
16:00 | 0 | 75 | 0 | 0 | 300 | 12 | 0 | 332 | 250 |  | 0 | 225 | 0 | 24 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 0 | 82 | 0 | 0 | 0 | 54 | 55 | 0 | 16 | 25 | 22 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 100 | 100 | 0 | 0 | 280 | 0 | 8 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 22 | 76 | 84 | 32 | 20 | 0 | 20 | 32 | 2 | 2 | 0 | 152 | 30 | 73 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 6 | 80 | 101 | 80 | 0 | 95 | 0 | 0 | 1 | 142 | 0 | 0 | 0 | 0 | 20 | 412 | 104 | 6 | 0 | 35 | 0 |  | 569 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 404 | 53 | 0 | 70 | 0 | 42 | 0 | 1 | 0 | 320 | 13 | 0 | 55 |  | 4675 | 1990 | 6665 | 2841 | 569 | 1449 | 1287 | 384 | 45 | 0 | 76 | 14 | 0 | 98.42
17:00 | 0 | 74 | 0 | 0 | 300 | 12 | 0 | 379 | 270 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 8 | 32 | 50 | 94 | 0 | 0 | 0 | 54 | 55 | 8 | 19 | 25 | 22 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 100 | 130 | 0 | 0 | 305 | 0 | 8 | 51 | 26 | 51 | 0 | 51 | 0 | 0 | 14 | 20 | 11 | 33 | 22 | 76 | 82 | 42 | 20 | 0 | 20 | 32 | 46 | 8 | 0 | 152 | 33 | 72 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 104 | 0 | 0 | 5 | 0 | 15 | 0 | 100 | 101 | 102 | 0 | 115 | 0 | 0 | 0 | 212 | 14 | 0 | 0 | 36 | 100 | 0 | 104 | 1 | 0 | 10 | 0 |  | 569 | 0 | 180 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 2 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 146 | 0 | 270 | 53 | 0 | 87 | 0 | 105 | 0 | 0 | 0 | 380 | 16 | 0 | 55 |  | 4909 | 2049 | 6958 | 2567 | 569 | 1388 | 1800 | 443 | 46 | 68 | 76 | 1 | 0 | 98.42
18:00 | 0 | 74 | 0 | 0 | 300 | 12 | 0 | 355 | 285 |  | 0 | 225 | 0 | 100 | 5 | 30 | 0 | 0 | 0 | 70 | 32 | 120 | 94 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 14 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 15 | 50 | 0 | 22 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 28 | 20 | 11 | 33 | 22 | 106 | 92 | 84 | 20 | 0 | 20 | 32 | 53 | 42 | 0 | 150 | 33 | 72 | 0 | 182 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 204 | 0 | 0 | 53 | 0 | 23 | 0 | 100 | 108 | 142 | 0 | 115 | 0 | 0 | 0 | 251 | 47 | 0 | 34 | 36 | 100 | 0 | 104 | 0 | 35 | 0 | 0 |  | 805 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 152 | 0 | 395 | 70 | 0 | 111 | 0 | 113 | 0 | 0 | 70 | 430 | 38 | 0 | 55 |  | 5681 | 2757 | 8438 | 2597 | 805 | 1589 | 2569 | 493 | 46 | 233 | 106 | 0 | 0 | 98.42
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 73 | 0 | 0 | 300 | 12 | 0 | 354 | 285 |  | 0 | 225 | 0 | 100 | 40 | 30 | 0 | 0 | 0 | 100 | 7 | 150 | 92 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 26 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 57 | 50 | 0 | 17 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 35 | 21 | 11 | 33 | 22 | 102 | 90 | 90 | 20 | 0 | 20 | 32 | 53 | 43 | 0 | 150 | 33 | 72 | 0 | 182 | 0 | 0 | 0 | 285 | 16 | 11 | 0 | 281 | 0 | 0 | 70 | 0 | 101 | 0 | 100 | 120 | 142 | 0 | 115 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 100 | 0 | 104 | 0 | 35 | 0 | 0 |  | 805 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 35 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 150 | 0 | 400 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 500 | 35 | 0 | 55 |  | 5951 | 2892 | 8843 | 2620 | 805 | 1592 | 2852 | 563 | 46 | 263 | 102 | 0 | 0 | 98.41
19:30 | 0 | 74 | 0 | 0 | 300 | 12 | 0 | 365 | 285 |  | 0 | 225 | 0 | 100 | 48 | 30 | 0 | 0 | 0 | 50 | 0 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 0 | 33 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 22 | 104 | 90 | 90 | 20 | 0 | 20 | 32 | 53 | 46 | 0 | 152 | 33 | 72 | 0 | 182 | 19 | 0 | 0 | 310 | 16 | 11 | 0 | 300 | 0 | 0 | 70 | 0 | 100 | 0 | 100 | 120 | 142 | 0 | 115 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 100 | 0 | 104 | 0 | 0 | 0 | 0 |  | 805 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 35 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 150 | 0 | 417 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 500 | 36 | 0 | 55 |  | 5900 | 2864 | 8764 | 2653 | 805 | 1655 | 2690 | 563 | 48 | 246 | 104 | 0 | 0 | 0
20:00 | 0 | 74 | 0 | 0 | 300 | 12 | 0 | 361 | 285 |  | 0 | 225 | 0 | 100 | 48 | 30 | 0 | 0 | 0 | 50 | 0 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 0 | 33 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 22 | 104 | 90 | 90 | 20 | 0 | 20 | 32 | 53 | 46 | 0 | 150 | 33 | 73 | 0 | 182 | 19 | 0 | 0 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 70 | 0 | 105 | 0 | 100 | 120 | 143 | 0 | 115 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 100 | 0 | 104 | 0 | 0 | 0 | 0 |  | 805 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 44 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 150 | 0 | 405 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 500 | 35 | 0 | 55 |  | 5862 | 2861 | 8723 | 2646 | 805 | 1624 | 2687 | 563 | 48 | 246 | 104 | 0 | 0 | 98.41
21:00 | 0 | 74 | 0 | 0 | 300 | 12 | 0 | 380 | 263 |  | 0 | 225 | 0 | 100 | 30 | 30 | 0 | 0 | 0 | 15 | 0 | 140 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 32 | 0 | 35 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 100 | 91 | 90 | 20 | 0 | 20 | 32 | 53 | 46 | 0 | 150 | 33 | 73 | 0 | 182 | 19 | 0 | 0 | 295 | 16 | 11 | 0 | 250 | 0 | 0 | 60 | 0 | 97 | 0 | 100 | 120 | 148 | 0 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 100 | 0 | 104 | 0 | 0 | 0 | 0 |  | 806 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 150 | 0 | 412 | 90 | 0 | 111 | 0 | 35 | 0 | 0 | 113 | 500 | 34 | 0 | 55 |  | 5684 | 2708 | 8392 | 2666 | 806 | 1614 | 2359 | 563 | 48 | 236 | 100 | 0 | 0 | 98.41
22:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 376 | 253 |  | 0 | 225 | 0 | 100 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 38 | 100 | 110 | 0 | 0 | 330 | 0 | 8 | 45 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 92 | 91 | 90 | 20 | 0 | 20 | 32 | 53 | 46 | 0 | 150 | 34 | 73 | 0 | 182 | 19 | 0 | 0 | 300 | 16 | 11 | 0 | 145 | 0 | 0 | 16 | 0 | 56 | 0 | 100 | 120 | 142 | 0 | 115 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 70 | 0 | 104 | 0 | 0 | 0 | 0 |  | 806 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 353 | 90 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 | 55 |  | 5335 | 2471 | 7806 | 2645 | 806 | 1553 | 1939 | 563 | 48 | 160 | 92 | 0 | 0 | 98.4
23:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 314 | 285 |  | 0 | 225 | 0 | 100 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 100 | 110 | 0 | 0 | 320 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 88 | 90 | 66 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 152 | 34 | 73 | 0 | 182 | 19 | 0 | 0 | 250 | 15 | 11 | 0 | 145 | 0 | 0 | 0 | 0 | 46 | 0 | 100 | 120 | 142 | 0 | 115 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 |  | 616 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 284 | 70 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 500 | 39 | 0 | 55 |  | 5162 | 2154 | 7316 | 2574 | 616 | 1470 | 1833 | 563 | 48 | 124 | 88 | 0 | 0 | 98.4
24:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 345 | 294 |  | 0 | 225 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 100 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 33 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 74 | 91 | 24 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 153 | 33 | 73 | 0 | 183 | 19 | 0 | 0 | 270 | 15 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 27 | 0 | 100 | 120 | 142 | 0 | 109 | 0 | 0 | 0 | 252 | 54 | 0 | 0 | 0 | 10 | 0 | 70 | 0 | 0 | 0 | 0 |  | 428 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 360 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 450 | 37 | 0 | 55 |  | 4873 | 1891 | 6764 | 2588 | 428 | 1565 | 1534 | 512 | 47 | 16 | 74 | 0 | 0 | 98.4
KWH | 0 | 2271200 | 0 | 0 | 7393436 | 290636 | 0 | 9463960 | 7114000 |  | 0 | 4747000 | 0 | 1324800 | 251784 | 647480 | 0 | 0 | 0 | 331709 | 116352 | 833280 | 1256961 | 0 | 0 | 0 | 1059120 | 942973 | 260716 | 420372 | 600000 | 646920 | 411800 | 811300 | 0 | 0 | 1103476 | 0 | 0 | 0 | 0 | 3851464 | 0 | 0 | 0 |  | 0 | 0 | 176296 | 0 | 79680 | 433440 | 0 | 537600 | 2580246 | 2444065 | 0 | 0 | 7432000 | 0 | 200727 | 1160190 | 594144 | 1286400 | 0 | 1223698 | 0 | 0 | 171310 | 489132 | 251820 | 820800 | 491120 | 1957440 | 2242360 | 832320 | 441864 | 10150 | 570000 | 755760 | 480600 | 455976 | 0 | 3511000 | 766080 | 1768320 | 0 | 3470690 | 77000 | 0 | 0 | 7048000 | 96480 | 203032 | 0 | 2248145 | 0 | 0 | 309600 | 0 | 655200 | 120285 | 1699200 | 1907040 | 2194618 | 0 | 2173200 | 0 | 0 | 24960 | 3856473 | 1177753 | 0 | 33060 | 479640 | 894720 | 5747900 | 2009280 | 234610 | 112320 | 242127 | 0 |  | 13552727 | 0 | 5503104 | 0 | 58560 | 0 | 0 | 0 | 0 | 0 | 78000 | 0 | 434700 | 333888 | 0 | 0 | 0 | 0 | 0 | 357584 | 0 | 0 | 0 | 101760 | 0 | 511440 | 0 | 217044 | 1495418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246761 | 0 | 3735618 | 0 | 8918145 | 1367520 | 0 | 1664928 | 0 | 796800 | 0 | 25817 | 480288 | 11030800 | 751474 | 0 | 690000 |  | 117330610 | 52352376 | 169682986 | 69471901 | 13552727 | 36015477 | 33272765 | 12526218 | 1103476 | 1367160 | 1957440 | 415822 | 0
Fuel Cost | 0 | 3361376 | 0 | 0 | 8206713.96 | 383639.52 | 0 | 9558599.6 | 7327420 |  | 0 | 5174230 | 0 | 10055232 | 1734791.76 | 5477680.8 | 0 | 0 | 0 | 2497768.77 | 1061130.24 | 8199475.2 | 11589180.42 | 0 | 0 | 0 | 7731576 | 7289181.29 | 2570659.76 | 315279 | 450000 | 0 | 0 | 0 | 0 | 0 | 297938.52 | 0 | 0 | 0 | 0 | 4198095.76 | 0 | 0 | 0 |  | 0 | 0 | 1710071.2 | 0 | 693216 | 3432844.8 | 0 | 1596672 | 3818764.08 | 3617216.2 | 0 | 0 | 7432000 | 0 | 258937.83 | 1334218.5 | 671382.72 | 1800960 | 0 | 2092523.58 | 0 | 0 | 1636010.5 | 621197.64 | 188865 | 1436400 | 368340 | 14680800 | 2376901.6 | 7557465.6 | 561167.28 | 161791 | 934800 | 1209216 | 855468 | 711322.56 | 0 | 3651440 | 1509177.6 | 3377491.2 | 0 | 6004293.7 | 168630 | 0 | 0 | 7118480 | 72360 | 154304.32 | 0 | 16995976.2 | 0 | 0 | 1609920 | 0 | 6447168 | 1406131.65 | 13848480 | 20691384 | 15472056.9 | 0 | 19819584 | 0 | 0 | 0 | 29154935.88 | 10258228.63 | 0 | 329938.8 | 4110514.8 | 5958835.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 78063707.52 | 0 | 5778259.2 | 0 | 460281.6 | 0 | 0 | 0 | 0 | 0 | 812760 | 0 | 673785 | 3258746.88 | 0 | 0 | 0 | 0 | 0 | 3164618.4 | 0 | 0 | 0 | 986054.4 | 0 | 981964.8 | 0 | 164302.308 | 9017370.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370141.5 | 0 | 4370673.06 | 0 | 8828963.55 | 14276908.8 | 0 | 15800166.72 | 0 | 6183168 | 0 | 285277.85 | 3549328.32 | 48425212 | 0 | 0 | 0 |  | 327397851.57 | 205451690.448 | 532849542.018 | 72533973.528 | 78063707.52 | 41551999.54 | 253351175.07 | 57442582.54 | 297938.52 | 13074164.8 | 14680800 | 1853200.5 | 0
Yesterday Day Peak | 0 | 92 | 0 | 0 | 300 | 11 | 0 | 362 | 300 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 0 | 7 | 0 | 82 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 26 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 140 | 100 | 0 | 0 | 300 | 0 | 8 | 81 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 78 | 86 | 9 | 20 | 2 | 20 | 32 | 2 | 2 | 0 | 149 | 32 | 72 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 30 | 18 | 100 | 68 | 143 | 0 | 115 | 0 | 0 | 4 | 161 | 54 | 0 | 0 | 0 | 20 | 421 | 104 | 41 | 0 | 36 | 0 |  | 570 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 419 | 90 | 0 | 111 | 0 | 40 | 0 | 4 | 15 | 300 | 15 | 0 | 53 |  | 7231 | DayPeak
Yesterday Evening Peak | 0 | 73 | 0 | 0 | 300 | 12 | 0 | 354 | 285 | 0 | 0 | 225 | 0 | 100 | 40 | 30 | 0 | 0 | 0 | 100 | 7 | 150 | 92 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 26 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 57 | 50 | 0 | 17 | 100 | 130 | 0 | 0 | 330 | 0 | 8 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 35 | 21 | 11 | 33 | 22 | 102 | 90 | 90 | 20 | 0 | 20 | 32 | 53 | 43 | 0 | 150 | 33 | 72 | 0 | 182 | 0 | 0 | 0 | 285 | 16 | 11 | 0 | 281 | 0 | 0 | 70 | 0 | 101 | 0 | 100 | 120 | 142 | 0 | 115 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 100 | 0 | 104 | 0 | 35 | 0 | 0 |  | 805 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 35 | 0 | 22 | 0 | 11 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 150 | 0 | 400 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 500 | 35 | 0 | 55 |  | 8843 | EvPeak
Forecast for Evening | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 412 | 340 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 92 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 49 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 102 | 50 | 19 | 15 | 135 | 130 | 0 | 0 | 360 | 0 | 8 | 50 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 22 | 148 | 120 | 95 | 20 | 0 | 30 | 30 | 51 | 44 | 163 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 104 | 0 | 160 |  | 100 |  | 821 | 16 | 270 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35 |  | 55
Forecast for Day | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 412 | 340 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 49 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 19 | 15 | 135 | 120 | 0 | 0 | 360 | 0 | 8 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 20 | 110 | 120 | 95 | 20 | 1.6 | 30 | 30 | 51 | 44 | 163 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 104 | 50 | 100 |  | 100 |  | 580 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35 |  | 55
Generation at 08:00(Today) | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 330 | 322 | 0 | 0 | 225 | 0 | 29 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 33 | 17 |  | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 12 | 120 | 120 | 0 | 0 | 350 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 1 | 21 | 11 | 33 | 20 | 60 | 108 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 148 | 33 | 74 | 0 | 150 | 19 | 0 | 0 | 300 | 13 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 86 | 0 | 48 | 0 | 0 | 1 | 161 | 35 | 0 | 0 | 0 | 10 | 0 | 104 | 8 | 0 | 0 | 0 | 0 | 523 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 418 | 90 | 0 | 54 | 0 | 0 | 0 | 1 | 0 | 400 | 18 | 0 | 55 | 0
199
| Minimum Generation |  | 5545 | 5:00
| Highest Generation |  | 8843 | 19:00
| Day Peak Generation |  | 7231 | 12:00
| Evening Peak Generation |  | 8843 | 19:00
| HVDC Max Flow |  | 806 | 21:00
| HVDC EvPeak Flow |  | 805 | 19:00
| Load factor L.F |  | 79.95%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-28
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7231 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5588 | MW
Evening Peak Generation : |  | 8843 | MW Hour : | 19:00 | Available Max Generation : |  | 13586 | MW
E.P. Demand (at gen end) : |  | 8843 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8843 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4586 | MW
Total Gen. (MKWH) : |  | 169.683 | System Load Factor : | 79.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -103 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-28
Actual : | 98.38 | Ft.(MSL) , | Rule curve : | 103.4 | Ft.( MSL )
Gas Consumed : | Total = | 807.73 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 114085973.068
: |  | Coal : | 57442582.54 | Oil : | 266425339.87 | Total : | 437953895.478
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3187.8869 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1078.5476 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 965.361 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 871.9364 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 788.1486 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 635.9941 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 362.7077 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 163.939 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 490.4763 |  |  | 0 | 0%
Total | 0 |  | 8544.9976 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Ashuganj(N)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Barishal(N)-Madaripur 132 kV Ckt-1 was under shut down from 08:26 to 17:56 for A/M.
b) Noapara-Jashore 132 kV Ckt-2 was under shut down from 08:37 to 14:43 for A/M.
c) Hathazari-AKSM 230 kV Ckt was under shut down from 08:51 to 16:57 for A/M.
d) Halishahar-Khulshi 132 kV Ckt-3 was under shut down from 08:30 to 17:35 for A/M.
e) Ashuganj-Sirajganj 230 kV Ckt-2 was shut down from 08:57 to 17:10 for A/M.
f) Siddhirganj 230/132 kV T-2 transformer was under shut down from 09:03 to 17:12 for A/M.
g) Rampura-Moghbazar 132 kV Ckt-2 was under shut down from 08:31 to 16:49 for A/M.
h) Mymensingh 132/33 kV T-3 transformer was under shut down from 09:25 to 20:01 for A/M.
i) Hasnabad-APR 230 kV Ckt-2 was under shut down from 08:29 to 12:49 for A/M.
j) Chandpur 132/33 kV T-1 transformer was under shut down at 08:30 for A/M.
k) Polashbari-Mohasthangarh 132 kV Ckt-2 was under shut down from 08:37 to 17:42 for A/M.
l) Shahjadpur-Baghabari 132 kV Ckt-1 was under shut down from 08:10 to 16:52 for A/M.
m) Rajshahi-Amnura 132 kV Ckt-2 was under shut down from 08:37 to 17:42 for A/M.
n) Ruppur 132/33 kV T-1 transformer was under shut down at 08:26 for A/M.
o) Barapukuria S/S-Barapukuria P/S 230 kV Ckt-1 was under shut down from 09:50 to 15:52 for A/M.
p) Aminbazar 230/132 kV T-2 transformer was under shut down from 09:39 to 17:08 for A/M.
q) Ishurdi-Bheramara 132 kV Ckt-1 was shut down at 11:22 to 13:37 due to flashing at middle phase
LA at Ishurdi end.
r) Savar 132/33 kV T-3 transformer was under shut down from 09:46 to 16:09 for A/M.
s) Shyampur-APR 230 kV Ckt was under shut down from 12:44 to 17:36 for A/M.
t) Patuakhali-Payra 132 kV Ckt-1 was under shut down from 11:51 to 20:48 for A/M.
u) Fatullah-Shyampur 132 kV Ckt-1 was under shut down from 13:14 to 13:40 for A/M.
v) Siddhirganj S/S-Siddhirganj S/S 132 kV Ckt-1 was under shut down from 11:50 to 15:10 for A/M.
w) Bhola 230/33 kV transformer was under shut down from 12:30 to 14:12 for A/M. |  |  |  |  | About 10 MW power interruption occurred under Bhola S/S area
from 12:30 to 14:12.
x) Halishahar-Kulshi 132 kV Ckt-1 tripped at 15:48 from both end showing dist Z1,O/C relay at Hathazari
end & dist Y phase ,E/F relay at Kulshi end and was switched on at 16:19.
y) Bibiyana(S) PP tripped at 16:01 showing generator CB protection trip.
z) Sirajganj-Bogura 230 kV Ckt-2 tripped at 19:29 from both end showing dist Z1,3-phase SOTF at
Sirajganj end and dist Z1,E/F relay at Bogura end and was switched on at 20:11.
aa) Kabirpur 132/33 kV T-3 transformer was under shut down from 16:09 to 20:07 for relay replacement
work.
ab) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down since 07:05(28-12-2020) for A/M.
ac) Sikalbaha-Shahmirpur 132 kV Ckt-2 was under shut down since 07:22(28-12-2020) for A/M.
ad) Mongla 33 kV bus tripped at 06:18 due to bird fall and was switched on at 06:37(28-12-2020). |  |  |  |  | About 36 MW power interruption occurred under Mongla S/S area
from 06:18 to 06:37.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 73 | 2271200 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7393436
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 290636 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 354 | 9463960 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 285 | 7114000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4747000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1324800
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 40 | 251784 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 647480 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 92 | 1256961 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 420372 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 331709
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 116352 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1059120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 833280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 942973
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 36 | 260716 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1246920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 811300 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 2248145
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 101 | 655200 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2009280
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 112320 | Low demand
| Dhaka area Total |  |  |  | 6057 | 2546 | 46220744
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120285
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 433440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1103476 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 163 | 3851464 | Gas shortage & ST under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 176296 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1699200
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 537600
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 57 | 79680 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 251 | 3856473 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1177753
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 894720
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 242127
| Chattogram area Total |  |  |  | 2266 | 889 | 14197474
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2580246 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 130 | 2444065 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7432000
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 594144 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1286400
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1223698
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2194618 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1160190 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 1907040 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489132 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1957440
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 35 | 171310 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 491120
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 33060 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 479640 | Reserve.
| Cumilla Area Total |  |  |  | 2980 | 1234 | 25717450
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 90 | 2242360 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 441864
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 832320
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 70 | 309600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2173200 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 234610
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 687 | 385 | 6244104
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 570000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 755760 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 150 | 3511000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 480600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 43 | 455976
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 203032
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 766080 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1768320 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 182 | 3470690
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 77000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 96480 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7048000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 5747900 | On test
| Sylhet Area Total |  |  |  | 1988 | 897 | 24950838
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 805 | 13552727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 58560 | Reserve.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 5503104 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 78000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1367520 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1115 | 20559911
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 333888 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 434700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 246761 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 500 | 11030800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 35 | 751474 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 55 | 690000 | On test.
| Barisal Area Total |  |  |  | 1054 | 701 | 13487623
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 3735618 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 400 | 8918145 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511440
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217044
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 35 | 101760 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 62 | 357584 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1664928
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 480288
| Rajshahi Area Total |  |  |  | 2183 | 900 | 15986807
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1495418
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 796800
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25817
| Rangpur Area Total |  |  |  | 605 | 176 | 2318035
| Total |  |  |  | 20104 | 8843 | 169682986
| Eastern Grid Total |  |  |  | 13978 | 5951 | 117330610
| Western Grid Total |  |  |  | 6126 | 2892 | 52352376
| National Grid Total |  |  |  | 20104 | 8843 | 169682986
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-27
| (a) ENTIRE EASTERN GRID : |  | 5607 | MW | (b) ENTIRE WESTERN GRID : |  | 2777 | MW
| i) Dhaka area |  | 3033 | MW | i) Khulna area |  | 1079 | MW
| ii) Chittagong area |  | 858 | MW | ii) Rajshahi area |  | 861 | MW
| iii) Comilla area |  | 719 | MW | iii) Barisal area |  | 240 | MW
| iv) Mymensingh area |  | 696 | MW | iv) Rangpur area |  | 597 | MW
| v) Sylhet area |  | 301 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8384 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 94 | 11:00 | Jamalpur | 75 | 18:00 | Benapol | 36 | 18:00
| Munsiganj | 78 | 20:00 | Sherpur | 88 | 19:00 | Jhenida | 84 | 18:30
| Sonargaon | 57 | 20:00 | Srimongal | 29 | 18:00 | Bottail | 83 | 12:00
| Shyampur | 166 | 10:00 | Shahjibazar | 74 | 18:00 | G.K Project | 45 | 18:30
| Bhulta | 149 | 19:00 | Fenchuganj | 25 | 18:00 | Faridpur | 134 | 18:30
| Madanganj | 54 | 21:00 | Kulawara | 27 | 18:00 | Madaripur | 63 | 20:00
| Shitalakhya | 91 | 15:00 | Sylhet | 75 | 19:30 | Sariatpur | 42 | 20:00
| Rahim steel | 6 | 17:00 | Chatak | 20 | 18:00 | Gopalganj | 58 | 18:30
| Matuail | 48 | 7:00 | Sunamganj | 26 | 19:30 | Bagerhat | 82 | 18:00
| Ghorasal | 62 | 19:00 | Biani Bazar | 38 | 18:00 | Mongla | 38 | 11:00
| Narsingdi | 151 | 1:00 | Comilla (S) | 106 | 18:00 | Satkhira | 77 | 19:00
| Haripur (SBU) | 97 | 11:00 | Comilla(N) | 55 | 19:30 | Gallamari | 16 | 19:30
| Ullon | 38 | 14:00 | Chandpur | 66 | 19:00 | Magura | 40 | 18:30
| Hasnabad | 137 | 19:30 | Feni | 77 | 18:00 | Norail | 24 | 18:30
| Magbazar | 61 | 17:00 | Chowmuhani | 112 | 19:30 | Chuadanga | 68 | 18:00
| Maniknagar | 64 | 11:00 | Ashuganj | 36 | 18:30 | Barisal(N) | 28 | 19:30
| Bangabhaban | 20 | 13:00 | Daudkandi | 108 | 20:00 | Barisal (S) | 70 | 18:30
| Narinda | 68 | 18:30 | B.Baria | 94 | 19:30 | Patuakhali | 78 | 19:30
| Dhanmondi | 89 | 14:00 | Ramganj | 62 | 20:00 | Bhandaria | 40 | 18:30
| Lalbag | 68 | 13:00 | Chaddagram | 23 | 17:00 | Borhan Uddin | 27 | 20:00
| Madartek | 44 | 18:30 | PHP | 10 | 17:00 | Ishurdi | 48 | 19:00
| Dhaka University |  |  | Madunaghat | 49 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.75 | Hathazari | 57 | 0.77083 | Natore | 83 | 0.8125
| Fatullah | 41 | 10:00 | Khulshi | 135 | 15:00 | Bogra | 110 | 18:00
| Mirpur | 70 | 18:00 | Halishahar | 96 | 19:00 | Noagaon | 77 | 18:30
| Kalyanpur | 57 | 18:30 | Baraulia | 144 | 14:00 | Rajshahi | 96 | 19:30
| Gulshan | 70 | 13:00 | Sikalbaha | 21 | 18:00 | Rajshahi New | 9 | 20:00
| Uttara | 64 | 18:30 | Dohazari | 58 | 19:00 | C.Nawabganj | 52 | 20:00
| Uttara New | 23 | 18:00 | Cox'sbazar | 71 | 18:30 | Amnura | 30 | 20:00
| Kamrangirchar | 73 | 13:00 | Chandraghona | 20 | 18:00 | Pabna | 76 | 18:00
| Savar | 93 | 12:00 | Kaptai | 3.8 | 18:00 | Shahjadpur | 74 | 20:00
| Bhasantec | 95 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 64 | 18:30
| Agargaon | 44 | 13:00 | Bakulia | 73 | 18:00 | Niyamatpur | 43 | 20:00
| Satmosjid | 65 | 0.58333 | Julda | 21 | 0.5 | Joypurhat | 44 | 0.83333
| Tongi | 69 | 18:30 | TK chemical | 21 | 19:00 | Sherpur(Bogura) | 37 | 18:30
| Kabirpur | 169 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 88 | 18:00 | Shahmirpur | 18.6 | 18:00 | Rangpur | 110 | 18:00
| Manikganj | 52 | 18:00 | Khagrachhari | 20 | 17:00 | Lalmonirhat | 42 | 19:00
| Joydevpur | 108 | 19:00 | Matarbari | 23.5 | 20:00 | Saidpur | 83 | 18:00
| New Tongi | 83 | 12:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 90 | 18:00
| Kodda | 164 | 18:30 | Rangamati | 10 | 13:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 82 | 18:30 | Abul Khair 230 | 200 | 14:00 | Palashbari | 90 | 19:00
| Rajendrapur | 74 | 18:30 | BSRM | 151 | 5:00 | Barapukuria | 40 | 20:00
| Valuka | 92 | 18:00 | GPH Ispat | 86 | 5:00 | Panchagar | 43 | 18:00
| Tangail | 141 | 18:30 | Goalpara | 16 | 20:00 | Joldhaka | 24 | 18:30
| Mymensing | 140 | 18:00 | Central s/s | 81 | 18:00 | Kurigram | 40 | 18:00
| Kishorganj | 90 | 19:00 | Noapara | 53 | 18:30
| Netrokona | 84 | 18:00 | Jessore | 74 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 23:00 | 405 | 11:00 | Kaliakoir | 392 | 0.5 | 362 | 0.41667
| Bheramara | 409 | 18:30 | 398 | 10:00 | Bhulta | 381 | 0.95833 | 363 | 0.625
| Ashuganj(N) | 383 | 23:00 | 369 | 15:00 | Gopalganj | 414 | 0.5 | 400 | 0.041667
| Payra | 417 | 23:00 | 410 | 9:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 23:00 | 228 | 16:00 | Comilla (N) | 236 | 17:00 | 228 | 10:00
| Ishurdi | 237 | 4:00 | 227 | 8:00 | Hathazari | 226 | 18:00 | 212 | 15:00
| Ashuganj | 237 | 18:00 | 230 | 11:00 | Megnaghat | 233 | 17:00 | 226 | 13:00
| Serajganj | 235 | 17:00 | 226 | 7:00 | Fenchuganj | 244 | 23:00 | 236 | 13:00
| Baghabari | 240 | 3:00 | 237 | 9:00 | Siddhirganj | 230 | 20:00 | 222 | 10:00
| Barapukuria | 233 | 4:00 | 224 | 8:00 | Maniknagar | 228 | 23:00 | 220 | 11:00
| Bogra | 232 | 5:00 | 224 | 18:00 | Agargaon | 229 | 17:00 | 217 | 12:00
| Rajshahi | 229 | 23:00 | 218 | 8:00 | Barisal | 248 | 23:00 | 241 | 8:00
| Khulna South | 235 | 5:00 | 218 | 19:30 | AKSML | 226 | 24:00 | 207 | 14:00
| Rampura | 229 | 24:00 | 221 | 12:00 | BSRM | 229 | 18:00 | 213 | 5:00
| Haripur | 228 | 23:00 | 220 | 11:00 | Bibiyana | 244 | 23:00 | 238 | 14:00
| Hasnabad | 230 | 18:30 | 220 | 15:00 | Bhulta | 232 | 19:00 | 221 | 17:00
| Shyampur | 229 | 23:00 | 220 | 10:00 | Ashuganj (S) | 234 | 18:00 | 227 | 12:00
| Aminbazar | 229 | 24:00 | 218 | 10:00 | Kaliakoir | 227 | 23:00 | 215 | 10:00
| Tongi | 225 | 18:00 | 214 | 9:00 | GPH | 225 | 23:00 | 212 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 18:30 | 132 | 12:00 | Madanhat | 138 | 0.77083 | 131 | 0.5
| Munsiganj | 139 | 18:00 | 132 | 10:00 | Hathazari | 137 | 0.79167 | 130 | 0.45833
| Sonargaon | 137 | 23:00 | 133 | 12:00 | Khulshi | 135 | 0.70833 | 127 | 0.5
| Shyampur | 133 | 23:00 | 127 | 10:00 | Halishahar | 137 | 0.75 | 129 | 0.20833
| Bhulta | 132 | 4:00 | 129 | 14:00 | Baraulia | 137 | 0.70833 | 130 | 0.5
| Madanganj | 136 | 19:00 | 129 | 15:00 | Sikalbaha | 138 | 0.79167 | 129 | 0.16667
| Shitalakhya | 140 | 18:00 | 133 | 10:00 | Dohazari | 134 | 0.75 | 125 | 0.5
| Rahim steal | 138 | 18:30 | 133 | 11:00 | Cox'sbazar | 127 | 0.70833 | 121 | 0.45833
| Matuail | 138 | 18:30 | 132 | 12:00 | Chandraghona | 137 | 0.75 | 130 | 0.5
| Ghorasal | 138 | 22:00 | 134 | 1:00 | Kaptai | 137 | 0.77083 | 132 | 0.375
| Narsinghdi | 137 | 19:00 | 132 | 12:00 | A. Khaer Stl. | 134 | 0.70833 | 130 | 0.41667
| Haripur (SBU) | 138 | 19:00 | 133 | 12:00 | Bakulia | 136 | 0.75 | 129 | 0.45833
| Ullon | 131 | 21:00 | 124 | 11:00 | Julda | 138 | 0.75 | 126 | 0.041667
| Hasnabad | 140 | 23:00 | 134 | 9:00 | TK Chemical | 137 | 0.77083 | 130 | 0.45833
| Magbazar | 131 | 23:00 | 124 | 12:00 | Modern Steel | 136 | 0.83333 | 128 | 0.5
| Maniknagar | 137 | 23:00 | 132 | 11:00 | Shahmirpur | 137 | 0.75 | 129 | 0.5
| Bangabhaban | 137 | 23:00 | 132 | 11:00 | Khagrachhari | 136 | 0.70833 | 129 | 0.5
| Narinda | 137 | 23:00 | 132 | 11:00 | Matarbari | 130 | 0.77083 | 124 | 0.125
| Dhanmondi | 131 | 21:00 | 124 | 11:00 | Baroiar Hat | 137 | 0.75 | 133 | 0.41667
| Lalbag | 130 | 23:00 | 118 | 12:00 | Rangamati | 136 | 18:00 | 129 | 12:00
| Madartek | 131 | 23:00 | 124 | 10:00 | Goalpara S/S | 138 | 23:00 | 128 | 19:30
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 17:00 | 127 | 0.8125
| Aftabnagar | 132 | 24:00 | 123 | 12:00 | Noapara | 137 | 3:00 | 125 | 0.8125
| Fatuiiah | 134 | 19:00 | 128 | 10:00 | Jessore | 134 | 6:00 | 122 | 0.8125
| Mirpur | 131 | 23:00 | 122 | 12:00 | Benapol | 135 | 0.125 | 126 | 0.54167
| Kalyanpur | 132 | 18:00 | 121 | 12:00 | Jhenida | 134 | 3:00 | 121 | 0.8125
| Gulshan | 131 | 23:00 | 123 | 12:00 | Bottail | 137 | 0.083333 | 130 | 0.8125
| Uttara | 131 | 23:00 | 120 | 12:00 | G.K Project | 141 | 0.20833 | 137 | 0.5
| Uttara New | 136 | 19:00 | 127 | 15:00 | Faridpur | 137 | 0.125 | 131 | 0.77083
| Kamrangirchar | 139 | 18:00 | 134 | 9:00 | Madaripur | 139 | 0.58333 | 134 | 0.29167
| Savar | 132 | 18:30 | 120 | 10:00 | Shariyatpur S/S | 140 | 4:00 | 135 | 0.75
| Bhasantec | 134 | 23:00 | 126 | 10:00 | Gopalganj | 141 | 0.66667 | 135 | 0.375
| Agargaon | 135 | 23:00 | 127 | 12:00 | Bagerhat | 137 | 17:00 | 126 | 0.8125
| Satmosjid | 135 | 23:00 | 127 | 12:00 | Mongla | 135 | 9:00 | 125 | 0.8125
| Tongi | 136 | 21:00 | 130 | 15:00 | Satkhira | 137 | 5:00 | 125 | 19:30
| Kabirpur | 134 | 23:00 | 124 | 9:00 | Gallamari | 138 | 0.20833 | 129 | 0.8125
| Basundhara | 136 | 23:00 | 124 | 15:00 | Magura | 135 | 4:00 | 120 | 0.8125
| Manikganj | 140 | 19:00 | 130 | 15:00 | Norail | 134 | 0.16667 | 122 | 0.8125
| Joydevpur | 141 | 23:00 | 130 | 12:00 | Chuadanga | 131 | 4:00 | 118 | 0.8125
| New Tongi | 136 | 23:00 | 128 | 15:00 | Barisal(N) | 141 | 5:00 | 137 | 1:00
| Kodda | 134 | 19:00 | 123 | 16:00 | Barisal (S) | 140 | 0.79167 | 134 | 0.041667
| Dhamrai | 134 | 23:00 | 122 | 10:00 | Patuakhali(S) | 140 | 0.79167 | 132 | 0.29167
| Rajendrapur | 137 | 23:00 | 126 | 12:00 | Bhandaria | 139 | 0.58333 | 134 | 0.33333
| Valuka | 130 | 23:00 | 120 | 7:00 | Ishurdi | 138 | 5:00 | 134 | 8:00
| Tangail | 133 | 23:00 | 126 | 15:00 | Ruppur Paromanobik | 137 | 1:00 | 134 | 8:00
| Mymensing | 132 | 23:00 | 124 | 6:00 | Natore | 139 | 3:00 | 133 | 8:00
| Kishorganj | 130 | 3:00 | 124 | 15:00 | Bogra | 136 | 17:00 | 131 | 7:00
| Netrokona | 130 | 23:00 | 122 | 8:00 | Noagaon | 134 | 3:00 | 126 | 8:00
| Jamalpur | 139 | 21:00 | 123 | 3:00 | Rajshahi | 139 | 4:00 | 133 | 8:00
| Sherpur | 138 | 20:00 | 122 | 3:00 | Rajshahi New | 141 | 4:00 | 134 | 8:00
| Srimongal | 137 | 17:00 | 134 | 1:00 | C.Nawabganj | 140 | 3:00 | 131 | 9:00
| Shahjibazar | 133 | 17:00 | 129 | 12:00 | Amnura | 138 | 4:00 | 132 | 8:00
| Fenchuganj | 138 | 23:00 | 134 | 9:00 | Pabna | 138 | 1:00 | 132 | 14:00
| Khulawara | 138 | 24:00 | 133 | 12:00 | Shahjadpur | 140 | 1:00 | 135 | 9:00
| Sylhet | 136 | 24:00 | 132 | 15:00 | Serajganj | 135 | 1:00 | 130 | 7:00
| Chatak | 135 | 17:00 | 132 | 12:00 | Niyamatpur | 132 | 5:00 | 125 | 9:00
| Sunamganj | 135 | 23:00 | 132 | 12:00 | Joypurhat | 136 | 3:00 | 124 | 8:00
| Biani Bazar | 136 | 23:00 | 132 | 12:00 | Sherpur(Bogura) | 137 | 3:00 | 131 | 10:00
| Comilla(s) | 131 | 4:00 | 125 | 18:00 | Mohastangor | 136 | 6:00 | 128 | 8:00
| Comilla(n) | 141 | 18:00 | 137 | 10:00 | Rangpur | 129 | 6:00 | 121 | 18:00
| Chandpur | 143 | 18:00 | 141 | 21:00 | Lalmonirhat | 131 | 3:00 | 120 | 18:00
| Feni | 139 | 18:00 | 134 | 15:00 | Saidpur | 130 | 4:00 | 119 | 18:00
| Chowmuhani | 136 | 9:00 | 134 | 7:00 | Purbasadipur | 130 | 3:00 | 119 | 18:00
| Ashuganj | 134 | 5:00 | 130 | 12:00 | Thakurgaon | 133 | 6:00 | 118 | 8:00
| Daudkandi | 139 | 17:00 | 134 | 12:00 | Palashbari | 133 | 4:00 | 122 | 9:00
| B.Baria | 131 | 23:00 | 126 | 12:00 | Barapukuria | 133 | 4:00 | 124 | 8:00
| Ramganj | 136 | 19:00 | 132 | 9:00 | Panchagar | 132 | 6:00 | 115 | 18:00
| Chaddagram | 139 | 17:00 | 135 | 12:00 | Joldhaka | 133 | 5:00 | 117 | 8:00
| PHP | 138 | 17:00 | 131 | 2:00 | Kurigram | 130 | 0.125 | 119 | 0.33333

## L-Curve
Date | 2020-12-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 103 | 4873 | 1891 | 6764 |  |  |  | QF-LDC-11
0:30 | 51.5 | 4655.5 | 1856 | 6511.5 | Date: | 2020-12-27
1:00 | 0 | 4438 | 1821 | 6259
1:30 | 33 | 4294.5 | 1804 | 6098.5
2:00 | 66 | 4151 | 1787 | 5938
2:30 | 66 | 4053 | 1765.5 | 5818.5 | [5 empty] | Gen. at Eve. Peak | 8843 | 8843 MW (19:00 )
3:00 | 66 | 3955 | 1744 | 5699 | [6 empty] | 19:00
3:30 | 58 | 3952 | 1694.5 | 5646.5 | [5 empty] | Gen. at Day Peak | 7231 | 7231 MW (12:00 )
4:00 | 50 | 3949 | 1645 | 5594 | [6 empty] | 12:00
4:30 | 38.5 | 3922.5 | 1647 | 5569.5 | [5 empty] | Highest Generation | 8843
5:00 | 27 | 3896 | 1649 | 5545 | [6 empty] | 19:00
5:30 | 22.5 | 3966.5 | 1668 | 5634.5
6:00 | 18 | 4037 | 1687 | 5724
6:30 | 26 | 4094.5 | 1786 | 5880.5
7:00 | 34 | 4152 | 1885 | 6037
7:30 | 62.5 | 4331.5 | 1972.5 | 6304
8:00 | 91 | 4511 | 2060 | 6571
8:30 | 56 | 4699 | 2061 | 6760
9:00 | 21 | 4887 | 2062 | 6949
9:30 | 95.5 | 4851.5 | 2106 | 6957.5
10:00 | 170 | 4816 | 2150 | 6966
10:30 | 116.5 | 4886 | 2117.5 | 7003.5
11:00 | 63 | 4956 | 2085 | 7041
11:30 | 50 | 5030 | 2106 | 7136
12:00 | 37 | 5104 | 2127 | 7231
12:30 | 29.5 | 5190 | 2126.5 | 7316.5
13:00 | 22 | 5276 | 2126 | 7402
13:30 | 57.5 | 5185 | 2094 | 7279
14:00 | 93 | 5094 | 2062 | 7156
14:30 | 179 | 4939 | 2071.5 | 7010.5
15:00 | 265 | 4784 | 2081 | 6865
15:30 | 248 | 4729.5 | 2035.5 | 6765
16:00 | 231 | 4675 | 1990 | 6665
16:30 | 160.5 | 4792 | 2019.5 | 6811.5
17:00 | 90 | 4909 | 2049 | 6958
17:30 | 74.5 | 5295 | 2403 | 7698
18:00 | 59 | 5681 | 2757 | 8438
18:30 | 58.5 | 5816 | 2824.5 | 8640.5
19:00 | 58 | 5951 | 2892 | 8843
19:30 | 26 | 5900 | 2864 | 8764
20:00 | 52 | 5862 | 2861 | 8723 |  |  |  | Executive Engineer
20:30 | 39 | 5773 | 2784.5 | 8557.5 |  |  |  | Network Operation Division
21:00 | 26 | 5684 | 2708 | 8392
21:30 | 27 | 5509.5 | 2589.5 | 8099
22:00 | 28 | 5335 | 2471 | 7806 |  |  |  |  | Page 6 of 7
22:30 | 31.5 | 5248.5 | 2312.5 | 7561
23:00 | 35 | 5162 | 2154 | 7316
23:30 | 69 | 5017.5 | 2022.5 | 7040
24:00 | 103 | 4873 | 1891 | 6764
8843 MW (19:00 )
7231 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-27 |  | Energy | 169682986
[11 empty] | 2020-12-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2588 | 428 | 1565 | 1833 | 512 | 47 | 16 | 0 | 74 | 0
0:30 | 2799 | 428 | 1556.5 | 1206 | 542.5 | 46 | 8 | 0 | 75 | 0 | Date: | 2020-12-27
1:00 | 3010 | 428 | 1548 | 579 | 573 | 45 | 0 | 0 | 76 | 0
1:30 | 2996 | 427.5 | 1568 | 445 | 542.5 | 44.5 | 0 | 0 | 75 | 0 | [7 empty] | Total Energy | 169.683 | Total Energy Gen 169.683 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.683 MKWHr
2:00 | 2982 | 427 | 1588 | 311 | 512 | 44 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2980 | 427.5 | 1602 | 204 | 487.5 | 43.5 | 0 | 0 | 74 | 0 | [7 empty] | Energy Requirement | 169.683
3:00 | 2978 | 428 | 1616 | 97 | 463 | 43 | 0 | 0 | 74 | 0
3:30 | 2988 | 381 | 1601 | 97 | 463 | 43.5 | 0 | 0 | 73 | 0 | [6 empty] | Shortage
4:00 | 2998 | 334 | 1586 | 97 | 463 | 44 | 0 | 0 | 72 | 0
4:30 | 2978.5 | 334 | 1578 | 100 | 462.5 | 44.5 | 0 | 0 | 72 | 0
5:00 | 2959 | 334 | 1570 | 103 | 462 | 45 | 0 | 0 | 72 | 0
5:30 | 2967.5 | 333.5 | 1585 | 165 | 467 | 45.5 | 0 | 0 | 71 | 0
6:00 | 2976 | 333 | 1600 | 227 | 472 | 46 | 0 | 0 | 70 | 0
6:30 | 2994.5 | 380 | 1567.5 | 330 | 492 | 46.5 | 0 | 0 | 69 | 1 |  |  |  |  | Coal
7:00 | 3013 | 427 | 1535 | 433 | 512 | 47 | 0 | 0 | 68 | 2
7:30 | 3053 | 474.5 | 1511 | 626 | 512.5 | 47 | 0 | 0 | 70 | 10 |  |  |  | Oil |  |  |  | ,
8:00 | 3093 | 522 | 1487 | 819 | 513 | 47 | 0 | 0 | 72 | 18
8:30 | 3083.5 | 522.5 | 1461 | 1025.5 | 523 | 46 | 0 | 0 | 70 | 28.5
9:00 | 3074 | 523 | 1435 | 1232 | 533 | 45 | 0 | 0 | 68 | 39
9:30 | 3036.5 | 546.5 | 1426.5 | 1270.5 | 513 | 46 | 0 | 0 | 70 | 48.5
10:00 | 2999 | 570 | 1418 | 1309 | 493 | 47 | 0 | 0 | 72 | 58
10:30 | 3013.5 | 570 | 1402 | 1362 | 473 | 47 | 0 | 0 | 73 | 63
11:00 | 3028 | 570 | 1386 | 1415 | 453 | 47 | 0 | 0 | 74 | 68
11:30 | 3038.5 | 570 | 1447 | 1481.5 | 408 | 46.5 | 0 | 0 | 76 | 68.5
12:00 | 3049 | 570 | 1508 | 1548 | 363 | 46 | 0 | 0 | 78 | 69
12:30 | 3033 | 569.5 | 1487 | 1652 | 373 | 46 | 8 | 0 | 79 | 69
13:00 | 3017 | 569 | 1466 | 1756 | 383 | 46 | 16 | 0 | 80 | 69
13:30 | 3017 | 569 | 1466 | 1756 | 383 | 46 | 16 | 0 | 80 | 69
14:00 | 3017 | 569 | 1466 | 1756 | 383 | 46 | 16 | 0 | 80 | 69
14:30 | 2942 | 569 | 1488.5 | 1553 | 403.5 | 45.5 | 8 | 0 | 77 | 47
15:00 | 2867 | 569 | 1511 | 1350 | 424 | 45 | 0 | 0 | 74 | 25
15:30 | 2854 | 569 | 1480 | 1318.5 | 404 | 45 | 0 | 0 | 75 | 19.5
16:00 | 2841 | 569 | 1449 | 1287 | 384 | 45 | 0 | 0 | 76 | 14
16:30 | 2704 | 569 | 1418.5 | 1543.5 | 413.5 | 45.5 | 34 | 0 | 76 | 7.5
17:00 | 2567 | 569 | 1388 | 1800 | 443 | 46 | 68 | 0 | 76 | 1
17:30 | 2582 | 687 | 1488.5 | 2184.5 | 468 | 46 | 150.5 | 0 | 91 | 0.5
18:00 | 2597 | 805 | 1589 | 2569 | 493 | 46 | 233 | 0 | 106 | 0
18:30 | 2608.5 | 805 | 1590.5 | 2710.5 | 528 | 46 | 248 | 0 | 104 | 0
19:00 | 2620 | 805 | 1592 | 2852 | 563 | 46 | 263 | 0 | 102 | 0
19:30 | 2653 | 805 | 1655 | 2690 | 563 | 48 | 246 | 0 | 104 | 0
20:00 | 2646 | 805 | 1624 | 2687 | 563 | 48 | 246 | 0 | 104 | 0
20:30 | 2656 | 805.5 | 1619 | 2523 | 563 | 48 | 241 | 0 | 102 | 0
21:00 | 2666 | 806 | 1614 | 2359 | 563 | 48 | 236 | 0 | 100 | 0
21:30 | 2655.5 | 806 | 1583.5 | 2149 | 563 | 48 | 198 | 0 | 96 | 0
22:00 | 2645 | 806 | 1553 | 1939 | 563 | 48 | 160 | 0 | 92 | 0
22:30 | 2609.5 | 711 | 1511.5 | 1886 | 563 | 48 | 142 | 0 | 90 | 0
23:00 | 2574 | 616 | 1470 | 1833 | 563 | 48 | 124 | 0 | 88 | 0
23:30 | 2581 | 522 | 1517.5 | 1833 | 537.5 | 47.5 | 70 | 0 | 81 | 0 | Max Temp. in Dhaka |  | 25.0° C
24:00 | 2588 | 428 | 1565 | 1833 | 512 | 47 | 16 | 0 | 74 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 169.683 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.683 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 44 | 43 | 44 | 45 | 46 | 47 | 47 | 45 | 47 | 47 | 46 | 46 | 46 | 45 | 45 | 46 | 46 |  | 46 | 48 | 48 | 48 | 48 | 48 | 47 | 1103476
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 12 | 17 | 18 | 18 | 17 | 15 |  | 6 | 0 | [9 empty] | 120285
6 | Sikalbaha 225MW CCPP (Gas) | 163 | 162 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 163 | 165 | 164 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 165 | 164 | 163 | 3851464
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 34 | 34 | 34 |  |  | 0 | 176296
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 4 | 45 | 45 | 69 | 79 | 91 | 95 | 95 | 95 | 104 | 204 |  | 281 | 300 | 300 | 250 | 145 | 145 | 80 | 2248145
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 95 | 95 | 94 | 94 | 94 | 94 | 94 | 93 | 94 | 94 | 94 | 92 | 93 | 93 | 73 | 75 | 74 | 74 |  | 73 | 74 | 74 | 74 | 94 | 94 | 94 | 2271200
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7393436
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 140 | 140 | 140 | 140 | 140 | 125 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2580246
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 |  | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 2444065
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 594144
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 295 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 305 | 330 |  | 330 | 330 | 330 | 330 | 330 | 320 | 300 | 7432000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 51 | 54 |  | 53 | 54 | 54 | 54 | 53 | 54 | 54 | 1286400
36 | Chandpur 150 MW CCPP | 51 | 52 | 51 | 51 | 50 | 45 | 51 | 50 | 47 | 46 | 46 | 81 | 46 | 45 | 45 | 50 | 51 | 45 |  | 50 | 50 | 45 | 50 | 45 | 51 | 51 | 1160190
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 438 | 435 | 434 | 437 | 384 | 399 | 441 | 436 | 435 | 403 | 370 | 362 | 412 | 386 | 347 | 332 | 379 | 355 |  | 354 | 365 | 361 | 380 | 376 | 314 | 345 | 9463960
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4747000
41 | Haripur 360MW CCPP(HPL) | 323 | 327 | 355 | 354 | 352 | 353 | 284 | 284 | 315 | 280 | 280 | 300 | 295 | 295 | 295 | 250 | 270 | 285 |  | 285 | 285 | 285 | 263 | 253 | 285 | 294 | 7114000
42 | RPCL 210MW CCPP | 110 | 110 | 108 | 108 | 108 | 108 | 109 | 111 | 109 | 89 | 90 | 86 | 80 | 77 | 77 | 84 | 82 | 92 |  | 90 | 90 | 90 | 91 | 91 | 90 | 91 | 2242360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 23 | 33 | 40 | 41 | 42 | 25 | 20 | 6 | 1 | [9 empty] | 234610
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 570000
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 755760
46 | Shajibazar 330 MW CCPP | 153 | 153 | 154 | 152 | 153 | 150 | 150 | 150 | 151 | 152 | 150 | 149 | 150 | 156 | 152 | 152 | 152 | 150 |  | 150 | 152 | 150 | 150 | 150 | 152 | 153 | 3511000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 20 | 20 | 32 | 32 | 31 | 31 | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 34 | 34 | 33 | 766080
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 76 | 77 | 77 | 77 | 77 | 77 | 71 | 73 | 72 | 72 | 72 | 73 | 73 | 72 | 72 |  | 72 | 72 | 73 | 73 | 73 | 73 | 73 | 1768320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 128 | 128 | 129 | 128 | 128 | 128 | 128 | 128 | 130 | 130 | 122 | 122 | 122 | 122 | 122 | 150 | 182 |  | 182 | 182 | 182 | 182 | 182 | 182 | 183 | 3470690
51 | Sylhet 20 MW GTPP | [20 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 77000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | [5 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 203032
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 2 | 46 | 53 |  | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 480600
56 | Shahjahanulla 25 MW PP | [19 empty] | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 96480
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 305 | 300 | 300 | 305 | 265 | 255 | 270 | 270 | 270 | 295 | 285 | 270 | 280 | 295 | 300 | 280 |  | 285 | 310 | 290 | 295 | 300 | 250 | 270 | 7048000
| Bibiyana South 400 MW | 330 | 330 | 329 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 407 | 421 | 414 | 412 | 412 | 412 | [10 empty] | 5747900
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 10 | 17 | 17 | 17 | 25 | 35 |  |  | 8 | 36 |  | 36 | 17 | 17 |  |  |  | 0 | 260716
59 | Tangail Palli Power Gen 22 MW
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 420372
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 441864
63 | Impoprt (Tripura) | 76 | 74 | 74 | 72 | 72 | 70 | 68 | 72 | 68 | 72 | 74 | 78 | 80 | 76 | 74 | 76 | 76 | 106 |  | 102 | 104 | 104 | 100 | 92 | 88 | 74 | 1957440
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 30 | 30 | 30 | 15 | 8 | 8 | 8 | 8 | 13 | 10 | 5 | 8 | 14 | 22 |  | 17 | 33 | 33 | 35 | 38 | 40 | 33 | 537600
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 489132
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251820
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820800
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 26 | 26 | 16 | 18 | 22 | 22 | 22 | 14 |  | 26 | 28 | 32 | 32 | 32 | 33 | 33 | 646920
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 811300
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 290636
| Feni Lanka Power | [17 empty] | 34 | [7 empty] | 0 | 33060
| Chowmuhani 113 MW | [16 empty] | 36 | 36 | [7 empty] | 0 | 479640
| Manikgonj 162MW PP(MPGL) | [17 empty] | 35 |  | 35 | [5 empty] | 0 | 112320
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 20 | 7 |  |  | 8 | 70 |  | 100 | 50 | 50 | 15 |  |  | 0 | 331709
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [12 empty] | 16 |  |  |  | 50 | 120 |  | 150 | 150 | 150 | 140 | 98 | 98 | 16 | 833280
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 4 | 8 | 8 | 9 | 51 | 64 | 32 | 32 | 42 | 84 |  | 90 | 90 | 90 | 90 | 90 | 66 | 24 | 832320
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 9 | 8 | 8 | 8 | 14 | 28 |  | 35 | 43 | 25 |  |  |  |  | 171310
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24960
| Jodiac Power | 54 | 41 | 36 | 36 | 36 | 38 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 14 | 47 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1177753
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [12 empty] | 15 | 15 | 8 |  |  | 5 |  | 40 | 48 | 48 | 30 | 15 | 15 | 0 | 251784
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 12 | 12 | 0 | [7 empty] | 20 | 82 | 86 | 87 | 64 | 82 | 94 | 94 |  | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 1256961
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 75 | 45 | 0 |  |  |  | 19 | 24 | 44 | 50 | 50 | 50 | 50 | 50 | 35 | 24 | 48 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1324800
| Meghnaghat 104 MW PP (OPCL) | 104 | 40 | 0 |  | 0 | 16 | 53 | 87 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 70 | 70 | 2009280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 8 | 42 |  | 43 | 46 | 46 | 46 | 46 | 47 | 47 | 455976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1223698
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 7 | 16 | 7 | 7 | 7 | 32 | 32 |  | 7 | [6 empty] | 116352
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 12 | 12 | 0 | [10 empty] | 8 | 46 | 50 |  | 50 | 50 | 50 | 32 | 32 | 32 | 32 | 433440
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 15 |  | 57 | [5 empty] | 0 | 79680
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 4 | 18 | 45 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 647480
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 942973
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 10150
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1059120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 5 | 53 |  | 70 | 70 | 70 | 60 | 16 |  | 0 | 309600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 15 | 30 | 60 | 32 | 15 | 15 | 15 | 23 |  | 101 | 100 | 105 | 97 | 56 | 46 | 27 | 655200
115 | Juldah 100 MW PP Unit-3 (Acorn) |  |  |  |  | 0 | 10 | 30 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1699200
116 | Chandpur 200MW (Desh energy) | 85 | 45 | 0 |  | 0 | 17 | 52 | 64 | 68 | 68 | 68 | 68 | 85 | 85 | 89 | 101 | 101 | 108 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 1907040
117 | Ashuganj 150MW PP (Midland) | [6 empty] | 11 | 40 | 107 | 125 | 135 | 143 | 143 | 143 | 80 | 80 | 102 | 142 |  | 142 | 142 | 143 | 148 | 142 | 142 | 142 | 2194618
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 65 | 35 | 16 | 16 | 16 | 19 | 55 | 85 | 115 | 115 | 115 | 115 | 115 | 115 | 95 | 95 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 109 | 2173200
| Anwara 300 MW PP (United) | 124 | 33 | 16 | 16 | 34 | 102 | 120 | 175 | 212 | 197 | 180 | 161 | 161 | 160 | 142 | 142 | 212 | 251 |  | 251 | 251 | 251 | 253 | 253 | 251 | 252 | 3856473
| Juldah unit-2 (Acorn) | [7 empty] | 20 | 50 | 20 | 20 | 20 | 40 | 20 | 20 | 20 | 100 | 100 |  | 100 | 100 | 100 | 100 | 70 | 70 | 10 | 894720
| Anlima Energy Ltd. | [9 empty] | 22 | 41 | 36 | 35 | 32 | 27 | 35 | 10 | [8 empty] | 0 | 242127
120 | Eastern Zone Total | 4438 | 4151 | 3955 | 3949 | 3896 | 4037 | 4152 | 4511 | 4887 | 4816 | 4956 | 5104 | 5276 | 5094 | 4784 | 4675 | 4909 | 5681 |  | 5951 | 5900 | 5862 | 5684 | 5335 | 5162 | 4873 | 117330610
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 20 | 32 | [7 empty] | 0 | 58560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 53 | 53 | 70 |  | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 1367520
130
131
132 | United Payra Power Ltd. | [10 empty] | 18 | 53 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 690000
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 36 | 36 | 36 | 37 | 36 | 36 | 13 | 15 | 34 | 32 | 15 | 14 | 35 | 35 | 13 | 16 | 38 |  | 35 | 36 | 35 | 34 | 36 | 39 | 37 | 751474
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 5 | 48 |  | 80 | 80 | 80 | 48 | 32 | 32 | 0 | 333888
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 11 | 10 | 10 | 10 | 10 | 246761
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 22 | 19 | 19 | 21 | 20 | 15 | 15 | 15 | 15 | 14 | 16 | 17 | 17 | 21 | 13 | 20 |  | 21 | 21 | 21 | 21 | 20 | 20 | 19 | 434700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 24 | 40 |  | 40 | [5 empty] | 0 | 78000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 428 | 427 | 428 | 334 | 334 | 333 | 427 | 522 | 523 | 570 | 570 | 570 | 569 | 570 | 569 | 569 | 569 | 805 |  | 805 | 805 | 805 | 806 | 806 | 616 | 428 | 13552727
147 | Bheramara 410 MW CCPP | 225 | 225 | 230 | 250 | 260 | 265 | 285 | 285 | 270 | 270 | 260 | 250 | 240 | 220 | 195 | 195 | 180 | 185 |  | 180 | 170 | 170 | 165 | 160 | 155 | 160 | 5503104
148 | Payra 1320 MW | 510 | 450 | 400 | 400 | 400 | 410 | 450 | 450 | 470 | 430 | 390 | 300 | 320 | 350 | 360 | 320 | 380 | 430 |  | 500 | 500 | 500 | 500 | 500 | 500 | 450 | 11030800
149
150 | Barapukuria TPP Unit-1 | 63 | 62 | 63 | 63 | 62 | 62 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 64 | 64 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 1495418
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 146 | 152 |  | 150 | 150 | 150 | 150 | 140 | 140 | 140 | 3735618
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 357 | 388 | 388 | 366 | 360 | 383 | 428 | 433 | 340 | 345 | 313 | 419 | 385 | 365 | 420 | 404 | 270 | 395 |  | 400 | 417 | 405 | 412 | 353 | 284 | 360 | 8918145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 217044
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 2 | 25 |  | 35 | 35 | 44 |  |  |  | 0 | 101760
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 18 | 62 |  | 62 | 62 | 62 | 62 | 62 | 26 | 0 | 357584
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 28 | 89 | 110 | 111 | 111 | 111 | 70 | 70 | 70 | 87 | 111 |  | 111 | 111 | 111 | 111 | 111 | 111 | 70 | 1664928
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 15 | 35 |  |  |  |  | 70 |  | 109 | 113 | 113 | 113 |  |  | 0 | 480288
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 5 | 39 | 36 | 40 | 41 | 41 | 41 | 42 | 105 | 113 |  | 113 | 113 | 113 | 35 |  |  | 0 | 796800
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 25817
178
178