## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-29 | Tuesday
|  |  | Date (day): | 2020-12-29 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12381.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13822 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-28 | 2020-12-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 94 | 94 | 102 | 102 |  | 68 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 98 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 315 | 418 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 275 | 270 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 82 | 82 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 65 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 28 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 84 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 15 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 58 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 34 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 112 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 100 | 160
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1872 | 2687 | 3447 | 3797 | 1424 | 769
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 39 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 47 | 46 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 163 | 0 | 160 | 160 | 65 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 15 | 10 | 15
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 52 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 161 | 217 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 38 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 678 | 755 | 1400 | 1380 | 760 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 135 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 70 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 60 | 200
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 350 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 57 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 143 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 49 | 50 | 50 | 113 |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 90 | 85 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 108 | 110 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 25 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 22 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1104 | 1231 | 1554 | 1992 | 577 | 373
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 89 | 92 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 42 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 32 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 0 | 0 | 0 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 306 | 351 | 591.6 | 562 | 92 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 30 | 30 | 30
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 32 | 32 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 163 | 163
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 152 | 152 | 155 | 155 | 175 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 53 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 34 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 72 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 122 | 215 | 200 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 16 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 320 | 320
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 20 | 280 | 280
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 871 | 996 | 1539 | 1539 | 175 | 442
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 569 | 806 | 581 | 821
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 190 | 230 | 230 | 180 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 884 | 1201 | 1311 | 1837 | 180 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 28 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 69 | 10 | 10 | 85 |  | Gas shortage
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 360 | 450 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 15 | 31 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 55 | 55 | 55 | 55
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 454 | 649 | 835 | 895 | 85 | 202
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 34 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 143 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 293 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 53 | 34 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 752 | 761 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 64 | 68 | 68
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 149 | 149 |  | 274 | Under maint.
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 37 | 113 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 105 | 177 | 338 | 330 | 0 | 399
|  | Total |  |  |  |  | 20595 | 20104 | 7026 | 8808 | 12381.6 | 13822 | 3894 | 2374
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6674.2214 | 8367 | 11761.6766 | 13129.9584
| A. |  | 2020-12-28 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 8808 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5588 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8808 | MW
| 3 | Day peak Generation : |  |  | 7026 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8367 | MW
| 4 | Evening peak Generation : |  |  | 8808 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 170.2193 | MKWHr | By Solar | 0.35755 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 101.7705 | MKWHr |  | By Oil: | 39.0112 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.4834 | MKWHr |  | By Hydro: | 1.0938 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3894 | MW | Dhaka | 2957 | 2957 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2374 | MW | Chittagong | 878 | 878 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6268 | MW | Khulna | 1092 | 1092 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 825.37 | MMCFD |  |  | Rajshahi | 866 | 866 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 117242963.886 | ii) Oil : | Taka | 295372739.26 | Comilla | 727 | 727 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 57862849.73 | Total | Taka | 470478552.876 | Mymensingh | 710 | 710 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.455 | MKWHr. | Sylhet | 313 | 313 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -162 | MW (E to W) at | 19:00 | hrs | Barisal | 239 | 239 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -164 | MW at | 20:00 | hrs | Rangpur | 585 | 585 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.4° C |  |  | Total | 8367 | 8367 |  | 0
| B. |  | 2020-12-29 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 25.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13822 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4922 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 171.9973 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5419 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.6145 | MKWHr. | ii) HVDC Flow at Peak Time |  | 806 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8883 | MKWHr. | iii) Maximum HVDC Flow : |  | 811 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.38 |  | (b) Today: | 98.32 |  | (c) Rule Curve: |  | 103.3
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 291 | 353 |  | 0 | 225 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 70 | 100 | 8 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 151 | 34 | 73 | 0 | 182 | 20 | 0 | 0 | 290 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 100 | 100 | 0 | 65 | 0 | 0 | 0 | 215 | 54 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 428 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 317 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 37 | 0 | 55 |  | 4507 | 1701 | 6208 | 2550 | 428 | 1606 | 1049 | 462 | 43 | 0 | 70 | 0 | 0 | 98.39
2:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 281 | 355 |  | 0 | 225 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 54 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 68 | 110 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 151 | 34 | 73 | 0 | 182 | 19 | 0 | 0 | 290 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 24 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 428 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 55 |  | 4128 | 1723 | 5851 | 2559 | 428 | 1653 | 638 | 462 | 43 | 0 | 68 | 0 | 0 | 98.39
3:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 281 | 354 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 19 | 68 | 110 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 152 | 33 | 73 | 0 | 182 | 19 | 0 | 0 | 300 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 24 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 428 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 55 |  | 3964 | 1743 | 5707 | 2564 | 428 | 1667 | 474 | 462 | 44 | 0 | 68 | 0 | 0 | 98.39
4:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 309 | 354 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 68 | 108 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 151 | 33 | 73 | 0 | 182 | 19 | 0 | 0 | 310 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 24 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 334 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 35 | 0 | 55 |  | 3988 | 1631 | 5619 | 2593 | 334 | 1683 | 464 | 433 | 44 | 0 | 68 | 0 | 0 | 98.39
5:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 303 | 355 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 41 | 100 | 110 | 0 | 0 | 300 | 0 | 8 | 47 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 68 | 107 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 150 | 34 | 73 | 0 | 182 | 19 | 0 | 0 | 300 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 24 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 334 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 36 | 0 | 55 |  | 3950 | 1638 | 5588 | 2597 | 334 | 1667 | 444 | 433 | 45 | 0 | 68 | 0 | 0 | 98.38
6:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 324 | 364 |  | 0 | 225 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 3 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 40 | 120 | 120 | 0 | 0 | 325 | 0 | 8 | 52 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 68 | 109 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 150 | 33 | 74 | 0 | 183 | 19 | 0 | 0 | 315 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 70 | 2 | 0 | 24 | 0 | 0 | 0 | 122 | 47 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 |  | 334 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 406 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 370 | 37 | 0 | 55 |  | 4164 | 1708 | 5872 | 2701 | 334 | 1731 | 560 | 432 | 46 | 0 | 68 | 0 | 0 | 98.38
7:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 324 | 294 |  | 0 | 225 | 0 | 7 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 41 | 120 | 100 | 0 | 0 | 330 | 0 | 8 | 51 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 66 | 110 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 147 | 33 | 74 | 0 | 150 | 19 | 0 | 0 | 290 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 70 | 38 | 0 | 24 | 0 | 0 | 0 | 161 | 35 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 0 | 0 |  | 428 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 385 | 53 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 35 | 0 | 55 |  | 4210 | 1868 | 6078 | 2665 | 428 | 1611 | 829 | 432 | 46 | 0 | 66 | 1 | 0 | 98.38
8:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 330 | 322 |  | 0 | 225 | 0 | 29 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 12 | 120 | 120 | 0 | 0 | 350 | 0 | 8 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 1 | 21 | 11 | 33 | 20 | 60 | 108 | 0 | 20 | 0 | 20 | 32 | 50 | 47 | 0 | 148 | 33 | 74 | 0 | 150 | 19 | 0 | 0 | 300 | 13 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 68 | 86 | 0 | 48 | 0 | 0 | 1 | 161 | 35 | 0 | 0 | 0 | 10 | 0 | 104 | 8 | 0 | 0 | 0 |  | 523 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 418 | 90 | 0 | 54 | 0 | 0 | 0 | 1 | 0 | 400 | 18 | 0 | 55 |  | 4445 | 2076 | 6521 | 2717 | 523 | 1636 | 1066 | 462 | 47 | 0 | 60 | 10 | 0 | 98.38
9:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 340 | 300 |  | 0 | 225 | 0 | 82 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 0 | 94 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 10 | 120 | 120 | 0 | 0 | 375 | 0 | 8 | 45 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 64 | 108 | 19 | 20 | 1 | 20 | 32 | 50 | 47 | 0 | 150 | 33 | 74 | 0 | 150 | 19 | 0 | 0 | 310 | 13 | 11 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 80 | 122 | 0 | 115 | 0 | 0 | 2 | 161 | 35 | 0 | 0 | 0 | 40 | 0 | 104 | 17 | 0 | 0 | 0 |  | 524 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 387 | 90 | 0 | 106 | 0 | 2 | 0 | 2 | 0 | 420 | 16 | 0 | 55 |  | 4820 | 2161 | 6981 | 2743 | 524 | 1585 | 1462 | 482 | 48 | 51 | 64 | 22 | 0 | 98.37
10:00 | 0 | 94 | 0 | 0 | 305 | 12 | 0 | 319 | 260 |  | 0 | 225 | 0 | 82 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 3 | 120 | 106 | 0 | 0 | 350 | 0 | 8 | 50 | 23 | 54 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 68 | 109 | 32 | 20 | 1 | 20 | 32 | 50 | 47 | 0 | 152 | 20 | 73 | 0 | 122 | 18 | 0 | 0 | 280 | 13 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 85 | 128 | 0 | 115 | 0 | 0 | 4 | 161 | 35 | 0 | 0 | 0 | 40 | 0 | 104 | 28 | 0 | 28 | 0 |  | 569 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 328 | 90 | 0 | 111 | 0 | 38 | 0 | 3 | 0 | 350 | 36 | 0 | 55 |  | 4762 | 2139 | 6901 | 2652 | 569 | 1467 | 1597 | 411 | 48 | 53 | 68 | 36 | 0 | 98.37
11:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 312 | 290 |  | 0 | 225 | 0 | 82 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 2 | 115 | 100 | 0 | 0 | 350 | 0 | 8 | 50 | 19 | 54 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 69 | 88 | 32 | 20 | 2 | 20 | 32 | 50 | 47 | 0 | 151 | 20 | 73 | 0 | 122 | 18 | 0 | 0 | 295 | 13 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 85 | 133 | 0 | 115 | 0 | 0 | 4 | 161 | 35 | 0 | 0 | 0 | 40 | 0 | 104 | 36 | 0 | 39 | 0 |  | 569 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 313 | 53 | 0 | 111 | 0 | 40 | 0 | 4 | 0 | 350 | 14 | 0 | 55 |  | 4792 | 2057 | 6849 | 2588 | 569 | 1467 | 1578 | 414 | 48 | 53 | 69 | 63 | 0 | 98.37
12:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 315 | 275 |  | 0 | 225 | 0 | 82 | 0 | 28 | 0 | 0 | 0 | 15 | 0 | 0 | 92 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 3 | 100 | 100 | 0 | 0 | 325 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 10 | 21 | 11 | 33 | 20 | 70 | 89 | 42 | 20 | 2 | 20 | 32 | 49 | 47 | 0 | 152 | 20 | 73 | 0 | 122 | 18 | 0 | 0 | 315 | 15 | 8 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 18 | 100 | 90 | 135 | 0 | 115 | 0 | 0 | 4 | 161 | 35 | 0 | 0 | 0 | 70 | 0 | 104 | 38 | 0 | 38 | 0 |  | 569 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 409 | 90 | 0 | 111 | 0 | 37 | 0 | 4 | 0 | 360 | 15 | 0 | 55 |  | 4831 | 2195 | 7026 | 2550 | 569 | 1582 | 1665 | 424 | 47 | 53 | 70 | 66 | 0 | 98.37
13:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 401 | 276 |  | 0 | 225 | 0 | 82 | 24 | 55 | 0 | 0 | 0 | 15 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 55 | 10 | 19 | 25 | 32 | 17 | 33 | 6 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 7 | 140 | 0 | 0 | 0 | 350 | 0 | 8 | 44 | 26 | 53 | 0 | 51 | 0 | 0 | 24 | 21 | 11 | 33 | 20 | 75 | 88 | 72 | 20 | 2 | 20 | 32 | 53 | 47 | 0 | 151 | 32 | 73 | 0 | 178 | 18 | 0 | 0 | 300 | 16 | 8 | 0 | 115 | 0 | 0 | 0 | 0 | 12 | 18 | 100 | 100 | 140 | 0 | 95 | 0 | 0 | 4 | 196 | 38 | 0 | 0 | 0 | 100 | 15 | 104 | 36 | 0 | 18 | 0 |  | 570 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 20 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 140 | 0 | 288 | 90 | 0 | 113 | 0 | 40 | 0 | 4 | 0 | 410 | 21 | 0 | 55 |  | 5132 | 2142 | 7274 | 2667 | 570 | 1469 | 1858 | 474 | 45 | 52 | 75 | 64 | 7274 | 98.36
14:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 370 | 250 |  | 0 | 225 | 0 | 82 | 48 | 55 | 0 | 0 | 0 | 15 | 0 | 0 | 86 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 28 | 17 | 16 | 16 | 0 | 45 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 4 | 140 | 0 | 0 | 0 | 350 | 0 | 8 | 49 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 33 | 21 | 75 | 85 | 40 | 0 | 1 | 20 | 32 | 53 | 47 | 0 | 150 | 20 | 72 | 0 | 163 | 18 | 0 | 0 | 280 | 16 | 8 | 0 | 164 | 0 | 0 | 0 | 0 | 46 | 15 | 70 | 68 | 135 | 0 | 85 | 0 | 0 | 3 | 196 | 54 | 0 | 0 | 0 | 60 | 100 | 104 | 26 | 0 | 15 | 0 |  | 569 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 311 | 90 | 0 | 70 | 0 | 41 | 0 | 3 | 0 | 370 | 34 | 0 | 55 |  | 5019 | 2107 | 7126 | 2647 | 569 | 1466 | 1790 | 434 | 45 | 52 | 75 | 48 | 0 | 98.36
15:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 345 | 250 |  | 0 | 225 | 0 | 82 | 42 | 30 | 0 | 0 | 0 | 8 | 0 | 0 | 84 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 28 | 17 | 33 | 8 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 5 | 140 | 0 | 0 | 0 | 350 | 0 | 8 | 49 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 21 | 74 | 86 | 8 | 0 | 1 | 20 | 32 | 50 | 43 | 0 | 150 | 20 | 72 | 0 | 163 | 18 | 0 | 0 | 285 | 16 | 8 | 0 | 95 | 0 | 0 | 0 | 0 | 38 | 11 | 70 | 51 | 142 | 0 | 85 | 0 | 0 | 2 | 162 | 54 | 0 | 0 | 0 | 40 | 100 | 104 | 14 | 0 | 10 | 0 |  | 573 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 340 | 90 | 0 | 35 | 0 | 35 | 0 | 2 | 0 | 350 | 33 | 0 | 55 |  | 4740 | 2055 | 6795 | 2638 | 573 | 1493 | 1488 | 414 | 45 | 40 | 74 | 30 | 0 | 98.36
16:00 | 0 | 95 | 0 | 0 | 300 | 12 | 0 | 372 | 272 |  | 0 | 225 | 0 | 82 | 15 | 30 | 0 | 0 | 0 | 8 | 0 | 0 | 77 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 28 | 17 | 33 | 8 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 5 | 140 | 0 | 0 | 0 | 340 | 0 | 8 | 51 | 26 | 57 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 76 | 88 | 8 | 20 | 0 | 20 | 32 | 47 | 47 | 0 | 152 | 31 | 72 | 0 | 195 | 18 | 0 | 0 | 300 | 16 | 2 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 6 | 100 | 51 | 135 | 0 | 85 | 0 | 0 | 1 | 162 | 54 | 0 | 0 | 0 | 40 | 100 | 104 | 10 | 0 | 41 | 0 |  | 570 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 158 | 0 | 402 | 90 | 0 | 35 | 0 | 35 | 0 | 1 | 0 | 390 | 35 | 0 | 55 |  | 4684 | 2178 | 6862 | 2566 | 570 | 1602 | 1487 | 455 | 45 | 43 | 76 | 18 | 0 | 98.36
17:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 391 | 270 |  | 0 | 225 | 0 | 82 | 15 | 37 | 0 | 0 | 0 | 10 | 16 | 85 | 84 | 0 | 0 | 0 | 54 | 17 | 22 | 0 | 25 | 28 | 17 | 33 | 30 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 20 | 39 | 0 | 6 | 140 | 0 | 0 | 0 | 330 | 0 | 8 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 12 | 21 | 11 | 33 | 21 | 100 | 90 | 24 | 20 | 0 | 20 | 32 | 53 | 50 | 0 | 152 | 33 | 72 | 0 | 215 | 18 | 0 | 0 | 275 | 16 | 5 | 0 | 95 | 0 | 0 | 10 | 0 | 23 | 0 | 100 | 52 | 138 | 0 | 85 | 12 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 70 | 15 | 104 | 1 | 6 | 0 | 0 |  | 569 | 0 | 195 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 155 | 0 | 292 | 90 | 0 | 35 | 0 | 70 | 0 | 0 | 25 | 380 | 30 | 0 | 55 |  | 4827 | 2140 | 6967 | 2491 | 569 | 1474 | 1714 | 445 | 45 | 128 | 100 | 1 | 0 | 98.35
18:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 368 | 270 |  | 0 | 225 | 0 | 82 | 45 | 55 | 0 | 0 | 0 | 70 | 16 | 115 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 32 | 17 | 33 | 34 | 0 | 45 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 50 | 39 | 0 | 6 | 140 | 0 | 0 | 0 | 340 | 0 | 45 | 50 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 22 | 110 | 90 | 90 | 22 | 0 | 30 | 32 | 53 | 50 | 0 | 150 | 31 | 72 | 0 | 216 | 18 | 0 | 0 | 300 | 16 | 8 | 0 | 210 | 0 | 0 | 31 | 0 | 63 | 0 | 100 | 75 | 140 | 0 | 101 | 17 | 0 | 0 | 184 | 54 | 0 | 0 | 0 | 100 | 20 | 104 | 0 | 20 | 0 | 0 |  | 811 | 0 | 185 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 66 | 25 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 154 | 0 | 401 | 90 | 0 | 62 | 0 | 50 | 0 | 0 | 70 | 390 | 34 | 0 | 55 |  | 5712 | 2625 | 8337 | 2588 | 811 | 1665 | 2380 | 455 | 45 | 283 | 110 | 0 | 0 | 98.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 418 | 270 |  | 0 | 225 | 0 | 82 | 65 | 55 | 0 | 0 | 0 | 100 | 24 | 115 | 84 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 33 | 17 | 33 | 34 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 30 | 52 | 39 | 0 | 15 | 135 | 70 | 0 | 0 | 350 | 0 | 45 | 49 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 22 | 108 | 92 | 90 | 22 | 0 | 30 | 32 | 53 | 47 | 0 | 152 | 34 | 72 | 0 | 215 | 19 | 0 | 0 | 295 | 16 | 11 | 0 | 270 | 0 | 0 | 32 | 0 | 112 | 0 | 100 | 85 | 143 | 0 | 115 | 17 | 0 | 0 | 217 | 54 | 0 | 0 | 0 | 100 | 20 | 104 | 0 | 35 | 0 | 0 |  | 806 | 0 | 190 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 143 | 0 | 293 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 450 | 31 | 0 | 55 |  | 6020 | 2788 | 8808 | 2643 | 806 | 1585 | 2855 | 514 | 46 | 251 | 108 | 0 | 0 | 98.34
19:30 | 0 | 93 | 0 | 0 | 300 | 12 | 0 | 418 | 270 |  | 0 | 225 | 0 | 84 | 81 | 55 | 0 | 0 | 0 | 100 | 24 | 115 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 33 | 17 | 33 | 34 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 52 | 39 | 0 | 17 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 50 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 22 | 108 | 94 | 90 | 22 | 0 | 30 | 32 | 53 | 47 | 0 | 152 | 33 | 72 | 0 | 215 | 19 | 0 | 0 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 32 | 0 | 115 | 0 | 100 | 85 | 143 | 0 | 115 | 0 | 0 | 0 | 217 | 54 | 0 | 0 | 0 | 100 | 20 | 104 | 0 | 35 | 0 | 0 |  | 806 | 0 | 190 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 143 | 0 | 304 | 90 | 0 | 111 | 0 | 108 | 0 | 0 | 113 | 450 | 34 | 0 | 55 |  | 5974 | 2773 | 8747 | 2629 | 806 | 1603 | 2824 | 514 | 46 | 217 | 108 | 0 | 0 | 0
20:00 | 0 | 100 | 0 | 0 | 300 | 12 | 0 | 419 | 265 |  | 0 | 225 | 0 | 82 | 80 | 55 | 0 | 0 | 0 | 100 | 24 | 115 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 38 | 39 | 0 | 18 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 45 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 92 | 90 | 22 | 0 | 30 | 32 | 53 | 47 | 0 | 150 | 33 | 72 | 0 | 215 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 7 | 0 | 117 | 0 | 100 | 85 | 142 | 0 | 115 | 0 | 0 | 0 | 217 | 54 | 0 | 0 | 60 | 100 | 50 | 104 | 0 | 35 | 0 | 0 |  | 806 | 0 | 190 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 143 | 0 | 298 | 90 | 0 | 111 | 0 | 70 | 0 | 0 | 113 | 450 | 30 | 0 | 55 |  | 5910 | 2727 | 8637 | 2657 | 806 | 1580 | 2711 | 566 | 47 | 166 | 104 | 0 | 0 | 98.35
21:00 | 0 | 101 | 0 | 0 | 300 | 12 | 0 | 402 | 253 |  | 0 | 225 | 0 | 82 | 70 | 55 | 0 | 0 | 0 | 100 | 0 | 115 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 27 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 45 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 102 | 94 | 82 | 22 | 0 | 30 | 32 | 31 | 47 | 0 | 150 | 34 | 66 | 0 | 215 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | 82 | 0 | 100 | 51 | 148 | 0 | 85 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 113 | 100 | 66 | 70 | 0 | 17 | 0 | 0 |  | 806 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 66 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 143 | 0 | 288 | 90 | 0 | 111 | 0 | 41 | 0 | 0 | 113 | 450 | 27 | 0 | 55 |  | 5825 | 2706 | 8531 | 2804 | 806 | 1538 | 2446 | 656 | 47 | 132 | 102 | 0 | 0 | 98.34
22:00 | 0 | 101 | 0 | 0 | 300 | 12 | 0 | 382 | 242 |  | 0 | 225 | 0 | 82 | 0 | 40 | 0 | 0 | 0 | 50 | 0 | 84 | 84 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 46 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 96 | 92 | 34 | 22 | 0 | 30 | 32 | 31 | 50 | 0 | 150 | 34 | 66 | 0 | 215 | 19 | 0 | 0 | 280 | 16 | 11 | 0 | 260 | 0 | 0 | 0 | 0 | 25 | 0 | 100 | 51 | 148 | 0 | 85 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 0 | 100 | 66 | 70 | 0 | 0 | 0 | 0 |  | 806 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 66 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 144 | 0 | 308 | 90 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 400 | 39 | 0 | 55 |  | 5278 | 2527 | 7805 | 2789 | 806 | 1550 | 1817 | 616 | 47 | 84 | 96 | 0 | 0 | 98.34
23:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 328 | 244 |  | 0 | 225 | 0 | 82 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 64 | 84 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 32 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 86 | 93 | 30 | 22 | 0 | 30 | 32 | 31 | 50 | 0 | 152 | 33 | 67 | 0 | 162 | 19 | 0 | 0 | 285 | 16 | 11 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 51 | 100 | 0 | 85 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 50 | 66 | 70 | 0 | 0 | 0 | 0 |  | 617 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 143 | 0 | 394 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 400 | 35 | 0 | 55 |  | 4838 | 2287 | 7125 | 2683 | 617 | 1655 | 1359 | 614 | 47 | 64 | 86 | 0 | 0 | 98.34
24:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 371 | 245 |  | 0 | 225 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 16 | 85 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 33 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 32 | 110 | 80 | 0 | 0 | 350 | 0 | 45 | 48 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 82 | 93 | 8 | 22 | 0 | 30 | 32 | 31 | 50 | 0 | 152 | 34 | 68 | 0 | 163 | 19 | 0 | 0 | 290 | 16 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 51 | 100 | 0 | 85 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 20 | 66 | 70 | 0 | 0 | 0 | 0 |  | 429 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 65 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 143 | 0 | 312 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 400 | 38 | 0 | 55 |  | 4691 | 2017 | 6708 | 2722 | 429 | 1582 | 1216 | 615 | 46 | 16 | 82 | 0 | 0 | 98.34
KWH | 0 | 2455900 | 0 | 0 | 7201127 | 287500 | 0 | 8475896 | 6976000 |  | 0 | 4750000 | 0 | 1584960 | 450144 | 713470 | 0 | 0 | 0 | 591360 | 78048 | 720000 | 2064104 | 0 | 0 | 0 | 1204200 | 801525 | 259185 | 416880 | 600000 | 685620 | 411700 | 811500 | 146748 | 0 | 1093789 | 0 | 0 | 0 | 0 | 3195871 | 0 | 0 | 0 |  | 0 | 0 | 257216 | 49800 | 168000 | 828960 | 0 | 498240 | 2936142 | 1771205 | 0 | 0 | 8094000 | 0 | 434909 | 1154070 | 584856 | 1313280 | 0 | 1209874 | 0 | 0 | 224429 | 503064 | 245520 | 821100 | 510420 | 1888320 | 2302400 | 809280 | 417204 | 9550 | 542000 | 755760 | 1154400 | 1135008 | 0 | 3421000 | 734112 | 1718400 | 0 | 4269280 | 447000 | 0 | 0 | 7371000 | 355248 | 231500 | 0 | 2754981 | 0 | 0 | 146400 | 0 | 562608 | 87885 | 1860480 | 1874400 | 2457236 | 0 | 1944000 | 47616 | 0 | 27600 | 4064727 | 1169524 | 0 | 0 | 816480 | 1128000 | 628200 | 2137920 | 205820 | 122400 | 203236 | 0 |  | 13614545 | 0 | 5186016 | 0 | 259200 | 0 | 0 | 0 | 0 | 744 | 0 | 0 | 412300 | 45312 | 0 | 0 | 0 | 0 | 0 | 546732 | 362940 | 0 | 0 | 26880 | 0 | 515760 | 0 | 171468 | 1515491 | 0 | 558600 | 0 | 0 | 0 | 0 | 0 | 0 | 738175 | 0 | 3711255 | 0 | 8424273 | 1584000 | 0 | 1556352 | 0 | 689280 | 0 | 26699 | 390336 | 10409300 | 784091 | 0 | 1308000 |  | 117381587 | 52837749 | 170219336 | 64047314 | 13614545 | 37723210 | 37486521 | 12483391 | 1093789 | 1524692 | 1888320 | 357554 | 0
Fuel Cost | 0 | 3634732 | 0 | 0 | 7993250.97 | 379500 | 0 | 8560654.96 | 7185280 |  | 0 | 5177500 | 0 | 12029846.4 | 3101492.16 | 6035956.2 | 0 | 0 | 0 | 4452940.8 | 711797.76 | 7084800 | 19031038.88 | 0 | 0 | 0 | 8790660 | 6195788.25 | 2555564.1 | 312660 | 450000 | 0 | 0 | 0 | 1419053.16 | 0 | 295323.03 | 0 | 0 | 0 | 0 | 3483499.39 | 0 | 0 | 0 |  | 0 | 0 | 2494995.2 | 475590 | 1461600 | 6565363.2 | 0 | 1479772.8 | 4345490.16 | 2621383.4 | 0 | 0 | 8094000 | 0 | 561032.61 | 1327180.5 | 660887.28 | 1838592 | 0 | 2068884.54 | 0 | 0 | 2143296.95 | 638891.28 | 184140 | 1436925 | 382815 | 14162400 | 2440544 | 7348262.4 | 529849.08 | 152227 | 888880 | 1209216 | 2054832 | 1770612.48 | 0 | 3557840 | 1446200.64 | 3282144 | 0 | 7385854.4 | 978930 | 0 | 0 | 7444710 | 266436 | 175940 | 0 | 20827656.36 | 0 | 0 | 761280 | 0 | 5536062.72 | 1027375.65 | 15162912 | 20337240 | 17323513.8 | 0 | 17729280 | 449971.2 | 0 | 0 | 30729336.12 | 10186554.04 | 0 | 0 | 6997233.6 | 7512480 | 0 | 0 | 0 | 0 | 0 | 0 |  | 78419779.2 | 0 | 5445316.8 | 0 | 2037312 | 0 | 0 | 0 | 0 | 7797.12 | 0 | 0 | 639065 | 442245.12 | 0 | 0 | 0 | 0 | 0 | 4838578.2 | 2794638 | 0 | 0 | 260467.2 | 0 | 990259.2 | 0 | 129801.276 | 9138410.73 | 0 | 3027612 | 0 | 0 | 0 | 0 | 0 | 0 | 1107262.5 | 0 | 4342168.35 | 0 | 8340030.27 | 16536960 | 0 | 14769780.48 | 0 | 5348812.8 | 0 | 295023.95 | 2884583.04 | 45696827 | 0 | 0 | 0 |  | 357337951.47 | 207492730.236 | 564830681.706 | 72923486.486 | 78419779.2 | 44319477.4 | 280946568.74 | 57862849.73 | 295323.03 | 14426170.52 | 14162400 | 1474626.6 | 0
Yesterday Day Peak | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 315 | 275 |  | 0 | 225 | 0 | 82 | 0 | 28 | 0 | 0 | 0 | 15 | 0 | 0 | 92 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 3 | 100 | 100 | 0 | 0 | 325 | 0 | 8 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 10 | 21 | 11 | 33 | 20 | 70 | 89 | 42 | 20 | 2 | 20 | 32 | 49 | 47 | 0 | 152 | 20 | 73 | 0 | 122 | 18 | 0 | 0 | 315 | 15 | 8 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 18 | 100 | 90 | 135 | 0 | 115 | 0 | 0 | 4 | 161 | 35 | 0 | 0 | 0 | 70 | 0 | 104 | 38 | 0 | 38 | 0 |  | 569 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 140 | 0 | 409 | 90 | 0 | 111 | 0 | 37 | 0 | 4 | 0 | 360 | 15 | 0 | 55 |  | 7026 | DayPeak
Yesterday Evening Peak | 0 | 94 | 0 | 0 | 300 | 12 | 0 | 418 | 270 | 0 | 0 | 225 | 0 | 82 | 65 | 55 | 0 | 0 | 0 | 100 | 24 | 115 | 84 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 33 | 17 | 33 | 34 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 30 | 52 | 39 | 0 | 15 | 135 | 70 | 0 | 0 | 350 | 0 | 45 | 49 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 22 | 108 | 92 | 90 | 22 | 0 | 30 | 32 | 53 | 47 | 0 | 152 | 34 | 72 | 0 | 215 | 19 | 0 | 0 | 295 | 16 | 11 | 0 | 270 | 0 | 0 | 32 | 0 | 112 | 0 | 100 | 85 | 143 | 0 | 115 | 17 | 0 | 0 | 217 | 54 | 0 | 0 | 0 | 100 | 20 | 104 | 0 | 35 | 0 | 0 |  | 806 | 0 | 190 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 143 | 0 | 293 | 90 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 450 | 31 | 0 | 55 |  | 8808 | EvPeak
Forecast for Evening | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 102 | 50 | 19 | 15 | 110 | 80 | 0 | 0 | 360 | 200 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 22 | 148 | 110 | 95 | 20 | 0 | 30 | 30 | 51 | 44 | 163 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 280 | 104 | 0 | 160 |  | 100 |  | 821 | 16 | 230 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 68 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35 |  | 55
Forecast for Day | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 102 | 50 | 19 | 10 | 110 | 80 | 0 | 0 | 360 | 60 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 20 | 110 | 110 | 95 | 20 | 1.6 | 30 | 30 | 51 | 44 | 163 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 280 | 104 | 50 | 100 |  | 100 |  | 581 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 68 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35 |  | 55
Generation at 08:00(Today) | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 376 | 326 | 0 | 0 | 225 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 28 | 17 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 110 | 80 | 0 | 0 | 340 | 61 | 8 | 51 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 72 | 110 | 0 | 22 | 0 | 30 | 32 | 31 | 47 | 0 | 149 | 33 | 67 | 0 | 215 | 19 | 0 | 0 | 310 | 14 | 11 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 49 | 60 | 0 | 79 | 0 | 0 | 1 | 191 | 54 | 0 | 0 | 0 | 42 | 66 | 46 | 6 | 0 | 0 | 0 | 0 | 523 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 66 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 160 | 0 | 402 | 70 | 0 | 44 | 0 | 0 | 0 | 1 | 0 | 400 | 14 | 0 | 0 | 0
199
| Minimum Generation |  | 5588 | 5:00
| Highest Generation |  | 8808 | 19:00
| Day Peak Generation |  | 7026 | 12:00
| Evening Peak Generation |  | 8808 | 19:00
| HVDC Max Flow |  | 811 | 18:00
| HVDC EvPeak Flow |  | 806 | 19:00
| Load factor L.F |  | 80.52%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7026 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5419 | MW
Evening Peak Generation : |  | 8808 | MW Hour : | 19:00 | Available Max Generation : |  | 13822 | MW
E.P. Demand (at gen end) : |  | 8808 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8900 | MW
Maximum Generation : |  | 8808 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4922 | MW
Total Gen. (MKWH) : |  | 170.2193 | System Load Factor : | 80.52% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -164 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-29
Actual : | 98.32 | Ft.(MSL) , | Rule curve : | 103.3 | Ft.( MSL )
Gas Consumed : | Total = | 825.37 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 117242963.886
: |  | Coal : | 57862849.73 | Oil : | 295372739.26 | Total : | 470478552.876
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3158.893 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1068.4778 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 956.3014 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 863.737 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 780.7462 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 630.0201 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 359.6378 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 162.4081 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 485.8676 |  |  | 0 | 0%
Total | 0 |  | 8466.0891 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Ashuganj(N)-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Madunaghat-Chandraghona 132 kV Ckt-1 was under shut down from 08:20 to 16:28 for A/M.
b) Hathazari-AKSM 230 kV Ckt was under shut down from 08:39 to 15:46 for A/M.
c) Kallyanpur 132/33 kV GT-3 transformer was under shut down from 08:39 to 20:28 for A/M.
d) Comilla(S)-Tripura 132 kV Ckt-1 was under shut down from 08:05 to 14:16 for A/M.
e) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 08:26 to 16:56 for A/M.
f) Rajshahi(New)-Amnura 132 kV Ckt was under shut down from 08:23 to 16:56 for A/M.
g) B.Pukuria P/S-B.Pukuria S/S 230 kV Ckt-2 was under shut down from 09:14 to 16:12 for A/M.
h) Shyampur-Meghnaghat 230 kV Ckt-1 was shut down from 08:19 to 20:38 for A/M.
i) Barishal(N)-Madaripur 132 kV Ckt-1 was under shut down from 09:01 to 16:49 for A/M.
j) Gopalganj 400 kV S/S-Madaripur 132 kV Ckt-2 was under shut down from 08:29 to 17:00 for A/M.
k) Aminbazar 230/132 kV T02 transformer was under shut down from 09:38 to 16:52 for A/M.
l) Fenchuganj-Kulaura 132 kV Ckt-2 was under shut down from 09:29 to 13:43 for A/M.
m) Narshingdi 132 kV Bus-2 was under shut down from 09:20 to 16:40 for A/M.
n) Savar 132/33 kV T-2 transformer was under shut down from 09:10 to 16:32 for A/M.
o) Sitalakhya 132/33 kV GT-2 transformer was under shut down from 10:02 to 18:23 for A/M.
p) Feni-Chowmuhoni 132 kV Ckt-1 was under shut down from 09:15 to 17:05 for A/M.
q) Dohazari-Cox's Bazar 132 kV Ckt-2 was shut at down at 09:10 for A/M.
r) Bheramara HVDC 400 kV 10CF25 filter was under shut down from 09:40 to 14:46 for A/M.
s) Polashbari-Mohasthangarh 132 kV Ckt-1 was under shut down from 09:45 to 15:20 for A/M.
t) Baghabari 230/132 kV T01 transformer was under shut down from 08:30 to 17:30 for A/M.
u) Natore 132/33 kV T-4 transformer was shut down at 09:13 for A/M.
v) Jhenaidah-Bottail 132 kV Ckt was under shut down from 09:59 to 14:12 for protection test.
w) Faridpur132/33 kV T-3 transformer was under shut down from 09:40 to 17:03 for A/M.
x) Shyampur 230/132 kV T02 transformer was under shut down from 10:41 to 11:20 for D/W.
y) Bhaluka 132/33 kV T-1 transformer was under shut down from 11:50 12:04 for D/W.
z) Bhaluka 132/33 kV T-2 transformer was under shut down from 12:08 12:35 for D/W.
aa) Ashuganj unit-4 tripped at 12:01 due to FD fan tripped and was synchronized at 18:36.
ab) Kabirpur 132/33 kV T-1,T-2 & T-3 transformers were shut down at 10:36 due to Dc fail and metering |  |  |  |  | About 110 MW power interruption occurred under Kabirpur S/S area
panel problem due to 33 kV Ifad feeder on fire and T-1 & T-3 were switched on at 13:04 & 23:23 respectively. |  |  |  |  | from 10:38 to 13:04.
ac) Bheramara HVDC-Bheramara 230 kV Ckt-2 was under shut down from 12:01 to 15:12 for protection test.
ad) Sikalbaha 225 MW tripped at 15:00 due to problem with GBC and was GT was synchronized at 17:12
and ST was synchronized at 20:16.
ae) After maintenance work Barapukuria unit-3 was synchronized at 19:19.
af) After maintenance work Ishwardi 230/132 kV T02 transformer was switched on at 15:50.
ag) Payra united tripped at 04:42(29/12/2020) showing high voltage.
ah) After maintenance work Ashuganj 225 MW CCPP GT was synchronized at 05:05(29/12/2020).
ai) Mongla 33 kV Bus tripped at 05:59(29/12/2020) showing E/F relay where was the bird short Ckted and was |  |  |  |  | About 30 MW power interruption occurred under Mongla S/S area
switched on at 06:24. |  |  |  |  | from 05:59(29/12/2020) to 06:24.
aj) Rangpur S/S-Rangpur Confodence PP 132 kV Ckt-1 was shut down at 07:41(29/12/2020) for A/M.
ak) Sikalbaha-Dohazari 132 kV Ckt-1 was shut down at 07:37(29/12/2020) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 94 | 2455900 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7201127
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 287500 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 418 | 8475896
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 270 | 6976000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4750000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 82 | 1584960 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 65 | 450144 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 713470
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 84 | 2064104 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 416880 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 591360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 78048 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1204200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 720000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 801525
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 259185 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1285620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 34 | 146748 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 2754981
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 112 | 562608 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 47616 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2137920
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 122400 | Low demand
| Dhaka area Total |  |  |  | 6057 | 2687 | 47311392
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 87885
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 828960 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1093789 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 3195871 | Gas shortage & ST under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 257216
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 49800 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1860480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 498240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 52 | 168000 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27600
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 217 | 4064727 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1169524
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1128000
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 203236
| Chattogram area Total |  |  |  | 2266 | 755 | 14633328
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2936142
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 1771205 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 350 | 8094000
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 584856 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 57 | 1313280
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 434909 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1209874
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 2457236
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 49 | 1154070 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 1874400 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 503064
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245520
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 1888320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 224429 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 510420
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 816480 | Reserve.
| Cumilla Area Total |  |  |  | 2980 | 1231 | 26839305
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 92 | 2302400 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 417204
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 809280 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 32 | 146400
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1944000 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 205820
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 687 | 351 | 5834654
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 542000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 755760 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3421000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1154400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1135008
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 231500
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 34 | 734112 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1718400 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 215 | 4269280
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 447000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 355248 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7371000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 20 | 628200 | On test
| Sylhet Area Total |  |  |  | 1988 | 996 | 22762908
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 806 | 13614545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 259200
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 744 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 190 | 5186016 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1584000 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1201 | 20644505
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 45312 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 412300 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 69 | 738175 | Gas shortage
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 450 | 10409300
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 31 | 784091 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 55 | 1308000 | On test.
| Barisal Area Total |  |  |  | 1054 | 649 | 13697178
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 34 | 362940 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 143 | 3711255 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 293 | 8424273 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 515760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 171468
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 26880 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 34 | 546732 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1556352
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 390336
| Rajshahi Area Total |  |  |  | 2183 | 761 | 15705996
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 64 | 1515491
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 558600 | Under maint.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 689280
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26699
| Rangpur Area Total |  |  |  | 605 | 177 | 2790070
| Total |  |  |  | 20104 | 8808 | 170219336
| Eastern Grid Total |  |  |  | 13978 | 6020 | 117381587
| Western Grid Total |  |  |  | 6126 | 2788 | 52837749
| National Grid Total |  |  |  | 20104 | 8808 | 170219336
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-28
| (a) ENTIRE EASTERN GRID : |  | 5585 | MW | (b) ENTIRE WESTERN GRID : |  | 2782 | MW
| i) Dhaka area |  | 2957 | MW | i) Khulna area |  | 1092 | MW
| ii) Chittagong area |  | 878 | MW | ii) Rajshahi area |  | 866 | MW
| iii) Comilla area |  | 727 | MW | iii) Barisal area |  | 239 | MW
| iv) Mymensingh area |  | 710 | MW | iv) Rangpur area |  | 585 | MW
| v) Sylhet area |  | 313 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8367 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 100 | 10:00 | Jamalpur | 75 | 19:00 | Benapol | 38 | 18:30
| Munsiganj | 80 | 20:00 | Sherpur | 90 | 18:00 | Jhenida | 84 | 18:30
| Sonargaon | 64 | 19:30 | Srimongal | 31 | 18:30 | Bottail | 78 | 18:00
| Shyampur | 162 | 13:00 | Shahjibazar | 76 | 20:00 | G.K Project | 46 | 18:30
| Bhulta | 161 | 12:00 | Fenchuganj | 23 | 18:00 | Faridpur | 134 | 18:30
| Madanganj | 61 | 17:00 | Kulawara | 27 | 18:30 | Madaripur | 62 | 20:00
| Shitalakhya | 81 | 19:30 | Sylhet | 76 | 19:30 | Sariatpur | 42 | 19:30
| Rahim steel | 17 | 16:00 | Chatak | 19 | 18:00 | Gopalganj | 59 | 20:00
| Matuail | 48 | 10:00 | Sunamganj | 26 | 19:00 | Bagerhat | 79 | 18:30
| Ghorasal | 60 | 18:30 | Biani Bazar | 37 | 18:00 | Mongla | 40 | 18:30
| Narsingdi | 116 | 19:30 | Comilla (S) | 110 | 18:00 | Satkhira | 76 | 19:30
| Haripur (SBU) | 100 | 18:30 | Comilla(N) | 65 | 19:30 | Gallamari | 20 | 13:00
| Ullon | 40 | 18:30 | Chandpur | 66 | 19:00 | Magura | 40 | 18:30
| Hasnabad | 137 | 18:00 | Feni | 76 | 18:00 | Norail | 25 | 18:30
| Magbazar | 64 | 13:00 | Chowmuhani | 118 | 19:30 | Chuadanga | 68 | 18:30
| Maniknagar | 72 | 18:00 | Ashuganj | 37 | 18:00 | Barisal(N) | 28 | 19:30
| Bangabhaban | 20 | 15:00 | Daudkandi | 106 | 18:00 | Barisal (S) | 74 | 21:00
| Narinda | 64 | 12:00 | B.Baria | 91 | 18:30 | Patuakhali | 80 | 19:30
| Dhanmondi | 89 | 13:00 | Ramganj | 62 | 19:00 | Bhandaria | 42 | 20:00
| Lalbag | 68 | 18:00 | Chaddagram | 27 | 15:00 | Borhan Uddin | 27 | 22:00
| Madartek | 44 | 19:30 | PHP | 10 | 2:00 | Ishurdi | 47 | 20:00
| Dhaka University | 0 | #NUM! | Madunaghat | 49 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.5 | Hathazari | 57 | 0.79167 | Natore | 78 | 0.75
| Fatullah | 39 | 10:00 | Khulshi | 169 | 14:00 | Bogra | 116 | 18:30
| Mirpur | 70 | 18:00 | Halishahar | 91 | 18:00 | Noagaon | 80 | 19:30
| Kalyanpur | 56 | 18:00 | Baraulia | 135 | 12:00 | Rajshahi | 98 | 20:00
| Gulshan | 72 | 13:00 | Sikalbaha | 22 | 19:00 | Rajshahi New | 9 | 19:00
| Uttara | 62 | 18:00 | Dohazari | 58 | 20:00 | C.Nawabganj | 51 | 19:00
| Uttara New | 24 | 18:00 | Cox'sbazar | 74 | 18:30 | Amnura | 30 | 19:00
| Kamrangirchar | 70 | 13:00 | Chandraghona | 22 | 18:00 | Pabna | 77 | 18:00
| Savar | 90 | 14:00 | Kaptai | 3.6 | 18:00 | Shahjadpur | 76 | 19:00
| Bhasantec | 95 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 66 | 19:00
| Agargaon | 42 | 18:00 | Bakulia | 79 | 11:00 | Niyamatpur | 44 | 18:30
| Satmosjid | 65 | 0.54167 | Julda | 19 | 0.5 | Joypurhat | 44 | 0.79167
| Tongi | 74 | 12:00 | TK chemical | 20.2 | 18:30 | Sherpur(Bogura) | 34 | 20:00
| Kabirpur | 151 | 9:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 19:00
| Basundhara | 90 | 18:00 | Shahmirpur | 17.5 | 18:00 | Rangpur | 108 | 18:30
| Manikganj | 50 | 18:30 | Khagrachhari | 20 | 1:00 | Lalmonirhat | 47 | 18:00
| Joydevpur | 112 | 18:00 | Matarbari | 24.5 | 18:30 | Saidpur | 84 | 18:00
| New Tongi | 89 | 18:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 87 | 19:00
| Kodda | 188 | 17:00 | Rangamati | 8 | 12:00 | Thakurgaon | 58 | 20:00
| Dhamrai | 82 | 18:30 | Abul Khair 230 | 155 | 0:00 | Palashbari | 84 | 18:00
| Rajendrapur | 78 | 19:00 | BSRM | 149 | 16:00 | Barapukuria | 38 | 20:00
| Valuka | 92 | 18:30 | GPH Ispat | 82 | 12:00 | Panchagar | 45 | 18:30
| Tangail | 144 | 18:30 | Goalpara | 17 | 13:00 | Joldhaka | 25 | 18:30
| Mymensing | 143 | 18:30 | Central s/s | 78 | 18:30 | Kurigram | 40 | 18:30
| Kishorganj | 92 | 21:00 | Noapara | 49 | 19:00
| Netrokona | 88 | 18:00 | Jessore | 82 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 1:00 | 411 | 4:00 | Kaliakoir | 391 | 0.25 | 369 | 0.66667
| Bheramara | 411 | 19:00 | 396 | 13:00 | Bhulta | 382 | 0.875 | 366 | 0.66667
| Ashuganj(N) | 385 | 17:00 | 372 | 12:00 | Gopalganj | 414 | 0.16667 | 404 | 0.75
| Payra | 418 | 19:00 | 411 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 228 | 15:00 | Comilla (N) | 238 | 21:00 | 230 | 10:00
| Ishurdi | 237 | 4:00 | 228 | 12:00 | Hathazari | 226 | 18:30 | 211 | 10:00
| Ashuganj | 240 | 20:00 | 230 | 15:00 | Megnaghat | 234 | 1:00 | 230 | 1:00
| Serajganj | 234 | 17:00 | 230 | 8:00 | Fenchuganj | 244 | 20:00 | 239 | 15:00
| Baghabari | 242 | 4:00 | 238 | 8:00 | Siddhirganj | 231 | 1:00 | 222 | 16:00
| Barapukuria | 231 | 19:30 | 225 | 8:00 | Maniknagar | 229 | 20:00 | 220 | 15:00
| Bogra | 234 | 5:00 | 224 | 18:00 | Agargaon | 230 | 5:00 | 218 | 16:00
| Rajshahi | 231 | 17:00 | 219 | 12:00 | Barisal | 250 | 1:00 | 244 | 12:00
| Khulna South | 234 | 17:00 | 222 | 12:00 | AKSML | 226 | 19:00 | 214 | 9:00
| Rampura | 230 | 2:00 | 222 | 12:00 | BSRM | 229 | 18:30 | 216 | 16:00
| Haripur | 229 | 24:00 | 221 | 12:00 | Bibiyana | 246 | 19:30 | 239 | 6:00
| Hasnabad | 231 | 19:00 | 220 | 15:00 | Bhulta | 231 | 19:00 | 222 | 17:00
| Shyampur | 229 | 19:00 | 220 | 16:00 | Ashuganj (S) | 236 | 19:00 | 227 | 16:00
| Aminbazar | 230 | 19:30 | 217 | 16:00 | Kaliakoir | 227 | 18:30 | 213 | 16:00
| Tongi | 230 | 18:00 | 215 | 12:00 | GPH | 227 | 18:30 | 214 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 19:00 | 133 | 12:00 | Madanhat | 139 | 0.79167 | 131 | 0.41667
| Munsiganj | 140 | 19:00 | 133 | 12:00 | Hathazari | 138 | 0.79167 | 131 | 0.41667
| Sonargaon | 138 | 21:00 | 134 | 11:00 | Khulshi | 135 | 0.25 | 128 | 0.41667
| Shyampur | 134 | 20:00 | 127 | 12:00 | Halishahar | 138 | 0.77083 | 130 | 0.41667
| Bhulta | 132 | 4:00 | 127 | 12:00 | Baraulia | 138 | 0.25 | 130 | 0.45833
| Madanganj | 139 | 20:00 | 128 | 12:00 | Sikalbaha | 138 | 0.77083 | 131 | 0.5
| Shitalakhya | 142 | 17:00 | 134 | 10:00 | Dohazari | 133 | 0.58333 | 129 | 0.41667
| Rahim steal | 138 | 1:00 | 134 | 12:00 | Cox'sbazar | 130 | 0.25 | 118 | 0.45833
| Matuail | 139 | 19:00 | 133 | 12:00 | Chandraghona | 138 | 0.77083 | 130 | 0.41667
| Ghorasal | 138 | 1:00 | 134 | 15:00 | Kaptai | 136 | 0.875 | 130 | 0.45833
| Narsinghdi | 137 | 1:00 | 130 | 12:00 | A. Khaer Stl. | 136 | 0 | 130 | 0.33333
| Haripur (SBU) | 139 | 18:30 | 134 | 12:00 | Bakulia | 137 | 0.77083 | 130 | 0.5
| Ullon | 132 | 6:00 | 125 | 15:00 | Julda | 138 | 0.77083 | 131 | 0.45833
| Hasnabad | 140 | 18:00 | 134 | 12:00 | TK Chemical | 137 | 0.29167 | 131 | 0.5
| Magbazar | 132 | 3:00 | 125 | 16:00 | Modern Steel | 137 | 0.77083 | 131 | 0.375
| Maniknagar | 137 | 1:00 | 132 | 15:00 | Shahmirpur | 138 | 0.77083 | 131 | 0.45833
| Bangabhaban | 137 | 1:00 | 132 | 15:00 | Khagrachhari | 137 | 0.041667 | 129 | 0.5
| Narinda | 137 | 1:00 | 132 | 15:00 | Matarbari | 133 | 0.25 | 123 | 0.45833
| Dhanmondi | 132 | 6:00 | 125 | 15:00 | Baroiar Hat | 137 | 0.77083 | 133 | 0.45833
| Lalbag | 131 | 24:00 | 121 | 16:00 | Rangamati | 137 | 18:30 | 129 | 12:00
| Madartek | 132 | 1:00 | 126 | 12:00 | Goalpara S/S | 139 | 19:00 | 131 | 12:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Khulna Central S/S | 138 | 3:00 | 131 | 0.5
| Aftabnagar | 131 | 1:00 | 126 | 12:00 | Noapara | 138 | 6:00 | 128 | 0.5
| Fatuiiah | 134 | 7:00 | 128 | 12:00 | Jessore | 135 | 6:00 | 124 | 0.5
| Mirpur | 131 | 1:00 | 125 | 12:00 | Benapol | 134 | 0.125 | 124 | 0.54167
| Kalyanpur | 132 | 6:00 | 125 | 12:00 | Jhenida | 133 | 1:00 | 123 | 0.5
| Gulshan | 131 | 1:00 | 125 | 12:00 | Bottail | 137 | 0.041667 | 130 | 0.75
| Uttara | 131 | 6:00 | 124 | 12:00 | G.K Project | 140 | 0.041667 | 136 | 0.75
| Uttara New | 134 | 5:00 | 126 | 12:00 | Faridpur | 136 | 0.041667 | 132 | 0.66667
| Kamrangirchar | 140 | 6:00 | 134 | 12:00 | Madaripur | 141 | 0.20833 | 134 | 0.54167
| Savar | 132 | 19:00 | 124 | 12:00 | Shariyatpur S/S | 141 | 4:00 | 135 | 0.75
| Bhasantec | 134 | 20:00 | 127 | 12:00 | Gopalganj | 141 | 0.16667 | 136 | 0.5
| Agargaon | 135 | 20:00 | 128 | 12:00 | Bagerhat | 140 | 17:00 | 130 | 0.45833
| Satmosjid | 134 | 20:00 | 128 | 12:00 | Mongla | 136 | 4:00 | 129 | 0.75
| Tongi | 140 | 18:00 | 129 | 15:00 | Satkhira | 137 | 5:00 | 129 | 18:00
| Kabirpur | 134 | 20:00 | 0 | 13:00 | Gallamari | 139 | 0.70833 | 131 | 0.75
| Basundhara | 138 | 19:30 | 127 | 16:00 | Magura | 135 | 4:00 | 121 | 0.54167
| Manikganj | 143 | 19:00 | 129 | 12:00 | Norail | 133 | 0.25 | 121 | 0.75
| Joydevpur | 141 | 21:00 | 131 | 16:00 | Chuadanga | 132 | 2:00 | 118 | 0.75
| New Tongi | 139 | 19:00 | 129 | 12:00 | Barisal(N) | 142 | 3:00 | 137 | 12:00
| Kodda | 138 | 19:00 | 120 | 12:00 | Barisal (S) | 141 | 0.25 | 137 | 0.75
| Dhamrai | 133 | 24:00 | 125 | 16:00 | Patuakhali(S) | 139 | 0.125 | 136 | 0.5
| Rajendrapur | 137 | 23:00 | 128 | 16:00 | Bhandaria | 140 | 0.25 | 135 | 0.8125
| Valuka | 131 | 17:00 | 119 | 16:00 | Ishurdi | 138 | 17:00 | 134 | 12:00
| Tangail | 133 | 0:00 | 125 | 16:00 | Ruppur Paromanobik | 138 | 6:00 | 134 | 12:00
| Mymensing | 133 | 17:00 | 123 | 7:00 | Natore | 139 | 18:30 | 133 | 12:00
| Kishorganj | 132 | 17:00 | 120 | 7:00 | Bogra | 138 | 5:00 | 131 | 8:00
| Netrokona | 130 | 11:00 | 120 | 7:00 | Noagaon | 134 | 19:30 | 126 | 8:00
| Jamalpur | 141 | 17:00 | 125 | 5:00 | Rajshahi | 140 | 18:30 | 134 | 12:00
| Sherpur | 140 | 17:00 | 123 | 1:00 | Rajshahi New | 140 | 19:00 | 136 | 12:00
| Srimongal | 137 | 1:00 | 135 | 15:00 | C.Nawabganj | 140 | 19:00 | 134 | 12:00
| Shahjibazar | 134 | 8:00 | 130 | 16:00 | Amnura | 143 | 19:00 | 135 | 12:00
| Fenchuganj | 138 | 1:00 | 135 | 15:00 | Pabna | 137 | 6:00 | 132 | 12:00
| Khulawara | 138 | 1:00 | 136 | 11:00 | Shahjadpur | 140 | 19:00 | 138 | 13:00
| Sylhet | 136 | 1:00 | 134 | 16:00 | Serajganj | 135 | 19:00 | 130 | 18:00
| Chatak | 136 | 5:00 | 134 | 11:00 | Niyamatpur | 133 | 3:00 | 125 | 8:00
| Sunamganj | 135 | 1:00 | 134 | 10:00 | Joypurhat | 136 | 3:00 | 128 | 8:00
| Biani Bazar | 136 | 2:00 | 134 | 12:00 | Sherpur(Bogura) | 137 | 19:00 | 132 | 12:00
| Comilla(s) | 131 | 6:00 | 125 | 10:00 | Mohastangor | 136 | 19:30 | 128 | 8:00
| Comilla(n) | 142 | 18:30 | 138 | 10:00 | Rangpur | 130 | 5:00 | 120 | 18:00
| Chandpur | 143 | 1:00 | 141 | 16:00 | Lalmonirhat | 130 | 6:00 | 122 | 8:00
| Feni | 139 | 19:00 | 135 | 16:00 | Saidpur | 130 | 6:00 | 117 | 18:00
| Chowmuhani | 139 | 19:00 | 135 | 11:00 | Purbasadipur | 129 | 4:00 | 119 | 18:00
| Ashuganj | 135 | 13:00 | 131 | 15:00 | Thakurgaon | 130 | 6:00 | 119 | 18:00
| Daudkandi | 140 | 19:00 | 136 | 15:00 | Palashbari | 134 | 19:30 | 125 | 18:00
| B.Baria | 131 | 7:00 | 128 | 15:00 | Barapukuria | 131 | 19:30 | 125 | 18:00
| Ramganj | 138 | 18:30 | 137 | 20:00 | Panchagar | 129 | 5:00 | 115 | 18:00
| Chaddagram | 138 | 15:00 | 137 | 18:00 | Joldhaka | 131 | 6:00 | 121 | 9:00
| PHP | 138 | 1:00 | 133 | 10:00 | Kurigram | 129 | 0.25 | 117 | 0.75

## L-Curve
Date | 2020-12-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 8 | 4691 | 2017 | 6708 |  |  |  | QF-LDC-11
0:30 | 26.5 | 4599 | 1859 | 6458 | Date: | 2020-12-28
1:00 | 45 | 4507 | 1701 | 6208
1:30 | 33.5 | 4317.5 | 1712 | 6029.5
2:00 | 22 | 4128 | 1723 | 5851
2:30 | 15 | 4046 | 1733 | 5779 | [5 empty] | Gen. at Eve. Peak | 8808 | 9500 MW (19:30 )
3:00 | 8 | 3964 | 1743 | 5707 | [6 empty] | 19:00
3:30 | 21.5 | 3976 | 1687 | 5663 | [5 empty] | Gen. at Day Peak | 7026 | 7952.5 MW (12:00 )
4:00 | 35 | 3988 | 1631 | 5619 | [6 empty] | 12:00
4:30 | 21.5 | 3969 | 1634.5 | 5603.5 | [5 empty] | Highest Generation | 8808
5:00 | 8 | 3950 | 1638 | 5588 | [6 empty] | 19:00
5:30 | 11 | 4057 | 1673 | 5730
6:00 | 14 | 4164 | 1708 | 5872
6:30 | 24.5 | 4187 | 1788 | 5975
7:00 | 35 | 4210 | 1868 | 6078
7:30 | 45 | 4327.5 | 1972 | 6299.5
8:00 | 55 | 4445 | 2076 | 6521
8:30 | 53 | 4632.5 | 2118.5 | 6751
9:00 | 51 | 4820 | 2161 | 6981
9:30 | 134 | 4791 | 2150 | 6941
10:00 | 217 | 4762 | 2139 | 6901
10:30 | 178 | 4777 | 2098 | 6875
11:00 | 139 | 4792 | 2057 | 6849
11:30 | 177.5 | 4811.5 | 2126 | 6937.5
12:00 | 216 | 4831 | 2195 | 7026
12:30 | 109.5 | 4981.5 | 2168.5 | 7150
13:00 | 3 | 5132 | 2142 | 7274
13:30 | 80.5 | 5075.5 | 2124.5 | 7200
14:00 | 158 | 5019 | 2107 | 7126
14:30 | 229 | 4879.5 | 2081 | 6960.5
15:00 | 300 | 4740 | 2055 | 6795
15:30 | 332.5 | 4712 | 2116.5 | 6828.5
16:00 | 365 | 4684 | 2178 | 6862
16:30 | 265 | 4755.5 | 2159 | 6914.5
17:00 | 165 | 4827 | 2140 | 6967
17:30 | 138.5 | 5269.5 | 2382.5 | 7652
18:00 | 112 | 5712 | 2625 | 8337
18:30 | 137 | 5866 | 2706.5 | 8572.5
19:00 | 162 | 6020 | 2788 | 8808
19:30 | 117 | 5974 | 2773 | 8747
20:00 | 164 | 5910 | 2727 | 8637 |  |  |  | Executive Engineer
20:30 | 136.5 | 5867.5 | 2716.5 | 8584 |  |  |  | Network Operation Division
21:00 | 109 | 5825 | 2706 | 8531
21:30 | 100 | 5551.5 | 2616.5 | 8168
22:00 | 91 | 5278 | 2527 | 7805 |  |  |  |  | Page 6 of 7
22:30 | 106.5 | 5058 | 2407 | 7465
23:00 | 122 | 4838 | 2287 | 7125
23:30 | 65 | 4764.5 | 2152 | 6916.5
24:00 | 8 | 4691 | 2017 | 6708
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-12-28 |  | Energy | 170219336
[11 empty] | 2020-12-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2722 | 429 | 1582 | 1359 | 615 | 46 | 16 | 0 | 82 | 0
0:30 | 2636 | 428.5 | 1594 | 1204 | 538.5 | 44.5 | 8 | 0 | 76 | 0 | Date: | 2020-12-28
1:00 | 2550 | 428 | 1606 | 1049 | 462 | 43 | 0 | 0 | 70 | 0
1:30 | 2554.5 | 428 | 1629.5 | 843.5 | 462 | 43 | 0 | 0 | 69 | 0 | [7 empty] | Total Energy | 170.2193 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2559 | 428 | 1653 | 638 | 462 | 43 | 0 | 0 | 68 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2561.5 | 428 | 1660 | 556 | 462 | 43.5 | 0 | 0 | 68 | 0 | [7 empty] | Energy Requirement | 170.2193
3:00 | 2564 | 428 | 1667 | 474 | 462 | 44 | 0 | 0 | 68 | 0
3:30 | 2578.5 | 381 | 1675 | 469 | 447.5 | 44 | 0 | 0 | 68 | 0 | [6 empty] | Shortage
4:00 | 2593 | 334 | 1683 | 464 | 433 | 44 | 0 | 0 | 68 | 0
4:30 | 2595 | 334 | 1675 | 454 | 433 | 44.5 | 0 | 0 | 68 | 0
5:00 | 2597 | 334 | 1667 | 444 | 433 | 45 | 0 | 0 | 68 | 0
5:30 | 2649 | 334 | 1699 | 502 | 432.5 | 45.5 | 0 | 0 | 68 | 0
6:00 | 2701 | 334 | 1731 | 560 | 432 | 46 | 0 | 0 | 68 | 0
6:30 | 2683 | 381 | 1671 | 694.5 | 432 | 46 | 0 | 0 | 67 | 0.5 |  |  |  |  | Coal
7:00 | 2665 | 428 | 1611 | 829 | 432 | 46 | 0 | 0 | 66 | 1
7:30 | 2691 | 475.5 | 1623.5 | 947.5 | 447 | 46.5 | 0 | 0 | 63 | 5.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2717 | 523 | 1636 | 1066 | 462 | 47 | 0 | 0 | 60 | 10
8:30 | 2730 | 523.5 | 1610.5 | 1264 | 472 | 47.5 | 25.5 | 0 | 62 | 16
9:00 | 2743 | 524 | 1585 | 1462 | 482 | 48 | 51 | 0 | 64 | 22
9:30 | 2697.5 | 546.5 | 1526 | 1529.5 | 446.5 | 48 | 52 | 0 | 66 | 29
10:00 | 2652 | 569 | 1467 | 1597 | 411 | 48 | 53 | 0 | 68 | 36
10:30 | 2620 | 569 | 1467 | 1587.5 | 412.5 | 48 | 53 | 0 | 68.5 | 49.5
11:00 | 2588 | 569 | 1467 | 1578 | 414 | 48 | 53 | 0 | 69 | 63
11:30 | 2569 | 569 | 1524.5 | 1621.5 | 419 | 47.5 | 53 | 0 | 69.5 | 64.5
12:00 | 2550 | 569 | 1582 | 1665 | 424 | 47 | 53 | 0 | 70 | 66
12:30 | 2608.5 | 569.5 | 1525.5 | 1761.5 | 449 | 46 | 52.5 | 0 | 72.5 | 65
13:00 | 2667 | 570 | 1469 | 1858 | 474 | 45 | 52 | 0 | 75 | 64
13:30 | 2667 | 570 | 1469 | 1858 | 474 | 45 | 52 | 0 | 75 | 64
14:00 | 2667 | 570 | 1469 | 1858 | 474 | 45 | 52 | 0 | 75 | 64
14:30 | 2652.5 | 571.5 | 1481 | 1673 | 444 | 45 | 46 | 0 | 74.5 | 47
15:00 | 2638 | 573 | 1493 | 1488 | 414 | 45 | 40 | 0 | 74 | 30
15:30 | 2602 | 571.5 | 1547.5 | 1487.5 | 434.5 | 45 | 41.5 | 0 | 75 | 24
16:00 | 2566 | 570 | 1602 | 1487 | 455 | 45 | 43 | 0 | 76 | 18
16:30 | 2528.5 | 569.5 | 1538 | 1600.5 | 450 | 45 | 85.5 | 0 | 88 | 9.5
17:00 | 2491 | 569 | 1474 | 1714 | 445 | 45 | 128 | 0 | 100 | 1
17:30 | 2539.5 | 690 | 1569.5 | 2047 | 450 | 45 | 205.5 | 0 | 105 | 0.5
18:00 | 2588 | 811 | 1665 | 2380 | 455 | 45 | 283 | 0 | 110 | 0
18:30 | 2615.5 | 808.5 | 1625 | 2617.5 | 484.5 | 45.5 | 267 | 0 | 109 | 0
19:00 | 2643 | 806 | 1585 | 2855 | 514 | 46 | 251 | 0 | 108 | 0
19:30 | 2629 | 806 | 1603 | 2824 | 514 | 46 | 217 | 0 | 108 | 0
20:00 | 2657 | 806 | 1580 | 2711 | 566 | 47 | 166 | 0 | 104 | 0
20:30 | 2730.5 | 806 | 1559 | 2578.5 | 611 | 47 | 149 | 0 | 103 | 0
21:00 | 2804 | 806 | 1538 | 2446 | 656 | 47 | 132 | 0 | 102 | 0
21:30 | 2796.5 | 806 | 1544 | 2131.5 | 636 | 47 | 108 | 0 | 99 | 0
22:00 | 2789 | 806 | 1550 | 1817 | 616 | 47 | 84 | 0 | 96 | 0
22:30 | 2736 | 711.5 | 1602.5 | 1588 | 615 | 47 | 74 | 0 | 91 | 0
23:00 | 2683 | 617 | 1655 | 1359 | 614 | 47 | 64 | 0 | 86 | 0
23:30 | 2702.5 | 523 | 1618.5 | 1359 | 614.5 | 46.5 | 40 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 25.4° C
24:00 | 2722 | 429 | 1582 | 1359 | 615 | 46 | 16 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 43 | 44 | 44 | 45 | 46 | 46 | 47 | 48 | 48 | 48 | 47 | 45 | 45 | 45 | 45 | 45 | 45 |  | 46 | 46 | 47 | 47 | 47 | 47 | 46 | 1093789
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [10 empty] | 17 | 18 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 87885
6 | Sikalbaha 225MW CCPP (Gas) | 163 | 163 | 163 | 162 | 162 | 163 | 162 | 162 | 162 | 163 | 163 | 163 | 163 | 165 | 163 |  |  | 80 |  |  |  |  | 158 | 163 | 163 | 162 | 3195871
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 102 |  | 102 | 68 | 34 | 17 |  |  |  | 257216
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 15 | 70 | 95 | 95 | 95 | 115 | 164 | 95 | 95 | 95 | 210 |  | 270 | 300 | 300 | 300 | 260 | 130 | 80 | 2754981
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 434909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 95 | 94 | 94 |  | 94 | 93 | 100 | 101 | 101 | 102 | 102 | 2455900
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 305 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7201127
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 115 | 100 | 140 | 140 | 140 | 140 | 140 | 140 |  | 135 | 110 | 110 | 110 | 110 | 110 | 110 | 2936142
29 | Ashuganj TPP Unit- 4 | 110 | 110 | 110 | 110 | 110 | 120 | 100 | 120 | 120 | 106 | 100 | 100 | [7 empty] | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 1771205
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 19 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 584856
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 325 | 330 | 350 | 375 | 350 | 350 | 325 | 350 | 350 | 350 | 340 | 330 | 340 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8094000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 54 | 54 | 54 | 52 | 54 | 54 | 54 | 54 | 54 | 53 | 55 | 56 | 57 | 56 | 57 |  | 57 | 57 | 56 | 56 | 56 | 56 | 56 | 1313280
36 | Chandpur 150 MW CCPP | 51 | 54 | 50 | 51 | 47 | 52 | 51 | 51 | 45 | 50 | 50 | 50 | 44 | 49 | 49 | 51 | 50 | 50 |  | 49 | 50 | 45 | 45 | 46 | 50 | 48 | 1154070
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 291 | 281 | 281 | 309 | 303 | 324 | 324 | 330 | 340 | 319 | 312 | 315 | 401 | 370 | 345 | 372 | 391 | 368 |  | 418 | 418 | 419 | 402 | 382 | 328 | 371 | 8475896
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4750000
41 | Haripur 360MW CCPP(HPL) | 353 | 355 | 354 | 354 | 355 | 364 | 294 | 322 | 300 | 260 | 290 | 275 | 276 | 250 | 250 | 272 | 270 | 270 |  | 270 | 270 | 265 | 253 | 242 | 244 | 245 | 6976000
42 | RPCL 210MW CCPP | 100 | 110 | 110 | 108 | 107 | 109 | 110 | 108 | 108 | 109 | 88 | 89 | 88 | 85 | 86 | 88 | 90 | 90 |  | 92 | 94 | 92 | 94 | 92 | 93 | 93 | 2302400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 17 | 28 | 36 | 38 | 36 | 26 | 14 | 10 | 1 | [9 empty] | 205820
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 542000
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 755760
46 | Shajibazar 330 MW CCPP | 151 | 151 | 152 | 151 | 150 | 150 | 147 | 148 | 150 | 152 | 151 | 152 | 151 | 150 | 150 | 152 | 152 | 150 |  | 152 | 152 | 150 | 150 | 150 | 152 | 152 | 3421000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 33 | 33 | 34 | 33 | 33 | 33 | 33 | 20 | 20 | 20 | 32 | 20 | 20 | 31 | 33 | 31 |  | 34 | 33 | 33 | 34 | 34 | 33 | 34 | 734112
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 73 | 73 | 73 | 74 | 74 | 74 | 74 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 66 | 66 | 67 | 68 | 1718400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 182 | 182 | 182 | 182 | 182 | 183 | 150 | 150 | 150 | 122 | 122 | 122 | 178 | 163 | 163 | 195 | 215 | 216 |  | 215 | 215 | 215 | 215 | 215 | 162 | 163 | 4269280
51 | Sylhet 20 MW GTPP | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 2 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 231500
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 53 | 53 | 50 | 47 | 53 | 53 |  | 53 | 53 | 53 | 31 | 31 | 31 | 31 | 1154400
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 355248
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 300 | 310 | 300 | 315 | 290 | 300 | 310 | 280 | 295 | 315 | 300 | 280 | 285 | 300 | 275 | 300 |  | 295 | 290 | 280 | 280 | 280 | 285 | 290 | 7371000
| Bibiyana South 400 MW | [12 empty] | 15 | 100 | 100 | 100 | 15 | 20 |  | 20 | 20 | 50 | 66 | 66 | 66 | 66 | 628200
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 10 | 17 | 17 | 17 | 22 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 259185
59 | Tangail Palli Power Gen 22 MW
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 416880
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 417204
63 | Impoprt (Tripura) | 70 | 68 | 68 | 68 | 68 | 68 | 66 | 60 | 64 | 68 | 69 | 70 | 75 | 75 | 74 | 76 | 100 | 110 |  | 108 | 108 | 104 | 102 | 96 | 86 | 82 | 1888320
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 41 | 40 | 41 | 12 | 10 | 3 | 2 | 3 | 7 | 4 | 5 | 5 | 6 | 6 |  | 15 | 17 | 18 | 27 | 17 | 32 | 32 | 498240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503064
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245520
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821100
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 19 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 32 | 32 | 28 | 28 | 28 | 28 | 32 |  | 33 | 33 | 32 | 23 | 23 | 33 | 33 | 685620
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811500
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287500
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [21 empty] | 60 | 113 |  |  |  | 816480
| Manikgonj 162MW PP(MPGL) | [16 empty] | 6 | 20 |  | 35 | 35 | 35 | 17 |  |  |  | 122400
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 8 | 15 | 15 | 15 | 15 | 15 | 8 | 8 | 10 | 70 |  | 100 | 100 | 100 | 100 | 50 |  |  | 591360
78 | Gazipur 52 MW PP | [12 empty] | 6 | 16 | 8 | 8 | 30 | 34 |  | 34 | 34 | [5 empty] | 146748
79 | Kodda 150MW PP | [16 empty] | 85 | 115 |  | 115 | 115 | 115 | 115 | 84 | 64 | 16 | 720000
80 | Jamalpur 95 MW PP(Powerpac) | 8 | [7 empty] | 19 | 32 | 32 | 42 | 72 | 40 | 8 | 8 | 24 | 90 |  | 90 | 90 | 90 | 82 | 34 | 30 | 8 | 809280
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 10 | 24 | 34 | 8 | 8 | 12 | 25 |  | 25 | 25 | [5 empty] | 224429
| Gazipur 100 MW PP | [16 empty] | 12 | 17 |  | 17 | [6 empty] | 47616
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27600
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 47 | 35 | 35 | 35 | 35 | 35 | 35 | 38 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1169524
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [12 empty] | 24 | 48 | 42 | 15 | 15 | 45 |  | 65 | 81 | 80 | 70 |  |  |  | 450144
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 94 | 100 | 100 | 92 | 86 | 86 | 84 | 77 | 84 | 86 |  | 84 | 85 | 85 | 85 | 84 | 84 | 85 | 2064104
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 100 | 50 |  |  |  | 2 | 7 | 29 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 84 | 82 | 82 | 82 | 82 | 40 | 1584960
| Meghnaghat 104 MW PP (OPCL) | 70 | 70 | 34 | 34 | 34 | 48 | 100 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 70 | 70 | 70 | 70 | 2137920
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 9 | 20 |  | 30 | [6 empty] | 49800
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 43 | 47 | 50 | 50 |  | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 1135008
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1209874
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 16 | 16 |  | 24 | 24 | 24 |  |  |  |  | 78048
95 | Patenga 50MW PP (Baraka) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 35 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 32 | 19 | 19 | 19 | 828960
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 20 | 50 |  | 52 | 52 | 38 |  |  |  |  | 168000
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | [5 empty] | 6 | 15 | 15 | 15 | 15 | 28 | 55 | 55 | 30 | 30 | 37 | 55 |  | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 713470
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 3 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 801525
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 9550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1204200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 10 | 31 |  | 32 | 32 | 7 |  |  |  |  | 146400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [12 empty] | 12 | 46 | 38 | 17 | 23 | 63 |  | 112 | 115 | 117 | 82 | 25 |  |  | 562608
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 |  |  |  |  | 20 | 72 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1860480
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 90 | 70 | 70 | 70 | 68 | 80 | 85 | 85 | 90 | 100 | 68 | 51 | 51 | 52 | 75 |  | 85 | 85 | 85 | 51 | 51 | 51 | 51 | 1874400
117 | Ashuganj 150MW PP (Midland) | 100 | 5 |  |  |  | 2 | 38 | 86 | 122 | 128 | 133 | 135 | 140 | 135 | 142 | 135 | 138 | 140 |  | 143 | 143 | 142 | 148 | 148 | 100 | 100 | 2457236
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 65 | 24 | 24 | 24 | 24 | 24 | 24 | 48 | 115 | 115 | 115 | 115 | 95 | 85 | 85 | 85 | 85 | 101 |  | 115 | 115 | 115 | 85 | 85 | 85 | 85 | 1944000
| Anwara 300 MW PP (United) | 215 | 124 | 88 | 88 | 88 | 122 | 161 | 161 | 161 | 161 | 161 | 161 | 196 | 196 | 162 | 162 | 162 | 184 |  | 217 | 217 | 217 | 216 | 216 | 180 | 180 | 4064727
| Juldah unit-2 (Acorn) | [7 empty] | 10 | 40 | 40 | 40 | 70 | 100 | 60 | 40 | 40 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 20 | 1128000
| Anlima Energy Ltd. | [9 empty] | 28 | 39 | 38 | 18 | 15 | 10 | 41 | [10 empty] | 203236
120 | Eastern Zone Total | 4507 | 4128 | 3964 | 3988 | 3950 | 4164 | 4210 | 4445 | 4820 | 4762 | 4792 | 4831 | 5132 | 5019 | 4740 | 4684 | 4827 | 5712 |  | 6020 | 5974 | 5910 | 5825 | 5278 | 4838 | 4691 | 117381587
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 24 | 49 |  | 115 | 84 | 49 | 16 |  |  |  | 259200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 |  |  |  |  | 10 | 53 | 90 | 90 | 90 | 53 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 1584000
130
131
132 | United Payra Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1308000
133 | Bhola Nutan Biddut BD LTD (GAS) | 37 | 36 | 36 | 35 | 36 | 37 | 35 | 18 | 16 | 36 | 14 | 15 | 21 | 34 | 33 | 35 | 30 | 34 |  | 31 | 34 | 30 | 27 | 39 | 35 | 38 | 784091
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 |  |  |  |  | 45312
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 30 | 30 | 32 | 30 | 39 |  | 69 | 76 | 78 | 81 | 80 | 81 | 81 | 738175
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 16 | 15 | 15 | 16 | 15 | 13 | 9 | 8 | 9 | 14 | 11 | 12 | 12 | 15 | 22 | 28 |  | 28 | 28 | 28 | 27 | 26 | 25 | 24 | 412300
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [26 empty] | 744
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 428 | 428 | 428 | 334 | 334 | 334 | 428 | 523 | 524 | 569 | 569 | 569 | 570 | 569 | 573 | 570 | 569 | 811 |  | 806 | 806 | 806 | 806 | 806 | 617 | 429 | 13614545
147 | Bheramara 410 MW CCPP | 170 | 185 | 200 | 205 | 220 | 240 | 250 | 250 | 245 | 245 | 230 | 225 | 215 | 205 | 205 | 200 | 195 | 185 |  | 190 | 190 | 190 | 185 | 185 | 170 | 170 | 5186016
148 | Payra 1320 MW | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 400 | 420 | 350 | 350 | 360 | 410 | 370 | 350 | 390 | 380 | 390 |  | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 10409300
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 63 | 63 | 62 | 62 | 62 | 62 | 61 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 65 |  | 64 | 64 | 64 | 66 | 66 | 64 | 65 | 1515491
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | [21 empty] | 52 | 140 | 150 | 150 | 150 | 558600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 158 | 155 | 154 |  | 143 | 143 | 143 | 143 | 144 | 143 | 143 | 3711255
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 317 | 363 | 369 | 377 | 368 | 406 | 385 | 418 | 387 | 328 | 313 | 409 | 288 | 311 | 340 | 402 | 292 | 401 |  | 293 | 304 | 298 | 288 | 308 | 394 | 312 | 8424273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 171468
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 12 | 12 | 12 | 12 | 12 | 20 | 34 | 25 | 25 | 25 | 25 |  | 34 | 34 | 34 | 34 | 34 |  |  | 362940
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 8 | [8 empty] | 26880
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 51 | 53 | 53 | 53 | 52 | 52 | 40 | 43 | 43 | 66 |  | 34 | 34 | 17 |  |  |  |  | 546732
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 1 | 35 | 54 | 106 | 111 | 111 | 111 | 113 | 70 | 35 | 35 | 35 | 62 |  | 111 | 111 | 111 | 111 | 111 | 50 | 50 | 1556352
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 25 | 70 |  | 113 | 113 | 113 | 113 |  |  |  | 390336
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 2 | 38 | 40 | 37 | 40 | 41 | 35 | 35 | 70 | 50 |  | 113 | 108 | 70 | 41 |  |  |  | 689280
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26699
178
178