## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-12-31 | Thursday
|  |  | Date (day): | 2020-12-31 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11685.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12866 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-12-30 | 2020-12-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 330 | 300 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 11 | 12 | 12 | 12 | 98 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 396 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 255 | 274 | 360 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 68 | 93 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 70 | 78 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 2 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 16 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 16 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 270 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 79 | 125 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2130 | 2851 | 3437 | 3697 | 1424 | 871
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 47 | 45 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 164 | 163 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 100 | 100
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 70 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 12 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 216 | 215 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 38 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 780 | 891 | 1240 | 1225 | 920 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 140 | 70 | 135 | 135 | 0 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 184 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 95 | 273 | 260 | 260 |  | 100 | GT Only
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 5 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 148 | 150 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 45 | 50 | 50 | 113 |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 100 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 18 | 18 |  | 4 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 100 | 110 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 18 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1027 | 1093 | 1568 | 1858 | 552 | 473
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 86 | 106 | 110 | 149 | 53 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 56 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 165 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 8 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 26 | 26 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 363 | 416 | 613.6 | 601 | 53 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 20 | 30 | 30
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 30 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 145 | 143 | 155 | 155 | 175 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 8 | 51 | 51
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 20 | 44 | 44
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 67 | 69 | 86 | 86
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 137 | 176 | 200 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 220 | 260 | 320 | 320
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 417 | 435 | 420 | 435
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1069 | 1197 | 1516 | 1531 | 175 | 442
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 572 | 813 | 589 | 830
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 175 | 270 | 270 | 140 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 60 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 52 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 862 | 1239 | 1359 | 1886 | 140 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 25 | 25 |  | 8 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 72 | 90 | 90 | 90 | 85 |  | Gas shortage
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 0 | 0 | 0 |  | 622 | Unit-1 & 2 Under maint
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 17 | 34 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 19 | 55 | 55 | 55
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 126 | 220 | 315 | 315 | 85 | 824
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 130 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 383 | 313 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 52 | 94 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 92 | 111 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 817 | 819 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 40 | 35 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 193 | 185 | 271 | 263 | 124 | 125
|  | Total |  |  |  |  | 20595 | 20104 | 7367 | 8911 | 11685.6 | 12866 | 4074 | 2924
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6885.8426 | 8329 | 10922.3838 | 12025.6889
| A. |  | 2020-12-30 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 8911 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5616 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8911 | MW
| 3 | Day peak Generation : |  |  | 7367 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8329 | MW
| 4 | Evening peak Generation : |  |  | 8911 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 171.9429 | MKWHr | By Solar | 0.45406 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.1834 | MKWHr |  | By Oil: | 47.9396 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 3.6729 | MKWHr |  | By Hydro: | 1.0921 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4074 | MW | Dhaka | 2960 | 2960 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2924 | MW | Chittagong | 876 | 876 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6998 | MW | Khulna | 1078 | 1078 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 792.18 | MMCFD |  |  | Rajshahi | 873 | 873 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 104921644.168 | ii) Oil : | Taka | 328350054.41 | Comilla | 721 | 721 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 19907118 | Total | Taka | 453178816.578 | Mymensingh | 699 | 699 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 4.33 | MKWHr. | Sylhet | 311 | 311 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -512 | MW (E to W) at | 19:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -512 | MW at | 19:00 | hrs | Rangpur | 575 | 575 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 26.6° C |  |  | Total | 8329 | 8329 |  | 0
| B. |  | 2020-12-31 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 26.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12866 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7400 | MW
| 4 | Reserve(Generation end) |  |  |  | 3866 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 173.6602 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5571 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.6865 | MKWHr. | ii) HVDC Flow at Peak Time |  | 813 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9142 | MKWHr. | iii) Maximum HVDC Flow : |  | 813 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.27 |  | (b) Today: | 98.21 |  | (c) Rule Curve: |  | 103.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-12-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 388 | 245 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 40 | 80 | 0 | 0 | 95 | 250 | 166 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 72 | 109 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 158 | 33 | 68 | 0 | 136 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 95 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 235 | 54 | 0 | 0 | 0 | 100 | 330 | 70 | 0 | 162 | 0 | 0 |  | 432 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 139 | 0 | 334 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 35 |  | 4723 | 1519 | 6242 | 2953 | 432 | 1383 | 1206 | 150 | 46 | 0 | 72 | 0 | 0 | 98.27
2:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 392 | 243 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 100 | 0 | 0 | 95 | 0 | 202 | 8 | 50 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 68 | 110 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 158 | 34 | 68 | 0 | 136 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 60 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 100 | 330 | 28 | 0 | 162 | 0 | 0 |  | 433 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 147 | 0 | 305 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 24 |  | 4500 | 1441 | 5941 | 2780 | 433 | 1368 | 1097 | 150 | 45 | 0 | 68 | 0 | 0 | 98.27
3:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 393 | 243 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 100 | 0 | 0 | 95 | 0 | 185 | 8 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 66 | 112 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 157 | 34 | 69 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 15 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 68 | 120 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 100 | 330 | 0 | 0 | 162 | 0 | 0 |  | 427 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 151 | 0 | 311 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 12 |  | 4400 | 1396 | 5796 | 2775 | 427 | 1410 | 924 | 150 | 44 | 0 | 66 | 0 | 0 | 98.27
4:00 | 0 | 102 | 0 | 0 | 300 | 12 | 0 | 398 | 296 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 100 | 0 | 0 | 95 | 0 | 183 | 26 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 64 | 112 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 154 | 34 | 70 | 0 | 136 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 68 | 120 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 100 | 330 | 0 | 0 | 162 | 0 | 0 |  | 338 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 160 | 0 | 284 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 14 |  | 4401 | 1325 | 5726 | 2813 | 338 | 1469 | 849 | 150 | 43 | 0 | 64 | 0 | 0 | 98.27
5:00 | 0 | 101 | 0 | 0 | 300 | 12 | 0 | 351 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 110 | 0 | 0 | 95 | 0 | 183 | 26 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 68 | 110 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 156 | 34 | 70 | 0 | 135 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 252 | 54 | 0 | 0 | 0 | 30 | 330 | 0 | 0 | 162 | 0 | 0 |  | 338 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 160 | 0 | 365 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 14 |  | 4224 | 1392 | 5616 | 2799 | 338 | 1582 | 637 | 150 | 42 | 0 | 68 | 0 | 0 | 98.27
6:00 | 0 | 101 | 0 | 0 | 300 | 12 | 0 | 350 | 335 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 32 | 110 | 0 | 0 | 95 | 0 | 189 | 26 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 70 | 111 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 155 | 33 | 70 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 252 | 54 | 0 | 0 | 5 | 100 | 330 | 1 | 0 | 162 | 0 | 0 |  | 338 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 160 | 0 | 359 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 10 | 0 | 37 | 0 | 18 |  | 4359 | 1412 | 5771 | 2804 | 338 | 1582 | 783 | 150 | 44 | 0 | 70 | 0 | 0 | 98.27
7:00 | 0 | 101 | 0 | 0 | 300 | 12 | 0 | 350 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 29 | 16 | 28 | 110 | 0 | 0 | 95 | 0 | 197 | 26 | 50 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 70 | 111 | 0 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 159 | 34 | 70 | 0 | 136 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 68 | 123 | 0 | 0 | 0 | 0 | 0 | 252 | 54 | 0 | 0 | 8 | 100 | 330 | 34 | 1 | 162 | 0 | 0 |  | 435 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 160 | 0 | 374 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 35 | 0 | 37 | 0 | 23 |  | 4529 | 1600 | 6129 | 2822 | 435 | 1578 | 1027 | 150 | 45 | 0 | 70 | 2 | 0 | 98.26
8:00 | 0 | 103 | 0 | 0 | 300 | 12 | 0 | 381 | 310 |  | 0 | 225 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 32 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 38 | 16 | 12 | 140 | 0 | 0 | 95 | 0 | 183 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 62 | 111 | 2 | 22 | 0 | 20 | 22 | 5 | 5 | 0 | 157 | 34 | 70 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 58 | 0 | 3 | 0 | 90 | 68 | 147 | 0 | 0 | 0 | 0 | 1 | 250 | 54 | 0 | 0 | 8 | 100 | 330 | 71 | 10 | 162 | 0 | 0 |  | 529 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 180 | 0 | 353 | 0 | 0 | 93 | 0 | 34 | 0 | 1 | 100 | 0 | 13 | 0 | 26 |  | 4866 | 1813 | 6679 | 2901 | 529 | 1539 | 1442 | 149 | 45 | 0 | 62 | 12 | 0 | 98.26
9:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 396 | 304 |  | 0 | 225 | 0 | 24 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 23 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 16 | 5 | 140 | 0 | 0 | 95 | 0 | 184 | 26 | 46 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 68 | 110 | 8 | 20 | 1 | 20 | 22 | 5 | 5 | 0 | 155 | 33 | 70 | 0 | 137 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 140 | 0 | 0 | 155 | 0 | 34 | 12 | 90 | 68 | 147 | 0 | 0 | 0 | 0 | 2 | 252 | 54 | 0 | 0 | 9 | 100 | 330 | 90 | 24 | 162 | 0 | 0 |  | 529 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 178 | 0 | 412 | 53 | 0 | 93 | 0 | 39 | 0 | 2 | 113 | 0 | 18 | 0 | 23 |  | 5101 | 1938 | 7039 | 2787 | 529 | 1586 | 1833 | 150 | 45 | 0 | 68 | 41 | 0 | 98.26
10:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 347 | 262 |  | 0 | 225 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 23 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 19 | 5 | 140 | 0 | 0 | 95 | 0 | 183 | 26 | 45 | 26 | 57 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 89 | 8 | 20 | 2 | 20 | 22 | 5 | 5 | 0 | 146 | 33 | 69 | 0 | 137 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 238 | 0 | 0 | 155 | 0 | 65 | 16 | 20 | 68 | 143 | 0 | 0 | 0 | 0 | 4 | 233 | 54 | 0 | 0 | 36 | 100 | 415 | 90 | 36 | 162 | 11 | 0 |  | 579 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 150 | 0 | 314 | 53 | 0 | 92 | 0 | 40 | 0 | 3 | 113 | 0 | 38 | 0 | 11 |  | 5201 | 1869 | 7070 | 2757 | 579 | 1399 | 1965 | 149 | 46 | 42 | 72 | 61 | 0 | 98.26
11:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 313 | 279 |  | 0 | 225 | 0 | 32 | 64 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 19 | 5 | 140 | 0 | 0 | 95 | 0 | 186 | 26 | 49 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 70 | 87 | 8 | 17 | 2 | 20 | 22 | 5 | 5 | 0 | 145 | 32 | 68 | 0 | 137 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 65 | 18 | 33 | 68 | 148 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 18 | 100 | 417 | 90 | 42 | 162 | 41 | 0 |  | 572 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 150 | 0 | 363 | 60 | 0 | 92 | 0 | 40 | 0 | 4 | 113 | 0 | 14 | 0 | 11 |  | 5209 | 1932 | 7141 | 2712 | 572 | 1463 | 2008 | 149 | 47 | 50 | 70 | 70 | 0 | 98.25
12:00 | 0 | 0 | 0 | 0 | 300 | 11 | 0 | 327 | 255 |  | 0 | 225 | 0 | 68 | 70 | 2 | 0 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 25 | 19 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 19 | 5 | 140 | 0 | 0 | 95 | 0 | 201 | 26 | 51 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 74 | 86 | 24 | 17 | 2 | 20 | 22 | 5 | 5 | 0 | 145 | 31 | 67 | 0 | 137 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 270 | 0 | 0 | 165 | 0 | 79 | 18 | 70 | 68 | 148 | 0 | 0 | 0 | 0 | 4 | 216 | 54 | 0 | 0 | 18 | 100 | 417 | 90 | 43 | 162 | 38 | 0 |  | 572 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 150 | 0 | 383 | 90 | 0 | 92 | 0 | 40 | 0 | 4 | 113 | 0 | 17 | 0 | 19 |  | 5369 | 1998 | 7367 | 2751 | 572 | 1430 | 2221 | 149 | 47 | 52 | 74 | 71 | 0 | 98.25
13:00 | 0 | 0 | 0 | 0 | 300 | 11 | 0 | 371 | 278 |  | 0 | 225 | 0 | 84 | 78 | 28 | 0 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 0 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 19 | 8 | 140 | 0 | 0 | 95 | 0 | 185 | 26 | 44 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 85 | 24 | 17 | 2 | 20 | 22 | 8 | 5 | 0 | 145 | 31 | 67 | 0 | 137 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 300 | 0 | 0 | 165 | 0 | 100 | 18 | 90 | 90 | 145 | 0 | 0 | 0 | 0 | 4 | 217 | 54 | 0 | 0 | 18 | 100 | 417 | 90 | 43 | 162 | 36 | 0 |  | 572 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 150 | 0 | 343 | 90 | 0 | 92 | 32 | 40 | 0 | 4 | 113 | 0 | 25 | 0 | 14 |  | 5540 | 1969 | 7509 | 2725 | 572 | 1430 | 2389 | 149 | 47 | 50 | 76 | 71 | 7509 | 98.25
14:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 347 | 278 |  | 0 | 225 | 0 | 50 | 70 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 0 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 19 | 2 | 140 | 0 | 0 | 200 | 0 | 193 | 26 | 51 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 83 | 24 | 17 | 2 | 20 | 22 | 8 | 5 | 0 | 149 | 32 | 67 | 0 | 136 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 140 | 0 | 73 | 15 | 20 | 100 | 143 | 0 | 0 | 0 | 0 | 3 | 180 | 54 | 0 | 0 | 18 | 100 | 430 | 90 | 32 | 162 | 31 | 0 |  | 575 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 300 | 90 | 0 | 92 | 32 | 35 | 0 | 4 | 70 | 0 | 13 | 0 | 11 |  | 5353 | 1860 | 7213 | 2813 | 575 | 1393 | 2051 | 150 | 46 | 53 | 76 | 56 | 0 | 98.25
15:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 360 | 277 |  | 0 | 225 | 0 | 16 | 64 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 19 | 2 | 100 | 0 | 0 | 263 | 0 | 164 | 8 | 51 | 26 | 24 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 72 | 87 | 8 | 20 | 1 | 20 | 22 | 8 | 5 | 0 | 145 | 31 | 63 | 0 | 137 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 50 | 11 | 20 | 100 | 142 | 0 | 0 | 0 | 0 | 2 | 181 | 54 | 0 | 0 | 18 | 100 | 426 | 90 | 25 | 162 | 31 | 0 |  | 576 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 318 | 94 | 0 | 100 | 32 | 35 | 0 | 3 | 70 | 0 | 14 | 0 | 0 |  | 5174 | 1872 | 7046 | 2830 | 576 | 1351 | 1928 | 150 | 46 | 51 | 72 | 42 | 0 | 98.24
16:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 396 | 277 |  | 0 | 225 | 0 | 16 | 64 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 100 | 0 | 0 | 260 | 0 | 148 | 8 | 51 | 26 | 24 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 6 | 21 | 72 | 104 | 8 | 20 | 1 | 20 | 22 | 8 | 5 | 0 | 150 | 32 | 63 | 0 | 137 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 23 | 6 | 10 | 100 | 143 | 0 | 0 | 0 | 0 | 1 | 181 | 54 | 0 | 0 | 18 | 100 | 430 | 90 | 10 | 162 | 21 | 0 |  | 575 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 130 | 0 | 308 | 53 | 0 | 111 | 15 | 35 | 0 | 1 | 70 | 0 | 14 | 0 | 9 |  | 5085 | 1821 | 6906 | 2847 | 575 | 1351 | 1795 | 150 | 46 | 51 | 72 | 19 | 0 | 98.24
17:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 397 | 277 |  | 0 | 225 | 0 | 16 | 64 | 15 | 0 | 0 | 0 | 3 | 7 | 16 | 80 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 20 | 17 | 25 | 8 | 0 | 45 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 50 | 18 | 3 | 70 | 0 | 0 | 260 | 0 | 218 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 94 | 104 | 10 | 20 | 0 | 20 | 22 | 8 | 5 | 0 | 150 | 31 | 65 | 0 | 137 | 0 | 0 | 0 | 230 | 0 | 5 | 0 | 200 | 0 | 0 | 110 | 0 | 17 | 0 | 30 | 100 | 142 | 0 | 4 | 2 | 0 | 0 | 180 | 54 | 0 | 0 | 18 | 100 | 427 | 90 | 1 | 162 | 21 | 0 |  | 576 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 130 | 0 | 351 | 53 | 0 | 111 | 15 | 45 | 0 | 0 | 70 | 0 | 37 | 0 | 27 |  | 5224 | 1928 | 7152 | 2917 | 576 | 1403 | 1899 | 150 | 45 | 67 | 94 | 1 | 0 | 98.24
18:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 371 | 278 |  | 0 | 225 | 0 | 50 | 72 | 15 | 0 | 0 | 0 | 50 | 7 | 100 | 94 | 0 | 0 | 0 | 17 | 35 | 30 | 16 | 25 | 14 | 17 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 10 | 163 | 0 | 0 | 0 |  | 26 | 0 | 34 | 5 | 11 | 50 | 19 | 7 | 70 | 0 | 0 | 263 | 0 | 206 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 104 | 103 | 27 | 20 | 0 | 20 | 22 | 8 | 15 | 0 | 150 | 32 | 65 | 0 | 164 | 0 | 0 | 0 | 260 | 0 | 8 | 0 | 265 | 0 | 0 | 163 | 0 | 59 | 0 | 100 | 100 | 145 | 0 | 10 | 38 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 422 | 90 | 0 | 162 | 0 | 0 |  | 812 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 350 | 53 | 0 | 111 | 15 | 70 | 0 | 0 | 95 | 0 | 34 | 0 | 55 |  | 5868 | 2430 | 8298 | 2913 | 812 | 1454 | 2595 | 150 | 46 | 224 | 104 | 0 | 0 | 98.24
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 396 | 274 |  | 0 | 225 | 0 | 93 | 78 | 15 | 0 | 0 | 0 | 100 | 16 | 150 | 100 | 0 | 0 | 0 | 35 | 35 | 35 | 16 | 25 | 32 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 163 | 0 | 0 | 0 |  | 26 | 0 | 68 | 10 | 30 | 50 | 19 | 12 | 70 | 0 | 0 | 273 | 0 | 184 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 106 | 56 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 143 | 33 | 69 | 0 | 176 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 125 | 0 | 100 | 100 | 150 | 0 | 8 | 105 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 435 | 90 | 0 | 162 | 0 | 0 |  | 813 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 313 | 60 | 0 | 111 | 52 | 35 | 0 | 0 | 113 | 0 | 34 | 0 | 55 |  | 6448 | 2463 | 8911 | 2974 | 813 | 1428 | 3089 | 150 | 45 | 312 | 100 | 0 | 0 | 98.23
19:30 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 395 | 273 |  | 0 | 225 | 0 | 100 | 80 | 15 | 0 | 0 | 0 | 100 | 24 | 116 | 100 | 0 | 0 | 0 | 35 | 35 | 35 | 13 | 25 | 33 | 17 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 25 | 163 | 0 | 0 | 0 |  | 26 | 0 | 51 | 10 | 12 | 50 | 19 | 5 | 70 | 0 | 0 | 265 | 0 | 210 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 106 | 56 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 143 | 32 | 69 | 0 | 176 | 0 | 0 | 0 | 230 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 100 | 150 | 0 | 8 | 105 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 415 | 90 | 0 | 162 | 0 | 0 |  | 812 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 343 | 105 | 0 | 111 | 67 | 35 | 0 | 0 | 113 | 0 | 28 | 0 | 55 |  | 6339 | 2504 | 8843 | 2973 | 812 | 1413 | 3086 | 150 | 46 | 261 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 395 | 274 |  | 0 | 225 | 0 | 100 | 81 | 15 | 0 | 0 | 0 | 100 | 24 | 115 | 100 | 0 | 0 | 0 | 35 | 17 | 35 | 13 | 25 | 33 | 17 | 33 | 24 | 0 | 47 | 0 | 0 | 0 | 25 | 163 | 0 | 0 | 0 |  | 26 | 0 | 51 | 10 | 16 | 50 | 19 | 15 | 70 | 0 | 0 | 260 | 0 | 184 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 102 | 107 | 24 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 145 | 33 | 69 | 0 | 176 | 0 | 0 | 0 | 230 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 100 | 150 | 0 | 8 | 105 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 415 | 90 | 0 | 162 | 0 | 0 |  | 812 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 130 | 0 | 291 | 105 | 0 | 111 | 70 | 35 | 0 | 0 | 113 | 0 | 29 | 0 | 55 |  | 6278 | 2451 | 8729 | 2947 | 812 | 1376 | 3035 | 150 | 47 | 260 | 102 | 0 | 0 | 98.23
21:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 395 | 262 |  | 0 | 225 | 0 | 100 | 81 | 15 | 0 | 0 | 0 | 60 | 24 | 85 | 100 | 0 | 0 | 0 | 35 | 17 | 35 | 13 | 25 | 33 | 17 | 33 | 24 | 0 | 47 | 0 | 0 | 0 | 8 | 163 | 0 | 0 | 0 |  | 26 | 0 | 51 | 10 | 10 | 50 | 19 | 15 | 100 | 0 | 0 | 115 | 0 | 184 | 8 | 48 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 102 | 107 | 24 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 145 | 33 | 69 | 0 | 176 | 0 | 0 | 0 | 230 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 100 | 150 | 0 | 8 | 70 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 415 | 90 | 0 | 162 | 0 | 0 |  | 812 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 130 | 0 | 310 | 96 | 0 | 111 | 85 | 35 | 0 | 0 | 113 | 0 | 28 | 0 | 55 |  | 6022 | 2464 | 8486 | 2830 | 812 | 1384 | 2928 | 150 | 47 | 233 | 102 | 0 | 0 | 98.23
22:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 393 | 262 |  | 0 | 225 | 0 | 65 | 81 | 0 | 0 | 0 | 0 | 30 | 7 | 32 | 100 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 26 | 0 | 0 | 10 | 0 | 50 | 19 | 40 | 100 | 0 | 0 | 100 | 0 | 196 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 0 | 0 | 94 | 109 | 16 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 144 | 33 | 69 | 0 | 176 | 0 | 0 | 0 | 230 | 0 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 117 | 0 | 100 | 100 | 150 | 0 | 0 | 0 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 415 | 90 | 0 | 162 | 0 | 0 |  | 813 | 0 | 175 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 130 | 0 | 336 | 17 | 0 | 111 | 50 | 35 | 0 | 0 | 113 | 0 | 28 | 0 | 55 |  | 5577 | 2305 | 7882 | 2774 | 813 | 1415 | 2460 | 150 | 47 | 129 | 94 | 0 | 0 | 98.23
23:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 392 | 262 |  | 0 | 225 | 0 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 100 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 26 | 0 | 0 | 10 | 0 | 42 | 19 | 38 | 100 | 0 | 0 | 250 | 0 | 204 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 86 | 109 | 0 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 145 | 20 | 69 | 0 | 156 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 285 | 0 | 0 | 140 | 0 | 76 | 0 | 70 | 100 | 150 | 0 | 0 | 0 | 0 | 0 | 216 | 54 | 0 | 0 | 18 | 80 | 415 | 90 | 0 | 162 | 0 | 0 |  | 629 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 130 | 0 | 344 | 17 | 0 | 70 | 15 | 35 | 0 | 0 | 70 | 0 | 28 | 0 | 55 |  | 5417 | 1921 | 7338 | 2954 | 629 | 1360 | 2069 | 150 | 48 | 42 | 86 | 0 | 0 | 98.22
24:00 | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 393 | 303 |  | 0 | 225 | 0 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 100 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 33 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 |  | 26 | 0 | 0 | 10 | 0 | 32 | 19 | 32 | 100 | 0 | 0 | 195 | 0 | 184 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 82 | 112 | 0 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 145 | 20 | 69 | 0 | 156 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 285 | 0 | 0 | 100 | 0 | 50 | 0 | 70 | 100 | 150 | 0 | 0 | 0 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 80 | 405 | 86 | 0 | 162 | 0 | 0 |  | 435 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 130 | 0 | 285 | 17 | 0 | 70 | 15 | 35 | 0 | 0 | 70 | 0 | 28 | 0 | 55 |  | 5323 | 1613 | 6936 | 2822 | 435 | 1434 | 1948 | 151 | 48 | 16 | 82 | 0 | 0 | 98.22
KWH | 0 | 910800 | 0 | 0 | 7383673 | 290636 | 0 | 9114620 | 6660000 |  | 0 | 4757050 | 0 | 883200 | 1145640 | 170193 | 0 | 0 | 0 | 373440 | 302112 | 493440 | 1551864 | 0 | 0 | 0 | 376200 | 135270 | 401314 | 235692 | 600000 | 594540 | 411900 | 803900 | 129888 | 0 | 1092131 | 0 | 0 | 0 | 79900 | 3824048 | 0 | 0 | 0 |  | 432970 | 0 | 214346 | 60240 | 71040 | 860640 | 413424 | 486240 | 2619790 | 0 | 0 | 3711600 | 279000 | 4566000 | 418181 | 1153010 | 431568 | 833280 | 0 | 1202524 | 0 | 0 | 0 | 457020 | 252000 | 773600 | 512990 | 1914240 | 2397320 | 328320 | 448056 | 12100 | 478000 | 524640 | 162000 | 313920 | 0 | 3463000 | 771360 | 1631040 | 0 | 3484540 | 0 | 0 | 0 | 6356000 | 0 | 79000 | 0 | 4616726 | 0 | 0 | 2937600 | 0 | 1223712 | 118260 | 1116480 | 2030400 | 3298618 | 0 | 66000 | 386088 | 0 | 26880 | 5402073 | 1299841 | 0 | 0 | 751800 | 2307840 | 9350300 | 1686720 | 269000 | 3932640 | 229582 | 0 |  | 13686545 | 0 | 4696992 | 0 | 594240 | 0 | 0 | 0 | 0 | 0 | 29250 | 0 | 441000 | 53860 | 0 | 0 | 0 | 0 | 0 | 883064 | 0 | 0 | 0 | 42720 | 0 | 518160 | 0 | 146844 | 0 | 0 | 3672900 | 0 | 0 | 0 | 0 | 0 | 0 | 1512514 | 0 | 3815691 | 0 | 8167091 | 1034880 | 0 | 2276448 | 474624 | 681600 | 0 | 27818 | 1898400 | 0 | 728890 | 0 | 674400 |  | 125885010 | 46057931 | 171942941 | 68704918 | 13686545 | 34478526 | 46348773 | 3672900 | 1092131 | 1590850 | 1914240 | 454058 | 0
Fuel Cost | 0 | 1347984 | 0 | 0 | 8195877.03 | 383639.52 | 0 | 9205766.2 | 6859800 |  | 0 | 5185184.5 | 0 | 6703488 | 7893459.6 | 1439832.78 | 0 | 0 | 0 | 2812003.2 | 2755261.44 | 4855449.6 | 14308186.08 | 0 | 0 | 0 | 2746260 | 1045637.1 | 3956956.04 | 176769 | 450000 | 0 | 0 | 0 | 1256016.96 | 0 | 294875.37 | 0 | 0 | 0 | 742271 | 4168212.32 | 0 | 0 | 0 |  | 0 | 0 | 2079156.2 | 575292 | 618048 | 6816268.8 | 520914.24 | 1444132.8 | 3877289.2 | 0 | 0 | 2746584 | 279000 | 4200720 | 539453.49 | 1325961.5 | 487671.84 | 1166592 | 0 | 2056316.04 | 0 | 0 | 0 | 580415.4 | 189000 | 1353800 | 384742.5 | 14356800 | 2541159.2 | 2981145.6 | 569031.12 | 192874 | 783920 | 839424 | 288360 | 489715.2 | 0 | 3601520 | 1519579.2 | 3115286.4 | 0 | 6028254.2 | 0 | 0 | 0 | 6419560 | 0 | 60040 | 0 | 34902448.56 | 0 | 0 | 15275520 | 0 | 12041326.08 | 1382459.4 | 9099312 | 22029840 | 23255256.9 | 0 | 601920 | 3648531.6 | 0 | 0 | 40839671.88 | 11321615.11 | 0 | 0 | 6442926 | 15370214.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 78834499.2 | 0 | 4931841.6 | 0 | 4670726.4 | 0 | 0 | 0 | 0 | 0 | 304785 | 0 | 683550 | 525673.6 | 0 | 0 | 0 | 0 | 0 | 7815116.4 | 0 | 0 | 0 | 413956.8 | 0 | 994867.2 | 0 | 111160.908 | 0 | 0 | 19907118 | 0 | 0 | 0 | 0 | 0 | 0 | 2268771 | 0 | 4464358.47 | 0 | 8085420.09 | 10804147.2 | 0 | 21603491.52 | 4480450.56 | 5289216 | 0 | 307388.9 | 14029176 | 0 | 0 | 0 | 0 |  | 358021998.6 | 190525714.848 | 548547713.448 | 64940995.928 | 78834499.2 | 39980648.24 | 313600332.21 | 19907118 | 294875.37 | 14749722.2 | 14356800 | 1882722.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 11 | 0 | 327 | 255 |  | 0 | 225 | 0 | 68 | 70 | 2 | 0 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 25 | 19 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 45 | 19 | 5 | 140 | 0 | 0 | 95 | 0 | 201 | 26 | 51 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 74 | 86 | 24 | 17 | 2 | 20 | 22 | 5 | 5 | 0 | 145 | 31 | 67 | 0 | 137 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 270 | 0 | 0 | 165 | 0 | 79 | 18 | 70 | 68 | 148 | 0 | 0 | 0 | 0 | 4 | 216 | 54 | 0 | 0 | 18 | 100 | 417 | 90 | 43 | 162 | 38 | 0 |  | 572 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 150 | 0 | 383 | 90 | 0 | 92 | 0 | 40 | 0 | 4 | 113 | 0 | 17 | 0 | 19 |  | 7367 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 330 | 12 | 0 | 396 | 274 | 0 | 0 | 225 | 0 | 93 | 78 | 15 | 0 | 0 | 0 | 100 | 16 | 150 | 100 | 0 | 0 | 0 | 35 | 35 | 35 | 16 | 25 | 32 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 163 | 0 | 0 | 0 | 0 | 26 | 0 | 68 | 10 | 30 | 50 | 19 | 12 | 70 | 0 | 0 | 273 | 0 | 184 | 8 | 45 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 106 | 56 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 143 | 33 | 69 | 0 | 176 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 125 | 0 | 100 | 100 | 150 | 0 | 8 | 105 | 0 | 0 | 215 | 54 | 0 | 0 | 18 | 100 | 435 | 90 | 0 | 162 | 0 | 0 |  | 813 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 313 | 60 | 0 | 111 | 52 | 35 | 0 | 0 | 113 | 0 | 34 | 0 | 55 |  | 8911 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 102 | 50 | 19 | 20 | 135 |  | 0 | 260 |  | 221 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 22 | 148 | 149 | 95 | 20 | 0 | 30 | 30 | 51 | 44 | 0 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 435 | 104 | 0 | 162 |  | 100 |  | 830 | 16 | 270 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 0 | 35 |  | 55
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 412 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 102 | 50 | 19 | 10 | 135 |  | 0 | 260 |  | 221 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 20 | 110 | 110 | 95 | 20 | 1.6 | 30 | 30 | 51 | 44 | 0 | 155 | 33 | 86 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 420 | 104 | 50 | 162 |  | 100 |  | 589 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 0 | 35 |  | 55
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 396 | 363 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 25 | 32 | 17 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 19 | 14 | 140 | 0 | 0 | 195 | 0 | 224 | 8 | 50 | 17 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 68 | 109 | 0 | 20 | 0 | 20 | 22 | 8 | 20 | 0 | 146 | 33 | 71 | 0 | 156 | 0 | 0 | 0 | 320 | 0 | 11 | 0 | 55 | 0 | 0 | 139 | 0 | 32 | 7 | 52 | 111 | 140 | 0 | 0 | 0 | 0 | 1 | 125 | 54 | 0 | 0 | 0 | 100 | 420 | 43 | 10 | 162 | 0 | 0 | 0 | 531 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 135 | 0 | 431 | 0 | 0 | 86 | 0 | 24 | 0 | 1 | 85 | 0 | 28 | 0 | 0 | 0
199
| Minimum Generation |  | 5616 | 5:00
| Highest Generation |  | 8911 | 19:00
| Day Peak Generation |  | 7367 | 12:00
| Evening Peak Generation |  | 8911 | 19:00
| HVDC Max Flow |  | 813 | 19:00
| HVDC EvPeak Flow |  | 813 | 19:00
| Load factor L.F |  | 80.4%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-12-31
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-12-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7367 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5571 | MW
Evening Peak Generation : |  | 8911 | MW Hour : | 19:00 | Available Max Generation : |  | 12866 | MW
E.P. Demand (at gen end) : |  | 8911 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8911 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3866 | MW
Total Gen. (MKWH) : |  | 171.9429 | System Load Factor : | 80.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -512 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-12-31
Actual : | 98.21 | Ft.(MSL) , | Rule curve : | 103.2 | Ft.( MSL )
Gas Consumed : | Total = | 792.18 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104921644.168
: |  | Coal : | 19907118 | Oil : | 328350054.41 | Total : | 453178816.578
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3144.7865 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1063.5786 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 951.8936 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 859.7477 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 777.1447 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 627.1136 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 358.1442 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.6632 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 483.6253 |  |  | 0 | 0%
Total | 0 |  | 8427.6975 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Dohazari 132/33 kV T1 transformer was under shut down from 09:45 to 17:46 for A/M.
b) Feni-Baroirhat 132 kV Ckt-1 was under shut down from 09:12 to 15:35 for A/M.
c) Kodda 132/33 kV T4 transformer was under shut down from 08:48 to 16:04 for A/M.
d) Aminbazar 230/132 kV T-02 transformer was under shut down from 11:13 to 16:29 for A/M.
e) Cumilla(N)-Chaddogram 132 kV Ckt-1 was under shut down from 10:13 to 12:39 for A/M.
f) Rampura-Bashundhara 132 kV Ckt-2 was under shut down from 08:38 to 20:26 for A/M.
g) Tangail-RPCL 132 kV Ckt-1 was under shut down from 09:21 to 16:53 for A/M.
h) Hasnabad-Aminbazar 230 kV Ckt-1 was under shut down from 08:56 to 15:14 for A/M.
i) Savar 132/33 kV T2 transformer was under shut down from 09:22 to 16:42 for A/M.
j) Feni-Chowmuhoni 132 kV Ckt-1 was under shut down from 08:32 to 20:22 for C/M.
k) HVDC 10CF23 Filter was under shut down from 09:45 to 13:43 for A/M.
l) Polashbari-Mahasthangar 132 kV Ckt-2 was under shut down from 08:52 to 16:24 for A/M.
m) Chapainawabganj-Rajshahi(New) 132 kV Ckt was under shut down from 08:29 to 17:40 for A/M.
n) Barishal(N)-Madaripur 132 kV Ckt-1 was under shut down from 08:40 to 16:11 for A/M.
o) Gopalganj 400 kV-Madaripur 132 kV Ckt-3 was under shut down from 08:44 to 17:04 for A/M.
p) Shahjadpur-Baghabari 132 kV Ckt-2 was under shut down from 08:09 to 16:55 for A/M.
q) Sonargaon-Daudkandi 132 kV Ckt-2 tripped at 11:24 from both end showing dist Z1,B phase,
C phase and was switched on at 11:38.
r) Ghorasal #03 tripped at 08:23 due to temperature high.
s) Siddhirganj S/S- Siddhirganj P/S 132 kV Ckt-1 was under shut down from 10:17 to 13:54.
t) Sikalbaha 132/33 kV T4 transformer was under shut down from 13:05 to 13:44 for maintenance work.
u) Sirajganj 132/33 kV T4 transformer was under shut down from 18:09 to 19:30 due to red hot maint
at R-phase nut.
v) Barisal (S)-Barisal Summit 132 kV Ckt was under shut down from 15:08 to 16:00 due to CT oil
leakage maintenance.
w) Tongi 132/33 kV T1 transformer tripped at 20:55 due to 33 kV feeder fault and was switched on
at 21:31.
x) Cumilla(N) 132/33 kV T3 transformer tripped at 21:48 showing O/C,E/F relay due to 33 kV Kaliganj
feeder fault and was switched on at 21:59.
y) Sikalbaha-Dohazari 132 kV Ckt-1 was under shut down since 07:11(31-12-2020) for D/W.
z) Sikalbaha-Shahmirpur 132 kV Ckt-2 was under shut down since 07:13(31-12-2020) for D/W.
aa) Rampura-Bashundhara 132 kV Ckt-2 was under shut down since 07:40(31-12-2020) for A/M.
ag) Shahmirpur-Sikalbaha 132 kV Ckt-2 was shut down at 07:30(30/12/2020) for D/W.
ah) Goalpara-Bagerhat 132 kV Ckt-1 was shut down at 07:48(30/12/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-12-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 910800 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7383673
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 290636 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 396 | 9114620 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 274 | 6660000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4757050 | GT-1 under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 883200
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 78 | 1145640 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 170193 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1551864
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 235692 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 373440
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 302112 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 376200 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 493440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 135270 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 401314 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1194540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 129888 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4616726
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 125 | 1223712 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 386088
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1686720 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3932640
| Dhaka area Total |  |  |  | 6057 | 2851 | 49571258
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 79900
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 118260
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 860640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1092131 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 163 | 3824048 | Gas shortage & ST under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 214346 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 60240 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1116480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 413424 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 486240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 71040 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26880
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 215 | 5402073 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299841
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2307840
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 229582
| Chattogram area Total |  |  |  | 2266 | 891 | 17602965
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 2619790 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4566000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 273 | 3711600 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 279000 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 431568 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 833280 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 418181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1202524
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3298618
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1153010 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 2030400 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 457020
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252000
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 1914240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 773600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 512990
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 751800 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1093 | 25205621
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2397320 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 448056
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 56 | 328320 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2937600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 66000 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 269000
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 26 | 432970
| Mymensingh Area Total |  |  |  | 687 | 416 | 6891366
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 478000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 524640 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3463000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 8 | 162000 | Line O/L
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 20 | 313920 | Line O/L
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 79000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 771360 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 69 | 1631040 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 176 | 3484540
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6356000 | Gas shortage
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 435 | 9350300 | On test
| Sylhet Area Total |  |  |  | 1988 | 1197 | 26613800
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 813 | 13686545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 594240
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 4696992 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 29250 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 60 | 1034880 | Low demand
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 52 | 474624 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1239 | 20516531
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 53860 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 441000 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 90 | 1512514
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 0 | 0
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 34 | 728890 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 55 | 674400 | On test.
| Barisal Area Total |  |  |  | 1054 | 220 | 3410664
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3815691 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 313 | 8167091 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 518160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 146844
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 42720 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 883064
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 2276448
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1898400
| Rajshahi Area Total |  |  |  | 2183 | 819 | 17748418
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3672900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 681600 | Reserve.
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27818
| Rangpur Area Total |  |  |  | 605 | 185 | 4382318
| Total |  |  |  | 20104 | 8911 | 171942941
| Eastern Grid Total |  |  |  | 13978 | 6448 | 125885010
| Western Grid Total |  |  |  | 6126 | 2463 | 46057931
| National Grid Total |  |  |  | 20104 | 8911 | 171942941
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-12-30
| (a) ENTIRE EASTERN GRID : |  | 5567 | MW | (b) ENTIRE WESTERN GRID : |  | 2762 | MW
| i) Dhaka area |  | 2960 | MW | i) Khulna area |  | 1078 | MW
| ii) Chittagong area |  | 876 | MW | ii) Rajshahi area |  | 873 | MW
| iii) Comilla area |  | 721 | MW | iii) Barisal area |  | 236 | MW
| iv) Mymensingh area |  | 699 | MW | iv) Rangpur area |  | 575 | MW
| v) Sylhet area |  | 311 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8329 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 94 | 10:00 | Jamalpur | 75 | 18:00 | Benapol | 36 | 18:30
| Munsiganj | 80 | 20:00 | Sherpur | 92 | 18:00 | Jhenida | 84 | 18:30
| Sonargaon | 58 | 2:00 | Srimongal | 31 | 18:00 | Bottail | 76 | 18:00
| Shyampur | 158 | 10:00 | Shahjibazar | 76 | 18:30 | G.K Project | 45 | 18:30
| Bhulta | 153 | 21:00 | Fenchuganj | 25 | 18:00 | Faridpur | 135 | 19:00
| Madanganj | 61 | 15:00 | Kulawara | 29 | 18:00 | Madaripur | 62 | 20:00
| Shitalakhya | 99 | 12:00 | Sylhet | 78 | 18:00 | Sariatpur | 40 | 19:30
| Rahim steel | 19 | 9:00 | Chatak | 19 | 18:00 | Gopalganj | 59 | 18:30
| Matuail | 42 | 1:00 | Sunamganj | 26 | 19:00 | Bagerhat | 84 | 18:30
| Ghorasal | 61 | 18:00 | Biani Bazar | 37 | 18:00 | Mongla | 40 | 18:00
| Narsingdi | 118 | 19:00 | Comilla (S) | 104 | 18:00 | Satkhira | 74 | 18:30
| Haripur (SBU) | 96 | 19:30 | Comilla(N) | 80 | 22:00 | Gallamari | 17 | 13:00
| Ullon | 40 | 19:00 | Chandpur | 70 | 19:30 | Magura | 38 | 18:00
| Hasnabad | 140 | 19:00 | Feni | 75 | 18:30 | Norail | 24 | 18:00
| Magbazar | 64 | 13:00 | Chowmuhani | 116 | 20:00 | Chuadanga | 67 | 18:30
| Maniknagar | 62 | 13:00 | Ashuganj | 37 | 18:30 | Barisal(N) | 30 | 19:30
| Bangabhaban | 20 | 12:00 | Daudkandi | 84 | 19:30 | Barisal (S) | 68 | 18:00
| Narinda | 68 | 11:00 | B.Baria | 96 | 19:00 | Patuakhali | 78 | 20:00
| Dhanmondi | 93 | 13:00 | Ramganj | 62 | 19:30 | Bhandaria | 42 | 20:00
| Lalbag | 69 | 12:00 | Chaddagram | 23 | 19:30 | Borhan Uddin | 26 | :20:00
| Madartek | 44 | 20:00 | PHP | 8 | 12:00 | Ishurdi | 49 | 18:00
| Dhaka University |  |  | Madunaghat | 52 | 18:00 | Ruppur Paromanobik | 2 | 18:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 58 | 0.79167 | Natore | 82 | 0.77083
| Fatullah | 42 | 11:00 | Khulshi | 159 | 4:00 | Bogra | 112 | 19:00
| Mirpur | 61 | 18:30 | Halishahar | 90 | 15:00 | Noagaon | 75 | 18:30
| Kalyanpur | 63 | 13:00 | Baraulia | 145 | 10:00 | Rajshahi | 94 | 19:00
| Gulshan | 72 | 13:00 | Sikalbaha | 20 | 19:30 | Rajshahi New | 8 | 18:00
| Uttara | 61 | 13:00 | Dohazari | 56 | 18:30 | C.Nawabganj | 51 | 18:30
| Uttara New | 22 | 18:00 | Cox'sbazar | 74 | 19:30 | Amnura | 30 | 18:00
| Kamrangirchar | 74 | 13:00 | Chandraghona | 22 | 18:00 | Pabna | 79 | 18:30
| Savar | 104 | 11:00 | Kaptai | 3.8 | 18:00 | Shahjadpur | 73 | 19:30
| Bhasantec | 98 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 74 | 18:00
| Agargaon | 43 | 18:30 | Bakulia | 71 | 18:00 | Niyamatpur | 44 | 18:30
| Satmosjid | 66 | 0.54167 | Julda | 20 | 0.625 | Joypurhat | 43 | 0.77083
| Tongi | 73 | 12:00 | TK chemical | 19.5 | 18:00 | Sherpur(Bogura) | 36 | 18:00
| Kabirpur | 174 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 34 | 18:00
| Basundhara | 82 | 18:30 | Shahmirpur | 18 | 8:00 | Rangpur | 100 | 19:00
| Manikganj | 52 | 19:00 | Khagrachhari | 20 | 19:00 | Lalmonirhat | 43 | 19:00
| Joydevpur | 109 | 18:30 | Matarbari | 24 | 19:00 | Saidpur | 80 | 18:30
| New Tongi | 87 | 12:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 83 | 20:00
| Kodda | 172 | 18:00 | Rangamati | 8 | 12:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 68 | 21:00 | Abul Khair 230 | 129 | 3:00 | Palashbari | 85 | 18:30
| Rajendrapur | 74 | 20:00 | BSRM | 146 | 1:00 | Barapukuria | 39 | 18:30
| Valuka | 88 | 18:30 | GPH Ispat | 82 | 9:00 | Panchagar | 42 | 18:00
| Tangail | 137 | 19:00 | Goalpara | 18 | 13:00 | Joldhaka | 24 | 18:30
| Mymensing | 144 | 19:00 | Central s/s | 78 | 18:00 | Kurigram | 41 | 18:00
| Kishorganj | 90 | 21:00 | Noapara | 49 | 18:30
| Netrokona | 88 | 19:00 | Jessore | 80 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-12-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 414 | 9:00 | 408 | 19:30 | Kaliakoir | 403 | 0.125 | 384 | 0.625
| Bheramara | 412 | 9:00 | 397 | 13:00 | Bhulta | 387 | 24:00 | 378 | 0.29167
| Ashuganj(N) | 394 | 24:00 | 383 | 5:00 | Gopalganj | 436 | 0.16667 | 392 | 0.75
| Payra | 440 | 24:00 | 399 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 18:00 | 232 | 1:00 | Comilla (N) | 238 | 21:00 | 233 | 9:00
| Ishurdi | 237 | 24:00 | 227 | 8:00 | Hathazari | 228 | 19:00 | 218 | 2:00
| Ashuganj | 240 | 24:00 | 235 | 4:00 | Megnaghat | 232 | 24:00 | 230 | 4:00
| Serajganj | 235 | 10:00 | 229 | 18:30 | Fenchuganj | 243 | 20:00 | 239 | 1:00
| Baghabari | 241 | 4:00 | 238 | 9:00 | Siddhirganj | 233 | 24:00 | 227 | 10:00
| Barapukuria | 233 | 4:00 | 228 | 18:00 | Maniknagar | 233 | 24:00 | 224 | 11:00
| Bogra | 235 | 1:00 | 229 | 19:00 | Agargaon | 235 | 15:00 | 226 | 14:00
| Rajshahi | 231 | 23:00 | 218 | 8:00 | Barisal | 255 | 19:00 | 243 | 21:00
| Khulna South | 235 | 15:00 | 217 | 8:00 | AKSML | 230 | 19:00 | 219 | 1:00
| Rampura | 232 | 24:00 | 226 | 16:00 | BSRM | 230 | 20:00 | 220 | 12:00
| Haripur | 233 | 23:00 | 224 | 15:00 | Bibiyana | 244 | 24:00 | 238 | 18:30
| Hasnabad | 234 | 23:00 | 230 | 1:00 | Bhulta | 237 | 19:00 | 226 | 17:00
| Shyampur | 232 | 24:00 | 220 | 16:00 | Ashuganj (S) | 237 | 24:00 | 232 | 16:00
| Aminbazar | 235 | 24:00 | 220 | 13:00 | Kaliakoir | 233 | 24:00 | 223 | 7:00
| Tongi | 231 | 1:00 | 223 | 8:00 | GPH | 228 | 24:00 | 216 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 20:00 | 136 | 3:00 | Madanhat | 139 | 0.83333 | 133 | 0.45833
| Munsiganj | 139 | 13:00 | 134 | 7:00 | Hathazari | 138 | 0.79167 | 133 | 0.5
| Sonargaon | 137 | 23:00 | 135 | 1:00 | Khulshi | 137 | 0.79167 | 129 | 0.66667
| Shyampur | 135 | 20:00 | 131 | 11:00 | Halishahar | 139 | 0.79167 | 132 | 0.45833
| Bhulta | 133 | 0:00 | 130 | 9:00 | Baraulia | 138 | 0.083333 | 130 | 0.41667
| Madanganj | 137 | 1:00 | 133 | 9:00 | Sikalbaha | 140 | 0.79167 | 131 | 0.66667
| Shitalakhya | 142 | 20:00 | 137 | 7:00 | Dohazari | 138 | 0.77083 | 129 | 0.5
| Rahim steal | 139 | 18:00 | 136 | 10:00 | Cox'sbazar | 127 | 0.125 | 117 | 0.77083
| Matuail | 140 | 20:00 | 136 | 3:00 | Chandraghona | 139 | 0.79167 | 131 | 0.66667
| Ghorasal | 140 | 23:00 | 136 | 13:00 | Kaptai | 139 | 0.77083 | 132 | 0.41667
| Narsinghdi | 137 | 22:00 | 132 | 7:00 | A. Khaer Stl. | 137 | 0.041667 | 132 | 0.41667
| Haripur (SBU) | 139 | 18:30 | 136 | 7:00 | Bakulia | 138 | 0.79167 | 132 | 0.45833
| Ullon | 134 | 24:00 | 128 | 11:00 | Julda | 140 | 0.77083 | 133 | 0.58333
| Hasnabad | 141 | 24:00 | 136 | 10:00 | TK Chemical | 139 | 0.79167 | 132 | 0.58333
| Magbazar | 134 | 24:00 | 128 | 11:00 | Modern Steel | 138 | 0.79167 | 130 | 0.45833
| Maniknagar | 138 | 1:00 | 130 | 8:00 | Shahmirpur | 139 | 0.79167 | 131 | 0.66667
| Bangabhaban | 138 | 1:00 | 130 | 8:00 | Khagrachhari | 137 | 0.79167 | 132 | 0.5
| Narinda | 138 | 1:00 | 130 | 8:00 | Matarbari | 131 | 0.083333 | 120 | 0.66667
| Dhanmondi | 134 | 24:00 | 128 | 11:00 | Baroiar Hat | 137 | 0.041667 | 133 | 0.41667
| Lalbag | 135 | 24:00 | 128 | 16:00 | Rangamati | 138 | 19:00 | 131 | 11:00
| Madartek | 133 | 24:00 | 129 | 11:00 | Goalpara S/S | 140 | 15:00 | 128 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 17:00 | 126 | 0.33333
| Aftabnagar | 133 | 22:00 | 128 | 16:00 | Noapara | 138 | 15:00 | 127 | 0.33333
| Fatuiiah | 135 | 21:00 | 131 | 11:00 | Jessore | 135 | 15:00 | 126 | 0.29167
| Mirpur | 137 | 5:00 | 131 | 8:00 | Benapol | 136 | 0.625 | 126 | 0.29167
| Kalyanpur | 135 | 21:00 | 130 | 12:00 | Jhenida | 134 | 15:00 | 125 | 0.33333
| Gulshan | 134 | 24:00 | 128 | 14:00 | Bottail | 136 | 0.041667 | 131 | 0.75
| Uttara | 137 | 23:00 | 129 | 16:00 | G.K Project | 140 | 0.125 | 136 | 0.75
| Uttara New | 139 | 20:00 | 130 | 15:00 | Faridpur | 139 | 0.20833 | 127 | 0.33333
| Kamrangirchar | 141 | 3:00 | 137 | 16:00 | Madaripur | 142 | 0.125 | 130 | 0.75
| Savar | 138 | 24:00 | 131 | 11:00 | Shariyatpur S/S | 142 | 4:00 | 132 | 0.75
| Bhasantec | 138 | 24:00 | 132 | 11:00 | Gopalganj | 145 | 0.70833 | 132 | 0.75
| Agargaon | 138 | 24:00 | 132 | 16:00 | Bagerhat | 137 | 19:00 | 122 | 0.33333
| Satmosjid | 138 | 24:00 | 132 | 11:00 | Mongla | 135 | 4:00 | 118 | 0.33333
| Tongi | 141 | 21:00 | 135 | 16:00 | Satkhira | 139 | 15:00 | 127 | 8:00
| Kabirpur | 138 | 24:00 | 130 | 15:00 | Gallamari | 138 | 0.16667 | 128 | 0.33333
| Basundhara | 136 | 13:00 | 130 | 18:00 | Magura | 134 | 3:00 | 125 | 0.75
| Manikganj | 144 | 19:00 | 133 | 16:00 | Norail | 134 | 0.125 | 124 | 0.75
| Joydevpur | 142 | 21:00 | 135 | 16:00 | Chuadanga | 131 | 1:00 | 122 | 0.75
| New Tongi | 140 | 23:00 | 132 | 15:00 | Barisal(N) | 144 | 15:00 | 137 | 18:00
| Kodda | 140 | 21:00 | 127 | 7:00 | Barisal (S) | 143 | 0.66667 | 137 | 0.29167
| Dhamrai | 137 | 24:00 | 130 | 16:00 | Patuakhali(S) | 141 | 0.041667 | 136 | 0.29167
| Rajendrapur | 137 | 20:00 | 130 | 13:00 | Bhandaria | 140 | 0.625 | 132 | 0.75
| Valuka | 131 | 9:00 | 123 | 5:00 | Ishurdi | 138 | 3:00 | 134 | 8:00
| Tangail | 135 | 1:00 | 129 | 7:00 | Ruppur Paromanobik | 137 | 3:00 | 135 | 6:00
| Mymensing | 133 | 10:00 | 122 | 7:00 | Natore | 139 | 5:00 | 134 | 8:00
| Kishorganj | 133 | 3:00 | 129 | 16:00 | Bogra | 140 | 3:00 | 136 | 8:00
| Netrokona | 133 | 9:00 | 123 | 7:00 | Noagaon | 135 | 3:00 | 130 | 8:00
| Jamalpur | 141 | 18:00 | 124 | 6:00 | Rajshahi | 139 | 4:00 | 134 | 8:00
| Sherpur | 139 | 18:00 | 119 | 7:00 | Rajshahi New | 141 | 16:00 | 134 | 8:00
| Srimongal | 137 | 1:00 | 135 | 14:00 | C.Nawabganj | 140 | 2:00 | 131 | 9:00
| Shahjibazar | 135 | 1:00 | 132 | 18:30 | Amnura | 140 | 4:00 | 133 | 8:00
| Fenchuganj | 138 | 11:00 | 135 | 11:00 | Pabna | 137 | 3:00 | 132 | 14:00
| Khulawara | 136 | 1:00 | 135 | 15:00 | Shahjadpur | 142 | 1:00 | 135 | 18:30
| Sylhet | 135 | 2:00 | 133 | 11:00 | Serajganj | 136 | 4:00 | 133 | 18:00
| Chatak | 134 | 1:00 | 132 | 15:00 | Niyamatpur | 135 | 4:00 | 128 | 18:30
| Sunamganj | 135 | 1:00 | 131 | 18:30 | Joypurhat | 136 | 3:00 | 131 | 8:00
| Biani Bazar | 135 | 1:00 | 132 | 18:00 | Sherpur(Bogura) | 139 | 4:00 | 135 | 8:00
| Comilla(s) | 131 | 1:00 | 128 | 9:00 | Mohastangor | 138 | 4:00 | 133 | 18:30
| Comilla(n) | 142 | 19:00 | 140 | 11:00 | Rangpur | 131 | 4:00 | 123 | 19:00
| Chandpur | 143 | 23:00 | 140 | 11:00 | Lalmonirhat | 132 | 4:00 | 122 | 19:00
| Feni | 139 | 19:30 | 137 | 12:00 | Saidpur | 131 | 4:00 | 122 | 18:30
| Chowmuhani | 136 | 12:00 | 135 | 7:00 | Purbasadipur | 129 | 3:00 | 122 | 18:00
| Ashuganj | 137 | 1:00 | 135 | 18:30 | Thakurgaon | 131 | 4:00 | 120 | 18:00
| Daudkandi | 140 | 20:00 | 136 | 11:00 | Palashbari | 134 | 2:00 | 129 | 19:00
| B.Baria | 134 | 9:00 | 131 | 20:00 | Barapukuria | 133 | 4:00 | 128 | 18:00
| Ramganj | 138 | 20:00 | 133 | 9:00 | Panchagar | 131 | 4:00 | 118 | 18:00
| Chaddagram | 140 | 20:00 | 136 | 10:00 | Joldhaka | 130 | 4:00 | 121 | 18:00
| PHP | 138 | 4:00 | 133 | 11:00 | Kurigram | 129 | 0.25 | 122 | 0.75

## L-Curve
Date | 2020-12-30
[5 empty] | . |  | POWER GRID COMPANY OF BANGLADESH LTD.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | NATIONAL LOAD DESPATCH CENTER
0:00 | 415 | 5323 | 1613 | 6936 |  |  |  | DAILY LOAD CURVE | QF-LDC-11
0:30 | 345.5 | 5023 | 1566 | 6589 | Date: | 2020-12-30
1:00 | 276 | 4723 | 1519 | 6242
1:30 | 285 | 4611.5 | 1480 | 6091.5
2:00 | 294 | 4500 | 1441 | 5941
2:30 | 266 | 4450 | 1418.5 | 5868.5 | [6 empty] | Gen. at Eve. Peak | 8911 | 8911 MW (19:00 )
3:00 | 238 | 4400 | 1396 | 5796 | [7 empty] | 19:00
3:30 | 229 | 4400.5 | 1360.5 | 5761 | [6 empty] | Gen. at Day Peak | 7367 | 7367 MW (12:00 )
4:00 | 220 | 4401 | 1325 | 5726 | [7 empty] | 12:00
4:30 | 224 | 4312.5 | 1358.5 | 5671 | [6 empty] | Highest Generation | 8911
5:00 | 228 | 4224 | 1392 | 5616 | [7 empty] | 19:00
5:30 | 231.5 | 4291.5 | 1402 | 5693.5
6:00 | 235 | 4359 | 1412 | 5771
6:30 | 237.5 | 4444 | 1506 | 5950
7:00 | 240 | 4529 | 1600 | 6129
7:30 | 322.5 | 4697.5 | 1706.5 | 6404
8:00 | 405 | 4866 | 1813 | 6679
8:30 | 334 | 4983.5 | 1875.5 | 6859
9:00 | 263 | 5101 | 1938 | 7039
9:30 | 225 | 5151 | 1903.5 | 7054.5
10:00 | 187 | 5201 | 1869 | 7070
10:30 | 145.5 | 5205 | 1900.5 | 7105.5
11:00 | 104 | 5209 | 1932 | 7141
11:30 | 148 | 5289 | 1965 | 7254
12:00 | 192 | 5369 | 1998 | 7367
12:30 | 228 | 5454.5 | 1983.5 | 7438
13:00 | 264 | 5540 | 1969 | 7509
13:30 | 168 | 5446.5 | 1914.5 | 7361
14:00 | 72 | 5353 | 1860 | 7213
14:30 | 61 | 5263.5 | 1866 | 7129.5
15:00 | 50 | 5174 | 1872 | 7046
15:30 | 31 | 5129.5 | 1846.5 | 6976
16:00 | 12 | 5085 | 1821 | 6906
16:30 | 28.5 | 5154.5 | 1874.5 | 7029
17:00 | 45 | 5224 | 1928 | 7152
17:30 | 197 | 5546 | 2179 | 7725
18:00 | 349 | 5868 | 2430 | 8298
18:30 | 430.5 | 6158 | 2446.5 | 8604.5
19:00 | 512 | 6448 | 2463 | 8911
19:30 | 440 | 6339 | 2504 | 8843
20:00 | 452 | 6278 | 2451 | 8729 |  |  |  |  | Executive Engineer
20:30 | 364.5 | 6150 | 2457.5 | 8607.5 |  |  |  |  | Network Operation Division
21:00 | 277 | 6022 | 2464 | 8486
21:30 | 227.5 | 5799.5 | 2384.5 | 8184
22:00 | 178 | 5577 | 2305 | 7882 | [5 empty] | Page 6 of 7
22:30 | 226 | 5497 | 2113 | 7610
23:00 | 274 | 5417 | 1921 | 7338
23:30 | 344.5 | 5370 | 1767 | 7137
24:00 | 415 | 5323 | 1613 | 6936
8911 MW (19:00 )
7367 MW (12:00 )

## En-Curve
NATIONAL LOAD DESPATCH CENTER
Date | 2020-12-30 |  | Energy | 171942941 | [7 empty] | DAILY ENERGY CURVE
[11 empty] | 2020-12-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2822 | 435 | 1434 | 2069 | 151 | 48 | 16 | 0 | 82 | 0
0:30 | 2887.5 | 433.5 | 1408.5 | 1637.5 | 150.5 | 47 | 8 | 0 | 77 | 0 | Date: | 2020-12-30
1:00 | 2953 | 432 | 1383 | 1206 | 150 | 46 | 0 | 0 | 72 | 0
1:30 | 2866.5 | 432.5 | 1375.5 | 1151.5 | 150 | 45.5 | 0 | 0 | 70 | 0 | [7 empty] | Total Energy | 171.9429 | Total Energy Gen 171.943 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.943 MKWHr
2:00 | 2780 | 433 | 1368 | 1097 | 150 | 45 | 0 | 0 | 68 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2777.5 | 430 | 1389 | 1010.5 | 150 | 44.5 | 0 | 0 | 67 | 0 | [7 empty] | Energy Requirement | 171.9429
3:00 | 2775 | 427 | 1410 | 924 | 150 | 44 | 0 | 0 | 66 | 0
3:30 | 2794 | 382.5 | 1439.5 | 886.5 | 150 | 43.5 | 0 | 0 | 65 | 0 | [6 empty] | Shortage
4:00 | 2813 | 338 | 1469 | 849 | 150 | 43 | 0 | 0 | 64 | 0
4:30 | 2806 | 338 | 1525.5 | 743 | 150 | 42.5 | 0 | 0 | 66 | 0
5:00 | 2799 | 338 | 1582 | 637 | 150 | 42 | 0 | 0 | 68 | 0
5:30 | 2801.5 | 338 | 1582 | 710 | 150 | 43 | 0 | 0 | 69 | 0
6:00 | 2804 | 338 | 1582 | 783 | 150 | 44 | 0 | 0 | 70 | 0
6:30 | 2813 | 386.5 | 1580 | 905 | 150 | 44.5 | 0 | 0 | 70 | 1 |  |  |  |  | Coal
7:00 | 2822 | 435 | 1578 | 1027 | 150 | 45 | 0 | 0 | 70 | 2
7:30 | 2861.5 | 482 | 1558.5 | 1234.5 | 149.5 | 45 | 0 | 0 | 66 | 7 |  |  |  | Oil |  |  |  | ,
8:00 | 2901 | 529 | 1539 | 1442 | 149 | 45 | 0 | 0 | 62 | 12
8:30 | 2844 | 529 | 1562.5 | 1637.5 | 149.5 | 45 | 0 | 0 | 65 | 26.5
9:00 | 2787 | 529 | 1586 | 1833 | 150 | 45 | 0 | 0 | 68 | 41
9:30 | 2772 | 554 | 1492.5 | 1899 | 149.5 | 45.5 | 21 | 0 | 70 | 51
10:00 | 2757 | 579 | 1399 | 1965 | 149 | 46 | 42 | 0 | 72 | 61
10:30 | 2734.5 | 575.5 | 1431 | 1986.5 | 149 | 46.5 | 46 | 0 | 71 | 65.5
11:00 | 2712 | 572 | 1463 | 2008 | 149 | 47 | 50 | 0 | 70 | 70
11:30 | 2731.5 | 572 | 1446.5 | 2114.5 | 149 | 47 | 51 | 0 | 72 | 70.5
12:00 | 2751 | 572 | 1430 | 2221 | 149 | 47 | 52 | 0 | 74 | 71
12:30 | 2738 | 572 | 1430 | 2305 | 149 | 47 | 51 | 0 | 75 | 71
13:00 | 2725 | 572 | 1430 | 2389 | 149 | 47 | 50 | 0 | 76 | 71
13:30 | 2725 | 572 | 1430 | 2389 | 149 | 47 | 50 | 0 | 76 | 71
14:00 | 2725 | 572 | 1430 | 2389 | 149 | 47 | 50 | 0 | 76 | 71
14:30 | 2777.5 | 574 | 1390.5 | 2158.5 | 149.5 | 46.5 | 50.5 | 0 | 74 | 56.5
15:00 | 2830 | 576 | 1351 | 1928 | 150 | 46 | 51 | 0 | 72 | 42
15:30 | 2838.5 | 575.5 | 1351 | 1861.5 | 150 | 46 | 51 | 0 | 72 | 30.5
16:00 | 2847 | 575 | 1351 | 1795 | 150 | 46 | 51 | 0 | 72 | 19
16:30 | 2882 | 575.5 | 1377 | 1847 | 150 | 45.5 | 59 | 0 | 83 | 10
17:00 | 2917 | 576 | 1403 | 1899 | 150 | 45 | 67 | 0 | 94 | 1
17:30 | 2915 | 694 | 1428.5 | 2247 | 150 | 45.5 | 145.5 | 0 | 99 | 0.5
18:00 | 2913 | 812 | 1454 | 2595 | 150 | 46 | 224 | 0 | 104 | 0
18:30 | 2943.5 | 812.5 | 1441 | 2842 | 150 | 45.5 | 268 | 0 | 102 | 0
19:00 | 2974 | 813 | 1428 | 3089 | 150 | 45 | 312 | 0 | 100 | 0
19:30 | 2973 | 812 | 1413 | 3086 | 150 | 46 | 261 | 0 | 102 | 0
20:00 | 2947 | 812 | 1376 | 3035 | 150 | 47 | 260 | 0 | 102 | 0
20:30 | 2888.5 | 812 | 1380 | 2981.5 | 150 | 47 | 246.5 | 0 | 102 | 0
21:00 | 2830 | 812 | 1384 | 2928 | 150 | 47 | 233 | 0 | 102 | 0
21:30 | 2802 | 812.5 | 1399.5 | 2694 | 150 | 47 | 181 | 0 | 98 | 0
22:00 | 2774 | 813 | 1415 | 2460 | 150 | 47 | 129 | 0 | 94 | 0
22:30 | 2864 | 721 | 1387.5 | 2264.5 | 150 | 47.5 | 85.5 | 0 | 90 | 0
23:00 | 2954 | 629 | 1360 | 2069 | 150 | 48 | 42 | 0 | 86 | 0
23:30 | 2888 | 532 | 1397 | 2069 | 150.5 | 48 | 29 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 26.6° C
24:00 | 2822 | 435 | 1434 | 2069 | 151 | 48 | 16 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 171.943 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 171.943 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2020-12-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 45 | 44 | 43 | 42 | 44 | 45 | 45 | 45 | 46 | 47 | 47 | 47 | 46 | 46 | 46 | 45 | 46 |  | 45 | 46 | 47 | 47 | 47 | 48 | 48 | 1092131
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 2 | 10 |  | 25 | 25 | 25 | 8 |  |  | 0 | 79900
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  | 12 | 16 | 18 | 18 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 118260
6 | Sikalbaha 225MW CCPP (Gas) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 163 | 165 | 164 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 164 | 164 | 112 | 3824048
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 68 | 51 | 51 | 51 |  |  | 0 | 214346
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 60 | 15 | 0 |  |  | 30 | 55 | 140 | 238 | 250 | 270 | 300 | 250 | 200 | 200 | 200 | 265 |  | 300 | 300 | 300 | 300 | 300 | 285 | 285 | 4616726
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 102 | 102 | 102 | 102 | 102 | 101 | 101 | 103 | [17 empty] | 0 | 910800
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7383673
26
28 | Ashuganj TPP Unit- 3 | 80 | 100 | 100 | 100 | 110 | 110 | 110 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 100 | 70 | 70 |  | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 2619790
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 431568
33 | Ashuganj 225 MW CCPP | 166 | 202 | 185 | 183 | 183 | 189 | 197 | 183 | 184 | 183 | 186 | 201 | 185 | 193 | 164 | 148 | 218 | 206 |  | 184 | 210 | 184 | 184 | 196 | 204 | 184 | 4566000
34 | Ashuganj 450 MW CCPP(South) | 250 | 0 | [23 empty] | 0 | 279000
| Ashuganj 450 MW CCPP(North) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 200 | 263 | 260 | 260 | 263 |  | 273 | 265 | 260 | 115 | 100 | 250 | 195 | 3711600
35 | Ashuganj 55 MW PP (Precision) | 5 | 20 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 57 | 56 | 56 | 56 | 56 | 24 | 24 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 833280
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 45 | 49 | 51 | 44 | 51 | 51 | 51 | 50 | 51 |  | 45 | 50 | 50 | 48 | 51 | 51 | 46 | 1153010
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 388 | 392 | 393 | 398 | 351 | 350 | 350 | 381 | 396 | 347 | 313 | 327 | 371 | 347 | 360 | 396 | 397 | 371 |  | 396 | 395 | 395 | 395 | 393 | 392 | 393 | 9114620
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4757050
41 | Haripur 360MW CCPP(HPL) | 245 | 243 | 243 | 296 | 332 | 335 | 332 | 310 | 304 | 262 | 279 | 255 | 278 | 278 | 277 | 277 | 277 | 278 |  | 274 | 273 | 274 | 262 | 262 | 262 | 303 | 6660000
42 | RPCL 210MW CCPP | 109 | 110 | 112 | 112 | 110 | 111 | 111 | 111 | 110 | 89 | 87 | 86 | 85 | 83 | 87 | 104 | 104 | 103 |  | 106 | 106 | 107 | 107 | 109 | 109 | 112 | 2397320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 10 | 24 | 36 | 42 | 43 | 43 | 32 | 25 | 10 | 1 | [9 empty] | 269000
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524640
46 | Shajibazar 330 MW CCPP | 158 | 158 | 157 | 154 | 156 | 155 | 159 | 157 | 155 | 146 | 145 | 145 | 145 | 149 | 145 | 150 | 150 | 150 |  | 143 | 143 | 145 | 145 | 144 | 145 | 145 | 3463000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 34 | 34 | 34 | 34 | 33 | 34 | 34 | 33 | 33 | 32 | 31 | 31 | 32 | 31 | 32 | 31 | 32 |  | 33 | 32 | 33 | 33 | 33 | 20 | 20 | 771360
48 | Shahjibazar 86MW PP (Shahjibazar) | 68 | 68 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 68 | 67 | 67 | 67 | 63 | 63 | 65 | 65 |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 1631040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 137 | 136 | 135 | 136 | 136 | 136 | 137 | 137 | 137 | 137 | 137 | 136 | 137 | 137 | 137 | 164 |  | 176 | 176 | 176 | 176 | 176 | 156 | 156 | 3484540
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | [16 empty] | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 79000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 162000
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 280 | 290 | 290 | 300 | 290 | 300 | 295 | 270 | 250 | 220 | 220 | 230 | 225 | 230 | 230 | 260 |  | 260 | 230 | 230 | 230 | 230 | 170 | 270 | 6356000
| Bibiyana South 400 MW | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 415 | 417 | 417 | 417 | 430 | 426 | 430 | 427 | 422 |  | 435 | 415 | 415 | 415 | 415 | 415 | 405 | 9350300
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 25 | 35 | 17 | 17 | 17 | 17 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 401314
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 432970
60 | Barabkunda 22 MW PP (Regent) | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 413424
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 11 | 11 | 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 16 |  | 16 | 13 | 13 | 13 | 16 | 16 | 16 | 235692
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 448056
63 | Impoprt (Tripura) | 72 | 68 | 66 | 64 | 68 | 70 | 70 | 62 | 68 | 72 | 70 | 74 | 76 | 76 | 72 | 72 | 94 | 104 |  | 100 | 102 | 102 | 102 | 94 | 86 | 82 | 1914240
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 32 | 28 | 12 | 5 | 5 | 5 | 5 | 8 | 2 | 2 | 2 | 3 | 7 |  | 12 | 5 | 15 | 15 | 40 | 38 | 32 | 486240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 457020
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252000
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 6 | 33 | 33 |  | 33 | 33 | 33 | 33 |  | 33 | 33 | 773600
68 | Cumilla 25 MW PP (Summit) | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 |  | 22 | 22 | 512990
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 23 | 23 | 23 | 23 | 0 |  | 22 | 22 | 20 | 14 |  | 32 | 33 | 33 | 33 | 32 | 32 | 33 | 594540
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803900
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 290636
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW |  |  |  |  | 0 | 5 | 8 | 8 | 9 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 751800
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3932640
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 3 | 50 |  | 100 | 100 | 100 | 60 | 30 |  | 0 | 373440
78 | Gazipur 52 MW PP | [16 empty] | 8 | 24 |  | 52 | 24 | 24 | 24 |  |  | 0 | 129888
79 | Kodda 150MW PP | [16 empty] | 16 | 100 |  | 150 | 116 | 115 | 85 | 32 | 16 | 16 | 493440
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 2 | 8 | 8 | 8 | 24 | 24 | 24 | 8 | 8 | 10 | 27 |  | 56 | 56 | 24 | 24 | 16 |  | 0 | 328320
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [16 empty] | 2 | 38 |  | 105 | 105 | 105 | 70 |  |  | 0 | 386088
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26880
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299841
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [7 empty] | 8 | 35 | 60 | 64 | 70 | 78 | 70 | 64 | 64 | 64 | 72 |  | 78 | 80 | 81 | 81 | 81 | 48 | 48 | 1145640
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) |  |  |  |  | 0 | 13 | 20 | 45 | 73 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 94 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1551864
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 4 | 24 | 50 | 32 | 68 | 84 | 50 | 16 | 16 | 16 | 50 |  | 93 | 100 | 100 | 100 | 65 | 32 | 32 | 883200
| Meghnaghat 104 MW PP (OPCL) | 70 | 28 | 0 |  | 0 | 1 | 34 | 71 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 86 | 1686720
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 5 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60240
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 313920
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1202524
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 16 | 32 | 32 | 32 | 16 | 16 | 7 | 7 | 7 |  | 16 | 24 | 24 | 24 | 7 | 7 | 0 | 302112
95 | Patenga 50MW PP (Baraka) | 26 | 0 |  |  | 0 | 12 | 29 | 38 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 42 | 32 | 860640
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 11 |  | 30 | 12 | 16 | 10 |  |  | 0 | 71040
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 2 | 28 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 |  |  | 0 | 170193
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 35 | 17 | 17 |  |  | 0 | 135270
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | [10 empty] | 12100
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 0 | [8 empty] | 17 | 35 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 376200
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 70 | 70 | 8 | 0 |  |  | 58 | 155 | 155 | 161 | 165 | 165 | 140 | 140 | 100 | 110 | 163 |  | 200 | 200 | 200 | 200 | 170 | 140 | 100 | 2937600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 3 | 34 | 65 | 65 | 79 | 100 | 73 | 50 | 23 | 17 | 59 |  | 125 | 132 | 131 | 132 | 117 | 76 | 50 | 1223712
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 90 | 90 | 20 | 33 | 70 | 90 | 20 | 20 | 10 | 30 | 100 |  | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 1116480
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 50 | 60 | 68 | 68 | 68 | 68 | 68 | 68 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2030400
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 120 | 120 | 40 | 50 | 123 | 147 | 147 | 143 | 148 | 148 | 145 | 143 | 142 | 143 | 142 | 145 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3298618
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [16 empty] | 4 | 10 |  | 8 | 8 | 8 | 8 |  |  | 0 | 66000
| Anwara 300 MW PP (United) | 235 | 253 | 253 | 253 | 252 | 252 | 252 | 250 | 252 | 233 | 215 | 216 | 217 | 180 | 181 | 181 | 180 | 215 |  | 215 | 215 | 215 | 215 | 215 | 216 | 215 | 5402073
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 2307840
| Anlima Energy Ltd. | [9 empty] | 11 | 41 | 38 | 36 | 31 | 31 | 21 | 21 | [8 empty] | 0 | 229582
120 | Eastern Zone Total | 4723 | 4500 | 4400 | 4401 | 4225 | 4359 | 4529 | 4866 | 5101 | 5201 | 5209 | 5369 | 5540 | 5353 | 5174 | 5085 | 5224 | 5868 |  | 6448 | 6339 | 6278 | 6022 | 5577 | 5417 | 5323 | 125885010
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 115 |  | 115 | 115 | 115 | 115 | 66 | 49 | 16 | 594240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 53 | 53 | 60 | 90 | 90 | 90 | 94 | 53 | 53 | 53 |  | 60 | 105 | 105 | 96 | 17 | 17 | 17 | 1034880
130
131
132 | United Payra Power Ltd. | 35 | 24 | 12 | 14 | 14 | 18 | 23 | 26 | 23 | 11 | 11 | 19 | 14 | 11 |  | 9 | 27 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 674400
133 | Bhola Nutan Biddut BD LTD (GAS) | 38 | 36 | 36 | 36 | 37 | 37 | 37 | 13 | 18 | 38 | 14 | 17 | 25 | 13 | 14 | 14 | 37 | 34 |  | 34 | 28 | 29 | 28 | 28 | 28 | 28 | 728890
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 31 |  | 16 | 16 | 16 |  |  |  |  | 53860
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 33 | 32 | 32 | 32 | 32 | 31 | 31 | 60 | 63 | 30 | 73 | 72 | 79 | 85 | 85 | 86 | 86 | 90 |  | 90 | 90 | 91 | 91 | 72 | 72 | 72 | 1512514
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 16 | 15 | 19 | 14 | 16 | 14 | 20 | 18 | 16 | 17 | 18 | 14 | 13 | 12 | 16 | 18 | 24 |  | 25 | 24 | 26 | 28 | 27 | 26 | 25 | 441000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 24 | [6 empty] | 29250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [12 empty] | 32 | 32 | 32 | 15 | 15 | 15 |  | 52 | 67 | 70 | 85 | 50 | 15 | 15 | 474624
146 | Bheramara HVDC | 432 | 433 | 427 | 338 | 338 | 338 | 435 | 529 | 529 | 579 | 572 | 572 | 572 | 575 | 576 | 575 | 576 | 812 |  | 813 | 812 | 812 | 812 | 813 | 629 | 435 | 13686545
147 | Bheramara 410 MW CCPP | 160 | 160 | 165 | 195 | 220 | 220 | 225 | 225 | 220 | 215 | 200 | 200 | 175 | 180 | 175 | 170 | 170 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 180 | 4696992
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 3672900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 139 | 147 | 151 | 160 | 160 | 160 | 160 | 180 | 178 | 150 | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3815691
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 334 | 305 | 311 | 284 | 365 | 359 | 374 | 353 | 412 | 314 | 363 | 383 | 343 | 300 | 318 | 308 | 351 | 350 |  | 313 | 343 | 291 | 310 | 336 | 344 | 285 | 8167091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 518160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 5 | 2 | 2 | 5 | 5 | 5 | 5 | 5 |  |  |  | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 146844
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 25 | 8 |  |  |  |  | 0 | 42720
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 42 | 50 | 52 | 50 | 53 | 51 | 51 | 51 | 90 |  | 94 | 94 | 94 | 97 | 97 | 26 | 0 | 883064
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 111 | 111 | 70 | 70 | 35 | 46 | 89 | 93 | 93 | 92 | 92 | 92 | 92 | 92 | 100 | 111 | 111 | 111 |  | 111 | 111 | 111 | 111 | 111 | 70 | 70 | 2276448
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 0 |  |  | 0 | 10 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 95 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 1898400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 34 | 39 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 45 | 70 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 681600
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 27818
178
178