## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-02 | Saturday
|  |  | Date (day): | 2021-01-02 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11284.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12675 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-01 | 2021-01-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Gas shortage
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 40 | 50 | 80 | 80
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 103 | 100 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 305 | 380 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 315 | 348 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 30 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 13 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 24 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 130 | 280 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 50 | 80 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 34 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 54 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1824 | 2309 | 3366 | 3664 | 701 | 1525
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 24 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 48 | 45 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 23 | 38 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 32 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 122 | 123 | 124 | 124
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 456 | 498 | 1366 | 1351 | 920 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 70 | 70 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 204 | 221 | 221
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 80 | 260 | 260 | 260
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 100 | 0 | 120 | 120 |  | 240 | GT Only
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 133 | 150 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 51 | 50 | 50 | 113 |  | Gas shortage & ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 57 | 85 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 90 | 110 | 148
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 15 | 21 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 16 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 890 | 1089 | 1614 | 1902 | 628 | 252
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 120 | 140 | 150 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 48 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 32 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 6 | 19 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 229 | 429 | 655.6 | 604 | 52 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 50 | 50 | 50 | 50
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 146 | 146 | 155 | 155 | 175 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 8 | 8 | 8
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 20 | 20 | 20
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 72 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 137 | 210 | 210 | 210
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 320 | 320
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 280 | 300 | 300 | 400
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1027 | 1140 | 1215 | 1345 | 175 | 456
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 439 | 721 | 446 | 783
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 210 | 245 | 225 | 225 | 185 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 90 | 90 |  | 15 | Engine problem
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 85 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 732 | 1219 | 1171 | 1794 | 185 | 73
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 26 | 24 | 26 |  | 7 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 33 | 88 | 90 | 90
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 0 | 0 | 0 |  | 622 | Unit-1 & 2 Under maint
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 15 | 36 | 36 | 36
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 67 | 150 | 260 | 262 | 0 | 823
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 150 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 417 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 77 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 722 | 915 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 155 | 185 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 20595 | 20104 | 6102 | 7934 | 11284.6 | 12675 | 3386 | 3455
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5704.3779 | 7417 | 10549.2662 | 11849.0642
| A. |  | 2021-01-01 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 7934 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5422 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7934 | MW
| 3 | Day peak Generation : |  |  | 6102 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7417 | MW
| 4 | Evening peak Generation : |  |  | 7934 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 152.4266 | MKWHr | By Solar | 0.46707 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 101.1099 | MKWHr |  | By Oil: | 33.1609 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 3.6839 | MKWHr |  | By Hydro: | 1.0567 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3386 | MW | Dhaka | 2386 | 2386 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3455 | MW | Chittagong | 846 | 846 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6841 | MW | Khulna | 987 | 987 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 802 | MMCFD |  |  | Rajshahi | 782 | 782 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 106284701.304 | ii) Oil : | Taka | 207243978.79 | Comilla | 688 | 688 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 19966738 | Total | Taka | 333495418.094 | Mymensingh | 664 | 664 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.1435 | MKWHr. | Sylhet | 302 | 302 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -197 | MW (E to W) at | 19:30 | hrs | Barisal | 227 | 227 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -313 | MW at | 23:00 | hrs | Rangpur | 535 | 535 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.4° C |  |  | Total | 7417 | 7417 |  | 0
| B. |  | 2021-01-02 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 25.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12675 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6800 | MW
| 4 | Reserve(Generation end) |  |  |  | 3675 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 172.9065 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5153 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.2029 | MKWHr. | ii) HVDC Flow at Peak Time |  | 721 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7453 | MKWHr. | iii) Maximum HVDC Flow : |  | 722 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.15 |  | (b) Today: | 98.09 |  | (c) Rule Curve: |  | 102.81
.

## YesterdayGen
2021-01-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 10 | 0 | 300 | 101 | 0 | 362 | 362 |  | 0 | 225 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 14 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 80 | 0 | 0 | 195 | 0 | 160 | 8 | 52 | 5 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 76 | 110 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 154 | 33 | 68 | 0 | 137 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 215 | 0 | 0 | 48 | 0 | 0 | 0 | 50 | 85 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 100 | 350 | 90 | 0 | 162 | 124 | 0 |  | 437 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 369 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 50 | 0 | 36 | 0 | 29 |  | 4779 | 1672 | 6451 | 2560 | 437 | 1700 | 1481 | 150 | 47 | 0 | 76 | 0 | 0 | 98.16
2:00 | 0 | 0 | 10 | 0 | 300 | 101 | 0 | 361 | 362 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 14 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 39 | 80 | 0 | 0 | 195 | 0 | 156 | 8 | 50 | 5 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 74 | 111 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 156 | 33 | 68 | 0 | 137 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 100 | 350 | 65 | 0 | 162 | 124 | 0 |  | 437 | 0 | 185 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 130 | 0 | 360 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 50 | 0 | 36 | 0 | 0 |  | 4386 | 1647 | 6033 | 2566 | 437 | 1675 | 1084 | 150 | 47 | 0 | 74 | 0 | 0 | 98.16
3:00 | 0 | 0 | 10 | 0 | 300 | 101 | 0 | 362 | 362 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 14 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 70 | 0 | 0 | 195 | 0 | 151 | 8 | 49 | 5 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 70 | 117 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 145 | 33 | 69 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 100 | 350 | 53 | 0 | 162 | 124 | 0 |  | 438 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 130 | 0 | 340 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 |  | 4243 | 1527 | 5770 | 2548 | 438 | 1658 | 859 | 150 | 47 | 0 | 70 | 0 | 0 | 98.15
4:00 | 0 | 0 | 10 | 0 | 300 | 100 | 0 | 384 | 362 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 14 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 70 | 0 | 0 | 155 | 7 | 141 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 64 | 158 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 145 | 33 | 69 | 0 | 137 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 350 | 53 | 0 | 162 | 124 | 0 |  | 343 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 130 | 0 | 343 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 4151 | 1429 | 5580 | 2560 | 343 | 1633 | 783 | 151 | 46 | 0 | 64 | 0 | 0 | 98.15
5:00 | 0 | 0 | 10 | 0 | 300 | 100 | 0 | 393 | 311 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 14 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 125 | 11 | 123 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 64 | 167 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 145 | 33 | 40 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 350 | 53 | 0 | 162 | 124 | 0 |  | 344 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 160 | 0 | 405 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 |  | 3983 | 1439 | 5422 | 2569 | 344 | 1588 | 661 | 150 | 46 | 0 | 64 | 0 | 0 | 98.15
6:00 | 0 | 0 | 10 | 0 | 300 | 97 | 0 | 393 | 362 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 14 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 35 | 70 | 0 | 0 | 125 | 11 | 122 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 66 | 168 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 143 | 33 | 61 | 0 | 137 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 44 | 0 | 0 | 32 | 0 | 25 | 0 | 10 | 50 | 80 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 300 | 53 | 0 | 162 | 124 | 0 |  | 343 | 0 | 220 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 170 | 0 | 425 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 5 | 0 | 36 | 0 | 0 |  | 4127 | 1493 | 5620 | 2541 | 343 | 1703 | 772 | 149 | 46 | 0 | 66 | 0 | 0 | 98.15
7:00 | 0 | 0 | 10 | 0 | 300 | 97 | 0 | 382 | 362 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 14 | 17 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 100 | 7 | 130 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 64 | 167 | 0 | 22 | 0 | 20 | 22 | 8 | 5 | 0 | 145 | 34 | 70 | 0 | 137 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 115 | 0 | 0 | 32 | 0 | 59 | 1 | 30 | 50 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 53 | 1 | 162 | 122 | 0 |  | 343 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 174 | 0 | 375 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 |  | 4227 | 1520 | 5747 | 2501 | 343 | 1641 | 1002 | 151 | 43 | 0 | 64 | 2 | 0 | 98.14
8:00 | 0 | 0 | 10 | 0 | 300 | 101 | 0 | 377 | 368 |  | 0 | 225 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 14 | 17 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 100 | 14 | 164 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 32 | 165 | 0 | 22 | 1 | 29 | 22 | 8 | 5 | 0 | 145 | 34 | 70 | 0 | 137 | 0 | 0 | 0 | 320 | 0 | 11 | 0 | 118 | 0 | 0 | 32 | 0 | 72 | 6 | 30 | 50 | 85 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 53 | 8 | 162 | 124 | 0 |  | 438 | 0 | 225 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 182 | 0 | 407 | 0 | 0 | 70 | 0 | 0 | 0 | 1 | 50 | 0 | 14 | 0 | 0 |  | 4313 | 1718 | 6031 | 2541 | 438 | 1711 | 1099 | 150 | 44 | 0 | 32 | 16 | 0 | 98.14
9:00 | 0 | 0 | 10 | 0 | 300 | 101 | 0 | 346 | 314 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 19 | 0 | 22 | 14 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 100 | 15 | 167 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 60 | 165 | 0 | 22 | 1 | 40 | 0 | 8 | 5 | 0 | 145 | 33 | 70 | 0 | 137 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 138 | 0 | 0 | 32 | 0 | 68 | 11 | 30 | 50 | 123 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 53 | 27 | 162 | 124 | 0 |  | 439 | 0 | 225 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 185 | 0 | 359 | 17 | 0 | 70 | 0 | 0 | 0 | 2 | 70 | 0 | 15 | 0 | 0 |  | 4297 | 1724 | 6021 | 2478 | 439 | 1563 | 1243 | 150 | 46 | 0 | 60 | 42 | 0 | 98.14
10:00 | 0 | 0 | 41 | 0 | 300 | 101 | 0 | 272 | 256 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 0 | 11 | 14 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 100 | 25 | 181 | 8 | 46 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 60 | 140 | 0 | 22 | 2 | 50 | 0 | 8 | 5 | 0 | 146 | 33 | 70 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 165 | 0 | 0 | 32 | 0 | 53 | 14 | 38 | 50 | 133 | 0 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 53 | 39 | 162 | 123 | 0 |  | 439 | 0 | 195 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 185 | 0 | 340 | 17 | 0 | 70 | 0 | 0 | 0 | 4 | 70 | 0 | 15 | 0 | 0 |  | 4237 | 1675 | 5912 | 2404 | 439 | 1466 | 1284 | 150 | 46 | 0 | 60 | 63 | 0 | 98.14
11:00 | 0 | 0 | 22 | 0 | 300 | 102 | 0 | 260 | 256 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 11 | 14 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 100 | 65 | 186 | 8 | 50 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 68 | 124 | 0 | 22 | 2 | 50 | 0 | 8 | 5 | 0 | 145 | 32 | 70 | 0 | 138 | 0 | 0 | 0 | 280 | 0 | 2 | 0 | 150 | 0 | 0 | 32 | 0 | 52 | 16 | 50 | 50 | 122 | 0 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 279 | 45 | 45 | 162 | 123 | 0 |  | 439 | 0 | 195 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 150 | 0 | 382 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 70 | 0 | 14 | 0 | 0 |  | 4251 | 1630 | 5881 | 2388 | 439 | 1506 | 1212 | 150 | 47 | 0 | 68 | 71 | 0 | 98.13
12:00 | 0 | 0 | 40 | 0 | 300 | 102 | 0 | 305 | 315 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 11 | 14 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 23 | 70 | 0 | 0 | 80 | 100 | 186 | 8 | 50 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 120 | 0 | 22 | 2 | 50 | 0 | 8 | 5 | 0 | 146 | 31 | 70 | 0 | 137 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 130 | 0 | 0 | 32 | 0 | 50 | 16 | 100 | 57 | 133 | 0 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 34 | 47 | 162 | 122 | 0 |  | 439 | 0 | 210 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 150 | 0 | 405 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 70 | 0 | 15 | 0 | 0 |  | 4426 | 1676 | 6102 | 2475 | 439 | 1598 | 1246 | 150 | 48 | 0 | 72 | 74 | 0 | 98.13
13:00 | 0 | 0 | 10 | 0 | 300 | 102 | 0 | 390 | 360 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 11 | 14 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 29 | 70 | 0 | 0 | 20 | 100 | 179 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 74 | 118 | 0 | 22 | 2 | 50 | 0 | 8 | 10 | 0 | 146 | 31 | 69 | 0 | 181 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 130 | 0 | 0 | 41 | 0 | 53 | 16 | 100 | 86 | 127 | 0 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 310 | 34 | 44 | 162 | 121 | 0 |  | 438 | 0 | 230 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 180 | 0 | 385 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 90 | 0 | 35 | 0 | 0 |  | 4590 | 1802 | 6392 | 2593 | 438 | 1662 | 1356 | 150 | 48 | 0 | 74 | 71 | 6392 | 98.13
14:00 | 0 | 0 | 10 | 0 | 300 | 102 | 0 | 360 | 258 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 11 | 14 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 29 | 70 | 0 | 0 | 125 | 0 | 204 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 68 | 117 | 0 | 22 | 2 | 50 | 0 | 8 | 20 | 0 | 145 | 31 | 69 | 0 | 183 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 95 | 0 | 0 | 65 | 0 | 50 | 14 | 100 | 120 | 100 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 100 | 320 | 27 | 37 | 54 | 121 | 0 |  | 439 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 300 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 35 | 0 | 37 | 0 | 0 |  | 4335 | 1535 | 5870 | 2516 | 439 | 1468 | 1122 | 150 | 47 | 0 | 68 | 60 | 0 | 98.13
15:00 | 0 | 0 | 80 | 0 | 300 | 102 | 0 | 286 | 279 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 11 | 17 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 30 | 70 | 0 | 0 | 35 | 0 | 205 | 8 | 45 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 66 | 119 | 0 | 0 | 1 | 50 | 0 | 8 | 20 | 0 | 147 | 31 | 69 | 0 | 195 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 95 | 0 | 0 | 47 | 0 | 40 | 11 | 100 | 120 | 50 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 300 | 17 | 27 | 54 | 121 | 0 |  | 438 | 0 | 200 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 306 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 0 | 35 | 0 | 0 |  | 4098 | 1458 | 5556 | 2399 | 438 | 1479 | 935 | 150 | 45 | 0 | 66 | 44 | 0 | 98.12
16:00 | 0 | 0 | 20 | 0 | 300 | 102 | 0 | 287 | 308 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 11 | 17 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 33 | 70 | 0 | 0 | 100 | 0 | 205 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 66 | 119 | 0 | 22 | 1 | 50 | 0 | 8 | 20 | 0 | 145 | 31 | 69 | 0 | 176 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 95 | 0 | 0 | 45 | 0 | 34 | 6 | 20 | 85 | 20 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 50 | 300 | 17 | 12 | 54 | 123 | 0 |  | 439 | 0 | 180 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 333 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 0 | 35 | 0 | 0 |  | 3917 | 1462 | 5379 | 2394 | 439 | 1556 | 707 | 150 | 45 | 0 | 66 | 22 | 0 | 98.12
17:00 | 0 | 0 | 10 | 0 | 300 | 102 | 0 | 384 | 341 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13 | 25 | 11 | 17 | 25 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 20 | 19 | 35 | 70 | 0 | 0 | 105 | 0 | 204 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 9 | 70 | 137 | 0 | 22 | 0 | 50 | 0 | 8 | 20 | 0 | 148 | 32 | 72 | 0 | 189 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 95 | 0 | 0 | 48 | 0 | 34 | 0 | 75 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 90 | 300 | 17 | 1 | 54 | 121 | 0 |  | 439 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 344 | 2 | 0 | 41 | 0 | 15 | 0 | 0 | 50 | 0 | 35 | 0 | 0 |  | 4154 | 1530 | 5684 | 2528 | 439 | 1596 | 857 | 150 | 43 | 0 | 70 | 1 | 0 | 98.12
18:00 | 0 | 0 | 12 | 0 | 300 | 103 | 0 | 304 | 322 |  | 0 | 225 | 0 | 36 | 6 | 0 | 0 | 0 | 0 | 22 | 24 | 0 | 80 | 0 | 0 | 0 | 35 | 17 | 20 | 19 | 25 | 11 | 17 | 25 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 16 | 19 | 36 | 70 | 0 | 0 | 145 | 0 | 205 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 11 | 19 | 11 | 33 | 15 | 92 | 137 | 18 | 22 | 0 | 50 | 0 | 8 | 20 | 0 | 146 | 32 | 72 | 0 | 194 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 192 | 0 | 0 | 170 | 0 | 56 | 0 | 100 | 85 | 113 | 0 | 8 | 17 | 0 | 0 | 48 | 16 | 0 | 0 | 16 | 100 | 300 | 43 | 0 | 54 | 122 | 0 |  | 721 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 6 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 143 | 0 | 431 | 53 | 0 | 100 | 67 | 35 | 0 | 0 | 100 | 0 | 36 | 0 | 0 |  | 4874 | 2379 | 7253 | 2549 | 721 | 1695 | 1926 | 150 | 43 | 77 | 92 | 0 | 0 | 98.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 40 | 0 | 300 | 103 | 0 | 370 | 306 |  | 0 | 225 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 86 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 26 | 17 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 14 | 19 | 38 | 70 | 0 | 0 | 260 | 0 | 205 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 15 | 90 | 139 | 48 | 22 | 0 | 50 | 0 | 8 | 20 | 0 | 145 | 33 | 72 | 0 | 210 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 280 | 0 | 0 | 200 | 0 | 75 | 0 | 100 | 85 | 135 | 0 | 0 | 17 | 0 | 0 | 32 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 123 | 0 |  | 721 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 150 | 0 | 416 | 53 | 0 | 113 | 85 | 35 | 0 | 0 | 113 | 0 | 36 | 0 | 0 |  | 5359 | 2467 | 7826 | 2823 | 721 | 1723 | 2197 | 150 | 45 | 77 | 90 | 0 | 0 | 98.11
19:30 | 0 | 0 | 50 | 0 | 300 | 103 | 0 | 380 | 348 |  | 0 | 225 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 100 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 28 | 17 | 30 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 70 | 0 | 0 | 260 | 0 | 204 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 15 | 90 | 140 | 48 | 22 | 0 | 50 | 0 | 8 | 20 | 0 | 146 | 33 | 72 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 80 | 0 | 100 | 85 | 150 | 0 | 0 | 17 | 0 | 0 | 32 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 123 | 0 |  | 721 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 150 | 0 | 417 | 53 | 0 | 113 | 85 | 35 | 0 | 0 | 113 | 0 | 36 | 0 | 0 |  | 5465 | 2469 | 7934 | 2854 | 721 | 1757 | 2240 | 150 | 45 | 77 | 90 | 0 | 0 | 0
20:00 | 0 | 0 | 50 | 0 | 300 | 103 | 0 | 380 | 346 |  | 0 | 225 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 100 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 28 | 17 | 30 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 70 | 0 | 0 | 140 | 0 | 205 | 8 | 46 | 5 | 5 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 15 | 92 | 139 | 48 | 20 | 0 | 50 | 0 | 8 | 20 | 0 | 145 | 33 | 72 | 0 | 216 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 81 | 0 | 100 | 85 | 150 | 0 | 0 | 17 | 0 | 0 | 33 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 123 | 0 |  | 722 | 0 | 235 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 158 | 0 | 385 | 53 | 0 | 113 | 85 | 35 | 0 | 0 | 113 | 0 | 35 | 0 | 0 |  | 5368 | 2423 | 7791 | 2730 | 722 | 1734 | 2241 | 150 | 45 | 77 | 92 | 0 | 0 | 98.11
21:00 | 0 | 0 | 50 | 0 | 300 | 104 | 0 | 384 | 365 |  | 0 | 225 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 35 | 0 | 19 | 25 | 28 | 17 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 24 | 19 | 40 | 70 | 0 | 0 | 20 | 150 | 205 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 92 | 139 | 0 | 20 | 0 | 50 | 0 | 8 | 20 | 0 | 145 | 33 | 68 | 0 | 216 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 80 | 0 | 80 | 118 | 150 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 124 | 0 |  | 721 | 0 | 225 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 182 | 0 | 416 | 90 | 0 | 113 | 85 | 35 | 0 | 0 | 113 | 0 | 36 | 0 | 0 |  | 5298 | 2495 | 7793 | 2783 | 721 | 1771 | 2162 | 150 | 46 | 68 | 92 | 0 | 0 | 98.11
22:00 | 0 | 0 | 50 | 0 | 300 | 104 | 0 | 336 | 305 |  | 0 | 225 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 28 | 17 | 29 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 16 | 19 | 40 | 70 | 0 | 0 | 25 | 235 | 204 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 88 | 139 | 0 | 20 | 0 | 50 | 0 | 8 | 20 | 0 | 145 | 33 | 69 | 0 | 216 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 300 | 0 | 0 | 150 | 0 | 81 | 0 | 50 | 120 | 150 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 124 | 0 |  | 480 | 0 | 225 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 150 | 0 | 432 | 72 | 0 | 113 | 85 | 35 | 0 | 0 | 70 | 0 | 36 | 0 | 0 |  | 5103 | 2181 | 7284 | 2772 | 480 | 1722 | 1957 | 150 | 47 | 68 | 88 | 0 | 0 | 98.1
23:00 | 0 | 0 | 53 | 0 | 300 | 105 | 0 | 342 | 305 |  | 0 | 225 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 28 | 17 | 29 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 70 | 0 | 0 | 15 | 235 | 147 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 82 | 163 | 0 | 17 | 0 | 50 | 0 | 8 | 20 | 0 | 145 | 34 | 69 | 0 | 216 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 300 | 0 | 0 | 150 | 0 | 77 | 0 | 50 | 120 | 150 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 124 | 0 |  | 332 | 0 | 225 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 150 | 0 | 395 | 17 | 0 | 70 | 32 | 35 | 0 | 0 | 35 | 0 | 15 | 0 | 0 |  | 5044 | 1692 | 6736 | 2738 | 332 | 1660 | 1719 | 150 | 47 | 8 | 82 | 0 | 0 | 98.1
24:00 | 0 | 0 | 49 | 0 | 300 | 101 | 0 | 353 | 305 |  | 0 | 225 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 28 | 17 | 29 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 70 | 0 | 0 | 15 | 120 | 129 | 8 | 52 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 70 | 165 | 0 | 22 | 0 | 50 | 0 | 8 | 5 | 0 | 146 | 33 | 69 | 0 | 216 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 300 | 0 | 0 | 24 | 0 | 41 | 0 | 0 | 120 | 150 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 16 | 100 | 300 | 80 | 0 | 54 | 124 | 0 |  | 343 | 0 | 225 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 167 | 0 | 380 | 0 | 0 | 70 | 0 | 35 | 0 | 0 | 35 | 0 | 17 | 0 | 0 |  | 4588 | 1613 | 6201 | 2635 | 343 | 1631 | 1325 | 150 | 47 | 0 | 70 | 0 | 0 | 98.1
KWH | 0 | 0 | 632000 | 0 | 7024245 | 2406636 | 0 | 8515580 | 7750000 |  | 0 | 4679850 | 0 | 240960 | 242568 | 158056 | 0 | 0 | 0 | 79680 | 261648 | 0 | 834879 | 0 | 0 | 0 | 215640 | 139111 | 49634 | 344484 | 600000 | 511380 | 451100 | 629900 | 0 | 0 | 1056698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226800 | 0 | 0 | 0 | 0 | 527520 | 459944 | 1004160 | 1710278 | 0 | 0 | 2896200 | 1040000 | 4261000 | 217454 | 1154500 | 157608 | 157920 | 0 | 1201612 | 0 | 0 | 52464 | 439992 | 257580 | 820600 | 477270 | 1745280 | 3208280 | 141120 | 450144 | 12850 | 934000 | 193920 | 196800 | 392904 | 0 | 3249000 | 783168 | 1607040 | 0 | 3972380 | 0 | 0 | 0 | 7245500 | 0 | 136000 | 0 | 3889089 | 0 | 0 | 1869600 | 0 | 1108080 | 110700 | 1292160 | 2028480 | 2843636 | 0 | 10800 | 203412 | 0 | 24479 | 237360 | 124028 | 0 | 0 | 234360 | 2373120 | 7288400 | 1397760 | 288200 | 2725920 | 2949436 | 0 |  | 11202909 | 0 | 5295456 | 0 | 1603200 | 0 | 0 | 0 | 0 | 0 | 157875 | 0 | 452200 | 5664 | 0 | 0 | 0 | 0 | 0 | 385088 | 30250 | 0 | 0 | 0 | 0 | 516000 | 0 | 161212 | 0 | 0 | 3683900 | 0 | 0 | 0 | 0 | 0 | 0 | 1376136 | 0 | 4043745 | 0 | 9049872 | 413280 | 0 | 2076480 | 494784 | 246720 | 0 | 30838 | 1412064 | 0 | 756490 | 0 | 49200 |  | 108983285 | 43443363 | 152426648 | 62099366 | 11202909 | 39010574 | 32775766 | 3683900 | 1056698 | 385088 | 1745280 | 467067 | 0
Fuel Cost | 0 | 0 | 922720 | 0 | 7796911.95 | 3176759.52 | 0 | 8600735.8 | 7982500 |  | 0 | 5101036.5 | 0 | 1828886.4 | 1671293.52 | 1337153.76 | 0 | 0 | 0 | 599990.4 | 2386229.76 | 0 | 7697584.38 | 0 | 0 | 0 | 1574172 | 1075328.03 | 489391.24 | 258363 | 450000 | 0 | 0 | 0 | 0 | 0 | 285308.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4177958.4 | 579529.44 | 2982355.2 | 2531211.44 | 0 | 0 | 2143188 | 1040000 | 3920120 | 280515.66 | 1327675 | 178097.04 | 221088 | 0 | 2054756.52 | 0 | 0 | 501031.2 | 558789.84 | 193185 | 1436050 | 357952.5 | 13089600 | 3400776.8 | 1281369.6 | 571682.88 | 204829 | 1531760 | 310272 | 350304 | 612930.24 | 0 | 3378960 | 1542840.96 | 3069446.4 | 0 | 6872217.4 | 0 | 0 | 0 | 7317955 | 0 | 103360 | 0 | 29401512.84 | 0 | 0 | 9721920 | 0 | 10903507.2 | 1294083 | 10531104 | 22009008 | 20047633.8 | 0 | 98496 | 1922243.4 | 0 | 0 | 1794441.6 | 1080283.88 | 0 | 0 | 2008465.2 | 15804979.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64528755.84 | 0 | 5560228.8 | 0 | 12601152 | 0 | 0 | 0 | 0 | 0 | 1645057.5 | 0 | 700910 | 55280.64 | 0 | 0 | 0 | 0 | 0 | 3408028.8 | 232925 | 0 | 0 | 0 | 0 | 990720 | 0 | 122037.484 | 0 | 0 | 19966738 | 0 | 0 | 0 | 0 | 0 | 0 | 2064204 | 0 | 4731181.65 | 0 | 8959373.28 | 4314643.2 | 0 | 19705795.2 | 4670760.96 | 1914547.2 | 0 | 340759.9 | 10435152.96 | 0 | 0 | 0 | 0 |  | 246290501.88 | 166948252.414 | 413238754.294 | 60419846.984 | 64528755.84 | 45864854.32 | 203835949.99 | 19966738 | 285308.46 | 3408028.8 | 13089600 | 1839671.9 | 0
Yesterday Day Peak | 0 | 0 | 40 | 0 | 300 | 102 | 0 | 305 | 315 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 11 | 14 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 24 | 19 | 23 | 70 | 0 | 0 | 80 | 100 | 186 | 8 | 50 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 120 | 0 | 22 | 2 | 50 | 0 | 8 | 5 | 0 | 146 | 31 | 70 | 0 | 137 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 130 | 0 | 0 | 32 | 0 | 50 | 16 | 100 | 57 | 133 | 0 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 100 | 280 | 34 | 47 | 162 | 122 | 0 |  | 439 | 0 | 210 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 150 | 0 | 405 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 70 | 0 | 15 | 0 | 0 |  | 6102 | DayPeak
Yesterday Evening Peak | 0 | 0 | 50 | 0 | 300 | 103 | 0 | 380 | 348 | 0 | 0 | 225 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 100 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 28 | 17 | 30 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 70 | 0 | 0 | 260 | 0 | 204 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 15 | 90 | 140 | 48 | 22 | 0 | 50 | 0 | 8 | 20 | 0 | 146 | 33 | 72 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 80 | 0 | 100 | 85 | 150 | 0 | 0 | 17 | 0 | 0 | 32 | 17 | 0 | 0 | 16 | 100 | 300 | 90 | 0 | 54 | 123 | 0 |  | 721 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 150 | 0 | 417 | 53 | 0 | 113 | 85 | 35 | 0 | 0 | 113 | 0 | 36 | 0 | 0 |  | 7934 | EvPeak
Forecast for Evening | 0 | 0 | 80 | 0 | 300 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 20 | 80 |  | 0 | 260 | 120 | 221 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 21 | 148 | 150 | 95 | 22 | 0 | 50 | 30 | 8 | 20 | 0 | 155 | 33 | 72 | 0 | 210 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 124 | 0 |  | 783 | 16 | 225 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 0 | 36 |  | 0
Forecast for Day | 0 | 0 | 80 | 0 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 10 | 80 |  | 0 | 260 | 120 | 221 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 110 | 150 | 95 | 22 | 1.6 | 50 | 0 | 8 | 20 | 0 | 155 | 33 | 72 | 0 | 210 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 90 | 50 | 162 | 124 | 0 |  | 446 | 0 | 225 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 0 | 36 |  | 0
Generation at 08:00(Today) | 0 | 0 | 79 | 0 | 300 | 99 | 0 | 351 | 320 | 0 | 0 | 0 | 0 | 7 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 28 | 24 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 70 | 0 | 0 | 20 | 100 | 150 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 60 | 165 | 0 | 22 | 1 | 50 | 0 | 8 | 5 | 0 | 144 | 32 | 70 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 65 | 0 | 0 | 32 | 0 | 33 | 6 | 60 | 50 | 142 | 0 | 0 | 0 | 0 | 1 | 16 | 17 | 0 | 0 | 26 | 100 | 280 | 90 | 10 | 54 | 124 | 0 | 0 | 532 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 180 | 0 | 420 | 0 | 0 | 113 | 0 | 35 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 0
199
| Minimum Generation |  | 5422 | 5:00
| Highest Generation |  | 7934 | 19:30
| Day Peak Generation |  | 6102 | 12:00
| Evening Peak Generation |  | 7934 | 19:30
| HVDC Max Flow |  | 722 | 20:00
| HVDC EvPeak Flow |  | 721 | 19:30
| Load factor L.F |  | 80.05%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6102 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5153 | MW
Evening Peak Generation : |  | 7934 | MW Hour : | 19:30 | Available Max Generation : |  | 12675 | MW
E.P. Demand (at gen end) : |  | 7934 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 7934 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3675 | MW
Total Gen. (MKWH) : |  | 152.4266 | System Load Factor : | 80.05% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -313 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-02
Actual : | 98.09 | Ft.(MSL) , | Rule curve : | 102.81 | Ft.( MSL )
Gas Consumed : | Total = | 802 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106284701.304
: |  | Coal : | 19966738 | Oil : | 207243978.79 | Total : | 333495418.094
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3145.2686 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1063.746 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 952.0442 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 859.8841 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 777.2678 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 627.2129 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 358.1953 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.6887 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 483.7019 |  |  | 0 | 0%
Total | 0 |  | 8429.0093 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Cox'sbazar 132/33 kV T-1 transformer was under shut down from 09:29 to 16:48 for A/M.
b) Baroirhat-PHP 132 kV Ckt was under shut down from 09:09 to 15:34 for A/M.
c) Haripur-Madanganj 132 kV Ckt was under shut down from 08:28 to 15:17 for A/M.
d) Sitalakkhya 132/33 kV GT-1 transformer was under shut down from 09:17 to 14:58 for A/M.
e) Kustia 132 kV Busbar-A & B were under shut down from 08:15 to 15:39 for C/M. |  |  |  |  | About 45 MW power interruption was under Kustia S/S area
from 08:15 to 15:39.
f) Ashuganj(S)-450 MW tripped at 13:19 due to compressor problem and GT was synchronized at 20:06.
g) Bottail 132/33 kV T-2 transformer tripped at 18:14 showing E/F & O/C relays due to problem with |  |  |  |  | About 25 MW power interruption was under Bottail S/S area
auxiliary transformer and was switched on at 18:26. |  |  |  |  | from 18:14 to 18:26.
h) Dohazari-Sikalbaha 132 kV Ckt-1 is under shut down since 07:04(2/1/21) for D/W.
i) Shahmirpur-Sikalbaha 132 kV Ckt-2 is under shut down since 07:23(2/1/21) for D/W.
j) Ghorasal-Joydevpur 132 kV Ckt-1 is under shut down since 06:44(2/1/21) for D/W.
k) Ghorasal-Joydevpur 132 kV Ckt-2 is under shut down since 06:48(2/1/21) for D/W.
l) Jamalpur 132/33 kV T-3 transformer is under shut down since 07:24(2/1/21) for D/W.
m) Jhenaidah 132 kV Bus is under shut down since 07:11(2/1/21) for D/W.
n) Purbasadipur 132 kV Bus is under shut down since 07:31(2/1/21) for C/M.
o) Aminbazar-Megnaghat 230 kV Ckt-2 is under shut down since 07:28(2/1/21) for D/W.
p) Megnaghat-450 MW was shut down at 06:24(2/1/21) for maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 50 | 632000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7024245
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2406636
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 380 | 8515580
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7750000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4679850 | GT-1 under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 240960 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 30 | 242568 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 158056 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 834879
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 344484 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 79680 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 261648 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 215640 | High Voltage.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 139111 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 49634 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1111380 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 451100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 629900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 3889089
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 80 | 1108080 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 203412 | High Voltage.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1397760 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 2725920 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2309 | 45091612
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110700
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 527520 | Red hot.
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1056698 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage & ST under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1292160
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 459944 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 1004160
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24479
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 32 | 237360 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 124028 | High Voltage.
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2373120
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 123 | 2949436 | RRT
| Chattogram area Total |  |  |  | 2266 | 498 | 10159605
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1710278 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4261000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 2896200 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 1040000 | Sync at 20:06.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 157608 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 157920 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1201612
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 2843636
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1154500 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 2028480 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439992
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1745280
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 52464 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 477270
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 16 | 234360 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1089 | 21696234
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 3208280 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 450144
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 48 | 141120 | High Voltage.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1869600 | Reserve.
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 10800 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 288200
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 19 | 226800
| Mymensingh Area Total |  |  |  | 687 | 429 | 6207794
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 50 | 934000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 193920 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 146 | 3249000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 8 | 196800 | Line O/L
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 20 | 392904 | Line O/L
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 136000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 783168 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1607040 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 210 | 3972380
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7245500 | Gas shortage
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 300 | 7288400 | On test
| Sylhet Area Total |  |  |  | 1988 | 1140 | 25999112
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 721 | 11202909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1603200
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 5295456 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 157875 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 413280 | High Voltage.
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 85 | 494784 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1219 | 19167504
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 5664 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 452200 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 1376136
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 0 | 0
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 756490 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 49200 | On test.
| Barisal Area Total |  |  |  | 1054 | 150 | 2639690
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 30250 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4043745 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 417 | 9049872 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 516000
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 161212
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 77 | 385088 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2076480
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1412064
| Rajshahi Area Total |  |  |  | 2183 | 915 | 17674711
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3683900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 246720 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30838
| Rangpur Area Total |  |  |  | 605 | 185 | 3961458
| Total |  |  |  | 20104 | 7934 | 152597720
| Eastern Grid Total |  |  |  | 13978 | 5465 | 109154357
| Western Grid Total |  |  |  | 6126 | 2469 | 43443363
| National Grid Total |  |  |  | 20104 | 7934 | 152597720
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-01
| (a) ENTIRE EASTERN GRID : |  | 4886 | MW | (b) ENTIRE WESTERN GRID : |  | 2531 | MW
| i) Dhaka area |  | 2386 | MW | i) Khulna area |  | 987 | MW
| ii) Chittagong area |  | 846 | MW | ii) Rajshahi area |  | 782 | MW
| iii) Comilla area |  | 688 | MW | iii) Barisal area |  | 227 | MW
| iv) Mymensingh area |  | 664 | MW | iv) Rangpur area |  | 535 | MW
| v) Sylhet area |  | 302 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7417 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 68 | 22:00 | Jamalpur | 78 | 18:30 | Benapol | 34 | 20:00
| Munsiganj | 80 | 21:00 | Sherpur | 96 | 18:00 | Jhenida | 82 | 18:00
| Sonargaon | 52 | 1:00 | Srimongal | 28 | 18:30 | Bottail | 74 | 18:00
| Shyampur | 156 | 1:00 | Shahjibazar | 76 | 19:30 | G.K Project | 39 | 19:00
| Bhulta | 143 | 1:00 | Fenchuganj | 24 | 18:30 | Faridpur | 120 | 19:30
| Madanganj | 47 | 18:30 | Kulawara | 28 | 18:00 | Madaripur | 61 | 19:00
| Shitalakhya | 70 | 1:00 | Sylhet | 67 | 18:00 | Sariatpur | 42 | 20:00
| Rahim steel | 3 | 1:00 | Chatak | 20 | 18:30 | Gopalganj | 57 | 19:30
| Matuail | 40 | 1:00 | Sunamganj | 26 | 19:30 | Bagerhat | 79 | 18:30
| Ghorasal | 52 | 19:30 | Biani Bazar | 33 | 18:00 | Mongla | 27 | 3:00
| Narsingdi | 105 | 20:00 | Comilla (S) | 92 | 18:00 | Satkhira | 74 | 18:30
| Haripur (SBU) | 75 | 1:00 | Comilla(N) | 67 | 18:30 | Gallamari | 15 | 1:00
| Ullon | 36 | 13:00 | Chandpur | 58 | 18:30 | Magura | 40 | 18:30
| Hasnabad | 114 | 19:30 | Feni | 74 | 18:00 | Norail | 23 | 18:30
| Magbazar | 53 | 13:00 | Chowmuhani | 110 | 18:00 | Chuadanga | 62 | 18:30
| Maniknagar | 48 | 13:00 | Ashuganj | 35 | 20:00 | Barisal(N) | 27 | 19:30
| Bangabhaban | 7 | 8:00 | Daudkandi | 82 | 22:00 | Barisal (S) | 62 | 20:00
| Narinda | 48 | 12:00 | B.Baria | 93 | 20:00 | Patuakhali | 78 | 19:30
| Dhanmondi | 68 | 13:00 | Ramganj | 64 | 20:00 | Bhandaria | 42 | 20:00
| Lalbag | 45 | 1:00 | Chaddagram | 22 | 18:00 | Borhan Uddin | 24 | 19:00
| Madartek | 43 | 13:00 | PHP | 7 | 6:00 | Ishurdi | 39 | 18:00
| Dhaka University |  |  | Madunaghat | 38 | 18:00 | Ruppur Paromanobik | 1 | 1:00
| Aftabnagar | 6 | 0.5 | Hathazari | 57 | 0.83333 | Natore | 76 | 0.77083
| Fatullah | 32 | 1:00 | Khulshi | 134 | 18:30 | Bogra | 98 | 18:30
| Mirpur | 58 | 12:00 | Halishahar | 75 | 18:30 | Noagaon | 70 | 19:30
| Kalyanpur | 51 | 18:00 | Baraulia | 109 | 9:00 | Rajshahi | 92 | 19:00
| Gulshan | 58 | 18:00 | Sikalbaha | 20 | 21:00 | Rajshahi New | 8 | 18:00
| Uttara | 47 | 18:00 | Dohazari | 54 | 19:30 | C.Nawabganj | 49 | 20:00
| Uttara New | 16 | 18:00 | Cox'sbazar | 70 | 18:30 | Amnura | 26 | 18:30
| Kamrangirchar | 46 | 13:00 | Chandraghona | 20 | 18:30 | Pabna | 68 | 18:30
| Savar | 66 | 18:30 | Kaptai | 3.5 | 18:30 | Shahjadpur | 56 | 19:00
| Bhasantec | 86 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 51 | 19:00
| Agargaon | 40 | 13:00 | Bakulia | 55 | 20:00 | Niyamatpur | 56 | 19:00
| Satmosjid | 60 | 0.54167 | Julda | 16 | 0.041667 | Joypurhat | 42 | 0.8125
| Tongi | 51 | 1:00 | TK chemical | 18.4 | 19:30 | Sherpur(Bogura) | 36 | 18:00
| Kabirpur | 118 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 30 | 18:30
| Basundhara | 76 | 18:00 | Shahmirpur | 12 | 18:30 | Rangpur | 97 | 18:30
| Manikganj | 44 | 19:30 | Khagrachhari | 18 | 7:00 | Lalmonirhat | 41 | 18:00
| Joydevpur | 74 | 21:00 | Matarbari | 24 | 18:00 | Saidpur | 66 | 20:00
| New Tongi | 60 | 12:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 77 | 19:30
| Kodda | 115 | 11:00 | Rangamati | 8 | 12:00 | Thakurgaon | 56 | 18:30
| Dhamrai | 58 | 20:00 | Abul Khair 230 | 151 | 10:00 | Palashbari | 82 | 18:00
| Rajendrapur | 58 | 19:00 | BSRM | 153 | 10:00 | Barapukuria | 34 | 20:00
| Valuka | 80 | 18:00 | GPH Ispat | 89 | 23:00 | Panchagar | 40 | 18:00
| Tangail | 128 | 18:30 | Goalpara | 16 | 13:00 | Joldhaka | 24 | 18:30
| Mymensing | 139 | 18:00 | Central s/s | 69 | 19:30 | Kurigram | 37 | 18:00
| Kishorganj | 80 | 19:30 | Noapara | 39 | 18:00
| Netrokona | 84 | 19:00 | Jessore | 72 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 19:30 | 409 | 7:00 | Kaliakoir | 408 | 0.16667 | 393 | 0.625
| Bheramara | 414 | 14:00 | 397 | 18:30 | Bhulta | 393 | 0.77083 | 379 | 0.58333
| Ashuganj(N) | 396 | 23:00 | 383 | 15:00 | Gopalganj | 428 | 0.125 | 407 | 0.54167
| Payra | 433 | 23:00 | 407 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 22:00 | 238 | 1:00 | Comilla (N) | 239 | 22:00 | 233 | 16:00
| Ishurdi | 239 | 2:00 | 230 | 12:00 | Hathazari | 225 | 1:00 | 217 | 12:00
| Ashuganj | 235 | 16:00 | 235 | 16:00 | Megnaghat | 238 | 21:00 | 230 | 10:00
| Serajganj | 235 | 2:00 | 230 | 18:00 | Fenchuganj | 243 | 1:00 | 240 | 5:00
| Baghabari | 246 | 22:00 | 240 | 12:00 | Siddhirganj | 236 | 1:00 | 229 | 16:00
| Barapukuria | 233 | 1:00 | 228 | 18:00 | Maniknagar | 233 | 7:00 | 228 | 16:00
| Bogra | 237 | 1:00 | 232 | 8:00 | Agargaon | 235 | 9:00 | 227 | 16:00
| Rajshahi | 231 | 23:00 | 223 | 12:00 | Barisal | 253 | 3:00 | 243 | 13:00
| Khulna South | 239 | 22:00 | 221 | 12:00 | AKSML | 227 | 7:00 | 217 | 16:00
| Rampura | 232 | 1:00 | 229 | 16:00 | BSRM | 230 | 7:00 | 215 | 16:00
| Haripur | 234 | 1:00 | 228 | 17:00 | Bibiyana | 245 | 8:00 | 239 | 4:00
| Hasnabad | 235 | 1:00 | 230 | 15:00 | Bhulta | 237 | 19:00 | 230 | 17:00
| Shyampur | 234 | 23:00 | 220 | 16:00 | Ashuganj (S) | 239 | 19:00 | 232 | 14:00
| Aminbazar | 236 | 24:00 | 231 | 16:00 | Kaliakoir | 236 | 22:00 | 224 | 15:00
| Tongi | 236 | 22:00 | 226 | 15:00 | GPH | 228 | 22:00 | 213 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 1:00 | 137 | 15:00 | Madanhat | 140 | 0.58333 | 132 | 0.54167
| Munsiganj | 141 | 18:30 | 135 | 15:00 | Hathazari | 138 | 0.58333 | 132 | 0.54167
| Sonargaon | 137 | 1:00 | 135 | 13:00 | Khulshi | 136 | 0.375 | 131 | 0.125
| Shyampur | 136 | 18:30 | 131 | 16:00 | Halishahar | 139 | 0.83333 | 130 | 0.66667
| Bhulta | 134 | 9:00 | 132 | 4:00 | Baraulia | 137 | 0.8125 | 129 | 0.66667
| Madanganj | 138 | 9:00 | 133 | 16:00 | Sikalbaha | 138 | 0.79167 | 129 | 0.66667
| Shitalakhya | 143 | 8:00 | 138 | 15:00 | Dohazari | 133 | 0.79167 | 125 | 0.66667
| Rahim steal | 140 | 3:00 | 137 | 17:00 | Cox'sbazar | 128 | 0.41667 | 120 | 0.66667
| Matuail | 140 | 1:00 | 137 | 15:00 | Chandraghona | 139 | 0.29167 | 131 | 0.66667
| Ghorasal | 142 | 21:00 | 140 | 1:00 | Kaptai | 135 | 0.041667 | 132 | 0.45833
| Narsinghdi | 139 | 7:00 | 135 | 24:00 | A. Khaer Stl. | 137 | 0.625 | 131 | 0.45833
| Haripur (SBU) | 140 | 7:00 | 137 | 16:00 | Bakulia | 137 | 0.625 | 128 | 0.66667
| Ullon | 134 | 2:00 | 130 | 12:00 | Julda | 138 | 0.77083 | 128 | 0.66667
| Hasnabad | 141 | 5:00 | 138 | 13:00 | TK Chemical | 137 | 0.66667 | 131 | 0.5
| Magbazar | 134 | 1:00 | 129 | 13:00 | Modern Steel | 137 | 0.83333 | 132 | 0.5
| Maniknagar | 140 | 1:00 | 137 | 16:00 | Shahmirpur | 138 | 0.8125 | 128 | 0.66667
| Bangabhaban | 140 | 1:00 | 137 | 16:00 | Khagrachhari | 137 | 0.29167 | 130 | 0.66667
| Narinda | 140 | 1:00 | 137 | 16:00 | Matarbari | 130 | 0.125 | 124 | 0.5
| Dhanmondi | 134 | 2:00 | 130 | 12:00 | Baroiar Hat | 138 | 0.041667 | 134 | 0.45833
| Lalbag | 136 | 3:00 | 130 | 16:00 | Rangamati | 137 | 15:00 | 129 | 16:00
| Madartek | 133 | 1:00 | 129 | 13:00 | Goalpara S/S | 141 | 2:00 | 130 | 12:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 140 | 21:00 | 128 | 0.5
| Aftabnagar | 134 | 5:00 | 130 | 12:00 | Noapara | 139 | 22:00 | 126 | 0.5
| Fatuiiah | 138 | 20:00 | 133 | 16:00 | Jessore | 137 | 17:00 | 116 | 0.5
| Mirpur | 137 | 6:00 | 130 | 17:00 | Benapol | 137 | 0.041667 | 118 | 0.5
| Kalyanpur | 138 | 4:00 | 133 | 17:00 | Jhenida | 135 | 1:00 | 114 | 0.5
| Gulshan | 132 | 5:00 | 129 | 17:00 | Bottail | 138 | 0.16667 | 132 | 0.75
| Uttara | 137 | 6:00 | 132 | 17:00 | G.K Project | 140 | 0.041667 | 137 | 0.75
| Uttara New | 140 | 6:00 | 136 | 13:00 | Faridpur | 140 | 0.375 | 135 | 0.5
| Kamrangirchar | 142 | 6:00 | 138 | 17:00 | Madaripur | 142 | 0.083333 | 137 | 0.54167
| Savar | 137 | 6:00 | 131 | 15:00 | Shariyatpur S/S | 144 | 2:00 | 136 | 0.5
| Bhasantec | 138 | 1:00 | 133 | 16:00 | Gopalganj | 149 | 0.41667 | 140 | 0.5
| Agargaon | 137 | 6:00 | 134 | 16:00 | Bagerhat | 146 | 4:00 | 127 | 0.5
| Satmosjid | 138 | 6:00 | 133 | 16:00 | Mongla | 138 | 14:00 | 126 | 0.5
| Tongi | 142 | 19:30 | 137 | 12:00 | Satkhira | 140 | 2:00 | 129 | 12:00
| Kabirpur | 139 | 23:00 | 134 | 16:00 | Gallamari | 142 | 0.91667 | 130 | 0.5
| Basundhara | 140 | 21:00 | 129 | 16:00 | Magura | 135 | 1:00 | 108 | 0.5
| Manikganj | 144 | 9:00 | 138 | 17:00 | Norail | 135 | 0.083333 | 110 | 0.5
| Joydevpur | 140 | 21:00 | 135 | 16:00 | Chuadanga | 133 | 3:00 | 107 | 0.5
| New Tongi | 141 | 21:00 | 136 | 13:00 | Barisal(N) | 144 | 18:30 | 136 | 12:00
| Kodda | 139 | 9:00 | 133 | 17:00 | Barisal (S) | 143 | 0.125 | 135 | 0.5
| Dhamrai | 138 | 23:00 | 133 | 15:00 | Patuakhali(S) | 143 | 0.083333 | 133 | 0.79167
| Rajendrapur | 137 | 19:00 | 131 | 15:00 | Bhandaria | 139 | 0.625 | 130 | 0.5
| Valuka | 131 | 18:30 | 124 | 1:00 | Ishurdi | 140 | 3:00 | 136 | 12:00
| Tangail | 137 | 23:00 | 132 | 12:00 | Ruppur Paromanobik | 140 | 1:00 | 135 | 12:00
| Mymensing | 134 | 23:00 | 126 | 1:00 | Natore | 141 | 1:00 | 137 | 9:00
| Kishorganj | 133 | 10:00 | 129 | 7:00 | Bogra | 140 | 1:00 | 136 | 8:00
| Netrokona | 133 | 4:00 | 127 | 8:00 | Noagaon | 137 | 6:00 | 132 | 18:00
| Jamalpur | 142 | 20:00 | 126 | 7:00 | Rajshahi | 140 | 1:00 | 137 | 12:00
| Sherpur | 139 | 19:30 | 122 | 2:00 | Rajshahi New | 142 | 1:00 | 137 | 12:00
| Srimongal | 138 | 5:00 | 136 | 9:00 | C.Nawabganj | 140 | 1:00 | 135 | 12:00
| Shahjibazar | 135 | 3:00 | 134 | 1:00 | Amnura | 141 | 1:00 | 135 | 7:00
| Fenchuganj | 138 | 11:00 | 136 | 2:00 | Pabna | 139 | 3:00 | 135 | 12:00
| Khulawara | 137 | 8:00 | 135 | 1:00 | Shahjadpur | 142 | 10:00 | 140 | 1:00
| Sylhet | 135 | 1:00 | 134 | 10:00 | Serajganj | 138 | 1:00 | 135 | 18:00
| Chatak | 135 | 23:00 | 134 | 1:00 | Niyamatpur | 136 | 2:00 | 128 | 8:00
| Sunamganj | 134 | 1:00 | 133 | 8:00 | Joypurhat | 138 | 2:00 | 134 | 8:00
| Biani Bazar | 136 | 3:00 | 134 | 12:00 | Sherpur(Bogura) | 140 | 1:00 | 137 | 7:00
| Comilla(s) | 130 | 1:00 | 127 | 11:00 | Mohastangor | 138 | 6:00 | 134 | 18:00
| Comilla(n) | 143 | 7:00 | 140 | 16:00 | Rangpur | 130 | 2:00 | 123 | 18:00
| Chandpur | 143 | 1:00 | 140 | 23:00 | Lalmonirhat | 131 | 3:00 | 123 | 18:30
| Feni | 139 | 7:00 | 135 | 18:00 | Saidpur | 131 | 5:00 | 124 | 18:00
| Chowmuhani | 137 | 21:00 | 133 | 11:00 | Purbasadipur | 130 | 2:00 | 124 | 9:00
| Ashuganj | 138 | 10:00 | 136 | 2:00 | Thakurgaon | 131 | 3:00 | 120 | 18:00
| Daudkandi | 141 | 23:00 | 138 | 13:00 | Palashbari | 136 | 2:00 | 130 | 11:00
| B.Baria | 134 | 8:00 | 132 | 13:00 | Barapukuria | 133 | 1:00 | 128 | 18:00
| Ramganj | 138 | 17:00 | 133 | 8:00 | Panchagar | 130 | 4:00 | 118 | 18:00
| Chaddagram | 139 | 1:00 | 137 | 12:00 | Joldhaka | 132 | 2:00 | 121 | 18:00
| PHP | 139 | 3:00 | 133 | 16:00 | Kurigram | 130 | 0.041667 | 122 | 0.75

## L-Curve
Date | 2021-01-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 257 | 4588 | 1613 | 6201 |  |  |  | QF-LDC-11
0:30 | 243.5 | 4683.5 | 1642.5 | 6326 | Date: | 2021-01-01
1:00 | 230 | 4779 | 1672 | 6451
1:30 | 195 | 4582.5 | 1659.5 | 6242
2:00 | 160 | 4386 | 1647 | 6033
2:30 | 153.5 | 4314.5 | 1587 | 5901.5 | [5 empty] | Gen. at Eve. Peak | 7934 | 7934 MW (19:30 )
3:00 | 147 | 4243 | 1527 | 5770 | [6 empty] | 19:30
3:30 | 168.5 | 4197 | 1478 | 5675 | [5 empty] | Gen. at Day Peak | 6102 | 6102 MW (12:00 )
4:00 | 190 | 4151 | 1429 | 5580 | [6 empty] | 12:00
4:30 | 194 | 4067 | 1434 | 5501 | [5 empty] | Highest Generation | 7934
5:00 | 198 | 3983 | 1439 | 5422 | [6 empty] | 19:30
5:30 | 191.5 | 4055 | 1466 | 5521
6:00 | 185 | 4127 | 1493 | 5620
6:30 | 202.5 | 4177 | 1506.5 | 5683.5
7:00 | 220 | 4227 | 1520 | 5747
7:30 | 216 | 4270 | 1619 | 5889
8:00 | 212 | 4313 | 1718 | 6031
8:30 | 184 | 4305 | 1721 | 6026
9:00 | 156 | 4297 | 1724 | 6021
9:30 | 90 | 4267 | 1699.5 | 5966.5
10:00 | 24 | 4237 | 1675 | 5912
10:30 | 27.5 | 4244 | 1652.5 | 5896.5
11:00 | 31 | 4251 | 1630 | 5881
11:30 | 63 | 4338.5 | 1653 | 5991.5
12:00 | 95 | 4426 | 1676 | 6102
12:30 | 96.5 | 4508 | 1739 | 6247
13:00 | 98 | 4590 | 1802 | 6392
13:30 | 79 | 4462.5 | 1668.5 | 6131
14:00 | 60 | 4335 | 1535 | 5870
14:30 | 43 | 4216.5 | 1496.5 | 5713
15:00 | 26 | 4098 | 1458 | 5556
15:30 | 41 | 4007.5 | 1460 | 5467.5
16:00 | 56 | 3917 | 1462 | 5379
16:30 | 64 | 4035.5 | 1496 | 5531.5
17:00 | 72 | 4154 | 1530 | 5684
17:30 | 129.5 | 4514 | 1954.5 | 6468.5
18:00 | 187 | 4874 | 2379 | 7253
18:30 | 188.5 | 5116.5 | 2423 | 7539.5
19:00 | 190 | 5359 | 2467 | 7826
19:30 | 197 | 5465 | 2469 | 7934
20:00 | 236 | 5368 | 2423 | 7791 |  |  |  | Executive Engineer
20:30 | 158.5 | 5333 | 2459 | 7792 |  |  |  | Network Operation Division
21:00 | 81 | 5298 | 2495 | 7793
21:30 | 110.5 | 5200.5 | 2338 | 7538.5
22:00 | 140 | 5103 | 2181 | 7284 |  |  |  |  | Page 6 of 7
22:30 | 226.5 | 5073.5 | 1936.5 | 7010
23:00 | 313 | 5044 | 1692 | 6736
23:30 | 285 | 4816 | 1652.5 | 6468.5
24:00 | 257 | 4588 | 1613 | 6201
7934 MW (19:30 )
6102 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-01 |  | Energy | 152426648
[11 empty] | 2021-01-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2635 | 343 | 1631 | 1719 | 150 | 47 | 0 | 0 | 70 | 0
0:30 | 2597.5 | 390 | 1665.5 | 1600 | 150 | 47 | 0 | 0 | 73 | 0 | Date: | 2021-01-01
1:00 | 2560 | 437 | 1700 | 1481 | 150 | 47 | 0 | 0 | 76 | 0
1:30 | 2563 | 437 | 1687.5 | 1282.5 | 150 | 47 | 0 | 0 | 75 | 0 | [7 empty] | Total Energy | 152.4266 | Total Energy Gen 152.427 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.427 MKWHr
2:00 | 2566 | 437 | 1675 | 1084 | 150 | 47 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2557 | 437.5 | 1666.5 | 971.5 | 150 | 47 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 152.4266
3:00 | 2548 | 438 | 1658 | 859 | 150 | 47 | 0 | 0 | 70 | 0
3:30 | 2554 | 390.5 | 1645.5 | 821 | 150.5 | 46.5 | 0 | 0 | 67 | 0 | [6 empty] | Shortage
4:00 | 2560 | 343 | 1633 | 783 | 151 | 46 | 0 | 0 | 64 | 0
4:30 | 2564.5 | 343.5 | 1610.5 | 722 | 150.5 | 46 | 0 | 0 | 64 | 0
5:00 | 2569 | 344 | 1588 | 661 | 150 | 46 | 0 | 0 | 64 | 0
5:30 | 2555 | 343.5 | 1645.5 | 716.5 | 149.5 | 46 | 0 | 0 | 65 | 0
6:00 | 2541 | 343 | 1703 | 772 | 149 | 46 | 0 | 0 | 66 | 0
6:30 | 2521 | 343 | 1672 | 887 | 150 | 44.5 | 0 | 0 | 65 | 1 |  |  |  |  | Coal
7:00 | 2501 | 343 | 1641 | 1002 | 151 | 43 | 0 | 0 | 64 | 2
7:30 | 2521 | 390.5 | 1676 | 1050.5 | 150.5 | 43.5 | 0 | 0 | 48 | 9 |  |  |  | Oil |  |  |  | ,
8:00 | 2541 | 438 | 1711 | 1099 | 150 | 44 | 0 | 0 | 32 | 16
8:30 | 2509.5 | 438.5 | 1637 | 1171 | 150 | 45 | 0 | 0 | 46 | 29
9:00 | 2478 | 439 | 1563 | 1243 | 150 | 46 | 0 | 0 | 60 | 42
9:30 | 2441 | 439 | 1514.5 | 1263.5 | 150 | 46 | 0 | 0 | 60 | 52.5
10:00 | 2404 | 439 | 1466 | 1284 | 150 | 46 | 0 | 0 | 60 | 63
10:30 | 2396 | 439 | 1486 | 1248 | 150 | 46.5 | 0 | 0 | 64 | 67
11:00 | 2388 | 439 | 1506 | 1212 | 150 | 47 | 0 | 0 | 68 | 71
11:30 | 2431.5 | 439 | 1552 | 1229 | 150 | 47.5 | 0 | 0 | 70 | 72.5
12:00 | 2475 | 439 | 1598 | 1246 | 150 | 48 | 0 | 0 | 72 | 74
12:30 | 2534 | 438.5 | 1630 | 1301 | 150 | 48 | 0 | 0 | 73 | 72.5
13:00 | 2593 | 438 | 1662 | 1356 | 150 | 48 | 0 | 0 | 74 | 71
13:30 | 2593 | 438 | 1662 | 1356 | 150 | 48 | 0 | 0 | 74 | 71
14:00 | 2593 | 438 | 1662 | 1356 | 150 | 48 | 0 | 0 | 74 | 71
14:30 | 2496 | 438 | 1570.5 | 1145.5 | 150 | 46.5 | 0 | 0 | 70 | 57.5
15:00 | 2399 | 438 | 1479 | 935 | 150 | 45 | 0 | 0 | 66 | 44
15:30 | 2396.5 | 438.5 | 1517.5 | 821 | 150 | 45 | 0 | 0 | 66 | 33
16:00 | 2394 | 439 | 1556 | 707 | 150 | 45 | 0 | 0 | 66 | 22
16:30 | 2461 | 439 | 1576 | 782 | 150 | 44 | 0 | 0 | 68 | 11.5
17:00 | 2528 | 439 | 1596 | 857 | 150 | 43 | 0 | 0 | 70 | 1
17:30 | 2538.5 | 580 | 1645.5 | 1391.5 | 150 | 43 | 38.5 | 0 | 81 | 0.5
18:00 | 2549 | 721 | 1695 | 1926 | 150 | 43 | 77 | 0 | 92 | 0
18:30 | 2686 | 721 | 1709 | 2061.5 | 150 | 44 | 77 | 0 | 91 | 0
19:00 | 2823 | 721 | 1723 | 2197 | 150 | 45 | 77 | 0 | 90 | 0
19:30 | 2854 | 721 | 1757 | 2240 | 150 | 45 | 77 | 0 | 90 | 0
20:00 | 2730 | 722 | 1734 | 2241 | 150 | 45 | 77 | 0 | 92 | 0
20:30 | 2756.5 | 721.5 | 1752.5 | 2201.5 | 150 | 45.5 | 72.5 | 0 | 92 | 0
21:00 | 2783 | 721 | 1771 | 2162 | 150 | 46 | 68 | 0 | 92 | 0
21:30 | 2777.5 | 600.5 | 1746.5 | 2059.5 | 150 | 46.5 | 68 | 0 | 90 | 0
22:00 | 2772 | 480 | 1722 | 1957 | 150 | 47 | 68 | 0 | 88 | 0
22:30 | 2755 | 406 | 1691 | 1838 | 150 | 47 | 38 | 0 | 85 | 0
23:00 | 2738 | 332 | 1660 | 1719 | 150 | 47 | 8 | 0 | 82 | 0
23:30 | 2686.5 | 337.5 | 1645.5 | 1719 | 150 | 47 | 4 | 0 | 76 | 0 | Max Temp. in Dhaka |  | 27.4° C
24:00 | 2635 | 343 | 1631 | 1719 | 150 | 47 | 0 | 0 | 70 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 152.427 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.427 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 47 | 47 | 47 | 46 | 46 | 46 | 43 | 44 | 46 | 46 | 47 | 48 | 48 | 47 | 45 | 45 | 43 | 43 |  | 45 | 45 | 45 | 46 | 47 | 47 | 47 | 1056698
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 14 | 16 | 16 | 16 | 14 | 11 | 6 | 0 | [9 empty] | 110700
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 215 | 95 | 30 | 15 | 15 | 44 | 115 | 118 | 138 | 165 | 150 | 130 | 130 | 95 | 95 | 95 | 95 | 192 |  | 280 | 280 | 290 | 300 | 300 | 300 | 300 | 3889089
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 41 | 22 | 40 | 10 | 10 | 80 | 20 | 10 | 12 |  | 40 | 50 | 50 | 50 | 50 | 53 | 49 | 632000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7024245
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1710278
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 157608
33 | Ashuganj 225 MW CCPP | 160 | 156 | 151 | 141 | 123 | 122 | 130 | 164 | 167 | 181 | 186 | 186 | 179 | 204 | 205 | 205 | 204 | 205 |  | 205 | 204 | 205 | 205 | 204 | 147 | 129 | 4261000
34 | Ashuganj 450 MW CCPP(South) |  |  | 0 | 7 | 11 | 11 | 7 | 14 | 15 | 25 | 65 | 100 | 100 | [9 empty] | 150 | 235 | 235 | 120 | 1040000
| Ashuganj 450 MW CCPP(North) | 195 | 195 | 195 | 155 | 125 | 125 | 100 | 100 | 100 | 100 | 100 | 80 | 20 | 125 | 35 | 100 | 105 | 145 |  | 260 | 260 | 140 | 20 | 25 | 15 | 15 | 2896200
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 157920
36 | Chandpur 150 MW CCPP | 52 | 50 | 49 | 51 | 51 | 50 | 51 | 46 | 50 | 46 | 50 | 50 | 50 | 46 | 45 | 51 | 51 | 51 |  | 51 | 51 | 46 | 51 | 51 | 50 | 52 | 1154500
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 362 | 361 | 362 | 384 | 393 | 393 | 382 | 377 | 346 | 272 | 260 | 305 | 390 | 360 | 286 | 287 | 384 | 304 |  | 370 | 380 | 380 | 384 | 336 | 342 | 353 | 8515580
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4679850
41 | Haripur 360MW CCPP(HPL) | 362 | 362 | 362 | 362 | 311 | 362 | 362 | 368 | 314 | 256 | 256 | 315 | 360 | 258 | 279 | 308 | 341 | 322 |  | 306 | 348 | 346 | 365 | 305 | 305 | 305 | 7750000
42 | RPCL 210MW CCPP | 110 | 111 | 117 | 158 | 167 | 168 | 167 | 165 | 165 | 140 | 124 | 120 | 118 | 117 | 119 | 119 | 137 | 137 |  | 139 | 140 | 139 | 139 | 139 | 163 | 165 | 3208280
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 27 | 39 | 45 | 47 | 44 | 37 | 27 | 12 | 1 | [9 empty] | 288200
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 29 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 934000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | [16 empty] | 193920
46 | Shajibazar 330 MW CCPP | 154 | 156 | 145 | 145 | 145 | 143 | 145 | 145 | 145 | 146 | 145 | 146 | 146 | 145 | 147 | 145 | 148 | 146 |  | 145 | 146 | 145 | 145 | 145 | 145 | 146 | 3249000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 33 | 33 | 32 | 31 | 31 | 31 | 31 | 31 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 34 | 33 | 783168
48 | Shahjibazar 86MW PP (Shahjibazar) | 68 | 68 | 69 | 69 | 40 | 61 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 72 | 72 |  | 72 | 72 | 72 | 68 | 69 | 69 | 69 | 1607040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 138 | 137 | 181 | 183 | 195 | 176 | 189 | 194 |  | 210 | 210 | 216 | 216 | 216 | 216 | 216 | 3972380
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 8 | 2 |  | 2 |  |  | 5 | 5 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 136000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196800
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 280 | 285 | 280 | 305 | 285 | 320 | 290 | 280 | 280 | 300 | 300 | 290 | 280 | 290 | 280 | 280 |  | 300 | 290 | 300 | 290 | 280 | 285 | 280 | 7245500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 300 | 280 | 280 | 280 | 280 | 279 | 280 | 310 | 320 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7288400
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 20 | [7 empty] | 0 | 49634
59 | Tangail Palli Power Gen 22 MW | 26 | 0 |  |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 9 |  | 20 | 19 | 19 | 18 | 19 | 19 | 19 | 226800
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 459944
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 13 | 13 | 13 | 16 | 16 | 16 | 13 | 13 | 19 |  | 19 | 19 | 19 | 19 |  |  | 0 | 344484
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 22 | 22 | 20 | 20 | 20 | 17 | 22 | 450144
63 | Impoprt (Tripura) | 76 | 74 | 70 | 64 | 64 | 66 | 64 | 32 | 60 | 60 | 68 | 72 | 74 | 68 | 66 | 66 | 70 | 92 |  | 90 | 90 | 92 | 92 | 88 | 82 | 70 | 1745280
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 38 | 38 | 40 | 35 | 40 | 40 | 40 | 40 | 40 | 23 | 29 | 29 | 30 | 33 | 35 | 36 |  | 38 | 38 | 40 | 40 | 40 | 32 | 40 | 1004160
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439992
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820600
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 9 | 15 |  | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 477270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 18 | 18 | 28 | 28 | 22 | 22 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 26 | 28 | 28 | 28 | 28 | 28 | 28 | 511380
71 | Maona 33 MW PP(Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 451100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 30 | 30 | 30 | 29 | 29 | 29 | 629900
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 100 | 100 | 97 | 97 | 101 | 101 | 101 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 103 |  | 103 | 103 | 103 | 104 | 104 | 105 | 101 | 2406636
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 26 | 26 | 26 | 0 | [12 empty] | 1 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 234360
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 2725920
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 22 |  | 24 | 24 | 24 |  |  |  | 0 | 79680
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 18 |  | 48 | 48 | 48 |  |  |  | 0 | 141120
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 11 |  | 16 | 16 | 16 |  |  |  |  | 52464
| Gazipur 100 MW PP |  |  |  |  | 0 | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 203412
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24479
| Jodiac Power | [17 empty] | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 124028
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 0 | [15 empty] | 6 |  | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 242568
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 100 | 50 | 0 | [14 empty] | 80 |  | 86 | 100 | 100 | 100 | 100 | 100 | 30 | 834879
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 35 | 0 | [15 empty] | 36 |  | 50 | 50 | 50 | 42 |  |  | 0 | 240960
| Meghnaghat 104 MW PP (OPCL) | 90 | 65 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 45 | 34 | 34 | 27 | 17 | 17 | 17 | 43 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 1397760
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 392904
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1201612
94 | Gagnagar 102 MW PP (Digital Power) | [5 empty] | 0 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 5 | 24 |  | 7 | 7 | 7 |  |  |  | 0 | 261648
95 | Patenga 50MW PP (Baraka) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20 | 16 |  | 14 | 24 | 25 | 24 | 16 |  | 0 | 527520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 3 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [8 empty] | 0 | 158056
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 | 35 | 17 | 17 | 17 | 139111
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | [10 empty] | 12850
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 |  |  |  | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 215640
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 0 |  | 0 | 3 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 41 | 65 | 47 | 45 | 48 | 170 |  | 200 | 200 | 200 | 200 | 150 | 150 | 24 | 1869600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) |  |  |  |  | 0 | 25 | 59 | 72 | 68 | 53 | 52 | 50 | 53 | 50 | 40 | 34 | 34 | 56 |  | 75 | 80 | 81 | 80 | 81 | 77 | 41 | 937008
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 0 |  |  | 0 | 10 | 30 | 30 | 30 | 38 | 50 | 100 | 100 | 100 | 100 | 20 | 75 | 100 |  | 100 | 100 | 100 | 80 | 50 | 50 | 0 | 1292160
116 | Chandpur 200MW (Desh energy) | 85 | 85 | 85 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 57 | 86 | 120 | 120 | 85 | 87 | 85 |  | 85 | 85 | 85 | 118 | 120 | 120 | 120 | 2028480
117 | Ashuganj 150MW PP (Midland) | 140 | 141 | 142 | 142 | 80 | 80 | 80 | 85 | 123 | 133 | 122 | 133 | 127 | 100 | 50 | 20 | 26 | 113 |  | 135 | 150 | 150 | 150 | 150 | 150 | 150 | 2843636
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 8 | [7 empty] | 0 | 10800
| Anwara 300 MW PP (United) | [16 empty] | 4 | 48 |  | 32 | 32 | 33 | 33 | 33 | 33 | 16 | 237360
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2373120
| Anlima Energy Ltd. | 124 | 124 | 124 | 124 | 124 | 124 | 122 | 124 | 124 | 123 | 123 | 122 | 121 | 121 | 121 | 123 | 121 | 122 |  | 123 | 123 | 123 | 124 | 124 | 124 | 124 | 2949436
120 | Eastern Zone Total | 4779 | 4386 | 4243 | 4151 | 3983 | 4127 | 4227 | 4313 | 4297 | 4237 | 4251 | 4426 | 4590 | 4335 | 4098 | 3917 | 4154 | 4874 |  | 5359 | 5465 | 5368 | 5298 | 5103 | 5044 | 4588 | 108983285
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | 49 | 0 |  | 0 | 10 | 32 | 71 | 83 | 83 | 83 | 83 | 99 | 99 | 52 | 49 | 49 | 115 |  | 115 | 115 | 115 | 115 | 115 | 83 | 49 | 1603200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | [6 empty] | 2 | 53 |  | 53 | 53 | 53 | 90 | 72 | 17 | 0 | 413280
130
131
132 | United Payra Power Ltd. | 29 | 0 | [23 empty] | 0 | 49200
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 36 | 36 | 35 | 37 | 36 | 36 | 14 | 15 | 15 | 14 | 15 | 35 | 37 | 35 | 35 | 35 | 36 |  | 36 | 36 | 35 | 36 | 36 | 15 | 17 | 756490
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 5664
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 85 | 88 | 84 | 62 | 35 | 36 | 35 | 52 | 35 | 34 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 51 |  | 88 | 88 | 89 | 90 | 92 | 91 | 91 | 1376136
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 19 | 15 | 16 | 22 | 17 | 15 | 15 | 14 | 15 | 19 | 20 | 11 | 14 | 14 | 15 | 25 |  | 25 | 26 | 25 | 23 | 25 | 24 | 24 | 452200
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 16 | 32 | 32 |  |  | 40 |  |  |  |  | 16 | [7 empty] | 0 | 157875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 67 |  | 85 | 85 | 85 | 85 | 85 | 32 | 0 | 494784
146 | Bheramara HVDC | 437 | 437 | 438 | 343 | 344 | 343 | 343 | 438 | 439 | 439 | 439 | 439 | 438 | 439 | 438 | 439 | 439 | 721 |  | 721 | 721 | 722 | 721 | 480 | 332 | 343 | 11202909
147 | Bheramara 410 MW CCPP | 175 | 185 | 190 | 210 | 215 | 220 | 225 | 225 | 225 | 195 | 195 | 210 | 230 | 200 | 200 | 180 | 200 | 220 |  | 245 | 245 | 235 | 225 | 225 | 225 | 225 | 5295456
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 151 | 150 | 149 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3683900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 160 | 170 | 174 | 182 | 185 | 185 | 150 | 150 | 180 | 130 | 130 | 130 | 130 | 143 |  | 150 | 150 | 158 | 182 | 150 | 150 | 167 | 4043745
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 369 | 360 | 340 | 343 | 405 | 425 | 375 | 407 | 359 | 340 | 382 | 405 | 385 | 300 | 306 | 333 | 344 | 431 |  | 416 | 417 | 385 | 416 | 432 | 395 | 380 | 9049872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 516000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 161212
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 6 |  | 12 | 12 |  |  |  |  | 0 | 30250
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 77 |  | 77 | 77 | 77 | 68 | 68 | 8 | 0 | 385088
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 50 | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 41 | 100 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 2076480
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 0 |  | 0 | 5 | 35 | 50 | 70 | 70 | 70 | 70 | 90 | 35 | 35 | 35 | 50 | 100 |  | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 1412064
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 15 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 246720
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 30838
178
178