## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-09 | Friday
|  | Date (day): | 2019-08-09 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12960 | MW |  |  | (b) At Evening Peak Hour : |  | 14630 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-08 | 2019-08-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 169 | 219 | 200 | 200
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 170 | 220 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 50 | 70 | 70 |  | 8
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 93 | 95 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 372 | 345 | 370 | 370 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 325 | 325 | 325 | 325
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 277 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 63 | 90 | 90 | 120 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  |  | ST Commissioning
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 101
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 48 | 40 | 47 |  | 11 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 18 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 34 | 43 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 50 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 89 | 89 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2091 | 2181 | 3341 | 3949 | 265 | 773
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 10 | 90 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.16 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 213 | 214 | 213 | 213
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 142 | 130 | 140 | 150
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 40 | 80
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 42 | 34 | 34
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 95 | 96 |  | 12 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3.6 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 141 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 0 | 0 | 0 | 0
| Karnaphuli Power Lid. |  | HFO | IPP | 110 | 0 | 0 | 97 | 0 | 109 | 109 |  |  | RRT
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 929.76 | 1212 | 1667.4 | 1774 | 140 | 110
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 120 | 120
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 181 | 220 | 220 |  |  | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 335 | 360 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 305 | 360 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 48 | 51 | 52 | 52
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 105 | 108 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 16 | 35 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 139 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 164 | 131 | 180
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1477 | 1819 | 2015 | 2314 | 390 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 180 | 190 | 190 | 50 |  | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 91 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.8 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 100 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 287.8 | 456 | 523.6 | 622 | 50 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 58 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 63 | 63 | 63 | 63
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 266 | 250 | 260 | 260
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 35 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 30 | 44 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 64 | 66 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 72 | 73 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 45 | 44 | 44 |  | 6 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 123 | 109 | 120 | 120
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 38 | 42 | 42 | 43 |  | 7 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 290 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 85 | 84 | 85 | 85
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1299 | 1362 | 1431 | 1456 | 0 | 16
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 924 | 737 | 836
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 36
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 67 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 330 | 300 | 300 | 110 |  | Gas shortage
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 35 | 100 | 10 | 100 |  | 5 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1285 | 1721 | 1587 | 1939 | 110 | 5
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 36 | 33 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 180 | 175 | 180
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 27 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 224 | 360 | 373 | 450 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 40 | 40 |  | 10 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 8 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 199 | 180 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 133 | 197 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 355 | 390 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 16 | 14 | 14
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 5 | 110 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 763 | 1207 | 1559 | 1654 | 220 | 110
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 99 | 91 | 91
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 108 | 114 | 114 | 114
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 572 | 492 | 364.5 | 463 | 463 | 472 | 0 | 105
| Total |  |  |  |  | 18969 | 18446 | 8721.06 | 10781 | 12960 | 14630 | 1175 | 1144
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8272.9135 | 10227 | 12294.0284 | 13878.2126
A. |  | 2019-08-08 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10781 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7546.42 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10781 | MW
3 | Day peak Generation : |  |  | 8721.06 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10227 | MW
4 | Evening peak Generation : |  |  | 10781 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 220.1263 | MKWHr | By Solar | 0.11334 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 147.3642 | MKWHr |  | By Oil: | 35.5836 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.7115 | MKWHr |  | By Hydro: | 4.9277 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1175 | MW | Dhaka | 3548 | 3548 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1144 | MW | Chittagong | 1038 | 1038 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2319 | MW | Khulna | 1312 | 1312 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1322.23 | MMCFD |  |  | Rajshahi | 1002 | 1002 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 143414429.242 | ii) Oil : | Taka | 277294833.01 | Comilla | 1031 | 1031 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28891615.3 | Total | Taka | 449600877.552 | Mymensingh | 856 | 856 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.033 | MKWHr. | Sylhet | 509 | 509 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 260 | MW (E to W) at | 21:00 | hrs | Barisal | 329 | 329 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 125 | MW at | 1:00 | hrs | Rangpur | 602 | 602 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.1° C |  |  | Total | 10227 | 10227 |  | 0
B. |  | 2019-08-09 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14630 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 4130 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 214.3888 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7421.41 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1956 | MKWHr. | ii) HVDC Flow at Peak Time |  | 924 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2304 | MKWHr. | iii) Maximum HVDC Flow : |  | 927 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.01 |  | (b) Today: | 104.97 |  | (c) Rule Curve: |  | 91.56
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Lid. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 199 | 211 | 0 | 0 | 97 | 69 | 346 | 0 |  | 0 | 325 | 260 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 7 | 48 | 0 | 72 | 0 | 13 | 35 | 35 | 0 | 0 | 25 | 31 | 33 | 25 | 24 | 0 | 123 | 90 | 0 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 12 | 50 | 19 | 40 | 100 | 0 | 0 | 320 | 305 | 214 | 68 | 140 | 33 | 50 | 0 | 43 | 0 | 0 | 25 | 20 | 11 | 33 | 14 | 150 | 156 | 92 | 20 | 0 | 60 | 63 | 52 | 44 | 163 | 265 | 63 | 71 | 46 | 109 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 44 | 0 | 100 | 180 | 12 | 84 | 108 | 88 | 0 | 0 | 106 | 0 | 0 |  | 925 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 14 | 36 | 16 | 180 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 22 | 52 | 30 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 0 | 95 | 0 | 196 | 0 | 354 | 105 | 0 | 113 | 105 | 114 | 0 | 0 |  | 6765 | 3365 | 10130 | 4524 | 925 | 1927 | 1974 | 250 | 213 | 167 | 150 | 0 | 0 | 105.03
2:00 | 70 | 199 | 207 | 0 | 0 | 97 | 69 | 346 | 0 |  | 0 | 325 | 260 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 7 | 20 | 0 | 72 | 0 | 12 | 35 | 0 | 0 | 0 | 25 | 31 | 33 | 25 | 24 | 0 | 126 | 90 | 0 | 120 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 19 | 39 | 100 | 0 | 0 | 320 | 310 | 214 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 14 | 146 | 156 | 92 | 20 | 0 | 60 | 63 | 52 | 44 | 163 | 260 | 60 | 71 | 46 | 109 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 15 | 0 | 100 | 120 | 0 | 85 | 108 | 88 | 0 | 0 | 106 | 0 | 0 |  | 926 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 36 | 8 | 180 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 22 | 43 | 24 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 196 | 0 | 0 | 0 | 97 | 0 | 192 | 0 | 355 | 105 | 0 | 113 | 105 | 114 | 0 | 0 |  | 6518 | 3310 | 9828 | 4513 | 926 | 1930 | 1745 | 250 | 216 | 102 | 146 | 0 | 0 | 105.03
3:00 | 70 | 199 | 203 | 0 | 0 | 97 | 69 | 345 | 0 |  | 0 | 325 | 265 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 10 | 0 | 40 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 25 | 24 | 0 | 126 | 90 | 0 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 12 | 31 | 19 | 40 | 100 | 0 | 0 | 320 | 305 | 215 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 14 | 146 | 160 | 43 | 20 | 0 | 60 | 63 | 53 | 44 | 130 | 260 | 58 | 71 | 46 | 108 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 50 | 72 | 0 | 85 | 108 | 88 | 0 | 0 | 70 | 0 | 0 |  | 926 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 180 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 22 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 198 | 0 | 0 | 0 | 61 | 0 | 193 | 0 | 355 | 70 | 0 | 55 | 105 | 114 | 0 | 0 |  | 6198 | 3129 | 9327 | 4529 | 926 | 1863 | 1329 | 250 | 216 | 68 | 146 | 0 | 0 | 105.02
4:00 | 70 | 199 | 204 | 0 | 0 | 97 | 69 | 345 | 0 |  | 0 | 325 | 257 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 127 | 90 | 0 | 120 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 19 | 40 | 100 | 0 | 0 | 320 | 310 | 214 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 20 | 140 | 160 | 8 | 20 | 0 | 60 | 63 | 53 | 44 | 130 | 260 | 58 | 71 | 46 | 105 | 17 | 43 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 85 | 108 | 88 | 0 | 0 | 69 | 0 | 0 |  | 926 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 22 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 0 | 51 | 0 | 194 | 0 | 329 | 35 | 0 | 17 | 105 | 114 | 0 | 0 |  | 6005 | 2968 | 8973 | 4545 | 926 | 1824 | 1049 | 250 | 217 | 22 | 140 | 0 | 0 | 105.02
5:00 | 70 | 199 | 210 | 0 | 0 | 97 | 68 | 344 | 0 |  | 0 | 325 | 260 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 127 | 90 | 0 | 120 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 40 | 100 | 0 | 0 | 320 | 305 | 203 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 20 | 136 | 157 | 8 | 20 | 0 | 60 | 63 | 50 | 44 | 130 | 262 | 61 | 71 | 46 | 105 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 85 | 70 | 51 | 0 | 0 | 52 | 0 | 0 |  | 926 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 0 | 51 | 0 | 196 | 0 | 335 | 17 | 0 | 17 | 69 | 106 | 0 | 0 |  | 5856 | 2882 | 8738 | 4536 | 926 | 1823 | 850 | 250 | 217 | 0 | 136 | 0 | 0 | 105.01
6:00 | 70 | 160 | 183 | 0 | 0 | 61 | 50 | 344 | 0 |  | 0 | 325 | 230 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 105 | 90 | 0 | 120 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 32 | 100 | 0 | 0 | 260 | 260 | 181 | 68 | 140 | 33 | 15 | 0 | 24 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 116 | 160 | 8 | 20 | 0 | 60 | 63 | 22 | 20 | 100 | 262 | 64 | 20 | 10 | 105 | 17 | 22 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 10 | 17 | 0 | 85 | 70 | 51 | 0 | 0.3 | 52 | 0 | 54 |  | 926 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 54 | 0 | 198 | 0 | 306 | 17 | 0 | 17 | 35 | 107 | 0 | 0 |  | 5210.69 | 2704 | 7914.69 | 4171 | 926 | 1464 | 792 | 250 | 195 | 0 | 116 | 0.69 | 0 | 105.01
7:00 | 70 | 164 | 170 | 0 | 0 | 32 | 50 | 345 | 0 |  | 0 | 325 | 240 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 124 | 90 | 0 | 120 | 0 | 165 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 10 | 80 | 0 | 0 | 260 | 260 | 159 | 68 | 140 | 33 | 15 | 0 | 10 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 102 | 157 | 8 | 20 | 0.3 | 40 | 63 | 11 | 10 | 100 | 239 | 63 | 10 | 10 | 68 | 17 | 14 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 10 | 0 | 0 | 85 | 40 | 35 | 0 | 0.8 | 52 | 0 | 54 |  | 927 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 21 | 16 | 5 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 27 | 0 | 187 | 0 | 350 | 17 | 0 | 0 | 34 | 114 | 0 | 0.5 |  | 4896.92 | 2649.5 | 7546.42 | 3970 | 927 | 1395 | 686 | 250 | 214 | 0 | 102 | 2.42 | 0 | 105
8:00 | 70 | 170 | 170 | 0 | 0 | 32 | 50 | 346 | 0 |  | 0 | 325 | 240 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 16 | 0 | 0 | 124 | 90 | 0 | 120 | 0 | 165 | 0 | 103 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 5 | 80 | 0 | 0 | 270 | 265 | 172 | 68 | 140 | 33 | 16 | 0 | 10 | 0 | 0 | 0 | 20 | 11 | 33 | 11 | 96 | 153 | 8 | 20 | 0.2 | 40 | 63 | 11 | 10 | 100 | 238 | 63 | 10 | 10 | 71 | 17 | 13 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.29 | 10 | 0 | 0 | 84 | 40 | 35 | 0 | 1 | 52 | 0 | 73 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 0 | 0 | 0 | 249 | 0 | 0 | 167 | 0 | 0 | 0 | 27 | 0 | 164 | 0 | 355 | 17 | 0 | 0 | 34 | 114 | 0 | 0 |  | 4929.49 | 2620 | 7549.49 | 3946 | 923 | 1406 | 713 | 249 | 214 | 0 | 96 | 2.49 | 0 | 105
9:00 | 70 | 170 | 170 | 0 | 0 | 57 | 50 | 358 | 0 |  | 0 | 325 | 287 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 0 | 25 | 31 | 33 | 16 | 13 | 0 | 123 | 90 | 0 | 120 | 0 | 165 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 6 | 80 | 0 | 0 | 320 | 260 | 169 | 68 | 140 | 33 | 15 | 0 | 10 | 0 | 0 | 0 | 20 | 8 | 33 | 11 | 112 | 154 | 8 | 20 | 0.9 | 40 | 63 | 11 | 10 | 130 | 236 | 61 | 10 | 10 | 69 | 17 | 13 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9.93 | 10 | 0 | 0 | 85 | 72 | 50 | 0 | 1.5 | 52 | 0 | 92 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 3 | 0 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 27 | 0 | 167 | 0 | 355 | 17 | 0 | 0 | 35 | 114 | 0 | 5 |  | 5171.33 | 2629 | 7800.33 | 3970 | 923 | 1471 | 844 | 250 | 213 | 0 | 112 | 17.33 | 0 | 0
10:00 | 70 | 169 | 200 | 0 | 0 | 87 | 50 | 350 | 0 |  | 0 | 325 | 262 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 16 | 43 | 0 | 123 | 90 | 0 | 120 | 0 | 224 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 5 | 80 | 0 | 0 | 320 | 305 | 182 | 112 | 140 | 33 | 15 | 0 | 10 | 0 | 0 | 0 | 20 | 8 | 33 | 11 | 116 | 155 | 8 | 20 | 0.9 | 60 | 63 | 11 | 10 | 130 | 265 | 56 | 10 | 10 | 70 | 17 | 13 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 8.68 | 10 | 0 | 0 | 85 | 109 | 89 | 0 | 3 | 52 | 0 | 109 |  | 924 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 3 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 25 | 0 | 133 | 0 | 315 | 17 | 0 | 0 | 36 | 114 | 0 | 0 |  | 5624.58 | 2564 | 8188.58 | 4146 | 924 | 1492 | 1035 | 250 | 213 | 0 | 116 | 12.58 | 0 | 0
11:00 | 70 | 169 | 200 | 0 | 0 | 90 | 50 | 345 | 0 |  | 0 | 325 | 280 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 16 | 43 | 0 | 123 | 90 | 0 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 8 | 80 | 0 | 0 | 320 | 305 | 182 | 112 | 140 | 33 | 48 | 0 | 10 | 0 | 0 | 0 | 20 | 8 | 33 | 10 | 124 | 155 | 8 | 20 | 1.9 | 60 | 63 | 13 | 10 | 100 | 264 | 63 | 10 | 44 | 73 | 17 | 13 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 10 | 0 | 0 | 84 | 108 | 89 | 0 | 2.6 | 51 | 0 | 109 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 250 | 0 | 0 | 201 | 0 | 0 | 0 | 28 | 0 | 132 | 0 | 340 | 17 | 0 | 0 | 36 | 114 | 0 | 6.1 |  | 5720.5 | 2622.1 | 8342.6 | 4193 | 925 | 1563 | 1064 | 250 | 213 | 0 | 124 | 10.6 | 0 | 0
12:00 | 70 | 169 | 170 | 0 | 0 | 93 | 50 | 372 | 0 |  | 0 | 325 | 300 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 34 | 0 | 123 | 90 | 10 | 120 | 0 | 217 | 0 | 142 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 10 | 80 | 0 | 0 | 360 | 290 | 203 | 105 | 140 | 33 | 48 | 0 | 16 | 0 | 0 | 0 | 21 | 8 | 33 | 14 | 126 | 151 | 8 | 20 | 0.8 | 60 | 63 | 35 | 30 | 100 | 266 | 61 | 10 | 46 | 123 | 17 | 38 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 20.16 | 10 | 0 | 0 | 85 | 108 | 89 | 0 | 3.6 | 52 | 0 | 97 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 250 | 0 | 0 | 199 | 0 | 0 | 0 | 27 | 0 | 133 | 0 | 355 | 17 | 0 | 5 | 35 | 108 | 0 | 6.5 |  | 6084.56 | 2636.5 | 8721.06 | 4401 | 925 | 1673 | 1102 | 250 | 213 | 0 | 126 | 31.06 | 0 | 0
13:00 | 70 | 169 | 170 | 0 | 0 | 94 | 50 | 372 | 0 |  | 0 | 325 | 290 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 34 | 0 | 124 | 90 | 35 | 120 | 0 | 217 | 0 | 132 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 14 | 80 | 0 | 0 | 335 | 260 | 199 | 115 | 140 | 33 | 44 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 14 | 120 | 151 | 8 | 20 | 1.1 | 60 | 63 | 47 | 43 | 100 | 260 | 62 | 50 | 46 | 117 | 17 | 43 | 10 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 4.94 | 10 | 0 | 0 | 85 | 108 | 89 | 0 | 1.3 | 55 | 6 | 0 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 250 | 0 | 0 | 199 | 0 | 0 | 0 | 26 | 0 | 133 | 0 | 380 | 17 | 0 | 4 | 54 | 113 | 0 | 8.4 |  | 6025.34 | 2688.4 | 8713.74 | 4338 | 925 | 1800 | 1051 | 250 | 214 | 0 | 120 | 15.74 | 0 | 0
14:00 | 70 | 169 | 170 | 0 | 0 | 93 | 50 | 346 | 0 |  | 0 | 325 | 260 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 24 | 0 | 0 | 8 | 0 | 12 | 17 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 124 | 90 | 70 | 120 | 0 | 177 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 16 | 80 | 0 | 0 | 320 | 250 | 162 | 115 | 138 | 33 | 43 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 33 | 10 | 136 | 151 | 8 | 20 | 1.2 | 60 | 63 | 44 | 43 | 100 | 239 | 60 | 71 | 40 | 78 | 17 | 41 | 8 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 2 | 10 | 0 | 0 | 125 | 108 | 89 | 0 | 1.64 | 102 | 11 | 0 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 3 | 0 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 26 | 0 | 130 | 0 | 378 | 35 | 0 | 0 | 54 | 114 | 0 | 3.16 |  | 5821.84 | 2675.16 | 8497 | 4093 | 925 | 1767 | 1104 | 250 | 214 | 0 | 136 | 8 | 0 | 0
15:00 | 70 | 169 | 170 | 0 | 0 | 93 | 50 | 363 | 0 |  | 0 | 325 | 290 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 24 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 40 | 0 | 124 | 90 | 70 | 120 | 0 | 177 | 0 | 101 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 16 | 80 | 0 | 0 | 340 | 300 | 174 | 115 | 140 | 33 | 46 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 10 | 134 | 151 | 8 | 20 | 0.6 | 58 | 63 | 44 | 43 | 100 | 235 | 61 | 71 | 31 | 76 | 17 | 40 | 10 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 1 | 10 | 0 | 0 | 125 | 107 | 89 | 0 | 0.76 | 106 | 9 | 0 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 3 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 0 | 27 | 0 | 60 | 0 | 390 | 35 | 0 | 0 | 54 | 114 | 0 | 6.12 |  | 5963.36 | 2613.12 | 8576.48 | 4106 | 925 | 1811 | 1128 | 250 | 214 | 0 | 134 | 8.48 | 0 | 0
16:00 | 70 | 169 | 170 | 0 | 0 | 92 | 50 | 350 | 0 |  | 0 | 325 | 250 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 24 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 18 | 0 | 124 | 90 | 80 | 120 | 0 | 178 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 30 | 80 | 0 | 0 | 335 | 305 | 160 | 115 | 140 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 11 | 130 | 153 | 8 | 20 | 0.6 | 58 | 63 | 47 | 43 | 130 | 238 | 63 | 71 | 31 | 73 | 17 | 39 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 3 | 10 | 0 | 0 | 125 | 115 | 89 | 0 | 3.63 | 106 | 16 | 0 |  | 925 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 3 | 6 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 26 | 0 | 50 | 0 | 340 | 35 | 0 | 0 | 45 | 114 | 0 | 4.8 |  | 5879.23 | 2570.8 | 8450.03 | 4126 | 925 | 1778 | 1009 | 256 | 214 | 0 | 130 | 12.03 | 0 | 0
17:00 | 70 | 169 | 170 | 0 | 0 | 88 | 50 | 345 | 0 |  | 0 | 325 | 275 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 24 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 17 | 0 | 25 | 30 | 33 | 33 | 30 | 0 | 124 | 90 | 80 | 120 | 0 | 178 | 0 | 101 | 0 |  | 0 | 0 | 0 | 10 | 1 | 6 | 19 | 30 | 80 | 0 | 0 | 335 | 305 | 160 | 108 | 140 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 0 | 124 | 159 | 8 | 20 | 0.1 | 58 | 63 | 11 | 10 | 130 | 235 | 50 | 10 | 10 | 75 | 17 | 12 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 10 | 0 | 0 | 125 | 60 | 89 | 0 | 0.804 | 70 | 0 | 0 |  | 926 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 180 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 15 | 9 | 3 | 33 | 0 | 249 | 0 | 0 | 156 | 0 | 0 | 0 | 26 | 0 | 150 | 0 | 360 | 35 | 0 | 0 | 36 | 114 | 0 | 3 |  | 5513.904 | 2702 | 8215.904 | 4178 | 926 | 1589 | 880 | 282 | 214 | 17 | 124 | 5.904 | 0 | 0
18:00 | 70 | 169 | 170 | 0 | 0 | 52 | 50 | 344 | 0 |  | 0 | 325 | 250 | 0 | 0 | 1 | 0 | 0 | 34 | 0 | 0 | 24 | 16 | 0 | 8 | 0 | 13 | 17 | 18 | 17 | 0 | 25 | 31 | 33 | 33 | 43 | 0 | 124 | 90 | 80 | 120 | 1 | 178 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 10 | 6 | 19 | 23 | 80 | 0 | 0 | 335 | 305 | 160 | 108 | 138 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 0 | 124 | 204 | 8 | 20 | 0 | 58 | 63 | 14 | 10 | 100 | 235 | 64 | 10 | 10 | 74 | 17 | 13 | 10 | 270 | 24 | 11 | 0 | 2 | 0 | 0 | 4 | 0 | 15 | 0 | 10 | 10 | 10 | 124 | 60 | 89 | 2 | 0.09 | 70 | 0 | 0 |  | 925 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 20 | 33 | 8 | 180 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 16 | 11 | 3 | 70 | 0 | 250 | 0 | 0 | 154 | 0 | 0 | 0 | 26 | 0 | 173 | 0 | 295 | 35 | 0 | 0 | 36 | 114 | 0 | 0.5 |  | 5546.09 | 2743.5 | 8289.59 | 4253 | 925 | 1449 | 935 | 320 | 214 | 69 | 124 | 0.59 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 219 | 172 | 0 | 0 | 90 | 50 | 345 | 0 |  | 0 | 325 | 285 | 5 | 0 | 15 | 0 | 0 | 37 | 0 | 0 | 32 | 48 | 0 | 60 | 0 | 13 | 35 | 54 | 35 | 22 | 25 | 20 | 33 | 33 | 43 | 0 | 124 | 90 | 90 | 120 | 9 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 27 | 9 | 19 | 39 | 80 | 0 | 0 | 335 | 305 | 161 | 108 | 135 | 33 | 51 | 0 | 35 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 160 | 196 | 25 | 20 | 0 | 58 | 63 | 11 | 19 | 100 | 234 | 63 | 10 | 10 | 74 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 19 | 0 | 71 | 50 | 20 | 84 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 924 | 0 | 270 | 0 | 62 | 0 | 0 | 0 | 37 | 73 | 40 | 180 | 32 | 60 | 0 | 0 | 60 | 43 | 0 | 85 | 40 | 8 | 42 | 40 | 30 | 17 | 16 | 3 | 89 | 0 | 250 | 0 | 0 | 158 | 0 | 0 | 0 | 27 | 4 | 175 | 0 | 380 | 80 | 0 | 28 | 99 | 114 | 0 | 0 |  | 6398 | 3466 | 9864 | 4362 | 924 | 1672 | 1784 | 339 | 214 | 409 | 160 | 0 | 0 | 0
19:30 | 70 | 219 | 171 | 0 | 0 | 87 | 50 | 345 | 0 |  | 0 | 325 | 250 | 20 | 10 | 0 | 0 | 0 | 34 | 0 | 0 | 7 | 48 | 0 | 72 | 0 | 21 | 53 | 54 | 35 | 22 | 25 | 28 | 33 | 33 | 43 | 0 | 124 | 90 | 90 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 50 | 18 | 19 | 39 | 80 | 0 | 0 | 335 | 305 | 161 | 108 | 136 | 33 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 160 | 196 | 70 | 20 | 0 | 58 | 63 | 50 | 44 | 100 | 235 | 50 | 69 | 40 | 74 | 17 | 43 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 30 | 0 | 48 | 0 | 90 | 200 | 100 | 85 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 925 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 38 | 70 | 40 | 180 | 36 | 60 | 0 | 0 | 60 | 43 | 0 | 94 | 40 | 8 | 47 | 52 | 30 | 20 | 16 | 8 | 90 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 55 | 20 | 176 | 0 | 350 | 105 | 0 | 108 | 100 | 114 | 0 | 0 |  | 6924 | 3699 | 10623 | 4383 | 925 | 1798 | 2382 | 340 | 214 | 421 | 160 | 0 | 0 | 0
20:00 | 70 | 219 | 170 | 0 | 0 | 92 | 50 | 344 | 0 |  | 0 | 325 | 265 | 7 | 3 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 40 | 0 | 72 | 0 | 24 | 53 | 54 | 35 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 124 | 90 | 90 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 50 | 39 | 19 | 41 | 80 | 0 | 0 | 335 | 305 | 181 | 108 | 139 | 33 | 51 | 0 | 35 | 0 | 0 | 50 | 21 | 11 | 33 | 18 | 156 | 181 | 91 | 20 | 0 | 58 | 63 | 50 | 44 | 100 | 235 | 63 | 72 | 45 | 74 | 17 | 42 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 190 | 88 | 84 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 925 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 43 | 67 | 40 | 180 | 35 | 64 | 0 | 0 | 60 | 0 | 0 | 94 | 40 | 8 | 0 | 52 | 30 | 22 | 16 | 8 | 91 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 88 | 0 | 180 | 0 | 375 | 105 | 0 | 90 | 99 | 114 | 0 | 0 |  | 7021 | 3671 | 10692 | 4465 | 925 | 1871 | 2395 | 341 | 214 | 325 | 156 | 0 | 0 | 0
21:00 | 70 | 219 | 170 | 0 | 0 | 95 | 50 | 345 | 0 |  | 0 | 325 | 277 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 48 | 53 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 124 | 90 | 90 | 120 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 50 | 50 | 19 | 42 | 80 | 0 | 0 | 335 | 305 | 181 | 108 | 139 | 33 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 21 | 164 | 180 | 91 | 20 | 0 | 58 | 63 | 50 | 44 | 130 | 250 | 63 | 72 | 45 | 109 | 17 | 42 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 200 | 50 | 84 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 924 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 40 | 67 | 40 | 180 | 36 | 48 | 0 | 0 | 60 | 0 | 0 | 94 | 40 | 8 | 0 | 52 | 30 | 22 | 16 | 8 | 99 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 197 | 0 | 390 | 105 | 0 | 110 | 100 | 114 | 0 | 0 |  | 7030 | 3751 | 10781 | 4568 | 924 | 1949 | 2333 | 349 | 214 | 280 | 164 | 0 | 0 | 0
22:00 | 70 | 219 | 171 | 0 | 0 | 93 | 50 | 345 | 0 |  | 0 | 325 | 265 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 53 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 120 | 90 | 100 | 120 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 50 | 50 | 19 | 42 | 80 | 0 | 0 | 335 | 305 | 181 | 108 | 140 | 33 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 21 | 166 | 193 | 91 | 20 | 0 | 58 | 63 | 53 | 44 | 130 | 250 | 64 | 74 | 45 | 110 | 17 | 42 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 200 | 50 | 85 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 924 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 36 | 67 | 40 | 180 | 37 | 48 | 0 | 0 | 60 | 0 | 0 | 88 | 40 | 8 | 0 | 52 | 28 | 22 | 16 | 8 | 101 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 97 | 0 | 206 | 0 | 360 | 105 | 0 | 110 | 99 | 114 | 0 | 0 |  | 7042 | 3723 | 10765 | 4603 | 924 | 1924 | 2319 | 351 | 210 | 268 | 166 | 0 | 0 | 0
23:00 | 70 | 219 | 170 | 0 | 0 | 97 | 69 | 345 | 0 |  | 0 | 325 | 282 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 53 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 120 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 50 | 50 | 19 | 42 | 80 | 0 | 0 | 325 | 315 | 189 | 108 | 140 | 33 | 53 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 21 | 144 | 193 | 92 | 20 | 0 | 60 | 63 | 53 | 44 | 130 | 151 | 63 | 74 | 45 | 113 | 17 | 42 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 200 | 10 | 84 | 107 | 108 | 17 | 0 | 135 | 0 | 0 |  | 925 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 36 | 0 | 8 | 180 | 36 | 48 | 0 | 0 | 60 | 0 | 0 | 55 | 40 | 8 | 0 | 34 | 28 | 22 | 16 | 8 | 84 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 97 | 0 | 206 | 0 | 409 | 105 | 0 | 111 | 100 | 114 | 0 | 0 |  | 6918 | 3608 | 10526 | 4517 | 925 | 1987 | 2254 | 334 | 214 | 151 | 144 | 0 | 0 | 0
24:00 | 70 | 219 | 170 | 0 | 0 | 97 | 69 | 348 | 0 |  | 0 | 325 | 252 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 53 | 17 | 17 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 125 | 90 | 100 | 120 | 8 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 50 | 50 | 19 | 42 | 80 | 0 | 0 | 320 | 305 | 181 | 108 | 140 | 33 | 52 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 154 | 192 | 92 | 20 | 0 | 60 | 63 | 53 | 44 | 130 | 149 | 64 | 74 | 45 | 110 | 17 | 42 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 200 | 10 | 84 | 108 | 107 | 17 | 0 | 142 | 0 | 0 |  | 925 | 0 | 330 | 0 | 94 | 0 | 0 | 0 | 36 | 0 | 8 | 180 | 36 | 48 | 0 | 0 | 60 | 0 | 0 | 24 | 40 | 8 | 0 | 34 | 28 | 22 | 16 | 8 | 91 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 0 | 97 | 0 | 204 | 0 | 373 | 105 | 0 | 113 | 100 | 114 | 0 | 0 |  | 6889 | 3538 | 10427 | 4491 | 925 | 1970 | 2211 | 341 | 215 | 120 | 154 | 0 | 0 | 0
KWH | 1516000 | 4765000 | 4365000 | 0 | 0 | 1976954 | 1376704 | 8509440 | 0 |  | 0 | 7631500 | 6474124 | 34560 | 5160 | 26244 | 0 | 0 | 1525000 | 0 | 0 | 235008 | 400320 | 0 | 701760 | 0 | 463392 | 676080 | 252251 | 260881 | 393372 | 600000 | 705420 | 797500 | 692400 | 678756 | 0 | 2775671 | 2152000 | 900000 | 3100000 | 84866 | 4655738 | 0 | 2873358 | 0 |  | 0 | 0 | 153387 | 258600 | 358080 | 505440 | 453696 | 672480 | 2076060 | 0 | 0 | 8042300 | 7182000 | 4476000 | 2308363 | 3289180 | 764280 | 1075680 | 0 | 740574 | 0 | 0 | 322003 | 489420 | 228960 | 820900 | 357920 | 3230400 | 3852880 | 878400 | 452016 | 9650 | 1329000 | 1482720 | 831600 | 836640 | 3189305 | 5595000 | 1469568 | 1160640 | 816480 | 2372370 | 438350 | 780320 | 243720 | 7354750 | 511032 | 212448 | 0 | 27600 | 0 | 0 | 439200 | 0 | 1262880 | 42255 | 1002240 | 1538400 | 309454 | 2038000 | 2324400 | 1944960 | 104545 | 17280 | 2150291 | 53940 | 607197 |  | 22195636 | 0 | 8103168 | 0 | 669120 | 0 | 0 | 0 | 248640 | 451328 | 301125 | 4366000 | 530335 | 387648 | 0 | 0 | 378000 | 44611 | 0 | 415152 | 469590 | 465156 | 147236 | 622560 | 211240 | 488640 | 358992 | 126936 | 632290 | 0 | 6079200 | 0 | 0 | 4618391 | 0 | 0 | 0 | 1251016 | 25920 | 4187545 | 0 | 8627090 | 1296480 | 0 | 964992 | 1609632 | 2718720 | 0 | 44158 |  | 147089713 | 73036547 | 220126260 | 105112368 | 22195636 | 42251783 | 33511655 | 6711490 | 4927671 | 2071914 | 3230400 | 113343 | 0
Fuel Cost | 1697920 | 5146200 | 4670550 | 0 | 0 | 1917645.38 | 2009987.84 | 6126796.8 | 0 |  | 0 | 6105200 | 5826711.6 | 352512 | 55882.8 | 269263.44 | 0 | 0 | 1906250 | 0 | 0 | 2387681.28 | 3967171.2 | 0 | 6386016 | 0 | 4337349.12 | 6483607.2 | 2406474.54 | 2598374.76 | 295029 | 450000 | 0 | 0 | 0 | 6502482.48 | 0 | 721674.46 | 559520 | 1377000 | 4743000 | 815562.26 | 4888524.9 | 0 | 3649164.66 | 0 |  | 0 | 0 | 1609029.63 | 2660994 | 3405340.8 | 4730918.4 | 417400.32 | 1869494.4 | 2179863 | 0 | 0 | 5951302 | 6032880 | 4117920 | 2262195.74 | 4374609.4 | 626709.6 | 1107950.4 | 0 | 1059020.82 | 0 | 0 | 3026828.2 | 499208.4 | 171720 | 1551501 | 268440 | 22289760 | 3159361.6 | 8353584 | 461056.32 | 158260 | 1807440 | 2016499.2 | 1130976 | 1045800 | 3954738.2 | 5147400 | 2189656.32 | 2042726.4 | 906292.8 | 3606002.4 | 696976.5 | 912974.4 | 572742 | 5221872.5 | 383274 | 161460.48 | 0 | 288972 | 0 | 0 | 4225104 | 0 | 12742459.2 | 487622.7 | 9340876.8 | 14430192 | 2899583.98 | 1915720 | 20384988 | 17329593.6 | 987950.25 | 0 | 19825683.02 | 0 | 0 |  | 59928217.2 | 0 | 6320471.04 | 0 | 6450316.8 | 0 | 0 | 0 | 2884224 | 5912396.8 | 2978126.25 | 3492800 | 822019.25 | 4163339.52 | 0 | 0 | 710640 | 496966.54 | 0 | 4110004.8 | 4869648.3 | 5446976.76 | 1774193.8 | 6200697.6 | 2080714 | 537504 | 592336.8 | 96090.552 | 4027687.3 | 0 | 24863928 | 0 | 0 | 4064184.08 | 0 | 0 | 0 | 1989115.44 | 438048 | 3685039.6 | 0 | 6297775.7 | 12264700.8 | 0 | 8858626.56 | 14341821.12 | 25392844.8 | 0 | 0 |  | 307654476.5 | 226091455.412 | 533745931.912 | 101056061.172 | 59928217.2 | 42358368.07 | 254460132.24 | 28891615.3 | 1281194.46 | 22834700.77 | 22289760 | 645882.7 | 0
Yesterday Day Peak | 70 | 169 | 170 | 0 | 0 | 93 | 50 | 372 | 0 |  | 0 | 325 | 300 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 34 | 0 | 123 | 90 | 10 | 120 | 0 | 217 | 0 | 142 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 19 | 10 | 80 | 0 | 0 | 360 | 290 | 203 | 105 | 140 | 33 | 48 | 0 | 16 | 0 | 0 | 0 | 21 | 8 | 33 | 14 | 126 | 151 | 8 | 20 | 0.8 | 60 | 63 | 35 | 30 | 100 | 266 | 61 | 10 | 46 | 123 | 17 | 38 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 20.16 | 10 | 0 | 0 | 85 | 108 | 89 | 0 | 3.6 | 52 | 0 | 97 |  | 925 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 250 | 0 | 0 | 199 | 0 | 0 | 0 | 27 | 0 | 133 | 0 | 355 | 17 | 0 | 5 | 35 | 108 | 0 | 6.5 |  | 8721.06 | DayPeak
Yesterday Evening Peak | 70 | 219 | 170 | 0 | 0 | 95 | 50 | 345 | 0 | 0 | 0 | 325 | 277 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 48 | 53 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 124 | 90 | 90 | 120 | 8 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 17 | 10 | 50 | 50 | 19 | 42 | 80 | 0 | 0 | 335 | 305 | 181 | 108 | 139 | 33 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 21 | 164 | 180 | 91 | 20 | 0 | 58 | 63 | 50 | 44 | 130 | 250 | 63 | 72 | 45 | 109 | 17 | 42 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 100 | 200 | 50 | 84 | 115 | 89 | 17 | 0 | 141 | 0 | 0 |  | 924 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 40 | 67 | 40 | 180 | 36 | 48 | 0 | 0 | 60 | 0 | 0 | 94 | 40 | 8 | 0 | 52 | 30 | 22 | 16 | 8 | 99 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 197 | 0 | 390 | 105 | 0 | 110 | 100 | 114 | 0 | 0 |  | 10781 | EvPeak
Forecast for Evening | 70 | 200 | 220 | 0 | 0 | 100 | 70 | 370 | 0 | 0 | 0 | 325 | 280 | 100 | 100 | 55 | 0 | 0 | 90 | 0 | 100 | 101 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 123 | 90 | 100 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 80 | 100 | 96 | 50 | 22 | 34 | 120 | 0 | 0 | 360 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 180 | 190 | 95 | 22 | 0 | 60 | 63 | 51 | 44 | 163 | 260 | 66 | 75 | 44 | 120 | 17 | 43 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 85 | 115 | 100 | 100 | 0 | 260 |  | 109 |  | 836 | 32 | 300 | 0 | 115 | 200 | 0 | 0 | 36 | 75 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 40 | 50 | 47 | 52 | 35 | 22 | 14 | 11 | 91 | 0 | 250 | 0 | 17 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 114 | 0
Forecast for Day | 70 | 200 | 220 | 0 | 0 | 100 | 70 | 370 | 0 | 0 | 0 | 325 | 280 | 100 | 100 | 55 | 0 | 0 | 90 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 123 | 90 | 100 | 120 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 40 | 100 | 95 | 50 | 22 | 34 | 120 | 0 | 0 | 360 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 131 | 190 | 95 | 22 | 1.6 | 60 | 63 | 51 | 44 | 163 | 260 | 64 | 73 | 44 | 120 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 150 | 85 | 115 | 100 | 50 | 4.4 | 230 |  | 109 |  | 737 | 0 | 300 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 175 | 33 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 14 | 11 | 91 | 0 | 250 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 10 | 114 | 0 | 8
Generation at 08:00(Today) | 70 | 219 | 170 | 0 | 0 | 13 | 50 | 346 | 0 | 0 | 0 | 325 | 238 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 28 | 33 | 31 | 0 | 0 | 123 | 90 | 100 | 120 | 0 | 205 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 34 | 80 | 0 | 0 | 260 | 260 | 181 | 68 | 140 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 11 | 100 | 190 | 0 | 0 | 0.7 | 60 | 63 | 5 | 5 | 100 | 152 | 63 | 10 | 10 | 75 | 0 | 5 | 0 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 60 | 53 | 0 | 1.71 | 0 | 0 | 109 | 0 | 630 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 180 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 91 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 0 | 22 | 0 | 180 | 0 | 355 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0
199
| Minimum Generation |  | 7546.42 | 7:00
| Highest Generation |  | 10781 | 21:00
| Day Peak Generation |  | 8721.06 | 12:00
| Evening Peak Generation |  | 10781 | 21:00
| HVDC Max Flow |  | 927 | 7:00
| HVDC EvPeak Flow |  | 924 | 21:00
| Load factor L.F |  | 85.07%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-09
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8721.06 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7421.41 | MW
Evening Peak Generation : |  | 10781 | MW Hour : | 21:00 | Available Max Generation : |  | 14630 | MW
E.P. Demand (at gen end) : |  | 10781 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10781 | MW Hour : | 21:00 | Reserve(Generation end) |  | 4130 | MW
Total Gen. (MKWH) : |  | 220.1263 | System Load Factor : | 85.07% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 125 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-09
Actual : | 104.97 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 1322.23 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 143414429.242
|  | Coal : | 28891615.3 | Oil : | 277294833.01 | Total : | 449600877.552
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3712.3354 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1260.6913 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1129.2333 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1020.2495 |  |  | 0 | 0%
) | 0 | 0:00 | 922.0443 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 744.0528 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 418.2358 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 191.6318 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 573.8399 |  |  | 0 | 0%
Total | 0 |  | 9972.314 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-7
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-5
|  |  |  | 3) Sikalbaha ST 60 MW | 9) AES Haripur 360 MW
4) Siddhirganj ST
5) Ashuganj #4,5
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 08:25 to 13:55 for C/M.
b) Mymensingh-Jamalpur 132 kV Ckt-2 was under shut down from 08:25 to 11:08 for C/M.
c) Hathazari-Raozan 230 kV Ckt-1 was under shut at 09:54 for C/M.
d) Rampura-Basundhara 132 kV Ckt-1 was under shut down from 10:49 to 12:26 for C/M.
e) Shariatpur 132/33 kV T-2 & T-1 transformer was under shut down from 09:50 to 12:36 and 12:36 to 19:46
respectively for D/W.
f) Madaripur-Shariatpur 132 kV Ckt-2 was shut down at 10:30 for D/W.
g) Bheramara-Kustia 132 kV Ckt-1 was under shut down from 07:27 to 18:03 for D/W.
h) Kustia 132 kV Bus-A was under shut down from 07:52 to 17:25 for D/W.
i) Sirajganj Unit-3 St synchronized at 09:23.
j) Bibiyana unit-3 ST synchronized at 13:16.
k) Ghorasal-Ishurdi 230 kV Ckt-1 was switched on at 17:48.
l) Barishal(N)-Madaripur 132 kV Ckt-1 was switched on at 17:24.
m) Mohastanghor 132/33 kV T-1 transformer was switched on at 14:39.
n) Barapukuria unit-1 synchronized at 15:30.
o) Baghabari 71 MW GT synchronized at 17:32.
p) Narshingdi 132/33 kV T-3 (new) transformer was charged at 21:03.
q) Natore 33 kV Bus-1 was under shut down from 20:35 to 21:13 for R/H maintenance at 33 kV Bus Isolator. |  |  |  |  | About 55 MW power interruption occurred under Natore S/S
area from 20:35 to 21:13.
r) Aminbazar 230 kV main Bus-1 and Aminbazar-Agargaon 230 kV Ckt-1 was shut down at 06:38(09/8/19) for C/M.
s) Jamalpur 132/33 kV T-3 transformer with 33 kV Bus section was under shut down from 07:18(09/8/19) to 09:45 |  |  |  |  | About 30 MW power interruption occurred under Jamalpur S/S
for C/M. |  |  |  |  | area from 07:18(09/8/19) to 09:45.
t) Haripur-Siddhirganj 230 kV Ckt-1 was shut down at 07:43(09/8/19) for C/M.
u) Gopalganj 132/33 kV T-1 transformer was under shut down from 07:10(09/8/19) to 09:32 for C/M.
v) Bheramara-Kustia 132 kV Ckt-2 was shut down at 07:10(09/8/19) for D/W.
w) Bagerhat 132/33 T-2 transformer along with 33 kV Bus section-2 was under shut down from 06:38(09/8/2019) to 09:15 |  |  |  |  | About 10 MW power interruption occurred under Bagerhat S/S
for R/H maintenance. |  |  |  |  | area from 06:38(09/8/19) to 09:15.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1516000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 219 | 4765000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 4365000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 50 | 1376704 | Frequency control
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 1976954 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8509440 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 325 | 7631500 | Engine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 34560 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 277 | 6474124 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 5160 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 26244 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 393372
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 63 | 1525000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 0 | 0 | Testing
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 235008 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 463392
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 676080
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 400320 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 18 | 252251 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 260881 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 701760 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1305420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 797500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 692400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 678756 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 27600 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 50 | 1262880 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 89 | 1944960 | Low demand
| Dhaka area Total |  |  |  | 5693 | 2181 | 48298266
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3100000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 84866
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 42255
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 505440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 4927671
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4655738 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2873358 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 104545 | Low demand
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 153387
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258600 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1002240
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 453696
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 672480
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 358080 | Line O/L
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17280
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 141 | 2150291 | Low demand
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 53940 | on test
| Karnaphuli Power Lid. |  | IPP | 110 | 0 | 0 | 607197 | on test
| Chattogram area Total |  |  |  | 2053 | 1212 | 22921064
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2076060 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4476000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 8042300 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7182000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 764280 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1075680
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 108 | 2308363 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 740574 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 309454 | Low demand
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 139 | 3289180
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1538400
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489420
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3230400
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820900
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 322003
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 357920 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1819 | 37251894
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 180 | 3852880 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 452016
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 878400
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9650
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 439200 | Low demand
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2324400
| Mymensingh Area Total |  |  |  | 637 | 456 | 7956546
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1329000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1482720
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3189305 | Frequency control
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 250 | 5595000 | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 831600
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 836640
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 212448
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1469568 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1160640 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 45 | 816480 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 109 | 2372370 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 438350 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 42 | 780320 | Engine problem
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 511032
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7354750 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 84 | 2038000
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243720
| Sylhet Area Total |  |  |  | 1834 | 1362 | 30661943
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 924 | 22195636
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 669120
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 248640
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 67 | 451328
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8103168 | Gas shortage
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 301125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 25920 | Reserve
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1296480
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 100 | 1609632
| Khulna Area Total |  |  |  | 2314 | 1721 | 34901049
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 387648 | Line O/L
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 530335
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 180 | 4366000
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1251016
| Barisal Area Total |  |  |  | 462 | 360 | 6534999
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 378000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 44611 | Reserve
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 469590 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 465156 | Low demand
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 147236 | Reserve
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4618391 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 197 | 4187545 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 8627090 | Frequency control
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 211240
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 488640
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 16 | 358992
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 126936 | Engine problem
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 622560
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 415152
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 964992
| Rajshahi Area Total |  |  |  | 2070 | 1207 | 22126131
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 99 | 632290
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6079200
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 114 | 2718720 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44158
| Rangpur Area Total |  |  |  | 492 | 463 | 9474368
| Total |  |  |  | 18446 | 10781 | 220126260
| Eastern Grid Total |  |  |  | 13108 | 7030 | 147089713
| Western Grid Total |  |  |  | 5338 | 3751 | 73036547
| National Grid Total |  |  |  | 18446 | 10781 | 220126260
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-08-08
(a) ENTIRE EASTERN GRID : |  | 6982 | MW | (b) ENTIRE WESTERN GRID : |  | 3245 | MW
i) Dhaka area |  | 3548 | MW | i) Khulna area |  | 1312 | MW
ii) Chittagong area |  | 1038 | MW | ii) Rajshahi area |  | 1002 | MW
iii) Comilla area |  | 1031 | MW | iii) Barisal area |  | 329 | MW
iv) Mymensingh area |  | 856 | MW | iv) Rangpur area |  | 602 | MW
v) Sylhet area |  | 509 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10227 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 1100 | Sherpur | 86 | 2200 | Jhenida | 96 | 2000
Munsiganj | 108 | 2000 | Srimongal | 39 | 1930 | Bottail | 110 | 2000
Sonargaon | 87 | 2000 | Shahjibazar | 120 | 2100 | G.K Project | 55 | 100
Shyampur | 180 | 1000 | Fenchuganj | 46 | 2100 | Faridpur | 162 | 2100
Bhulta | 177 | 1200 | Kulawara | 50 | 1930 | Madaripur | 96 | 2000
Madanganj | 48 | 100 | Sylhet | 150 | 1900 | Sariatpur | 54 | 1930
Shitalakhya | 92 | 1500 | Chatak | 32 | 2200 | Gopalganj | 84 | 2000
Rahim steel | 12 | 1600 | Sunamganj | 39 | 2100 | Bagerhat | 70 | 1930
Matuail | 90 | 1000 | Biani Bazar | 54 | 1900 | Mongla | 32 | 100
Ghorasal | 70 | 2000 | Comilla (S) | 166 | 2200 | Satkhira | 88 | 2100
Narsingdi | 132 | 2000 | Comilla(N) | 109 | 1930 | Gallamari | 47 | 2000
Haripur (SBU) | 95 | 100 | Chandpur | 101 | 2100 | Magura | 48 | 2100
Ullon | 80 | 2100 | Feni | 121 | 1900 | Norail | 22 | 2000
Hasnabad | 161 | 100 | Chowmuhani | 166 | 2200 | Chuadanga | 82 | 1930
Magbazar | 128 | 1200 | Ashuganj | 57 | 2300 | Barisal(N) | 44 | 2200
Maniknagar | 110 | 1200 | Daudkandi | 118 | 2100 | Barisal (S) | 100 | 1930
Bangabhaban | 36 | 1300 | B.Baria | 131 | 2200 | Patuakhali | 108 | 2200
Narinda | 88 | 1200 | Ramganj | 86 | 2100 | Bhandaria | 50 | 1900
Dhanmondi | 150 | 1200 | Madunaghat | 51 | 2100 | Borhan Uddin | 41 | 1930
Lalbag | 71 | 1200 | Hathazari | 93 | 1900 | Ishurdi | 56 | 1900
Madartek | 49 | 2000 | Khulshi | 82 | 1300 | Ruppur Paromanobik | 2 | 100
Mirpur | 94 | 1900 | Halishahar | 121 | 1200 | Natore | 113 | 1930
Kalyanpur | 102 | 1900 | Baraulia | 152 | 200 | Bogra | 202 | 100
Gulshan | 150 | 1200 | Sikalbaha | 30 | 200 | Noagaon | 113 | 100
Uttara | 76 | 1300 | Dohazari | 80 | 2100 | Rajshahi | 137 | 100
Uttara New | 14 | 1300 | Cox'sbazar | 86 | 2000 | C.Nawabganj | 68 | 1930
Kamrangirchar | 63 | 1930 | Chandraghona | 28 | 1900 | Amnura | 32 | 1930
Savar | 108 | 1500 | Kaptai | 4 | 1900 | Pabna | 106 | 2000
Bhasantec | 150 | 1200 | A. Khaer Stl. | 6 | 500 | Shahjadpur | 80 | 1930
Agargaon | 54 | 1200 | Bakulia | 96 | 1930 | Serajganj | 86 | 2000
Satmosjid | 92 | 1930 | Julda | 20 | 100 | Niyamatpur | 63 | 2000
Tongi | 136 | 1100 | TK chemical | 3 | 1600 | Joypurhat | 44 | 100
Kabirpur | 170 | 1000 | Modern Steel | 12 | 1300 | Mohastangor | 15 | 2000
Basundhara | 123 | 1200 | Shahmirpur | 28 | 100 | Rangpur | 138 | 1900
Manikganj | 90 | 1930 | Khagrachhari | 20 | 2000 | Lalmonirhat | 68 | 1930
Joydevpur | 178 | 2100 | Matarbari | 27 | 2000 | Saidpur | 89 | 100
New Tongi | 94 | 1200 | Baroiar Hat | 32 | 1900 | Purbasadipur | 95 | 100
Korda | 238 | 1000 | Rangamati | 12 | 1930 | Thakurgaon | 68 | 100
Dhamrai | 56 | 2100 | Abul Khair 230 | 128 | 800 | Palashbari | 91 | 2000
Valuka | 78 | 1200 | BSRM | 110 | 100 | Barapukuria | 45 | 100
Tangail | 164 | 2100 | Goalpara | 23 | 1930 | Panchagar | 49 | 2000
Mymensing | 223 | 2200 | Central s/s | 87 | 2000 | Joldhaka | 25 | 1930
Kishorganj | 116 | 2000 | Noapara | 66 | 1930 | Kurigram | 35 | 1930
Netrokona | 98 | 2100 | Jessore | 98 | 2000
Jamalpur | 111 | 2200 | Benapol | 36 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-08
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 5:00 | 382 | 12:00 | Kaliakoir | 367 | 6:00 | 357
Bheramara | 397 | 6:00 | 390 | 19:30 | Bhulta | 383 | 6:00 | 368
Ashuganj(N) | 385 | 19:30 | 373 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
Ghorasal | 230 | 1:00 | 225 | 9:00 | Hathazari | 220 | 5:00 | 216
Ishurdi | 235 | 9:00 | 228 | 1:00 | Megnaghat | 222 | 4:00 | 214
Ashuganj | 237 | 19:00 | 230 | 12:00 | Fenchuganj | 236 | 6:00 | 231
Serajganj | 231 | 18:00 | 227 | 1:00 | Siddhirganj | 220 | 7:00 | 211
Baghabari | 235 | 19:00 | 231 | 1:00 | Maniknagar | 220 | 6:00 | 209
Barapukuria | 237 | 10:00 | 224 | 1:00 | Old Airport | 219 | 6:00 | 209
Bogra | 225 | 6:00 | 214 | 1:00 | Barisal | 227 | 2:00 | 218
Khulna South | 228 | 19:30 | 216 | 16:00 | AKSML | 217 | 19:00 | 212
Rampura | 220 | 3:00 | 212 | 11:00 | BSRM | 219 | 19:00 | 214
Haripur | 220 | 7:00 | 211 | 11:00 | Bibiyana | 233 | 18:00 | 227
Hasnabad | 218 | 4:00 | 210 | 12:00 | Bhulta | 222 | 6:00 | 212
Aminbazar | 220 | 5:00 | 209 | 12:00 | Ashuganj (S) | 233 | 19:30 | 226
Tongi | 220 | 19:00 | 214 | 11:00 | Kaliakoir | 222 | 6:00 | 215
Comilla (N) | 229 | 5:00 | 222 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 600 | 124 | 1200 | Khulshi | 129 | 1900 | 125
Munsiganj | 131 | 600 | 124 | 1100 | Halishahar | 132 | 200 | 128
Megnaghat | 129 | 1900 | 124 | 1200 | Baraulia | 130 | 800 | 124
Shyampur | 131 | 1930 | 125 | 1100 | Sikalbaha | 132 | 1900 | 128
Bhulta | 125 | 1900 | 120 | 1100 | Dohazari | 130 | 600 | 124
Madanganj | 131 | 1900 | 122 | 1200 | Cox'sbazar | 127 | 900 | 118
Shitalakhya | 133 | 1900 | 121 | 1200 | Chandraghona | 132 | 300 | 129
Rahim steal | 131 | 500 | 125 | 1200 | Kaptai | 132 | 100 | 130
Matuail | 130 | 500 | 123 | 1200 | A. Khaer Stl. | 130 | 100 | 127
Ghorasal | 137 | 200 | 135 | 100 | Bakulia | 131 | 1930 | 126
Narsinghdi | 130 | 1400 | 120 | 2100 | Julda | 132 | 600 | 126
Haripur (SBU) | 131 | 600 | 126 | 1100 | TK Chemical | 132 | 1900 | 128
Ullon | 134 | 600 | 127 | 1300 | Modern Steel | 132 | 500 | 126
Hasnabad | 130 | 700 | 124 | 1200 | Shahmirpur | 131 | 100 | 127
Magbazar | 135 | 600 | 125 | 1200 | Khagrachhari | 131 | 100 | 128
Maniknagar | 135 | 600 | 125 | 1200 | Matarbari | 130 | 900 | 121
Bangabhaban | 135 | 600 | 125 | 1200 | Baroiar Hat | 129 | 700 | 125
Narinda | 135 | 600 | 125 | 1200 | Rangamati | 131 | 100 | 129
Dhanmondi | 134 | 600 | 127 | 1300 | Goalpara | 139 | 1930 | 130
Lalbag | 130 | 700 | 120 | 1200 | Central s/s | 138 | 1930 | 129
Madartek | 135 | 600 | 126 | 1200 | Noapara | 135 | 600 | 124
Mirpur | 137 | 600 | 127 | 1400 | Jessore | 129 | 700 | 121
Kalyanpur | 136 | 700 | 129 | 1300 | Benapol | 132 | 1800 | 125
Gulshan | 134 | 600 | 125 | 1200 | Jhenida | 136 | 900 | 123
Uttara | 132 | 100 | 124 | 1300 | Bottail | 136 | 1500 | 130
Uttara New | 129 | 600 | 124 | 800 | G.K Project | 141 | 1800 | 135
Kamrangirchar | 131 | 300 | 121 | 1200 | Faridpur | 132 | 1300 | 126
Savar | 133 | 1930 | 125 | 1200 | Madaripur | 134 | 1400 | 126
Bhasantec | 134 | 600 | 126 | 1200 | Sariatpur | 132 | 1300 | 122
Agargaon | 135 | 600 | 127 | 1200 | Gopalganj | 141 | 1830 | 131
Satmosjid | 135 | 600 | 127 | 1200 | Bagerhat | 135 | 2200 | 128
Tongi | 134 | 1900 | 129 | 800 | Mongla | 134 | 1930 | 126
Kabirpur | 132 | 1800 | 127 | 400 | Satkhira | 136 | 600 | 128
Basundhara | 130 | 1900 | 127 | 1700 | Gallamari | 139 | 1930 | 128
Manikganj | 136 | 1400 | 128 | 800 | Magura | 130 | 700 | 118
Joydevpur | 136 | 2000 | 130 | 1300 | Norail | 130 | 800 | 117
New Tongi | 132 | 1900 | 126 | 800 | Chuadanga | 126 | 700 | 116
Kodda | 135 | 1400 | 120 | 800 | Barisal(N) | 137 | 200 | 129
Dhamrai | 132 | 1900 | 127 | 2100 | Barisal (S) | 134 | 100 | 129
Valuka | 129 | 1800 | 118 | 100 | Patuakhali | 134 | 700 | 124
Tangail | 131 | 400 | 122 | 2100 | Bhandaria | 135 | 300 | 129
Mymensing | 128 | 1000 | 118 | 2200 | Ishurdi | 139 | 1800 | 134
Kishorganj | 129 | 1000 | 122 | 2100 | Ruppur Paromanobik | 138 | 500 | 134
Netrokona | 127 | 1800 | 115 | 2100 | Natore | 136 | 600 | 130
Jamalpur | 135 | 1930 | 123 | 1700 | Bogra | 137 | 1700 | 129
Sherpur | 135 | 1900 | 122 | 800 | Noagaon | 132 | 600 | 123
Srimongal | 135 | 500 | 132 | 100 | Rajshahi | 134 | 1900 | 126
Shahjibazar | 134 | 1400 | 130 | 1200 | C.Nawabganj | 131 | 1900 | 123
Fenchuganj | 135 | 600 | 132 | 1200 | Amnura | 134 | 1900 | 122
Khulawara | 133 | 500 | 131 | 1900 | Pabna | 137 | 1800 | 131
Sylhet | 133 | 500 | 131 | 1900 | Shahjadpur | 141 | 1800 | 136
Chatak | 133 | 1400 | 129 | 1900 | Serajganj | 136 | 1800 | 131
Sunamganj | 132 | 700 | 127 | 2000 | Niyamatpur | 132 | 1700 | 120
Biani Bazar | 133 | 1400 | 127 | 1900 | Joypurhat | 135 | 1700 | 121
Comilla(s) | 125 | 500 | 120 | 1900 | Mohastangor | 137 | 1830 | 127
Comilla(n) | 135 | 600 | 132 | 1200 | Rangpur | 134 | 600 | 118
Chandpur | 135 | 700 | 127 | 1700 | Lalmonirhat | 131 | 900 | 112
Feni | 129 | 800 | 123 | 2300 | Saidpur | 134 | 600 | 118
Chowmuhani | 127 | 700 | 121 | 2200 | Purbasadipur | 134 | 800 | 116
Ashuganj | 135 | 500 | 130 | 2100 | Thakurgaon | 131 | 1000 | 112
Daudkandi | 131 | 700 | 123 | 1300 | Palashbari | 134 | 1830 | 122
B.Baria | 132 | 1100 | 127 | 100 | Barapukuria | 137 | 1000 | 124

## L-Curve
Date | 2019-08-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 250 | 6889 | 3538 | 10427 |  |  |  | QF-LDC-12
0:30 | 187.5 | 6827 | 3451.5 | 10278.5 | Date: | 2019-08-08
1:00 | 125 | 6765 | 3365 | 10130
1:30 | 140 | 6641.5 | 3337.5 | 9979
2:00 | 155 | 6518 | 3310 | 9828
2:30 | 182.5 | 6358 | 3219.5 | 9577.5 | [5 empty] | Gen. at Eve. Peak | 10781 | 10781 MW (21:00 )
3:00 | 210 | 6198 | 3129 | 9327 | [6 empty] | 21:00
3:30 | 215 | 6101.5 | 3048.5 | 9150 | [5 empty] | Gen. at Day Peak | 8721.06 | 8721.06 MW (12:00 )
4:00 | 220 | 6005 | 2968 | 8973 | [6 empty] | 12:00
4:30 | 240 | 5930.5 | 2925 | 8855.5 | [5 empty] | Highest Generation | 10781
5:00 | 260 | 5856 | 2882 | 8738 | [6 empty] | 21:00
5:30 | 338 | 5533.345 | 2793 | 8326.345
6:00 | 416 | 5210.69 | 2704 | 7914.69
6:30 | 423 | 5053.805 | 2676.75 | 7730.555
7:00 | 430 | 4896.92 | 2649.5 | 7546.42
7:30 | 500 | 4913.205 | 2634.75 | 7547.955
8:00 | 570 | 4929.49 | 2620 | 7549.49
8:30 | 570 | 5050.41 | 2624.5 | 7674.91
9:00 | 570 | 5171.33 | 2629 | 7800.33
9:30 | 552.5 | 5397.955 | 2596.5 | 7994.455
10:00 | 535 | 5624.58 | 2564 | 8188.58
10:30 | 552.5 | 5672.54 | 2593.05 | 8265.59
11:00 | 570 | 5720.5 | 2622.1 | 8342.6
11:30 | 535 | 5902.53 | 2629.3 | 8531.83
12:00 | 500 | 6084.56 | 2636.5 | 8721.06
12:30 | 497.5 | 6054.95 | 2662.45 | 8717.4
13:00 | 495 | 6025.34 | 2688.4 | 8713.74
13:30 | 512.5 | 5923.59 | 2681.78 | 8605.37
14:00 | 530 | 5821.84 | 2675.16 | 8497
14:30 | 475 | 5892.6 | 2644.14 | 8536.74
15:00 | 420 | 5963.36 | 2613.12 | 8576.48
15:30 | 445 | 5921.295 | 2591.96 | 8513.255
16:00 | 470 | 5879.23 | 2570.8 | 8450.03
16:30 | 515 | 5696.567 | 2636.4 | 8332.967
17:00 | 560 | 5513.904 | 2702 | 8215.904
17:30 | 488 | 5529.997 | 2722.75 | 8252.747
18:00 | 416 | 5546.09 | 2743.5 | 8289.59
18:30 | 333 | 5972.045 | 3104.75 | 9076.795
19:00 | 250 | 6398 | 3466 | 9864
19:30 | 230 | 6924 | 3699 | 10623
20:00 | 188 | 7021 | 3671 | 10692 |  |  |  | Executive Engineer
20:30 | 224 | 7025.5 | 3711 | 10736.5 |  |  |  | Network Operation Division
21:00 | 260 | 7030 | 3751 | 10781
21:30 | 255 | 7036 | 3737 | 10773
22:00 | 250 | 7042 | 3723 | 10765 |  |  |  |  | Page 6 of 7
22:30 | 275 | 6980 | 3665.5 | 10645.5
23:00 | 300 | 6918 | 3608 | 10526
23:30 | 275 | 6903.5 | 3573 | 10476.5
24:00 | 250 | 6889 | 3538 | 10427
10781 MW (21:00 )
8721.06 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-08 |  | Energy | 220126260
[10 empty] | 2019-08-08 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4491 | 925 | 1970 | 2211 | 341 | 215 | 120 | 0 | 154
0:30 | 4507.5 | 925 | 1948.5 | 2092.5 | 295.5 | 214 | 143.5 | 0 | 152 | Date: | 2019-08-08
1:00 | 4524 | 925 | 1927 | 1974 | 250 | 213 | 167 | 0 | 150
1:30 | 4518.5 | 925.5 | 1928.5 | 1859.5 | 250 | 214.5 | 134.5 | 0 | 148 | [7 empty] | Total Energy | 220.1263 | Total Energy Gen 220.126 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 220.126 MKWHr
2:00 | 4513 | 926 | 1930 | 1745 | 250 | 216 | 102 | 0 | 146 | [7 empty] | Energy not Served | 0
2:30 | 4521 | 926 | 1896.5 | 1537 | 250 | 216 | 85 | 0 | 146 | [7 empty] | Energy Requirement | 220.1263
3:00 | 4529 | 926 | 1863 | 1329 | 250 | 216 | 68 | 0 | 146
3:30 | 4537 | 926 | 1843.5 | 1189 | 250 | 216.5 | 45 | 0 | 143 | [6 empty] | Shortage
4:00 | 4545 | 926 | 1824 | 1049 | 250 | 217 | 22 | 0 | 140
4:30 | 4540.5 | 926 | 1823.5 | 949.5 | 250 | 217 | 11 | 0 | 138
5:00 | 4536 | 926 | 1823 | 850 | 250 | 217 | 0 | 0 | 136
5:30 | 4353.5 | 926 | 1643.5 | 821 | 250 | 206 | 0 | 0 | 126
6:00 | 4171 | 926 | 1464 | 792 | 250 | 195 | 0 | 0 | 116
6:30 | 4070.5 | 926.5 | 1429.5 | 739 | 250 | 204.5 | 0 | 0 | 109 |  |  |  |  | Coal
7:00 | 3970 | 927 | 1395 | 686 | 250 | 214 | 0 | 0 | 102
7:30 | 3958 | 925 | 1400.5 | 699.5 | 249.5 | 214 | 0 | 0 | 99 |  |  |  | Oil |  |  |  | ,
8:00 | 3946 | 923 | 1406 | 713 | 249 | 214 | 0 | 0 | 96
8:30 | 3958 | 923 | 1438.5 | 778.5 | 249.5 | 213.5 | 0 | 0 | 104
9:00 | 3970 | 923 | 1471 | 844 | 250 | 213 | 0 | 0 | 112
9:30 | 4058 | 923.5 | 1481.5 | 939.5 | 250 | 213 | 0 | 0 | 114
10:00 | 4146 | 924 | 1492 | 1035 | 250 | 213 | 0 | 0 | 116
10:30 | 4169.5 | 924.5 | 1527.5 | 1049.5 | 250 | 213 | 0 | 0 | 120
11:00 | 4193 | 925 | 1563 | 1064 | 250 | 213 | 0 | 0 | 124
11:30 | 4297 | 925 | 1618 | 1083 | 250 | 213 | 0 | 0 | 125
12:00 | 4401 | 925 | 1673 | 1102 | 250 | 213 | 0 | 0 | 126
12:30 | 4369.5 | 925 | 1736.5 | 1076.5 | 250 | 213.5 | 0 | 0 | 123
13:00 | 4338 | 925 | 1800 | 1051 | 250 | 214 | 0 | 0 | 120
13:30 | 4338 | 925 | 1800 | 1051 | 250 | 214 | 0 | 0 | 120
14:00 | 4338 | 925 | 1800 | 1051 | 250 | 214 | 0 | 0 | 120
14:30 | 4222 | 925 | 1805.5 | 1089.5 | 250 | 214 | 0 | 0 | 127
15:00 | 4106 | 925 | 1811 | 1128 | 250 | 214 | 0 | 0 | 134
15:30 | 4116 | 925 | 1794.5 | 1068.5 | 253 | 214 | 0 | 0 | 132
16:00 | 4126 | 925 | 1778 | 1009 | 256 | 214 | 0 | 0 | 130
16:30 | 4152 | 925.5 | 1683.5 | 944.5 | 269 | 214 | 8.5 | 0 | 127
17:00 | 4178 | 926 | 1589 | 880 | 282 | 214 | 17 | 0 | 124
17:30 | 4215.5 | 925.5 | 1519 | 907.5 | 301 | 214 | 43 | 0 | 124
18:00 | 4253 | 925 | 1449 | 935 | 320 | 214 | 69 | 0 | 124
18:30 | 4307.5 | 924.5 | 1560.5 | 1359.5 | 329.5 | 214 | 239 | 0 | 142
19:00 | 4362 | 924 | 1672 | 1784 | 339 | 214 | 409 | 0 | 160
19:30 | 4383 | 925 | 1798 | 2382 | 340 | 214 | 421 | 0 | 160
20:00 | 4465 | 925 | 1871 | 2395 | 341 | 214 | 325 | 0 | 156
20:30 | 4516.5 | 924.5 | 1910 | 2364 | 345 | 214 | 302.5 | 0 | 160
21:00 | 4568 | 924 | 1949 | 2333 | 349 | 214 | 280 | 0 | 164
21:30 | 4585.5 | 924 | 1936.5 | 2326 | 350 | 212 | 274 | 0 | 165
22:00 | 4603 | 924 | 1924 | 2319 | 351 | 210 | 268 | 0 | 166
22:30 | 4560 | 924.5 | 1955.5 | 2286.5 | 342.5 | 212 | 209.5 | 0 | 155
23:00 | 4517 | 925 | 1987 | 2254 | 334 | 214 | 151 | 0 | 144
23:30 | 4504 | 925 | 1978.5 | 2232.5 | 337.5 | 214.5 | 135.5 | 0 | 149 | Max Temp. in Dhaka |  | 30.1° C
24:00 | 4491 | 925 | 1970 | 2211 | 341 | 215 | 120 | 0 | 154
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 220.126 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 220.126 MKWHr
Note on W13: Author:

## Generation
2019-08-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 123 | 126 | 126 | 127 | 127 | 105 | 124 | 124 | 123 | 123 | 123 | 123 | 124 | 124 | 124 | 124 | 124 | 124 |  | 124 | 124 | 124 | 124 | 120 | 124 | 125 | 2775671
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2152000
3 | Chattogram TPP-1 | [10 empty] | 0 | 10 | 35 | 70 | 70 | 80 | 80 | 80 |  | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 900000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3100000
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 9 | 25 | 25 | 8 | 8 | 8 | 8 | 84866
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.39 | 0.82 | 1.29 | 9.93 | 8.68 | 0 | 20.16 | 4.94 | 2 | 1 | 3 | 2 | 0 | [8 empty] | 42255
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 205 | 204 | 206 | 206 | 205 | 165 | 165 | 165 | 224 | 204 | 217 | 217 | 177 | 177 | 178 | 178 | 178 |  | 203 | 203 | 204 | 204 | 204 | 204 | 205 | 4655738
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 103 | 100 | 100 | 130 | 142 | 132 | 100 | 101 | 100 | 101 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2873358
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 0 | [17 empty] | 51 | 51 | 51 | 17 | 17 | 0 | 0 | 153387
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 2 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 104545
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 97 | 97 | 97 | 97 | 35 | 37 | 37 | 37 | 35 | 37 | 97 | 97 | 35 | 37 | 30 | 34 | 34 |  | 37 | 34 | 60 | 63 | 59 | 61 | 59 | 1525000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 2 |  | 15 | 0 | 0 |  |  |  |  | 27600
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 112 | 112 | 105 | 115 | 115 | 115 | 115 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2308363
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1516000
21 | Ghorasal Repowered CCPP Unit-3 | 199 | 199 | 199 | 199 | 199 | 160 | 164 | 170 | 170 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4765000
22 | Ghorasal Repowered CCPP Unit-4 | 211 | 207 | 203 | 204 | 210 | 183 | 170 | 170 | 170 | 200 | 200 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 172 | 171 | 170 | 170 | 171 | 170 | 170 | 4365000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2076060
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 764280
33 | Ashuganj 225 MW CCPP | 214 | 214 | 215 | 214 | 203 | 181 | 159 | 172 | 169 | 182 | 182 | 203 | 199 | 162 | 174 | 160 | 160 | 160 |  | 161 | 161 | 181 | 181 | 181 | 189 | 181 | 4476000
34 | Ashuganj 450 MW CCPP(South) | 305 | 310 | 305 | 310 | 305 | 260 | 260 | 265 | 260 | 305 | 305 | 290 | 260 | 250 | 300 | 305 | 305 | 305 |  | 305 | 305 | 305 | 305 | 305 | 315 | 305 | 7182000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 260 | 260 | 270 | 320 | 320 | 320 | 360 | 335 | 320 | 340 | 335 | 335 | 335 |  | 335 | 335 | 335 | 335 | 335 | 325 | 320 | 8042300
35 | Ashuganj 55 MW PP (Precision) | 50 | 52 | 52 | 52 | 52 | 15 | 15 | 16 | 15 | 15 | 48 | 48 | 44 | 43 | 46 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 53 | 52 | 1075680
36 | Chandpur 150 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 140 | 140 | 140 | 138 |  | 135 | 136 | 139 | 139 | 140 | 140 | 140 | 3289180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 346 | 346 | 345 | 345 | 344 | 344 | 345 | 346 | 358 | 350 | 345 | 372 | 372 | 346 | 363 | 350 | 345 | 344 |  | 345 | 345 | 344 | 345 | 345 | 345 | 348 | 8509440
40 | Meghnaghat 450 MW CCPP(MPL) | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 |  | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 7631500
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 156 | 156 | 160 | 160 | 157 | 160 | 157 | 153 | 154 | 155 | 155 | 151 | 151 | 151 | 151 | 153 | 159 | 204 |  | 196 | 196 | 181 | 180 | 193 | 193 | 192 | 3852880
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 1329000
45 | Fenchugonj CCPP Phase-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1482720
46 | Shajibazar 330 MW CCPP | 265 | 260 | 260 | 260 | 262 | 262 | 239 | 238 | 236 | 265 | 264 | 266 | 260 | 239 | 235 | 238 | 235 | 235 |  | 234 | 235 | 235 | 250 | 250 | 151 | 149 | 5595000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 60 | 58 | 58 | 61 | 64 | 63 | 63 | 61 | 56 | 63 | 61 | 62 | 60 | 61 | 63 | 50 | 64 |  | 63 | 50 | 63 | 63 | 64 | 63 | 64 | 1469568
48 | Shahjibazar 86MW PP (Shahjibazar) | 71 | 71 | 71 | 71 | 71 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 71 | 71 | 71 | 10 | 10 |  | 10 | 69 | 72 | 72 | 74 | 74 | 74 | 1160640
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 44 | 46 | 46 | 40 | 31 | 31 | 10 | 10 |  | 10 | 40 | 45 | 45 | 45 | 45 | 45 | 816480
50 | Sylhet 150 MW CCPP | 109 | 109 | 108 | 105 | 105 | 105 | 68 | 71 | 69 | 70 | 73 | 123 | 117 | 78 | 76 | 73 | 75 | 74 |  | 74 | 74 | 74 | 109 | 110 | 113 | 110 | 2372370
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438350
52 | Sylhet 50MW PP (EPL) | 43 | 43 | 43 | 43 | 43 | 22 | 14 | 13 | 13 | 13 | 13 | 38 | 43 | 41 | 40 | 39 | 12 | 13 |  | 42 | 43 | 42 | 42 | 42 | 42 | 42 | 780320
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243720
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212448
55 | Fenchugonj 51 MW PP (Barakatullah) | 52 | 52 | 53 | 53 | 50 | 22 | 11 | 11 | 11 | 11 | 13 | 35 | 47 | 44 | 44 | 47 | 11 | 14 |  | 11 | 50 | 50 | 50 | 53 | 53 | 53 | 831600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 |  |  | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 511032
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 300 | 295 | 300 | 270 | 290 | 300 | 310 | 300 | 300 | 320 | 320 | 290 | 310 | 280 | 275 | 270 |  | 300 | 270 | 270 | 290 | 290 | 280 | 300 | 7354750
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 260881
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 453696
61 | Narshingdi 22 MW PP (Doreen) |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 393372
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 452016
63 | Impoprt (Tripura) | 150 | 146 | 146 | 140 | 136 | 116 | 102 | 96 | 112 | 116 | 124 | 126 | 120 | 136 | 134 | 130 | 124 | 124 |  | 160 | 160 | 156 | 164 | 166 | 144 | 154 | 3230400
64 | Malancha, Ctg. EPZ (United) | 40 | 39 | 40 | 40 | 40 | 32 | 10 | 5 | 6 | 5 | 8 | 10 | 14 | 16 | 16 | 30 | 30 | 23 |  | 39 | 39 | 41 | 42 | 42 | 42 | 42 | 672480
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 489420
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228960
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820900
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 20 | 20 | 15 | 15 | 11 | 11 | 11 | 10 | 14 | 14 | 10 | 10 | 11 | 0 |  |  | 20 | 20 | 18 | 21 | 21 | 21 | 20 | 357920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 31 |  | 20 | 28 | 32 | 32 | 32 | 32 | 32 | 705420
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 797500
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 692400
73 | Ghorashal 108MW PP (Regent) | 97 | 97 | 97 | 97 | 97 | 61 | 32 | 32 | 57 | 87 | 90 | 93 | 94 | 93 | 93 | 92 | 88 | 52 |  | 90 | 87 | 92 | 95 | 93 | 97 | 97 | 1976954
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 24 | 24 | 24 | 0 |  |  |  | 0 | 13 | 43 | 43 | 34 | 34 | 34 | 40 | 18 | 30 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 678756
79 | Kodda 150MW PP | 48 | 20 | 10 | 0 | [12 empty] | 0 | 16 |  | 48 | 48 | 40 | 32 | 32 | 32 | 32 | 400320
80 | Jamalpur 95 MW PP(Powerpac) | 92 | 92 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 70 | 91 | 91 | 91 | 92 | 92 | 878400
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 0 | [15 empty] | 0 |  | 8 | 52 | 50 | 52 | 52 | 52 | 52 | 322003
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 51 | 51 | 35 | 35 | 50 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 108 | 107 | 1944960
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.3 | 0.8 | 1 | 1.5 | 3 | 2.6 | 3.6 | 1.3 | 1.64 | 0.76 | 3.63 | 0.804 | 0.09 | [8 empty] | 17280
| Jodiac Power | [11 empty] | 0 | 6 | 11 | 9 | 16 | 0 | [9 empty] | 53940
| Karnaphuli Power Lid. |  |  |  |  | 0 | 54 | 54 | 73 | 92 | 109 | 109 | 97 | 0 | [13 empty] | 607197
82 | Madanganj 102 PP(Summit) | [19 empty] | 0 | 10 | 3 | 0 | 0 |  |  | 5160
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 265 | 257 | 260 | 230 | 240 | 240 | 287 | 262 | 280 | 300 | 290 | 260 | 290 | 250 | 275 | 250 |  | 285 | 250 | 265 | 277 | 265 | 282 | 252 | 6474124
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 5 | 20 | 7 |  |  |  |  | 34560
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 69 | 69 | 68 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 69 | 69 | 1376704
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258600
92 | Fenchuganj 44MW (Energyprima) | 44 | 44 | 44 | 44 | 44 | 20 | 10 | 10 | 10 | 10 | 10 | 30 | 43 | 43 | 43 | 43 | 10 | 10 |  | 19 | 44 | 44 | 44 | 44 | 44 | 44 | 836640
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 24 | 10 | 10 | 10 | 10 | 10 | 16 | 35 | 25 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 740574
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 0 | [8 empty] | 0 | 7 | 24 | 24 | 24 | 24 | 24 |  | 32 | 7 | 7 | 0 | 0 |  |  | 235008
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 31 | 25 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 9 | 18 | 39 | 50 | 50 | 50 | 50 | 505440
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 0 | [12 empty] | 1 | 10 |  | 27 | 50 | 50 | 50 | 50 | 50 | 50 | 358080
97 | Katpotti 52 MW PP (Sinha) | 13 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 13 | 13 | 13 |  | 13 | 21 | 24 | 48 | 47 | 47 | 47 | 463392
98 | Bosila 108MW PP(CLC) | 72 | 72 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 60 | 72 | 72 | 72 | 72 | 72 | 72 | 701760
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 1 |  | 15 | 0 | 0 |  |  |  |  | 26244
100 | Manikganj 55 MW PP (Northern) | 35 | 0 | 0 | 17 | 0 | [11 empty] | 0 | 18 |  | 54 | 54 | 54 | 18 | 18 | 18 | 17 | 252251
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 |  | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 3189305
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.3 | 0.2 | 0.9 | 0.9 | 1.9 | 0.8 | 1.1 | 1.2 | 0.6 | 0.6 | 0.1 | 0 | [8 empty] | 9650
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 676080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 70 | 36 | 0 | [13 empty] | 0 | 4 |  | 7 | 30 | 50 | 50 | 50 | 50 | 50 | 439200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 44 | 15 | 12 | 0 |  |  |  | 0 | 4 | 96 | 109 | 149 | 149 | 149 | 135 | 72 | 21 | 15 |  | 19 | 48 | 50 | 50 | 50 | 50 | 50 | 1262880
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 71 | 90 | 100 | 100 | 100 | 100 | 100 | 1002240
116 | Chandpur 200MW (Desh energy) | 180 | 120 | 72 | 34 | 22 | 17 | 0 | [9 empty] | 0 | 10 |  | 50 | 200 | 190 | 200 | 200 | 200 | 200 | 1538400
117 | Ashuganj 150MW PP (Midland) | 12 | 0 | [14 empty] | 0 | 10 |  | 20 | 100 | 88 | 50 | 50 | 10 | 10 | 309454
118 | Bibiyana-III 400 MW CCPP | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 84 | 85 | 85 | 125 | 125 | 125 | 125 | 124 |  | 84 | 85 | 84 | 84 | 85 | 84 | 84 | 2038000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 108 | 70 | 70 | 40 | 40 | 72 | 109 | 108 | 108 | 108 | 108 | 107 | 115 | 60 | 60 |  | 115 | 115 | 115 | 115 | 115 | 107 | 108 | 2324400
| Anwara 300 MW PP (United) | 106 | 106 | 70 | 69 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 55 | 102 | 106 | 106 | 70 | 70 |  | 141 | 141 | 141 | 141 | 141 | 135 | 142 | 2150291
120 | Eastern Zone Total | 6765 | 6518 | 6198 | 6005 | 5856 | 5210.69 | 4896.92 | 4929.49 | 5171.33 | 5624.58 | 5720.5 | 6084.56 | 6025.34 | 5821.84 | 5963.36 | 5879.23 | 5513.904 | 5546.09 |  | 6398 | 6924 | 7021 | 7030 | 7042 | 6918 | 6889 | 147089713
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | 16 | 0 | [13 empty] | 0 | 16 |  | 62 | 115 | 115 | 115 | 115 | 115 | 94 | 669120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 14 | 0 | [15 empty] | 20 |  | 37 | 38 | 43 | 40 | 36 | 36 | 36 | 248640
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 70 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 80 | 105 | 105 | 105 | 105 | 105 | 105 | 1296480
130
131
132
133
| Barisal 110 MW PP (Summit ) | 32 | 32 | 16 | 0 | [12 empty] | 0 | 0 |  | 60 | 60 | 64 | 48 | 48 | 48 | 48 | 387648
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 97 | 61 | 51 | 51 | 54 | 27 | 27 | 27 | 25 | 28 | 27 | 26 | 26 | 27 | 26 | 26 | 26 |  | 27 | 55 | 88 | 96 | 97 | 97 | 97 | 1251016
| Bhola 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4366000
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 18 | 20 | 12 | 17 | 16 | 16 | 16 | 16 | 14 | 17 | 20 | 21 | 27 | 25 | 24 | 20 |  | 32 | 36 | 35 | 36 | 37 | 36 | 36 | 530335
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 4 | 20 | 0 |  |  |  |  | 25920
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 8 | 0 |  |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 301125
143 | Gopalganj 100 MW Peaking PP | 36 | 36 | 36 | 0 | [11 empty] | 0 | 17 | 33 |  | 73 | 70 | 67 | 67 | 67 | 0 |  | 451328
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 69 | 35 | 34 | 34 | 35 | 36 | 36 | 35 | 54 | 54 | 54 | 45 | 36 | 36 |  | 99 | 100 | 99 | 100 | 99 | 100 | 100 | 1609632
146 | Bheramara HVDC | 925 | 926 | 926 | 926 | 926 | 926 | 927 | 923 | 923 | 924 | 925 | 925 | 925 | 925 | 925 | 925 | 926 | 925 |  | 924 | 925 | 925 | 924 | 924 | 925 | 925 | 22195636
147 | Bheramara 360 MW CCPP | 370 | 370 | 370 | 370 | 370 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 270 |  | 270 | 270 | 300 | 330 | 330 | 330 | 330 | 8103168
148
149
150 | Barapukuria TPP Unit-1 | [15 empty] | 6 | 33 | 70 |  | 89 | 90 | 91 | 99 | 101 | 84 | 91 | 632290
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6079200
153 | Baghabari 71 MW GTPP | [17 empty] | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 378000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 43 | 0 |  |  |  |  | 44611
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 197 | 196 | 198 | 195 | 193 | 181 | 177 | 167 | 163 | 177 | 201 | 199 | 199 | 182 | 168 | 163 | 156 | 154 |  | 158 | 179 | 180 | 180 | 182 | 183 | 194 | 4618391
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 196 | 192 | 193 | 194 | 196 | 198 | 187 | 164 | 167 | 133 | 132 | 133 | 133 | 130 | 60 | 50 | 150 | 173 |  | 175 | 176 | 180 | 197 | 206 | 206 | 204 | 4187545
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 354 | 355 | 355 | 329 | 335 | 306 | 350 | 355 | 355 | 315 | 340 | 355 | 380 | 378 | 390 | 340 | 360 | 295 |  | 380 | 350 | 375 | 390 | 360 | 409 | 373 | 8627090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 16 |  | 17 | 20 | 22 | 22 | 22 | 22 | 22 | 488640
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 9 | 11 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 358992
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 0 | 3 | 3 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 3 |  | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 126936
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 469590
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | 50 | 50 | 50 | 50 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 465156
167 | Katakhali 50 MW Peaking PP | 22 | 22 | 22 | 22 | 0 | [12 empty] | 0 |  | 42 | 47 | 0 |  |  |  |  | 147236
168 | Santahar 50 MW Peaking PP | 30 | 24 | 0 | [16 empty] | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 211240
169 | Natore 52 MW PP (Rajlanka) | 52 | 43 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 52 | 52 | 52 | 52 | 34 | 34 | 622560
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 85 | 94 | 94 | 94 | 88 | 55 | 24 | 415152
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 55 | 17 | 17 | 17 | 0 |  |  |  | 0 | 5 | 4 | 0 | [5 empty] | 28 | 108 | 90 | 110 | 110 | 111 | 113 | 964992
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 114 | 114 | 114 | 114 | 106 | 107 | 114 | 114 | 114 | 114 | 114 | 108 | 113 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2718720
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.5 | 0 | 5 | 0 | 6.1 | 6.5 | 8.4 | 3.16 | 6.12 | 4.8 | 3 | 0.5 | [8 empty] | 44158
178
178