## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-04 | Monday
|  |  | Date (day): | 2021-01-04 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12270.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13529 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-03 | 2021-01-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 184 | 278 | 180 | 180
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 270 | 330 | 330
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 13 | 0 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 350 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 310 | 360 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 38 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 8 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 57 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 37 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 25 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 268 | 283 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 105 | 123 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 46 | 70 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 75 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 55 | 55 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2032 | 2570 | 3446 | 3736 | 929 | 1355
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 75 | 75 | 155 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 19 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 27 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 87 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 40 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 121 | 0 | 124 | 124
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 494 | 534 | 1396 | 1381 | 890 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 155 | 165 | 160 | 160
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 310 | 300 | 310 | 50 |  | Gas shortage
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 380 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 150 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 85 | 100 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 102 | 140 | 149
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 21 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 46 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1211 | 1414 | 1733 | 2002 | 725 | 175
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 103 | 106 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 120 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
|  | Tangail Palli Power Gen 22 MW |  | HFO | SIPP | 4*6.7 | 0 | 0 | 20 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 695 | 687 | 312 | 436 | 615.6 | 564 | 92 | 0
| 85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 30 | 50 | 50
| 86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 20 | 30
| 87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 145 | 144 | 155 | 155 | 175 |  | GT-2 under shut down for gas shortage
| 89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 11 | 11 | 22
| 90 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 20 | 30 | 20 | 20
| 91 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 33 | 33 |  | 33 | GT-8 under maint.
| 93 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 68 | 71 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 30 | 129 | 100 | 200
| 95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 96 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
| 98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 295 | 320 | 320
| 99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 100 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 417 | 425 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1068 | 1205 | 1228 | 1349 | 175 | 456
| 101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 577 | 830 | 590 | 831
| 102 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 104 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 105 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 4 | 70 | 70 |  | 39 | Engine problem
| 106 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 185 | 155 | 250 | 250 | 160 |  | Gas shortage
| 107 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 0 | 40 | 40
| 108 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 109 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| 110 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 954 | 1209 | 1355 | 1882 | 160 | 58
| 111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 112 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 22 | 24 | 26 |  | 7 | Engine problem
| 113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 114 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 54 | 90 | 90
| 115 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 260 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 31 | 32 | 36 | 36
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 54 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 140 | 438 | 860 | 862 | 0 | 201
| 116 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 117 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 118 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 119 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 120 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 121 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 123 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 138 | 220 | 220
| 125 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 390 | 400 | 400 |  |  | FGMO
| 126 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 127 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 128 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 86 | 100 | 100
| 132 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 133 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 134 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 715 | 873 | 1366 | 1490 | 601 | 15
| 135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 34 | 113 | 113
| 140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 225 | 184 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 20595 | 20104 | 7151 | 8863 | 12270.6 | 13529 | 3696 | 2571
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6711.2736 | 8318 | 11516.0612 | 12697.0802
| A. |  | 2021-01-03 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 8863 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5435 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8863 | MW
| 3 | Day peak Generation : |  |  | 7151 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8318 | MW
| 4 | Evening peak Generation : |  |  | 8863 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 168.6863 | MKWHr | By Solar | 0.45645 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 107.8756 | MKWHr |  | By Oil: | 37.272 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 5.8553 | MKWHr |  | By Hydro: | 0.792 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3696 | MW | Dhaka | 2918 | 2918 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2571 | MW | Chittagong | 873 | 873 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6267 | MW | Khulna | 1078 | 1078 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 775.84 | MMCFD |  |  | Rajshahi | 870 | 870 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 107735035.994 | ii) Oil : | Taka | 252039511.01 | Comilla | 714 | 714 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 29503098 | Total | Taka | 389277645.004 | Mymensingh | 721 | 721 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.8055 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -247 | MW (E to W) at | 19:30 | hrs | Barisal | 245 | 245 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -290 | MW at | 2:00 | hrs | Rangpur | 583 | 583 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.4° C |  |  | Total | 8318 | 8318 |  | 0
| B. |  | 2021-01-04 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 27.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13529 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4529 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 171.2938 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5580 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.4276 | MKWHr. | ii) HVDC Flow at Peak Time |  | 830 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0074 | MKWHr. | iii) Maximum HVDC Flow : |  | 830 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.03 |  | (b) Today: | 97.97 |  | (c) Rule Curve: |  | 102.43
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 143 | 0 | 330 | 105 | 0 | 369 | 295 |  | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 70 | 0 | 0 | 150 | 250 | 198 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 76 | 106 | 0 | 22 | 0 | 60 | 0 | 53 | 50 | 0 | 145 | 33 | 73 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 34 | 100 | 0 | 0 | 0 | 0 | 0 | 70 | 54 | 0 | 0 | 46 | 100 | 415 | 90 | 0 | 55 | 124 | 0 |  | 437 | 0 | 205 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 139 | 0 | 380 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 50 |  | 4538 | 1591 | 6129 | 2934 | 437 | 1484 | 1018 | 150 | 30 | 0 | 76 | 0 | 0 | 98.04
2:00 | 0 | 0 | 148 | 0 | 330 | 105 | 0 | 384 | 267 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 70 | 0 | 0 | 240 | 300 | 176 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 76 | 107 | 0 | 22 | 0 | 60 | 0 | 53 | 44 | 0 | 146 | 33 | 73 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 32 | 54 | 0 | 0 | 46 | 70 | 415 | 60 | 0 | 55 | 124 | 0 |  | 437 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 150 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 4401 | 1432 | 5833 | 3090 | 437 | 1427 | 623 | 150 | 30 | 0 | 76 | 0 | 0 | 98.04
3:00 | 0 | 0 | 152 | 0 | 330 | 105 | 0 | 383 | 316 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 70 | 0 | 0 | 245 | 320 | 126 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 74 | 108 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 145 | 34 | 74 | 0 | 70 | 0 | 0 | 0 | 320 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 54 | 0 | 0 | 0 | 70 | 415 | 30 | 0 | 55 | 124 | 0 |  | 436 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 150 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 4202 | 1489 | 5691 | 3100 | 436 | 1456 | 445 | 150 | 30 | 0 | 74 | 0 | 0 | 98.03
4:00 | 0 | 0 | 154 | 0 | 330 | 105 | 0 | 371 | 316 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 70 | 0 | 0 | 255 | 250 | 129 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 74 | 108 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 144 | 34 | 74 | 0 | 70 | 0 | 0 | 0 | 320 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 30 | 415 | 0 | 0 | 55 | 124 | 0 |  | 436 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 4003 | 1493 | 5496 | 3017 | 436 | 1476 | 313 | 150 | 30 | 0 | 74 | 0 | 0 | 98.03
5:00 | 0 | 0 | 148 | 0 | 330 | 105 | 0 | 366 | 316 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 70 | 0 | 0 | 260 | 250 | 129 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 72 | 109 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 145 | 33 | 75 | 0 | 90 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 30 | 415 | 0 | 0 | 55 | 124 | 0 |  | 437 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 146 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 3934 | 1501 | 5435 | 3037 | 437 | 1433 | 276 | 150 | 30 | 0 | 72 | 0 | 0 | 98.03
6:00 | 0 | 0 | 148 | 0 | 330 | 102 | 0 | 383 | 316 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 1 | 19 | 42 | 70 | 0 | 0 | 265 | 250 | 130 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 72 | 108 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 145 | 33 | 74 | 0 | 90 | 0 | 0 | 0 | 320 | 0 | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 60 | 415 | 0 | 0 | 55 | 124 | 0 |  | 437 | 0 | 235 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 178 | 0 | 440 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 4033 | 1636 | 5669 | 3091 | 437 | 1479 | 410 | 150 | 30 | 0 | 72 | 0 | 0 | 98.03
7:00 | 0 | 0 | 148 | 0 | 330 | 102 | 0 | 382 | 316 |  | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 14 | 17 | 35 | 70 | 0 | 0 | 280 | 250 | 130 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 70 | 108 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 146 | 33 | 69 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 29 | 0 | 0 | 106 | 0 | 0 | 1 | 20 | 43 | 108 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 100 | 415 | 34 | 1 | 55 | 123 | 0 |  | 437 | 0 | 225 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 180 | 0 | 391 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 4365 | 1661 | 6026 | 3096 | 437 | 1405 | 836 | 150 | 30 | 0 | 70 | 2 | 0 | 98.02
8:00 | 0 | 0 | 158 | 0 | 330 | 104 | 0 | 413 | 346 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 22 | 17 | 15 | 70 | 0 | 0 | 280 | 250 | 129 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 74 | 109 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 145 | 33 | 69 | 0 | 90 | 0 | 0 | 0 | 330 | 0 | 5 | 0 | 46 | 0 | 0 | 149 | 0 | 5 | 6 | 40 | 52 | 150 | 0 | 0 | 4 | 0 | 1 | 49 | 0 | 0 | 0 | 4 | 100 | 415 | 37 | 10 | 55 | 125 | 0 |  | 530 | 0 | 220 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 177 | 0 | 432 | 0 | 0 | 58 | 0 | 77 | 0 | 1 | 0 | 0 | 22 | 0 | 0 |  | 4664 | 1882 | 6546 | 3135 | 530 | 1510 | 1099 | 150 | 30 | 0 | 74 | 18 | 0 | 98.02
9:00 | 0 | 0 | 169 | 0 | 330 | 53 | 0 | 370 | 345 |  | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 25 | 32 | 24 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 48 | 17 | 5 | 70 | 0 | 0 | 280 | 250 | 131 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 22 | 76 | 107 | 0 | 22 | 0 | 60 | 0 | 8 | 5 | 0 | 143 | 33 | 69 | 0 | 20 | 0 | 0 | 0 | 315 | 0 | 5 | 0 | 131 | 0 | 0 | 200 | 0 | 94 | 11 | 50 | 83 | 150 | 0 | 0 | 34 | 0 | 2 | 49 | 0 | 0 | 0 | 26 | 100 | 415 | 53 | 25 | 55 | 124 | 0 |  | 530 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 7 | 170 | 0 | 398 | 53 | 0 | 112 | 0 | 85 | 0 | 2 | 30 | 0 | 4 | 0 | 0 |  | 4930 | 2030 | 6960 | 3029 | 530 | 1393 | 1712 | 150 | 30 | 0 | 76 | 40 | 0 | 98.02
10:00 | 0 | 0 | 168 | 0 | 330 | 53 | 0 | 349 | 346 |  | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 25 | 32 | 24 | 25 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 50 | 17 | 7 | 0 | 0 | 0 | 260 | 350 | 131 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 25 | 9 | 76 | 106 | 0 | 22 | 2 | 60 | 0 | 22 | 5 | 0 | 143 | 32 | 68 | 0 | 20 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 259 | 0 | 0 | 160 | 0 | 100 | 15 | 50 | 85 | 147 | 0 | 0 | 35 | 0 | 3 | 49 | 0 | 0 | 0 | 26 | 100 | 415 | 53 | 36 | 55 | 123 | 0 |  | 577 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 20 | 164 | 0 | 346 | 53 | 0 | 113 | 0 | 90 | 0 | 3 | 35 | 0 | 7 | 0 | 0 |  | 5015 | 2028 | 7043 | 2968 | 577 | 1321 | 1862 | 150 | 30 | 0 | 76 | 59 | 0 | 98.02
11:00 | 0 | 0 | 172 | 0 | 330 | 13 | 0 | 351 | 309 |  | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 25 | 32 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 50 | 17 | 5 | 0 | 0 | 0 | 260 | 345 | 152 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 25 | 22 | 76 | 103 | 0 | 22 | 2 | 60 | 0 | 22 | 5 | 0 | 146 | 31 | 69 | 0 | 25 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 282 | 0 | 0 | 120 | 0 | 100 | 17 | 50 | 85 | 142 | 0 | 0 | 35 | 0 | 4 | 52 | 0 | 0 | 0 | 26 | 100 | 415 | 53 | 42 | 55 | 123 | 0 |  | 577 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 158 | 0 | 380 | 53 | 0 | 113 | 0 | 70 | 0 | 5 | 35 | 0 | 32 | 0 | 0 |  | 4956 | 2028 | 6984 | 2986 | 577 | 1284 | 1806 | 150 | 35 | 0 | 76 | 70 | 0 | 98.01
12:00 | 0 | 0 | 184 | 0 | 330 | 13 | 0 | 355 | 310 |  | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 38 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 32 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 50 | 17 | 7 | 0 | 0 | 0 | 280 | 325 | 155 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 22 | 80 | 103 | 0 | 22 | 2 | 60 | 0 | 22 | 20 | 0 | 145 | 31 | 68 | 0 | 30 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 268 | 0 | 0 | 120 | 0 | 105 | 18 | 90 | 85 | 123 | 0 | 0 | 46 | 0 | 4 | 52 | 0 | 0 | 0 | 26 | 100 | 417 | 75 | 45 | 55 | 121 | 0 |  | 577 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 156 | 0 | 360 | 53 | 0 | 113 | 0 | 70 | 0 | 5 | 60 | 0 | 31 | 0 | 0 |  | 5117 | 2034 | 7151 | 3011 | 577 | 1284 | 1940 | 150 | 35 | 0 | 80 | 74 | 0 | 98.01
13:00 | 0 | 0 | 180 | 0 | 330 | 13 | 0 | 383 | 358 |  | 0 | 0 | 0 | 24 | 70 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 32 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 50 | 17 | 11 | 0 | 0 | 0 | 330 | 330 | 136 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 22 | 88 | 101 | 0 | 22 | 2 | 60 | 0 | 39 | 35 | 0 | 145 | 31 | 70 | 0 | 35 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 272 | 0 | 0 | 120 | 0 | 100 | 16 | 90 | 85 | 135 | 0 | 0 | 70 | 0 | 4 | 52 | 0 | 0 | 0 | 42 | 100 | 425 | 90 | 42 | 55 | 121 | 0 |  | 577 | 0 | 180 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 149 | 0 | 380 | 35 | 0 | 113 | 0 | 70 | 0 | 5 | 70 | 0 | 7 | 0 | 34 |  | 5429 | 2041 | 7470 | 3070 | 577 | 1393 | 2088 | 150 | 35 | 0 | 88 | 69 | 7470 | 98.01
14:00 | 0 | 0 | 205 | 0 | 300 | 0 | 0 | 355 | 309 |  | 0 | 0 | 0 | 21 | 80 | 0 | 0 | 0 | 0 | 18 | 7 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 28 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 17 | 9 | 0 | 0 | 0 | 300 | 355 | 142 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 0 | 22 | 92 | 104 | 0 | 22 | 2 | 30 | 20 | 11 | 10 | 0 | 145 | 31 | 70 | 0 | 110 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 215 | 0 | 0 | 120 | 0 | 100 | 15 | 90 | 85 | 143 | 0 | 0 | 70 | 0 | 3 | 53 | 0 | 0 | 0 | 55 | 100 | 425 | 90 | 36 | 55 | 121 | 0 |  | 577 | 0 | 175 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 143 | 0 | 300 | 35 | 0 | 113 | 0 | 34 | 0 | 4 | 70 | 0 | 13 | 0 | 54 |  | 5219 | 1942 | 7161 | 3075 | 577 | 1162 | 2010 | 150 | 35 | 0 | 92 | 60 | 0 | 98.01
15:00 | 0 | 0 | 252 | 0 | 300 | 0 | 0 | 293 | 354 |  | 0 | 0 | 0 | 7 | 80 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 28 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 17 | 6 | 0 | 0 | 0 | 300 | 345 | 145 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 0 | 22 | 86 | 103 | 0 | 22 | 1 | 30 | 20 | 11 | 30 | 0 | 144 | 31 | 70 | 0 | 125 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 215 | 0 | 0 | 120 | 0 | 100 | 11 | 90 | 85 | 142 | 0 | 0 | 70 | 0 | 2 | 53 | 0 | 0 | 0 | 8 | 100 | 420 | 90 | 25 | 55 | 121 | 0 |  | 577 | 0 | 150 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 135 | 0 | 330 | 17 | 0 | 113 | 0 | 34 | 0 | 3 | 70 | 0 | 31 | 0 | 50 |  | 5204 | 1925 | 7129 | 3028 | 577 | 1315 | 1896 | 150 | 35 | 0 | 86 | 42 | 0 | 98
16:00 | 0 | 0 | 236 | 0 | 300 | 0 | 0 | 308 | 353 |  | 0 | 0 | 0 | 7 | 80 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 17 | 8 | 0 | 0 | 0 | 300 | 355 | 140 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 30 | 22 | 82 | 103 | 0 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 145 | 20 | 70 | 0 | 128 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 145 | 0 | 0 | 70 | 0 | 92 | 6 | 50 | 98 | 142 | 0 | 0 | 35 | 0 | 1 | 89 | 0 | 0 | 0 | 8 | 80 | 415 | 90 | 10 | 55 | 122 | 0 |  | 577 | 0 | 140 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 137 | 0 | 330 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 40 | 24 | 0 | 39 |  | 4984 | 1688 | 6672 | 3043 | 577 | 1210 | 1516 | 190 | 35 | 0 | 82 | 19 | 0 | 98
17:00 | 0 | 0 | 260 | 0 | 270 | 0 | 0 | 354 | 355 |  | 0 | 0 | 0 | 9 | 80 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 40 | 0 | 0 | 0 | 17 | 0 | 25 | 16 | 25 | 28 | 25 | 25 | 2 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 43 | 0 | 0 | 50 | 19 | 15 | 0 | 0 | 0 | 280 | 375 | 143 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 1 | 18 | 11 | 33 | 21 | 90 | 105 | 8 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 33 | 70 | 0 | 128 | 0 | 0 | 7 | 270 | 0 | 11 | 0 | 165 | 0 | 0 | 70 | 0 | 83 | 0 | 50 | 105 | 143 | 0 | 0 | 35 | 0 | 0 | 89 | 0 | 0 | 0 | 8 | 80 | 420 | 90 | 1 | 55 | 121 | 0 |  | 577 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 137 | 0 | 330 | 17 | 0 | 43 | 0 | 50 | 0 | 0 | 35 | 100 | 5 | 0 | 54 |  | 5166 | 1788 | 6954 | 3124 | 577 | 1214 | 1593 | 250 | 35 | 70 | 90 | 1 | 0 | 98
18:00 | 0 | 0 | 280 | 0 | 270 | 0 | 0 | 377 | 309 |  | 0 | 0 | 0 | 46 | 80 | 13 | 0 | 0 | 0 | 10 | 32 | 32 | 57 | 0 | 0 | 1 | 17 | 35 | 37 | 16 | 25 | 15 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 6 | 0 | 102 | 44 | 0 | 50 | 19 | 10 | 0 | 0 | 0 | 300 | 370 | 176 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 10 | 18 | 11 | 33 | 22 | 98 | 104 | 11 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 145 | 32 | 69 | 0 | 129 | 0 | 0 | 7 | 280 | 0 | 11 | 0 | 275 | 0 | 0 | 101 | 0 | 116 | 0 | 100 | 120 | 150 | 0 | 12 | 35 | 0 | 0 | 108 | 2 | 0 | 0 | 18 | 100 | 420 | 90 | 0 | 55 | 122 | 0 |  | 814 | 0 | 160 | 0 | 64 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 23 | 16 | 0 | 0 | 0 | 24 | 0 | 44 | 12 | 0 | 0 | 6 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 138 | 0 | 390 | 36 | 0 | 67 | 0 | 50 | 0 | 0 | 50 | 140 | 32 | 0 | 54 |  | 5809 | 2377 | 8186 | 3209 | 814 | 1302 | 2233 | 290 | 35 | 205 | 98 | 0 | 0 | 98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 353 | 309 |  | 0 | 0 | 0 | 87 | 80 | 0 | 0 | 0 | 0 | 72 | 57 | 32 | 100 | 0 | 0 | 12 | 17 | 35 | 37 | 22 | 25 | 28 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 0 | 51 | 0 | 30 | 50 | 19 | 17 | 0 | 0 | 0 | 310 | 370 | 168 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 30 | 18 | 11 | 33 | 22 | 104 | 104 | 90 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 32 | 71 | 0 | 129 | 0 | 0 | 7 | 275 | 0 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 100 | 150 | 0 | 0 | 50 | 0 | 0 | 87 | 15 | 0 | 0 | 46 | 100 | 423 | 90 | 0 | 55 | 0 | 0 |  | 814 | 0 | 155 | 0 | 115 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 140 | 0 | 393 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 170 | 32 | 0 | 54 |  | 6043 | 2603 | 8646 | 3203 | 814 | 1307 | 2690 | 320 | 35 | 173 | 104 | 0 | 0 | 97.99
19:30 | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 350 | 360 |  | 0 | 0 | 0 | 100 | 80 | 0 | 0 | 0 | 0 | 100 | 57 | 32 | 100 | 0 | 0 | 0 | 17 | 35 | 37 | 22 | 25 | 28 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 0 | 0 | 50 | 19 | 27 | 0 | 0 | 0 | 310 | 380 | 165 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 22 | 102 | 106 | 90 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 32 | 71 | 0 | 129 | 0 | 0 | 7 | 295 | 0 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 100 | 150 | 0 | 0 | 70 | 0 | 0 | 87 | 40 | 0 | 0 | 46 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 830 | 0 | 155 | 0 | 115 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 138 | 0 | 390 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 260 | 32 | 0 | 54 |  | 6159 | 2704 | 8863 | 3209 | 830 | 1385 | 2719 | 410 | 35 | 173 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 277 | 0 | 270 | 0 | 0 | 354 | 310 |  | 0 | 0 | 0 | 100 | 80 | 0 | 0 | 0 | 0 | 100 | 57 | 20 | 100 | 0 | 0 | 0 | 17 | 35 | 37 | 22 | 25 | 32 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 17 | 0 | 0 | 50 | 19 | 32 | 0 | 0 | 0 | 310 | 380 | 162 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 102 | 108 | 90 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 146 | 33 | 71 | 0 | 129 | 0 | 0 | 7 | 290 | 0 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 100 | 150 | 0 | 0 | 70 | 0 | 0 | 88 | 35 | 0 | 0 | 46 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 810 | 0 | 155 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 139 | 0 | 390 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 270 | 9 | 0 | 55 |  | 6045 | 2662 | 8707 | 3219 | 810 | 1313 | 2693 | 420 | 35 | 115 | 102 | 0 | 0 | 97.99
21:00 | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 350 | 340 |  | 0 | 0 | 0 | 70 | 80 | 0 | 0 | 0 | 0 | 85 | 24 | 16 | 100 | 0 | 0 | 0 | 17 | 35 | 37 | 22 | 25 | 32 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 0 | 320 | 305 | 192 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 100 | 108 | 64 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 33 | 71 | 0 | 129 | 0 | 0 | 7 | 275 | 0 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 122 | 0 | 100 | 100 | 150 | 0 | 0 | 35 | 0 | 0 | 89 | 42 | 0 | 0 | 46 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 810 | 0 | 145 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 139 | 0 | 392 | 53 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 305 | 8 | 0 | 54 |  | 5866 | 2624 | 8490 | 3169 | 810 | 1328 | 2492 | 455 | 35 | 101 | 100 | 0 | 0 | 97.99
22:00 | 0 | 0 | 276 | 0 | 270 | 0 | 0 | 349 | 355 |  | 0 | 0 | 0 | 55 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 38 | 19 | 41 | 0 | 0 | 0 | 390 | 270 | 194 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 90 | 107 | 16 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 145 | 33 | 71 | 0 | 129 | 0 | 0 | 7 | 255 | 0 | 11 | 0 | 286 | 0 | 0 | 170 | 0 | 122 | 0 | 70 | 68 | 150 | 0 | 0 | 17 | 0 | 0 | 51 | 36 | 0 | 0 | 46 | 100 | 415 | 90 | 0 | 55 | 0 | 0 |  | 810 | 0 | 150 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 139 | 0 | 393 | 8 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 36 | 0 | 54 |  | 5429 | 2465 | 7894 | 3198 | 810 | 1361 | 1950 | 450 | 35 | 0 | 90 | 0 | 0 | 97.99
23:00 | 0 | 0 | 276 | 0 | 270 | 0 | 0 | 350 | 326 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 42 | 0 | 0 | 0 | 263 | 390 | 193 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 84 | 108 | 0 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 145 | 33 | 71 | 0 | 129 | 0 | 0 | 7 | 265 | 0 | 11 | 0 | 180 | 0 | 0 | 72 | 0 | 123 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 53 | 36 | 0 | 0 | 46 | 100 | 415 | 60 | 0 | 55 | 0 | 0 |  | 810 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 139 | 0 | 376 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 300 | 38 | 0 | 54 |  | 4932 | 2280 | 7212 | 3197 | 810 | 1323 | 1313 | 450 | 35 | 0 | 84 | 0 | 0 | 97.98
24:00 | 0 | 0 | 287 | 0 | 270 | 0 | 0 | 350 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 17 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 42 | 0 | 0 | 0 | 265 | 390 | 156 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 78 | 110 | 0 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 146 | 33 | 72 | 0 | 129 | 0 | 0 | 7 | 265 | 0 | 11 | 0 | 95 | 0 | 0 | 72 | 0 | 74 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 53 | 36 | 0 | 0 | 46 | 100 | 415 | 53 | 0 | 55 | 0 | 0 |  | 622 | 0 | 160 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 141 | 0 | 378 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 300 | 37 | 0 | 54 |  | 4705 | 2061 | 6766 | 3161 | 622 | 1298 | 1122 | 450 | 35 | 0 | 78 | 0 | 0 | 97.98
KWH | 0 | 0 | 4932000 | 0 | 7279400 | 1051727 | 0 | 8771590 | 7686000 |  | 0 | 0 | 0 | 452160 | 1114776 | 24870 | 0 | 0 | 0 | 373440 | 361440 | 120480 | 1169685 | 0 | 0 | 19536 | 196560 | 153021 | 443755 | 288540 | 600000 | 696600 | 600800 | 708900 | 38592 | 0 | 0 | 792000 | 0 | 0 | 47253 | 0 | 0 | 0 | 0 |  | 266880 | 0 | 239784 | 43200 | 30720 | 795360 | 440640 | 599520 | 692020 | 0 | 0 | 6953400 | 7640000 | 3754000 | 217454 | 0 | 133920 | 140640 | 0 | 1165696 | 0 | 0 | 47779 | 428940 | 258840 | 677200 | 520650 | 2007360 | 2484240 | 304320 | 498744 | 12650 | 1117000 | 210000 | 397200 | 630648 | 0 | 3336000 | 761664 | 1700160 | 0 | 2205930 | 0 | 0 | 54540 | 7249000 | 0 | 186096 | 0 | 3939271 | 0 | 0 | 2767200 | 0 | 1707260 | 116910 | 1143360 | 1808640 | 2828581 | 0 | 32400 | 715176 | 0 | 24480 | 1382 | 491637 | 0 | 0 | 708120 | 2190720 | 9973000 | 1552320 | 272680 | 1323360 | 2268218 | 0 |  | 14427636 | 0 | 4703904 | 0 | 1642560 | 0 | 0 | 0 | 0 | 7424 | 289125 | 0 | 399700 | 60480 | 0 | 0 | 0 | 51872 | 0 | 291232 | 13170 | 0 | 0 | 6240 | 0 | 504960 | 0 | 206082 | 0 | 0 | 3687700 | 0 | 0 | 0 | 0 | 0 | 0 | 1373819 | 36480 | 3830118 | 0 | 9220900 | 744000 | 0 | 1850496 | 0 | 878400 | 0 | 29733 | 1037280 | 2167600 | 593400 | 0 | 642000 |  | 119990035 | 48696311 | 168686346 | 74890218 | 14427636 | 32985364 | 36561223 | 5855300 | 792000 | 710792 | 2007360 | 456453 | 0
Fuel Cost | 0 | 0 | 7200720 | 0 | 8080134 | 1388279.64 | 0 | 8859305.9 | 7916580 |  | 0 | 0 | 0 | 3431894.4 | 7680806.64 | 210400.2 | 0 | 0 | 0 | 2812003.2 | 3296332.8 | 1185523.2 | 10784495.7 | 0 | 0 | 177582.24 | 1434888 | 1182852.33 | 4375424.3 | 216405 | 450000 | 0 | 0 | 0 | 373184.64 | 0 | 0 | 213840 | 0 | 0 | 438980.37 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2325904.8 | 412560 | 267264 | 6299251.2 | 555206.4 | 1780574.4 | 1024189.6 | 0 | 0 | 5145516 | 7640000 | 3453680 | 280515.66 | 0 | 151329.6 | 196896 | 0 | 1993340.16 | 0 | 0 | 456289.45 | 544753.8 | 194130 | 1185100 | 390487.5 | 15055200 | 2633294.4 | 2763225.6 | 633404.88 | 201641 | 1831880 | 336000 | 707016 | 983810.88 | 0 | 3469440 | 1500478.08 | 3247305.6 | 0 | 3816258.9 | 0 | 0 | 111261.6 | 7321490 | 0 | 141432.96 | 0 | 29780888.76 | 0 | 0 | 14389440 | 0 | 16799438.4 | 1366677.9 | 9318384 | 19623744 | 19941496.05 | 0 | 295488 | 6758413.2 | 0 | 0 | 10447.92 | 4282158.27 | 0 | 0 | 6068588.4 | 14590195.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83103183.36 | 0 | 4939099.2 | 0 | 12910521.6 | 0 | 0 | 0 | 0 | 77803.52 | 3012682.5 | 0 | 619535 | 590284.8 | 0 | 0 | 0 | 510420.48 | 0 | 2577403.2 | 101409 | 0 | 0 | 60465.6 | 0 | 969523.2 | 0 | 156004.074 | 0 | 0 | 19987334 | 0 | 0 | 0 | 0 | 0 | 0 | 2060728.5 | 620524.8 | 4481238.06 | 0 | 9128691 | 7767360 | 0 | 17561207.04 | 0 | 6816384 | 0 | 328549.65 | 7665499.2 | 9515764 | 0 | 0 | 0 |  | 293985121.13 | 195561615.784 | 489546736.914 | 69029488.354 | 83103183.36 | 38705547.64 | 245362455.81 | 29503098 | 213840 | 6677055.2 | 15055200 | 1896868.55 | 0
Yesterday Day Peak | 0 | 0 | 184 | 0 | 330 | 13 | 0 | 355 | 310 |  | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 38 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 32 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 50 | 17 | 7 | 0 | 0 | 0 | 280 | 325 | 155 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 22 | 80 | 103 | 0 | 22 | 2 | 60 | 0 | 22 | 20 | 0 | 145 | 31 | 68 | 0 | 30 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 268 | 0 | 0 | 120 | 0 | 105 | 18 | 90 | 85 | 123 | 0 | 0 | 46 | 0 | 4 | 52 | 0 | 0 | 0 | 26 | 100 | 417 | 75 | 45 | 55 | 121 | 0 |  | 577 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 156 | 0 | 360 | 53 | 0 | 113 | 0 | 70 | 0 | 5 | 60 | 0 | 31 | 0 | 0 |  | 7151 | DayPeak
Yesterday Evening Peak | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 350 | 360 | 0 | 0 | 0 | 0 | 100 | 80 | 0 | 0 | 0 | 0 | 100 | 57 | 32 | 100 | 0 | 0 | 0 | 17 | 35 | 37 | 22 | 25 | 28 | 25 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 51 | 0 | 0 | 50 | 19 | 27 | 0 | 0 | 0 | 310 | 380 | 165 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 22 | 102 | 106 | 90 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 32 | 71 | 0 | 129 | 0 | 0 | 7 | 295 | 0 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 100 | 150 | 0 | 0 | 70 | 0 | 0 | 87 | 40 | 0 | 0 | 46 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 830 | 0 | 155 | 0 | 115 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 138 | 0 | 390 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 260 | 32 | 0 | 54 |  | 8863 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 330 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 20 | 0 |  | 0 | 310 | 360 | 160 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 21 | 149 | 110 | 95 | 22 | 0 | 50 | 30 | 22 | 20 | 0 | 155 | 33 | 72 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 124 | 0 |  | 831 | 16 | 250 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 36 |  | 0
Forecast for Day | 0 | 0 | 180 | 0 | 330 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 33 | 52 | 0 | 45 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 10 | 0 |  | 0 | 300 | 360 | 160 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 140 | 110 | 95 | 22 | 1.6 | 50 | 20 | 11 | 20 | 0 | 155 | 33 | 72 | 0 | 100 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 124 | 0 |  | 590 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 36 |  | 0
Generation at 08:00(Today) | 0 | 0 | 278 | 0 | 300 | 0 | 0 | 374 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 17 |  | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 8 | 0 | 0 | 0 | 280 | 355 | 154 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 74 | 110 | 0 | 22 | 1 | 30 | 20 | 11 | 5 | 0 | 144 | 20 | 70 | 0 | 128 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 94 | 0 | 0 | 96 | 0 | 0 | 4 | 90 | 68 | 107 | 0 | 0 | 0 | 0 | 1 | 121 | 54 | 0 | 0 | 5 | 100 | 280 | 34 | 7 | 55 | 0 | 0 | 0 | 530 | 0 | 255 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 198 | 0 | 322 | 0 | 0 | 48 | 0 | 0 | 0 | 1 | 20 | 360 | 39 | 0 | 0 | 0
199
| Minimum Generation |  | 5435 | 5:00
| Highest Generation |  | 8863 | 19:30
| Day Peak Generation |  | 7151 | 12:00
| Evening Peak Generation |  | 8863 | 19:30
| HVDC Max Flow |  | 830 | 19:30
| HVDC EvPeak Flow |  | 830 | 19:30
| Load factor L.F |  | 79.3%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7151 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5580 | MW
Evening Peak Generation : |  | 8863 | MW Hour : | 19:30 | Available Max Generation : |  | 13529 | MW
E.P. Demand (at gen end) : |  | 8863 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8863 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4529 | MW
Total Gen. (MKWH) : |  | 168.6863 | System Load Factor : | 79.3% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -290 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-04
Actual : | 97.97 | Ft.(MSL) , | Rule curve : | 102.43 | Ft.( MSL )
Gas Consumed : | Total = | 775.84 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 107735035.994
: |  | Coal : | 29503098 | Oil : | 252039511.01 | Total : | 389277645.004
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3157.0699 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1067.8446 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 955.7317 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 863.2215 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 780.2808 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 629.6445 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 359.4448 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 162.3118 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 485.5778 |  |  | 0 | 0%
Total | 0 |  | 8461.1274 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Baroaulia-Hathazari 132 kV Ckt-1 was under shut down from 09:16 to 16:53 for A/M.
b) Bakulia-Sikalbaha 132 kV Ckt-2 was under shut down from 08:32 to 15:24 for A/M.
c) Mirpur 132 kV reserve Bus was under shut down from 09:25 to 17:13 for A/M.
d) B.Baria-Shahjibazar 132 kV Ckt-1 was under shut down from 09:13 to 17:38 for A/M.
e) Feni-Baroirhat 132 kV Ckt-1 was under shut down from 09:18 to 16:18 for A/M.
f) Kaliakoir 400/132 kV T03 transformer was under shut down from 08:17 to 15:52 for A/M.
g) Hasnabad-Aminbazar 230 kV Ckt-2 was under shut down from 07:33 to 22:33 for D/W.
h) Baroaulia-KSRM 132 kV Ckt was under shut down from 09:45 to 17:42 for C/M.
i) Hathazari 230 kV Busbar-02 was under shut down from 08:06 to 16:16 for D/W.
j) HVDC-Rajshahi (N) Ckt-1 was under shut down from 08:26 to 20:13 for A/M.
k) Bogra-Mahasthangar 132 kV Ckt-1 was under shut down from 09:42 to 15:04 for A/M.
l) Barisal(N)-Madaripur 132 kV Ckt-2 was under shut down from 08:50 to 17:00 for A/M.
m) Orion-Bagerhat 132 kV Ckt-2 was under shut down from 08:29 to 16:39 for A/M.
n) Bheramara-Kustia 132 kV Ckt-1 was under shut down from 07:48 to 14:33 for A/M.
o) Shahjadpur-Pabna 132 kV Ckt was under shut down from 08:51 to 16:40 for A/M.
p) Ishurdi-Ruppur 132 kV Ckt-2 was under shut down from 08:40 to 16:12 for A/M.
q) Rajshahi 230/132 kV ATR-1 transformer was under shut down from 12:23 to 20:14 for D/W.
r) Rangpur-Confidence 132 kV Ckt-1 was under shut down from 07:18 to 18:36 for D/W.
s) Rangpur 132 kV Bus-B was under shut down from 08:02 to 18:28 for D/W.
t) Purbasadipur 132/33 kV T3 transformer was under shut down from 09:45 to 18:14 for A/M.
u) Comilla(N) 132/33 kV T3(Both Sides) & T4(33 kV side) transformers tripped at 09:19 showing O/C |  |  |  |  | About 37 MW power interruption occurred under Cumilla(N) S/S area
and were switched on at 09:37. |  |  |  |  | from 09:19 to 09:37.
v) Ashuganj-Bhulta 400 kV Ckt-01 tripped at 11:36 from Ashuganj end showing dist. and was switched
on at 12:11.
w) Sylhet 132/33 kV T1 transformer tripped at 11:30 due to B-phase underground cable burst.
x) Joydevpur-Ghorashal 132 kV Ckt-2 was under shut down from 18:35 to 21:11 for emergency maintenance work.
y) After maintenance Payra Unit-1 was synchronized at 15:18.
z) Haripur-Siddhirganj 230 kV Ckt-2 was shut down at 07:38(04/01/2021) for R-phase Loop change.
aa) Bibiyana-Shahjibazar 230 kV Ckt-2 was shut down at 07:39(04/01/2021) due to R/H at Y-phase
insulator of Tower#255.
ab) Hathazari 230 kV Busbar-02 & CB was shut down at 06:55(04/01/2021) for C/M.
ac) Rangpur-Rangpur Confidence 132 kV Ckt-1 was shut down at 08:00(04/01/2021) for A/M.
ag) Shahmirpur-Sikalbaha 132 kV Ckt-2 was shut down at 07:30(30/12/2020) for D/W.
ah) Goalpara-Bagerhat 132 kV Ckt-1 was shut down at 07:48(30/12/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 278 | 4932000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 7279400
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 1051727 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8771590 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 360 | 7686000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 452160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 1114776 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 24870 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1169685
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 288540
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 373440
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 57 | 361440 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 19536 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 196560 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 120480 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 153021 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 37 | 443755 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1296600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 600800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 708900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 38592 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 283 | 3939271
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 123 | 1707260 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 715176 | High Voltage.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1552320 | Engine problem
| Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 55 | 1323360 | Low demand
| Dhaka area Total |  |  |  | 6057 | 2570 | 46321259
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 47253
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 116910
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 795360
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 792000 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 239784 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 43200 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1143360
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440640 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 599520
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 30720 | High Voltage.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24480
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 87 | 1382 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 40 | 491637 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2190720
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 2268218 | RRT
| Chattogram area Total |  |  |  | 2266 | 534 | 9225184
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 692020 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 165 | 3754000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 6953400 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 380 | 7640000
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 133920 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 140640 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1165696
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 2828581
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1808640 | High Voltage.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 428940 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 258840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2007360
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 677200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 47779 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 520650
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 708120 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1414 | 29983240
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2484240 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 498744
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 304320
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2767200 | High Voltage.
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 32400 | #REF!
| Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 272680
| Tangail Palli Power Gen 22 MW |  | SIPP | 4*6.7 | 0 | 18 | 266880
| Mymensingh Area Total |  |  |  | 687 | 436 | 6639114
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 1117000 | Gas shortage & GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 210000 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3336000 | Gas shortage & GT-2 under shut down
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 397200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 30 | 630648
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 186096
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 761664 | Unit-9 under maint.
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1700160 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 129 | 2205930
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7249000 | Gas shortage
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 54540 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 425 | 9973000 | On test
| Sylhet Area Total |  |  |  | 1988 | 1205 | 27821238
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 830 | 14427636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1642560
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 7424 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 4703904 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 289125 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 36480 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 744000
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1209 | 21851129
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 60480 | High Voltage.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 399700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 54 | 1373819 | High Voltage.
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 260 | 2167600 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 32 | 593400 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 54 | 642000 | On test.
| Barisal Area Total |  |  |  | 1054 | 438 | 5236999
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 51872 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 13170 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 138 | 3830118 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 9220900 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 504960
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 206082
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 6240
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 291232 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1850496
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1037280
| Rajshahi Area Total |  |  |  | 2183 | 873 | 17012350
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3687700
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 34 | 878400 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29733
| Rangpur Area Total |  |  |  | 605 | 184 | 4595833
| Total |  |  |  | 20104 | 8863 | 168686346
| Eastern Grid Total |  |  |  | 13978 | 6159 | 119990035
| Western Grid Total |  |  |  | 6126 | 2704 | 48696311
| National Grid Total |  |  |  | 20104 | 8863 | 168686346
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-03
| (a) ENTIRE EASTERN GRID : |  | 5542 | MW | (b) ENTIRE WESTERN GRID : |  | 2776 | MW
| i) Dhaka area |  | 2918 | MW | i) Khulna area |  | 1078 | MW
| ii) Chittagong area |  | 873 | MW | ii) Rajshahi area |  | 870 | MW
| iii) Comilla area |  | 714 | MW | iii) Barisal area |  | 245 | MW
| iv) Mymensingh area |  | 721 | MW | iv) Rangpur area |  | 583 | MW
| v) Sylhet area |  | 316 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8318 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 92 | 9:00 | Jamalpur | 91 | 18:00 | Benapol | 38 | 18:30
| Munsiganj | 82 | 20:00 | Sherpur | 96 | 18:30 | Jhenida | 84 | 18:30
| Sonargaon | 56 | 18:00 | Srimongal | 24 | 18:00 | Bottail | 94 | 18:00
| Shyampur | 176 | 12:00 | Shahjibazar | 86 | 19:30 | G.K Project | 34 | 18:00
| Bhulta | 145 | 9:00 | Fenchuganj | 25 | 18:00 | Faridpur | 134 | 19:00
| Madanganj | 48 | 21:00 | Kulawara | 27 | 18:00 | Madaripur | 59 | 18:30
| Shitalakhya | 83 | 12:00 | Sylhet | 84 | 13:00 | Sariatpur | 42 | 19:00
| Rahim steel | 18 | 6:00 | Chatak | 18 | 18:00 | Gopalganj | 57 | 19:00
| Matuail | 50 | 9:00 | Sunamganj | 28 | 20:00 | Bagerhat | 86 | 19:00
| Ghorasal | 58 | 18:00 | Biani Bazar | 35 | 18:30 | Mongla | 40 | 18:00
| Narsingdi | 117 | 20:00 | Comilla (S) | 106 | 18:30 | Satkhira | 76 | 18:30
| Haripur (SBU) | 97 | 12:00 | Comilla(N) | 63 | 20:00 | Gallamari | 19 | 13:00
| Ullon | 38 | 13:00 | Chandpur | 60 | 19:00 | Magura | 40 | 18:00
| Hasnabad | 143 | 21:00 | Feni | 76 | 20:00 | Norail | 24 | 18:30
| Magbazar | 68 | 18:00 | Chowmuhani | 118 | 19:30 | Chuadanga | 65 | 18:30
| Maniknagar | 68 | 12:00 | Ashuganj | 37 | 18:30 | Barisal(N) | 29 | 20:00
| Bangabhaban | 15 | 10:00 | Daudkandi | 86 | 19:30 | Barisal (S) | 72 | 18:00
| Narinda | 66 | 13:00 | B.Baria | 96 | 19:00 | Patuakhali | 78 | 19:30
| Dhanmondi | 95 | 13:00 | Ramganj | 64 | 18:30 | Bhandaria | 42 | 19:30
| Lalbag | 67 | 13:00 | Chaddagram | 24 | 18:30 | Borhan Uddin | 26 | 20:00
| Madartek | 42 | 18:00 | PHP | 3 | 11:00 | Ishurdi | 46 | 18:00
| Dhaka University |  |  | Madunaghat | 45 | 18:30 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.5 | Hathazari | 63 | 0.79167 | Natore | 84 | 0.75
| Fatullah | 42 | 10:00 | Khulshi | 167 | 14:00 | Bogra | 116 | 18:00
| Mirpur | 69 | 18:00 | Halishahar | 89 | 14:00 | Noagaon | 74 | 20:00
| Kalyanpur | 57 | 18:00 | Baraulia | 136 | 1:00 | Rajshahi | 99 | 20:00
| Gulshan | 74 | 13:00 | Sikalbaha | 21 | 18:30 | Rajshahi New | 10 | 20:00
| Uttara | 63 | 18:00 | Dohazari | 54 | 18:00 | C.Nawabganj | 50 | 19:30
| Uttara New | 22 | 18:00 | Cox'sbazar | 77 | 18:00 | Amnura | 26 | 19:00
| Kamrangirchar | 70 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 80 | 20:00
| Savar | 99 | 18:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 73 | 18:30
| Bhasantec | 96 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 64 | 19:00
| Agargaon | 42 | 18:00 | Bakulia | 72 | 18:00 | Niyamatpur | 65 | 9:00
| Satmosjid | 61 | 0.75 | Julda | 21 | 0.29167 | Joypurhat | 43 | 0.79167
| Tongi | 54 | 16:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 156 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 30 | 18:00
| Basundhara | 86 | 14:00 | Shahmirpur | 20.5 | 18:00 | Rangpur | 105 | 18:30
| Manikganj | 46 | 19:00 | Khagrachhari | 20 | 18:30 | Lalmonirhat | 45 | 18:30
| Joydevpur | 109 | 18:30 | Matarbari | 26 | 18:30 | Saidpur | 80 | 18:30
| New Tongi | 99 | 12:00 | Baroiar Hat | 26 | 18:30 | Purbasadipur | 79 | 19:30
| Kodda | 166 | 18:00 | Rangamati | 9 | 18:00 | Thakurgaon | 60 | 18:30
| Dhamrai | 74 | 18:30 | Abul Khair 230 | 148 | 15:00 | Palashbari | 92 | 18:30
| Rajendrapur | 76 | 19:00 | BSRM | 142 | 1:00 | Barapukuria | 39 | 19:30
| Valuka | 82 | 18:30 | GPH Ispat | 81 | 11:00 | Panchagar | 43 | 18:30
| Tangail | 140 | 18:30 | Goalpara | 16 | 13:00 | Joldhaka | 26 | 18:30
| Mymensing | 150 | 18:30 | Central s/s | 81 | 20:00 | Kurigram | 38 | 19:30
| Kishorganj | 94 | 19:30 | Noapara | 50 | 18:30
| Netrokona | 90 | 19:00 | Jessore | 82 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 18:30 | 409 | 5:00 | Kaliakoir | 405 | 0.125 | 389 | 0.5
| Bheramara | 411 | 16:00 | 398 | 11:00 | Bhulta | 393 | 0.875 | 378 | 0.95833
| Ashuganj(N) | 400 | 21:00 | 390 | 6:00 | Gopalganj | 422 | 0.041667 | 389 | 0.54167
| Payra | 425 | 20:00 | 391 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 238 | 1:00 | Comilla (N) | 240 | 18:30 | 234 | 23:00
| Ishurdi | 241 | 5:00 | 232 | 13:00 | Hathazari | 224 | 18:30 | 210 | 24:00
| Ashuganj | 241 | 7:00 | 240 | 5:00 | Megnaghat | 235 | 16:00 | 229 | 7:00
| Serajganj | 235 | 14:00 | 230 | 8:00 | Fenchuganj | 244 | 12:00 | 238 | 7:00
| Baghabari | 245 | 17:00 | 240 | 13:00 | Siddhirganj | 235 | 21:00 | 230 | 15:00
| Barapukuria | 233 | 24:00 | 227 | 18:00 | Maniknagar | 234 | 20:00 | 227 | 11:00
| Bogra | 236 | 21:00 | 231 | 13:00 | Agargaon | 234 | 17:00 | 223 | 14:00
| Rajshahi | 232 | 23:00 | 223 | 13:00 | Barisal | 253 | 18:30 | 240 | 13:00
| Khulna South | 244 | 10:00 | 231 | 13:00 | AKSML | 230 | 18:30 | 217 | 6:00
| Rampura | 233 | 17:00 | 229 | 11:00 | BSRM | 232 | 17:00 | 219 | 13:00
| Haripur | 233 | 20:00 | 227 | 13:00 | Bibiyana | 244 | 21:00 | 238 | 13:00
| Hasnabad | 235 | 21:00 | 229 | 9:00 | Bhulta | 236 | 19:00 | 230 | 17:00
| Shyampur | 233 | 20:00 | 220 | 13:00 | Ashuganj (S) | 240 | 10:00 | 235 | 11:00
| Aminbazar | 235 | 19:30 | 228 | 11:00 | Kaliakoir | 232 | 19:30 | 225 | 6:00
| Tongi | 233 | 21:00 | 225 | 15:00 | GPH | 227 | 19:30 | 210 | 24:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 18:00 | 136 | 12:00 | Madanhat | 139 | 0.75 | 129 | 0
| Munsiganj | 142 | 18:30 | 135 | 11:00 | Hathazari | 136 | 0.041667 | 130 | 0
| Sonargaon | 139 | 20:00 | 134 | 13:00 | Khulshi | 138 | 0.77083 | 128 | 0.95833
| Shyampur | 133 | 19:30 | 129 | 11:00 | Halishahar | 140 | 0.77083 | 131 | 0.25
| Bhulta | 133 | 3:00 | 130 | 9:00 | Baraulia | 139 | 0.75 | 130 | 0.95833
| Madanganj | 138 | 1:00 | 131 | 9:00 | Sikalbaha | 138 | 0.70833 | 129 | 0.95833
| Shitalakhya | 143 | 18:00 | 137 | 11:00 | Dohazari | 135 | 0.58333 | 127 | 0.95833
| Rahim steal | 140 | 18:30 | 137 | 7:00 | Cox'sbazar | 132 | 0.77083 | 121 | 0
| Matuail | 140 | 18:00 | 136 | 12:00 | Chandraghona | 140 | 0.75 | 132 | 0.20833
| Ghorasal | 140 | 1:00 | 138 | 4:00 | Kaptai | 135 | 0.29167 | 132 | 0.41667
| Narsinghdi | 138 | 18:00 | 133 | 1:00 | A. Khaer Stl. | 136 | 0.041667 | 133 | 0.16667
| Haripur (SBU) | 140 | 3:00 | 137 | 11:00 | Bakulia | 138 | 0.77083 | 129 | 0.95833
| Ullon | 134 | 20:00 | 130 | 12:00 | Julda | 139 | 0.75 | 131 | 0.041667
| Hasnabad | 140 | 1:00 | 137 | 8:00 | TK Chemical | 137 | 0.58333 | 130 | 0.95833
| Magbazar | 135 | 4:00 | 130 | 11:00 | Modern Steel | 137 | 0.77083 | 130 | 0.95833
| Maniknagar | 140 | 4:00 | 136 | 11:00 | Shahmirpur | 140 | 0.77083 | 130 | 0.95833
| Bangabhaban | 140 | 4:00 | 136 | 11:00 | Khagrachhari | 139 | 0.77083 | 131 | 0.95833
| Narinda | 140 | 4:00 | 136 | 11:00 | Matarbari | 132 | 0.58333 | 121 | 0
| Dhanmondi | 134 | 20:00 | 130 | 12:00 | Baroiar Hat | 138 | 0.33333 | 133 | 0.16667
| Lalbag | 133 | 1:00 | 128 | 12:00 | Rangamati | 138 | 18:30 | 129 | 11:00
| Madartek | 134 | 1:00 | 130 | 13:00 | Goalpara S/S | 139 | 1:00 | 131 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 1:00 | 132 | 0.33333
| Aftabnagar | 134 | 2:00 | 130 | 11:00 | Noapara | 136 | 10:00 | 129 | 0.75
| Fatuiiah | 135 | 21:00 | 129 | 11:00 | Jessore | 134 | 1:00 | 125 | 0.54167
| Mirpur | 136 | 6:00 | 129 | 12:00 | Benapol | 133 | 0.16667 | 126 | 0.54167
| Kalyanpur | 133 | 6:00 | 130 | 12:00 | Jhenida | 134 | 2:00 | 123 | 0.54167
| Gulshan | 131 | 6:00 | 129 | 12:00 | Bottail | 136 | 0.20833 | 128 | 0.54167
| Uttara | 133 | 6:00 | 129 | 12:00 | G.K Project | 141 | 0.25 | 137 | 0.75
| Uttara New | 138 | 6:00 | 133 | 12:00 | Faridpur | 138 | 0.16667 | 130 | 0.54167
| Kamrangirchar | 142 | 6:00 | 135 | 12:00 | Madaripur | 141 | 0.66667 | 130 | 0.54167
| Savar | 134 | 6:00 | 128 | 12:00 | Shariyatpur S/S | 142 | 16:00 | 135 | 0.54167
| Bhasantec | 134 | 6:00 | 132 | 12:00 | Gopalganj | 144 | 0.66667 | 139 | 0.33333
| Agargaon | 135 | 6:00 | 130 | 12:00 | Bagerhat | 136 | 1:00 | 128 | 0.54167
| Satmosjid | 134 | 6:00 |  | 12:00 | Mongla | 135 | 1:00 | 129 | 0.66667
| Tongi | 142 | 13:00 | 138 | 15:00 | Satkhira | 138 | 1:00 | 130 | 13:00
| Kabirpur | 137 | 21:00 | 130 | 12:00 | Gallamari | 139 | 0.041667 | 132 | 0.54167
| Basundhara | 135 | 22:00 | 130 | 12:00 | Magura | 134 | 3:00 | 122 | 0.75
| Manikganj | 144 | 10:00 | 134 | 24:00 | Norail | 134 | 0.16667 | 123 | 0.54167
| Joydevpur | 142 | 20:00 | 138 | 7:00 | Chuadanga | 132 | 5:00 | 120 | 0.54167
| New Tongi | 141 | 21:00 | 135 | 7:00 | Barisal(N) | 144 | 17:00 | 135 | 13:00
| Kodda | 140 | 19:00 | 133 | 7:00 | Barisal (S) | 142 | 0.20833 | 137 | 0.33333
| Dhamrai | 136 | 21:00 | 129 | 13:00 | Patuakhali(S) | 142 | 0.70833 | 132 | 0.45833
| Rajendrapur | 139 | 18:30 | 134 | 7:00 | Bhandaria | 137 | 0.041667 | 130 | 0.54167
| Valuka | 130 | 1:00 | 123 | 13:00 | Ishurdi | 140 | 1:00 | 133 | 16:00
| Tangail | 135 | 7:00 | 129 | 15:00 | Ruppur Paromanobik | 138 | 1:00 | 135 | 12:00
| Mymensing | 132 | 9:00 | 125 | 18:00 | Natore | 140 | 6:00 | 135 | 13:00
| Kishorganj | 133 | 9:00 | 127 | 18:00 | Bogra | 140 | 14:00 | 136 | 8:00
| Netrokona | 132 | 7:00 | 124 | 15:00 | Noagaon | 136 | 4:00 | 130 | 9:00
| Jamalpur | 140 | 20:00 | 125 | 4:00 | Rajshahi | 141 | 3:00 | 134 | 13:00
| Sherpur | 138 | 9:00 | 124 | 3:00 | Rajshahi New | 142 | 2:00 | 135 | 13:00
| Srimongal | 139 | 3:00 | 136 | 18:00 | C.Nawabganj | 142 | 4:00 | 134 | 13:00
| Shahjibazar | 135 | 1:00 | 133 | 18:00 | Amnura | 140 | 1:00 | 131 | 13:00
| Fenchuganj | 138 | 2:00 | 136 | 8:00 | Pabna | 140 | 1:00 | 133 | 13:00
| Khulawara | 138 | 1:00 | 136 | 6:00 | Shahjadpur | 142 | 14:00 | 138 | 9:00
| Sylhet | 135 | 1:00 | 134 | 9:00 | Serajganj | 136 | 1:00 | 135 | 18:00
| Chatak | 135 | 23:00 | 133 | 7:00 | Niyamatpur | 136 | 15:00 | 127 | 13:00
| Sunamganj | 134 | 2:00 | 132 | 12:00 | Joypurhat | 137 | 15:00 | 131 | 13:00
| Biani Bazar | 136 | 1:00 | 133 | 18:00 | Sherpur(Bogura) | 140 | 1:00 | 136 | 18:30
| Comilla(s) | 131 | 3:00 | 126 | 18:30 | Mohastangor | 138 | 1:00 | 133 | 19:00
| Comilla(n) | 144 | 19:00 | 140 | 11:00 | Rangpur | 133 | 6:00 | 121 | 18:00
| Chandpur | 144 | 9:00 | 142 | 17:00 | Lalmonirhat | 132 | 4:00 | 123 | 19:00
| Feni | 140 | 18:30 | 136 | 7:00 | Saidpur | 132 | 6:00 | 121 | 18:30
| Chowmuhani | 138 | 9:00 | 134 | 7:00 | Purbasadipur | 130 | 5:00 | 119 | 18:00
| Ashuganj | 137 | 7:00 | 135 | 13:00 | Thakurgaon | 129 | 1:00 | 117 | 18:00
| Daudkandi | 140 | 14:00 | 137 | 11:00 | Palashbari | 134 | 1:00 | 129 | 18:00
| B.Baria | 133 | 8:00 | 131 | 18:00 | Barapukuria | 133 | 1:00 | 127 | 18:00
| Ramganj | 140 | 16:00 | 135 | 20:00 | Panchagar | 129 | 5:00 | 115 | 18:00
| Chaddagram | 140 | 9:00 | 136 | 17:00 | Joldhaka | 131 | 5:00 | 120 | 18:30
| PHP | 140 | 1:00 | 135 | 11:00 | Kurigram | 130 | 0.16667 | 119 | 0.75

## L-Curve
Date | 2021-01-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 20 | 4705 | 2061 | 6766 |  |  |  | QF-LDC-11
0:30 | 129 | 4621.5 | 1826 | 6447.5 | Date: | 2021-01-03
1:00 | 238 | 4538 | 1591 | 6129
1:30 | 264 | 4469.5 | 1511.5 | 5981
2:00 | 290 | 4401 | 1432 | 5833
2:30 | 224 | 4301.5 | 1460.5 | 5762 | [5 empty] | Gen. at Eve. Peak | 8863 | 8863 MW (19:30 )
3:00 | 158 | 4202 | 1489 | 5691 | [6 empty] | 19:30
3:30 | 142.5 | 4102.5 | 1491 | 5593.5 | [5 empty] | Gen. at Day Peak | 7151 | 7151 MW (12:00 )
4:00 | 127 | 4003 | 1493 | 5496 | [6 empty] | 12:00
4:30 | 115.5 | 3968.5 | 1497 | 5465.5 | [5 empty] | Highest Generation | 8863
5:00 | 104 | 3934 | 1501 | 5435 | [6 empty] | 19:30
5:30 | 103 | 3983.5 | 1568.5 | 5552
6:00 | 102 | 4033 | 1636 | 5669
6:30 | 169 | 4199 | 1648.5 | 5847.5
7:00 | 236 | 4365 | 1661 | 6026
7:30 | 238.5 | 4514.5 | 1771.5 | 6286
8:00 | 241 | 4664 | 1882 | 6546
8:30 | 156 | 4797 | 1956 | 6753
9:00 | 71 | 4930 | 2030 | 6960
9:30 | 36 | 4972.5 | 2029 | 7001.5
10:00 | 1 | 5015 | 2028 | 7043
10:30 | 30.5 | 4985.5 | 2028 | 7013.5
11:00 | 60 | 4956 | 2028 | 6984
11:30 | 57.5 | 5036.5 | 2031 | 7067.5
12:00 | 55 | 5117 | 2034 | 7151
12:30 | 101 | 5273 | 2037.5 | 7310.5
13:00 | 147 | 5429 | 2041 | 7470
13:30 | 99 | 5324 | 1991.5 | 7315.5
14:00 | 51 | 5219 | 1942 | 7161
14:30 | 45.5 | 5211.5 | 1933.5 | 7145
15:00 | 40 | 5204 | 1925 | 7129
15:30 | 55 | 5094 | 1806.5 | 6900.5
16:00 | 70 | 4984 | 1688 | 6672
16:30 | 67.5 | 5075 | 1738 | 6813
17:00 | 65 | 5166 | 1788 | 6954
17:30 | 150 | 5487.5 | 2082.5 | 7570
18:00 | 235 | 5809 | 2377 | 8186
18:30 | 244 | 5926 | 2490 | 8416
19:00 | 253 | 6043 | 2603 | 8646
19:30 | 247 | 6159 | 2704 | 8863
20:00 | 211 | 6045 | 2662 | 8707 |  |  |  | Executive Engineer
20:30 | 145.5 | 5955.5 | 2643 | 8598.5 |  |  |  | Network Operation Division
21:00 | 80 | 5866 | 2624 | 8490
21:30 | 64.5 | 5647.5 | 2544.5 | 8192
22:00 | 49 | 5429 | 2465 | 7894 |  |  |  |  | Page 6 of 7
22:30 | 65 | 5180.5 | 2372.5 | 7553
23:00 | 81 | 4932 | 2280 | 7212
23:30 | 50.5 | 4818.5 | 2170.5 | 6989
24:00 | 20 | 4705 | 2061 | 6766
8863 MW (19:30 )
7151 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-03 |  | Energy | 168686346
[11 empty] | 2021-01-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3161 | 622 | 1298 | 1313 | 450 | 35 | 0 | 0 | 78 | 0
0:30 | 3047.5 | 529.5 | 1391 | 1165.5 | 300 | 32.5 | 0 | 0 | 77 | 0 | Date: | 2021-01-03
1:00 | 2934 | 437 | 1484 | 1018 | 150 | 30 | 0 | 0 | 76 | 0
1:30 | 3012 | 437 | 1455.5 | 820.5 | 150 | 30 | 0 | 0 | 76 | 0 | [7 empty] | Total Energy | 168.6863 | Total Energy Gen 168.686 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 168.686 MKWHr
2:00 | 3090 | 437 | 1427 | 623 | 150 | 30 | 0 | 0 | 76 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3095 | 436.5 | 1441.5 | 534 | 150 | 30 | 0 | 0 | 75 | 0 | [7 empty] | Energy Requirement | 168.6863
3:00 | 3100 | 436 | 1456 | 445 | 150 | 30 | 0 | 0 | 74 | 0
3:30 | 3058.5 | 436 | 1466 | 379 | 150 | 30 | 0 | 0 | 74 | 0 | [6 empty] | Shortage
4:00 | 3017 | 436 | 1476 | 313 | 150 | 30 | 0 | 0 | 74 | 0
4:30 | 3027 | 436.5 | 1454.5 | 294.5 | 150 | 30 | 0 | 0 | 73 | 0
5:00 | 3037 | 437 | 1433 | 276 | 150 | 30 | 0 | 0 | 72 | 0
5:30 | 3064 | 437 | 1456 | 343 | 150 | 30 | 0 | 0 | 72 | 0
6:00 | 3091 | 437 | 1479 | 410 | 150 | 30 | 0 | 0 | 72 | 0
6:30 | 3093.5 | 437 | 1442 | 623 | 150 | 30 | 0 | 0 | 71 | 1 |  |  |  |  | Coal
7:00 | 3096 | 437 | 1405 | 836 | 150 | 30 | 0 | 0 | 70 | 2
7:30 | 3115.5 | 483.5 | 1457.5 | 967.5 | 150 | 30 | 0 | 0 | 72 | 10 |  |  |  | Oil |  |  |  | ,
8:00 | 3135 | 530 | 1510 | 1099 | 150 | 30 | 0 | 0 | 74 | 18
8:30 | 3082 | 530 | 1451.5 | 1405.5 | 150 | 30 | 0 | 0 | 75 | 29
9:00 | 3029 | 530 | 1393 | 1712 | 150 | 30 | 0 | 0 | 76 | 40
9:30 | 2998.5 | 553.5 | 1357 | 1787 | 150 | 30 | 0 | 0 | 76 | 49.5
10:00 | 2968 | 577 | 1321 | 1862 | 150 | 30 | 0 | 0 | 76 | 59
10:30 | 2977 | 577 | 1302.5 | 1834 | 150 | 32.5 | 0 | 0 | 76 | 64.5
11:00 | 2986 | 577 | 1284 | 1806 | 150 | 35 | 0 | 0 | 76 | 70
11:30 | 2998.5 | 577 | 1284 | 1873 | 150 | 35 | 0 | 0 | 78 | 72
12:00 | 3011 | 577 | 1284 | 1940 | 150 | 35 | 0 | 0 | 80 | 74
12:30 | 3040.5 | 577 | 1338.5 | 2014 | 150 | 35 | 0 | 0 | 84 | 71.5
13:00 | 3070 | 577 | 1393 | 2088 | 150 | 35 | 0 | 0 | 88 | 69
13:30 | 3070 | 577 | 1393 | 2088 | 150 | 35 | 0 | 0 | 88 | 69
14:00 | 3070 | 577 | 1393 | 2088 | 150 | 35 | 0 | 0 | 88 | 69
14:30 | 3049 | 577 | 1354 | 1992 | 150 | 35 | 0 | 0 | 87 | 55.5
15:00 | 3028 | 577 | 1315 | 1896 | 150 | 35 | 0 | 0 | 86 | 42
15:30 | 3035.5 | 577 | 1262.5 | 1706 | 170 | 35 | 0 | 0 | 84 | 30.5
16:00 | 3043 | 577 | 1210 | 1516 | 190 | 35 | 0 | 0 | 82 | 19
16:30 | 3083.5 | 577 | 1212 | 1554.5 | 220 | 35 | 35 | 0 | 86 | 10
17:00 | 3124 | 577 | 1214 | 1593 | 250 | 35 | 70 | 0 | 90 | 1
17:30 | 3166.5 | 695.5 | 1258 | 1913 | 270 | 35 | 137.5 | 0 | 94 | 0.5
18:00 | 3209 | 814 | 1302 | 2233 | 290 | 35 | 205 | 0 | 98 | 0
18:30 | 3206 | 814 | 1304.5 | 2461.5 | 305 | 35 | 189 | 0 | 101 | 0
19:00 | 3203 | 814 | 1307 | 2690 | 320 | 35 | 173 | 0 | 104 | 0
19:30 | 3209 | 830 | 1385 | 2719 | 410 | 35 | 173 | 0 | 102 | 0
20:00 | 3219 | 810 | 1313 | 2693 | 420 | 35 | 115 | 0 | 102 | 0
20:30 | 3194 | 810 | 1320.5 | 2592.5 | 437.5 | 35 | 108 | 0 | 101 | 0
21:00 | 3169 | 810 | 1328 | 2492 | 455 | 35 | 101 | 0 | 100 | 0
21:30 | 3183.5 | 810 | 1344.5 | 2221 | 452.5 | 35 | 50.5 | 0 | 95 | 0
22:00 | 3198 | 810 | 1361 | 1950 | 450 | 35 | 0 | 0 | 90 | 0
22:30 | 3197.5 | 810 | 1342 | 1631.5 | 450 | 35 | 0 | 0 | 87 | 0
23:00 | 3197 | 810 | 1323 | 1313 | 450 | 35 | 0 | 0 | 84 | 0
23:30 | 3179 | 716 | 1310.5 | 1313 | 450 | 35 | 0 | 0 | 81 | 0 | Max Temp. in Dhaka |  | 27.4° C
24:00 | 3161 | 622 | 1298 | 1313 | 450 | 35 | 0 | 0 | 78 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 168.686 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 168.686 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 792000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 25 | 25 |  |  |  |  | 0 | 47253
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 15 | 17 | 18 | 16 | 15 | 11 | 6 | 0 | [9 empty] | 116910
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 43 | 102 |  | 51 | 51 | 17 |  |  |  | 0 | 239784
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 29 | 46 | 131 | 259 | 282 | 268 | 272 | 215 | 215 | 145 | 165 | 275 |  | 283 | 283 | 286 | 286 | 286 | 180 | 95 | 3939271
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 143 | 148 | 152 | 154 | 148 | 148 | 148 | 158 | 169 | 168 | 172 | 184 | 180 | 205 | 252 | 236 | 260 | 280 |  | 278 | 278 | 277 | 278 | 276 | 276 | 287 | 4932000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7279400
26
28 | Ashuganj TPP Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | [16 empty] | 0 | 692020
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 133920
33 | Ashuganj 225 MW CCPP | 198 | 176 | 126 | 129 | 129 | 130 | 130 | 129 | 131 | 131 | 152 | 155 | 136 | 142 | 145 | 140 | 143 | 176 |  | 168 | 165 | 162 | 192 | 194 | 193 | 156 | 3754000
34 | Ashuganj 450 MW CCPP(South) | 250 | 300 | 320 | 250 | 250 | 250 | 250 | 250 | 250 | 350 | 345 | 325 | 330 | 355 | 345 | 355 | 375 | 370 |  | 370 | 380 | 380 | 305 | 270 | 390 | 390 | 7640000
| Ashuganj 450 MW CCPP(North) | 150 | 240 | 245 | 255 | 260 | 265 | 280 | 280 | 280 | 260 | 260 | 280 | 330 | 300 | 300 | 300 | 280 | 300 |  | 310 | 310 | 310 | 320 | 390 | 263 | 265 | 6953400
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 140640
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 369 | 384 | 383 | 371 | 366 | 383 | 382 | 413 | 370 | 349 | 351 | 355 | 383 | 355 | 293 | 308 | 354 | 377 |  | 353 | 350 | 354 | 350 | 349 | 350 | 350 | 8771590
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 295 | 267 | 316 | 316 | 316 | 316 | 316 | 346 | 345 | 346 | 309 | 310 | 358 | 309 | 354 | 353 | 355 | 309 |  | 309 | 360 | 310 | 340 | 355 | 326 | 300 | 7686000
42 | RPCL 210MW CCPP | 106 | 107 | 108 | 108 | 109 | 108 | 108 | 109 | 107 | 106 | 103 | 103 | 101 | 104 | 103 | 103 | 105 | 104 |  | 104 | 106 | 108 | 108 | 107 | 108 | 110 | 2484240
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 10 | 25 | 36 | 42 | 45 | 42 | 36 | 25 | 10 | 1 | [9 empty] | 272680
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1117000
45 | Fenchugonj CCPP Phase-2 | [13 empty] | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 210000
46 | Shajibazar 330 MW CCPP | 145 | 146 | 145 | 144 | 145 | 145 | 146 | 145 | 143 | 143 | 146 | 145 | 145 | 145 | 144 | 145 | 144 | 145 |  | 144 | 144 | 146 | 144 | 145 | 145 | 146 | 3336000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 31 | 31 | 31 | 31 | 20 | 33 | 32 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 761664
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 74 | 74 | 75 | 74 | 69 | 69 | 69 | 68 | 69 | 68 | 70 | 70 | 70 | 70 | 70 | 69 |  | 71 | 71 | 71 | 71 | 71 | 71 | 72 | 1700160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 70 | 70 | 70 | 70 | 90 | 90 | 90 | 90 | 20 | 20 | 25 | 30 | 35 | 110 | 125 | 128 | 128 | 129 |  | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 2205930
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [16 empty] | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 54540
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 186096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 22 | 22 | 22 | 39 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 397200
56 | Shahjahanulla 25 MW PP | [25 empty] | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 320 | 320 | 290 | 320 | 310 | 330 | 315 | 280 | 270 | 270 | 300 | 260 | 305 | 260 | 270 | 280 |  | 275 | 295 | 290 | 275 | 255 | 265 | 265 | 7249000
| Bibiyana South 400 MW | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 417 | 425 | 425 | 420 | 415 | 420 | 420 |  | 423 | 425 | 425 | 425 | 415 | 415 | 415 | 9973000
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 20 | 35 | 30 | 35 | 35 | 17 | 17 | 17 | 25 | 37 |  | 37 | 37 | 37 | 37 | 17 |  | 0 | 443755
59 | Tangail Palli Power Gen 22 MW | [5 empty] | 1 | 15 | 19 | 19 | 20 | 17 | 20 | 19 | 18 | 6 | 6 | 6 | 6 |  | 11 | 18 | 25 | 25 | 25 |  | 0 | 266880
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440640
61 | Narshingdi 22 MW PP (Doreen) |  |  | 16 | 16 |  |  |  |  | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 288540
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498744
63 | Impoprt (Tripura) | 76 | 76 | 74 | 74 | 72 | 72 | 70 | 74 | 76 | 76 | 76 | 80 | 88 | 92 | 86 | 82 | 90 | 98 |  | 104 | 102 | 102 | 100 | 90 | 84 | 78 | 2007360
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 42 | 42 | 42 | 35 | 15 | 5 | 7 | 5 | 7 | 11 | 9 | 6 | 8 | 15 | 10 |  | 17 | 27 | 32 | 33 | 41 | 42 | 42 | 599520
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428940
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 258840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 |  |  | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 677200
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 9 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 15 |  | 28 | 28 | 32 | 32 | 32 | 32 | 32 | 696600
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 600800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 708900
73 | Ghorashal 108MW PP (Regent) | 105 | 105 | 105 | 105 | 105 | 102 | 102 | 104 | 53 | 53 | 13 | 13 | 13 | [12 empty] | 0 | 1051727
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 46 | 46 | [5 empty] | 4 | 26 | 26 | 26 | 26 | 42 | 55 | 8 | 8 | 8 | 18 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 708120
| Manikgonj 162MW PP(MPGL) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1323360
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 8 | 24 | 18 | 7 | 7 | 7 | 10 |  | 72 | 100 | 100 | 85 |  |  | 0 | 373440
78 | Gazipur 52 MW PP | [16 empty] | 2 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 38592
79 | Kodda 150MW PP | [16 empty] | 16 | 32 |  | 32 | 32 | 20 | 16 |  |  | 0 | 120480
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 8 | 11 |  | 90 | 90 | 90 | 64 | 16 |  | 0 | 304320
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 10 |  | 30 | 8 | [5 empty] | 47779
| Gazipur 100 MW PP | [7 empty] | 4 | 34 | 35 | 35 | 46 | 70 | 70 | 70 | 35 | 35 | 35 |  | 50 | 70 | 70 | 35 | 17 |  | 0 | 715176
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24480
| Jodiac Power | 54 | 54 | 54 | 54 | 17 | 17 | [11 empty] | 2 |  | 15 | 40 | 35 | 42 | 36 | 36 | 36 | 491637
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 23 | 15 | 15 |  |  |  | 5 | 15 | 26 | 48 | 48 | 48 | 70 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 60 | 30 | 15 | 1114776
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 70 | 63 | 30 | [6 empty] | 1 | 12 | 38 | 40 | 40 | 40 | 40 | 40 | 57 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1169685
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 7 | 24 | 21 | 7 | 7 | 9 | 46 |  | 87 | 100 | 100 | 70 | 55 |  | 0 | 452160
| Meghnaghat 104 MW PP (OPCL) | 90 | 60 | 30 |  |  |  | 34 | 37 | 53 | 53 | 53 | 75 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 60 | 53 | 1552320
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 44 | [7 empty] | 0 | 43200
92 | Fenchuganj 44MW (Energyprima) | 50 | 44 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 35 | 10 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 630648
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1165696
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 24 | 16 | 16 | 16 | 16 | 7 | 7 | 7 | 7 | 32 |  | 57 | 57 | 57 | 24 |  |  | 0 | 361440
95 | Patenga 50MW PP (Baraka) | [5 empty] | 1 | 14 | 22 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 38 | 32 | 32 | 795360
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 30 | [5 empty] | 0 | 30720
97 | katpotti 52 MW | [17 empty] | 1 |  | 12 | [5 empty] | 0 | 19536
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 13 | [7 empty] | 0 | 24870
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 153021
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12650
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 196560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 90 | 20 |  |  |  | 4 | 106 | 149 | 200 | 160 | 120 | 120 | 120 | 120 | 120 | 70 | 70 | 101 |  | 200 | 200 | 200 | 200 | 170 | 72 | 72 | 2767200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 5 | 94 | 100 | 100 | 105 | 100 | 100 | 100 | 92 | 83 | 116 |  | 123 | 123 | 123 | 122 | 122 | 123 | 74 | 1707260
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 20 | 40 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 70 |  | 0 | 1143360
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 43 | 52 | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 98 | 105 | 120 |  | 100 | 100 | 100 | 100 | 68 | 68 | 68 | 1808640
117 | Ashuganj 150MW PP (Midland) | 100 | 50 |  |  |  | 15 | 108 | 150 | 150 | 147 | 142 | 123 | 135 | 143 | 142 | 142 | 143 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2828581
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 12 | [7 empty] | 0 | 32400
| Anwara 300 MW PP (United) | 70 | 32 | 33 | 16 | 16 | 16 | 16 | 49 | 49 | 49 | 52 | 52 | 52 | 53 | 53 | 89 | 89 | 108 |  | 87 | 87 | 88 | 89 | 51 | 53 | 53 | 1382
| Juldah unit-2 (Acorn) | 100 | 70 | 70 | 30 | 30 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2190720
| Anlima Energy Ltd. | 124 | 124 | 124 | 124 | 124 | 124 | 123 | 125 | 124 | 123 | 123 | 121 | 121 | 121 | 121 | 122 | 121 | 122 | [7 empty] | 0 | 2268218
120 | Eastern Zone Total | 4538 | 4401 | 4202 | 4003 | 3934 | 4033 | 4365 | 4664 | 4930 | 5015 | 4956 | 5117 | 5429 | 5219 | 5204 | 4984 | 5166 | 5809 |  | 6043 | 6159 | 6045 | 5866 | 5429 | 4932 | 4705 | 119990035
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 42 |  |  |  |  | 66 | 83 | 92 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 49 | 32 | 64 |  | 115 | 115 | 115 | 115 | 99 | 49 | 49 | 1642560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 53 | 53 | 53 | 53 | 35 | 35 | 17 | 17 | 17 | 36 |  | 105 | 105 | 105 | 53 | 8 |  | 0 | 744000
130
131
132 | United Payra Power Ltd. | 50 | [11 empty] | 34 | 54 | 50 | 39 | 54 | 54 |  | 54 | 54 | 55 | 54 | 54 | 54 | 54 | 642000
133 | Bhola Nutan Biddut BD LTD (GAS) | 35 | 16 | 16 | 35 | 34 | 34 | 35 | 22 | 4 | 7 | 32 | 31 | 7 | 13 | 31 | 24 | 5 | 32 |  | 32 | 32 | 9 | 8 | 36 | 38 | 37 | 593400
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 16 | 16 | 16 |  |  |  |  | 60480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 80 | 92 | 92 | 92 | 93 | 88 | 89 | 88 | 36 | 36 | 55 |  | 55 | 54 | 55 | 55 | 55 | 52 | 52 | 1373819
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 22 | 19 | 19 | 15 | 13 | 13 | 13 | 13 | 16 | 14 | 13 | 12 | 10 | 7 | 23 |  | 21 | 22 | 22 | 20 | 21 | 19 | 18 | 399700
141 | Noapara 100 MW PP (Bangla Trac) | [8 empty] | 7 | 20 | [15 empty] | 0 | 36480
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 33 |  |  | 16 | [8 empty] | 289125
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 1 | 3 |  | 4 | 4 |  |  |  |  | 0 | 7424
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 437 | 437 | 436 | 436 | 437 | 437 | 437 | 530 | 530 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 814 |  | 814 | 830 | 810 | 810 | 810 | 810 | 622 | 14427636
147 | Bheramara 410 MW CCPP | 205 | 210 | 225 | 230 | 235 | 235 | 225 | 220 | 215 | 200 | 185 | 185 | 180 | 175 | 150 | 140 | 155 | 160 |  | 155 | 155 | 155 | 145 | 150 | 155 | 160 | 4703904
148 | Payra 1320 MW | [15 empty] | 40 | 100 | 140 |  | 170 | 260 | 270 | 305 | 300 | 300 | 300 | 2167600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3687700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 10 | 24 | [8 empty] | 51872
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 139 | 150 | 150 | 130 | 146 | 178 | 180 | 177 | 170 | 164 | 158 | 156 | 149 | 143 | 135 | 137 | 137 | 138 |  | 140 | 138 | 139 | 139 | 139 | 139 | 141 | 3830118
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 387 | 430 | 430 | 420 | 440 | 391 | 432 | 398 | 346 | 380 | 360 | 380 | 300 | 330 | 330 | 330 | 390 |  | 393 | 390 | 390 | 392 | 393 | 376 | 378 | 9220900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 206082
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 | [7 empty] | 0 | 13170
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 6 | [7 empty] | 0 | 6240
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 44 |  | 86 | 86 | 78 | 85 |  |  |  | 291232
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 |  |  |  |  | 17 | 35 | 58 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 43 | 67 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 1850496
172 | Confidence Power Bogura Unit-1 113 MW | [8 empty] | 30 | 35 | 35 | 60 | 70 | 70 | 70 | 35 | 35 | 50 |  | 113 | 113 | 113 | 113 | 70 | 35 | 0 | 1037280
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 50 | 77 | 85 | 90 | 70 | 70 | 70 | 34 | 34 | 34 | 50 | 50 |  | 34 | 34 | 34 | 34 | 34 |  | 0 | 878400
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 29733
178
178