## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-05 | Tuesday
|  |  | Date (day): | 2021-01-05 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12244.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13621 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-04 | 2021-01-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 330 | 0 | 180 | 300
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 225 | 330 | 330 | 330
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 373 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 354 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 75 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 70 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 50 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 20 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 16 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 24 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 291 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 77 | 123 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 40 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 55 | 55 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1770 | 2459 | 3449 | 3864 | 929 | 1347
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 60 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 19 | 19 | 19 |  | 3 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 25 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 51 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 125 | 198 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 124 | 124
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 440 | 752 | 1356 | 1341 | 930 | 101
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 140 | 140
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 183 | 200 | 200
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 0 | 0 | 0 | 360 |  | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 310 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 26 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 49 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 36 | 36 | 36 | 159 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 107 | 102 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 80 | 90 | 90 |  | 73 | Gas shortage
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 50 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 106 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 21 | 21
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 18 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1232 | 1094 | 1797 | 2059 | 801 | 85
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 107 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 40 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 160 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 8 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 337 | 399 | 615.6 | 564 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 50 | 50
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 20 | 30
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 144 | 143 | 0 | 0 | 330 |  | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 14 | 5 | 11 | 22
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 5 | 20 | 20
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 33 | 33 | 33 |  | 33 | GT-8 under maint.
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 71 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 129 | 163 | 100 | 200
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 320 | 320
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 410 | 425 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1107 | 1186 | 1173 | 1294 | 330 | 456
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 579 | 817 | 592 | 833
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 6 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 220 | 250 | 250 | 160 |  | Gas shortage
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 0 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 10 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 84 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1031 | 1226 | 1357 | 1884 | 160 | 58
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 24 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 31 | 64 | 90 | 90
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 410 | 500 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 35 | 0 | 36 | 36
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 54 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 489 | 639 | 860 | 862 | 0 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 164 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 351 | 370 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 105 | 100 | 100
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 50 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 623 | 906 | 1366 | 1490 | 601 | 15
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 110 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 154 | 260 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7183 | 8921 | 12244.6 | 13621 | 3967 | 2473
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6826.3058 | 8478 | 11636.5563 | 12944.6069
| A. |  | 2021-01-04 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 8921 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5580 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8921 | MW
| 3 | Day peak Generation : |  |  | 7183 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8478 | MW
| 4 | Evening peak Generation : |  |  | 8921 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 170.6915 | MKWHr | By Solar | 0.40485 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.3726 | MKWHr |  | By Oil: | 35.7942 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.9673 | MKWHr |  | By Hydro: | 0.848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3967 | MW | Dhaka | 3027 | 3027 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2473 | MW | Chittagong | 882 | 882 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6440 | MW | Khulna | 1085 | 1085 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 751.92 | MMCFD |  |  | Rajshahi | 885 | 885 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 104399328.142 | ii) Oil : | Taka | 263430035.39 | Comilla | 717 | 717 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 65103448 | Total | Taka | 432932811.532 | Mymensingh | 737 | 737 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.361 | MKWHr. | Sylhet | 311 | 311 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 60 | MW (E to W) at | 19:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -113 | MW at | 1:00 | hrs | Rangpur | 598 | 598 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 28.2° C |  |  | Total | 8478 | 8478 |  | 0
| B. |  | 2021-01-05 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 28.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13621 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4421 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 176.0298 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5551 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.2731 | MKWHr. | ii) HVDC Flow at Peak Time |  | 817 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0314 | MKWHr. | iii) Maximum HVDC Flow : |  | 818 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.97 |  | (b) Today: | 97.9 |  | (c) Rule Curve: |  | 102.43
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 275 | 0 | 270 | 0 | 0 | 363 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 42 | 0 | 0 | 0 | 260 | 320 | 166 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 74 | 108 | 0 | 22 | 0 | 30 | 20 | 11 | 30 | 0 | 144 | 33 | 72 | 0 | 129 | 0 | 0 | 7 | 270 | 0 | 5 | 0 | 15 | 0 | 0 | 32 | 0 | 45 | 0 | 0 | 34 | 147 | 0 | 0 | 0 | 0 | 0 | 16 | 41 | 0 | 0 | 46 | 60 | 415 | 53 | 0 | 55 | 0 | 0 |  | 436 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 148 | 0 | 376 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 280 | 36 | 0 | 0 |  | 4317 | 1710 | 6027 | 3112 | 436 | 1279 | 661 | 430 | 35 | 0 | 74 | 0 | 0 | 97.98
2:00 | 0 | 0 | 276 | 0 | 270 | 0 | 0 | 358 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 42 | 0 | 0 | 0 | 260 | 320 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 72 | 110 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 144 | 33 | 72 | 0 | 129 | 0 | 0 | 7 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 46 | 60 | 415 | 53 | 0 | 55 | 0 | 0 |  | 436 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 161 | 0 | 376 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 0 |  | 4193 | 1729 | 5922 | 3157 | 436 | 1263 | 539 | 420 | 35 | 0 | 72 | 0 | 0 | 97.98
3:00 | 0 | 0 | 277 | 0 | 270 | 0 | 0 | 349 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 260 | 320 | 189 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 70 | 110 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 145 | 33 | 72 | 0 | 129 | 0 | 0 | 7 | 270 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 60 | 415 | 53 | 0 | 55 | 0 | 0 |  | 436 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 162 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 0 |  | 3976 | 1695 | 5671 | 3149 | 436 | 1253 | 308 | 420 | 35 | 0 | 70 | 0 | 0 | 97.97
4:00 | 0 | 0 | 272 | 0 | 270 | 0 | 0 | 350 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 260 | 320 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 64 | 108 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 145 | 34 | 72 | 0 | 129 | 0 | 0 | 7 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 60 | 415 | 0 | 0 | 55 | 0 | 0 |  | 436 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 172 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 0 |  | 3863 | 1724 | 5587 | 3175 | 436 | 1262 | 195 | 420 | 35 | 0 | 64 | 0 | 0 | 97.97
5:00 | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 349 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 260 | 320 | 200 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 66 | 110 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 145 | 34 | 40 | 0 | 128 | 0 | 0 | 7 | 260 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 60 | 415 | 0 | 0 | 55 | 0 | 0 |  | 437 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 180 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 0 |  | 3829 | 1751 | 5580 | 3219 | 437 | 1208 | 195 | 420 | 35 | 0 | 66 | 0 | 0 | 97.97
6:00 | 0 | 0 | 279 | 0 | 270 | 0 | 0 | 354 | 355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 42 | 0 | 0 | 0 | 260 | 355 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 68 | 110 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 145 | 34 | 40 | 0 | 128 | 0 | 0 | 7 | 275 | 0 | 5 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 10 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 100 | 415 | 0 | 0 | 55 | 0 | 0 |  | 436 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 192 | 0 | 377 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 0 |  | 4057 | 1804 | 5861 | 3282 | 436 | 1281 | 339 | 420 | 35 | 0 | 68 | 0 | 0 | 97.97
7:00 | 0 | 0 | 278 | 0 | 270 | 0 | 0 | 361 | 355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 42 | 0 | 0 | 0 | 265 | 355 | 174 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 66 | 107 | 0 | 22 | 0 | 30 | 20 | 11 | 5 | 0 | 143 | 33 | 71 | 0 | 128 | 0 | 0 | 7 | 300 | 0 | 5 | 0 | 34 | 0 | 0 | 58 | 0 | 0 | 1 | 32 | 37 | 66 | 0 | 0 | 0 | 0 | 0 | 66 | 54 | 0 | 0 | 0 | 100 | 350 | 11 | 1 | 55 | 0 | 0 |  | 436 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 200 | 0 | 378 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 290 | 36 | 0 | 0 |  | 4243 | 1883 | 6126 | 3234 | 436 | 1336 | 577 | 440 | 35 | 0 | 66 | 2 | 0 | 97.96
8:00 | 0 | 0 | 278 | 0 | 300 | 0 | 0 | 374 | 325 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 8 | 0 | 0 | 0 | 280 | 355 | 154 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 74 | 110 | 0 | 22 | 1 | 30 | 20 | 11 | 5 | 0 | 144 | 20 | 70 | 0 | 128 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 94 | 0 | 0 | 96 | 0 | 0 | 4 | 90 | 68 | 107 | 0 | 0 | 0 | 0 | 1 | 121 | 54 | 0 | 0 | 5 | 100 | 280 | 34 | 7 | 55 | 0 | 0 |  | 530 | 0 | 255 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 198 | 0 | 322 | 0 | 0 | 48 | 0 | 0 | 0 | 1 | 20 | 360 | 39 | 0 | 0 |  | 4442 | 2083 | 6525 | 3177 | 530 | 1190 | 995 | 510 | 35 | 0 | 74 | 14 | 0 | 97.96
9:00 | 0 | 0 | 273 | 0 | 270 | 0 | 0 | 350 | 288 |  | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 8 | 0 | 0 | 0 | 280 | 350 | 147 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 78 | 109 | 13 | 22 | 1 | 30 | 20 | 11 | 5 | 0 | 146 | 20 | 50 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 145 | 0 | 0 | 195 | 0 | 22 | 11 | 90 | 68 | 128 | 0 | 8 | 4 | 0 | 1 | 123 | 49 | 0 | 0 | 35 | 100 | 210 | 34 | 24 | 55 | 0 | 0 |  | 530 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 198 | 0 | 284 | 53 | 0 | 108 | 0 | 0 | 0 | 0 | 35 | 430 | 27 | 0 | 0 |  | 4629 | 2329 | 6958 | 3042 | 530 | 1121 | 1535 | 580 | 35 | 0 | 78 | 37 | 0 | 97.96
10:00 | 0 | 0 | 313 | 0 | 260 | 0 | 0 | 349 | 259 |  | 0 | 0 | 0 | 16 | 40 | 4 | 0 | 0 | 0 | 28 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 8 | 0 | 0 | 0 | 275 | 260 | 196 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 76 | 106 | 24 | 22 | 1 | 30 | 20 | 14 | 5 | 0 | 145 | 20 | 50 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 145 | 0 | 0 | 200 | 0 | 60 | 15 | 90 | 68 | 133 | 0 | 0 | 35 | 0 | 0 | 125 | 54 | 0 | 0 | 35 | 100 | 142 | 34 | 35 | 55 | 0 | 0 |  | 578 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 10 | 198 | 0 | 288 | 53 | 0 | 113 | 0 | 0 | 0 | 1 | 35 | 400 | 7 | 0 | 0 |  | 4668 | 2356 | 7024 | 2943 | 578 | 1098 | 1692 | 550 | 35 | 0 | 76 | 52 | 0 | 97.96
11:00 | 0 | 0 | 311 | 0 | 240 | 0 | 0 | 356 | 265 |  | 0 | 0 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 28 | 17 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 9 | 0 | 0 | 0 | 275 | 260 | 227 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 82 | 102 | 8 | 22 | 2 | 30 | 20 | 14 | 5 | 0 | 145 | 20 | 50 | 0 | 129 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 115 | 0 | 0 | 120 | 0 | 60 | 17 | 60 | 68 | 135 | 0 | 0 | 35 | 0 | 0 | 125 | 54 | 0 | 0 | 0 | 100 | 250 | 22 | 43 | 55 | 0 | 0 |  | 578 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 10 | 197 | 0 | 388 | 53 | 0 | 90 | 0 | 0 | 0 | 4 | 0 | 390 | 35 | 0 | 0 |  | 4586 | 2331 | 6917 | 3020 | 578 | 1179 | 1417 | 540 | 35 | 0 | 82 | 66 | 0 | 97.95
12:00 | 0 | 0 | 330 | 0 | 225 | 0 | 0 | 357 | 327 |  | 0 | 0 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 10 | 0 | 0 | 0 | 340 | 270 | 199 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 0 | 19 | 82 | 102 | 8 | 22 | 2 | 30 | 20 | 14 | 5 | 0 | 144 | 20 | 50 | 0 | 129 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 95 | 0 | 0 | 160 | 0 | 77 | 17 | 60 | 68 | 107 | 0 | 0 | 40 | 0 | 3 | 125 | 54 | 0 | 0 | 0 | 100 | 410 | 0 | 43 | 55 | 0 | 0 |  | 579 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 192 | 0 | 351 | 53 | 0 | 50 | 0 | 0 | 0 | 4 | 0 | 410 | 35 | 0 | 0 |  | 4886 | 2297 | 7183 | 3287 | 579 | 1202 | 1369 | 560 | 35 | 0 | 82 | 69 | 0 | 97.95
13:00 | 0 | 0 | 325 | 0 | 225 | 0 | 0 | 371 | 330 |  | 0 | 0 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 26 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 12 | 0 | 0 | 0 | 385 | 265 | 158 | 8 | 47 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 88 | 102 | 8 | 22 | 2 | 30 | 20 | 14 | 5 | 0 | 144 | 20 | 50 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 95 | 0 | 0 | 168 | 0 | 106 | 16 | 60 | 76 | 100 | 0 | 0 | 54 | 0 | 3 | 158 | 35 | 0 | 0 | 0 | 100 | 420 | 0 | 41 | 55 | 0 | 0 |  | 578 | 0 | 245 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 189 | 0 | 356 | 78 | 0 | 60 | 0 | 0 | 0 | 5 | 0 | 440 | 35 | 0 | 17 |  | 5036 | 2377 | 7413 | 3329 | 578 | 1213 | 1513 | 590 | 35 | 0 | 88 | 67 | 7413 | 97.95
14:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 359 | 255 |  | 0 | 0 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 20 | 0 | 72 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 29 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 10 | 18 | 11 | 0 | 0 | 0 | 0 | 305 | 183 | 8 | 47 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 88 | 102 | 8 | 22 | 2 | 30 | 20 | 5 | 5 | 0 | 144 | 31 | 40 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 95 | 154 | 0 | 190 | 0 | 111 | 14 | 78 | 50 | 70 | 0 | 0 | 105 | 0 | 3 | 175 | 35 | 0 | 0 | 18 | 100 | 420 | 0 | 29 | 55 | 0 | 0 |  | 578 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 10 | 182 | 0 | 390 | 105 | 0 | 83 | 0 | 0 | 0 | 4 | 10 | 430 | 0 | 0 | 54 |  | 4578 | 2467 | 7045 | 2697 | 578 | 1118 | 1897 | 580 | 35 | 0 | 88 | 52 | 0 | 97.95
15:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 351 | 244 |  | 0 | 0 | 0 | 14 | 48 | 15 | 0 | 0 | 0 | 20 | 50 | 0 | 77 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 22 | 19 | 5 | 0 | 0 | 0 | 0 | 285 | 183 | 8 | 47 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 92 | 103 | 8 | 22 | 1 | 30 | 20 | 5 | 5 | 0 | 144 | 20 | 40 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 168 | 0 | 0 | 160 | 0 | 118 | 11 | 78 | 50 | 10 | 0 | 0 | 105 | 0 | 2 | 198 | 36 | 0 | 0 | 18 | 100 | 420 | 24 | 18 | 55 | 0 | 0 |  | 579 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 178 | 0 | 374 | 53 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 430 | 0 | 0 | 54 |  | 4584 | 2345 | 6929 | 2760 | 579 | 1084 | 1764 | 580 | 35 | 0 | 92 | 35 | 0 | 97.94
16:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 352 | 275 |  | 0 | 0 | 0 | 16 | 48 | 15 | 0 | 0 | 0 | 16 | 50 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 25 | 32 | 17 | 8 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 19 | 7 | 0 | 0 | 0 | 0 | 285 | 183 | 36 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 88 | 102 | 8 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 143 | 20 | 40 | 0 | 131 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 118 | 6 | 50 | 50 | 10 | 0 | 0 | 105 | 0 | 1 | 198 | 49 | 0 | 0 | 18 | 100 | 420 | 17 | 7 | 55 | 0 | 0 |  | 578 | 0 | 235 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 175 | 0 | 393 | 17 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 400 | 0 | 0 | 54 |  | 4601 | 2179 | 6780 | 2744 | 578 | 1162 | 1607 | 550 | 35 | 0 | 88 | 16 | 0 | 97.94
17:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 364 | 324 |  | 0 | 0 | 0 | 16 | 48 | 15 | 0 | 0 | 0 | 7 | 50 | 0 | 50 | 0 | 0 | 0 | 17 | 13 | 35 | 19 | 25 | 32 | 17 | 16 | 5 | 0 | 0 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 19 | 13 | 0 | 0 | 0 | 0 | 305 | 197 | 36 | 70 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 90 | 103 | 8 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 144 | 20 | 40 | 0 | 131 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 118 | 0 | 50 | 50 | 13 | 0 | 0 | 105 | 0 | 0 | 199 | 54 | 0 | 0 | 18 | 100 | 418 | 17 | 0 | 55 | 0 | 0 |  | 578 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 173 | 0 | 399 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 400 | 0 | 0 | 54 |  | 4739 | 2168 | 6907 | 2814 | 578 | 1227 | 1612 | 551 | 35 | 0 | 90 | 0 | 0 | 97.94
18:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 385 | 334 |  | 0 | 0 | 0 | 28 | 55 | 15 | 0 | 0 | 0 | 36 | 50 | 115 | 75 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 20 | 25 | 16 | 20 | 0 | 0 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 25 | 0 | 82 | 10 | 14 | 37 | 19 | 15 | 0 | 0 | 0 | 0 | 335 | 201 | 36 | 91 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 108 | 103 | 40 | 20 | 0 | 30 | 20 | 5 | 5 | 0 | 146 | 32 | 71 | 0 | 163 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 273 | 0 | 0 | 182 | 0 | 124 | 0 | 100 | 50 | 60 | 0 | 8 | 105 | 0 | 0 | 198 | 54 | 0 | 0 | 18 | 100 | 419 | 41 | 0 | 55 | 0 | 0 |  | 722 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 169 | 0 | 423 | 53 | 0 | 82 | 0 | 35 | 0 | 0 | 90 | 420 | 0 | 0 | 54 |  | 5540 | 2711 | 8251 | 2922 | 722 | 1329 | 2297 | 571 | 35 | 267 | 108 | 0 | 0 | 97.94
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 373 | 354 |  | 0 | 0 | 0 | 75 | 70 | 15 | 0 | 0 | 0 | 100 | 50 | 115 | 85 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 32 | 25 | 16 | 24 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 10 | 51 | 50 | 19 | 25 | 0 | 0 | 0 | 0 | 310 | 183 | 36 | 80 | 26 | 49 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 106 | 107 | 40 | 20 | 0 | 30 | 20 | 5 | 5 | 0 | 143 | 33 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 291 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 50 | 102 | 0 | 8 | 105 | 0 | 0 | 198 | 54 | 0 | 0 | 18 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 817 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 164 | 0 | 370 | 84 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 5890 | 3031 | 8921 | 2868 | 817 | 1353 | 2781 | 650 | 35 | 311 | 106 | 0 | 0 | 97.93
19:30 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 373 | 354 |  | 0 | 0 | 0 | 75 | 80 | 15 | 0 | 0 | 0 | 100 | 50 | 84 | 85 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 32 | 20 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 53 | 0 | 12 | 50 | 19 | 27 | 0 | 0 | 0 | 0 | 335 | 196 | 36 | 89 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 106 | 106 | 40 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 145 | 32 | 71 | 0 | 163 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 50 | 102 | 0 | 8 | 53 | 0 | 0 | 199 | 54 | 0 | 0 | 18 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 817 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 159 | 0 | 415 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 5779 | 3086 | 8865 | 2914 | 817 | 1415 | 2680 | 650 | 35 | 248 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 355 | 359 |  | 0 | 0 | 0 | 75 | 80 | 15 | 0 | 0 | 0 | 85 | 50 | 84 | 87 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 61 | 0 | 15 | 50 | 19 | 30 | 0 | 0 | 0 | 0 | 310 | 182 | 36 | 90 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 104 | 107 | 40 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 145 | 32 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 124 | 0 | 100 | 50 | 102 | 0 | 8 | 53 | 0 | 0 | 199 | 54 | 0 | 0 | 18 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 817 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 158 | 0 | 399 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 5716 | 3070 | 8786 | 2859 | 817 | 1401 | 2665 | 650 | 35 | 255 | 104 | 0 | 0 | 97.93
21:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 359 | 353 |  | 0 | 0 | 0 | 75 | 80 | 15 | 0 | 0 | 0 | 7 | 50 | 48 | 86 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 17 | 0 | 0 | 50 | 19 | 35 | 0 | 0 | 0 | 0 | 310 | 183 | 36 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 98 | 107 | 40 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 145 | 33 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 110 | 0 | 100 | 50 | 102 | 0 | 0 | 17 | 0 | 0 | 199 | 54 | 0 | 0 | 18 | 100 | 427 | 90 | 0 | 55 | 0 | 0 |  | 818 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 156 | 0 | 402 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 5457 | 3068 | 8525 | 2861 | 818 | 1408 | 2480 | 650 | 35 | 175 | 98 | 0 | 0 | 97.93
22:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 349 | 353 |  | 0 | 0 | 0 | 41 | 48 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 41 | 0 | 0 | 0 | 0 | 310 | 182 | 36 | 81 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 94 | 108 | 0 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 147 | 33 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 283 | 0 | 0 | 160 | 0 | 35 | 0 | 50 | 50 | 102 | 0 | 0 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 18 | 100 | 427 | 90 | 0 | 55 | 0 | 0 |  | 818 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 156 | 0 | 378 | 90 | 0 | 113 | 0 | 49 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 5039 | 2911 | 7950 | 2845 | 818 | 1388 | 2062 | 650 | 35 | 58 | 94 | 0 | 0 | 97.93
23:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 349 | 306 |  | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 42 | 20 | 0 | 0 | 0 | 285 | 183 | 36 | 91 | 26 | 57 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 88 | 109 | 0 | 22 | 0 | 30 | 20 | 5 | 5 | 0 | 144 | 33 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 195 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 50 | 102 | 0 | 0 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 18 | 100 | 426 | 90 | 0 | 55 | 0 | 0 |  | 817 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 157 | 0 | 338 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 4612 | 2655 | 7267 | 2854 | 817 | 1279 | 1544 | 650 | 35 | 0 | 88 | 0 | 0 | 97.92
24:00 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 349 | 290 |  | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 19 | 42 | 40 | 0 | 0 | 0 | 280 | 181 | 36 | 82 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 80 | 107 | 0 | 22 | 0 | 30 | 20 | 7 | 5 | 0 | 145 | 20 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 130 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 50 | 102 | 0 | 0 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 0 | 100 | 400 | 70 | 0 | 55 | 0 | 0 |  | 628 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 162 | 0 | 305 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 35 | 450 | 0 | 0 | 47 |  | 4438 | 2323 | 6761 | 2825 | 628 | 1249 | 1344 | 600 | 35 | 0 | 80 | 0 | 0 | 97.92
KWH | 0 | 0 | 3936000 | 0 | 6932845 | 0 | 0 | 8759392 | 7416000 |  | 0 | 0 | 0 | 391680 | 833520 | 225129 | 0 | 0 | 0 | 361920 | 588384 | 306720 | 1014385 | 0 | 0 | 0 | 371520 | 106892 | 525374 | 447480 | 600000 | 705600 | 504700 | 581700 | 59424 | 0 | 0 | 848000 | 0 | 0 | 85937 | 0 | 0 | 0 | 0 |  | 209760 | 0 | 218162 | 15720 | 83520 | 613920 | 436848 | 591360 | 49430 | 0 | 0 | 3946700 | 7538000 | 4479000 | 434909 | 882700 | 298944 | 452160 | 0 | 1211642 | 0 | 0 | 0 | 428832 | 257580 | 808600 | 498530 | 2031360 | 2502440 | 248640 | 495468 | 11150 | 716000 | 475440 | 217200 | 230184 | 0 | 3281000 | 664896 | 1431360 | 0 | 3278160 | 0 | 0 | 55800 | 6839000 | 0 | 174500 | 0 | 3301962 | 100193 | 0 | 2988000 | 0 | 1415950 | 110025 | 1159680 | 1115520 | 2085890 | 0 | 40800 | 930168 | 0 | 14726 | 3088691 | 1227660 | 0 | 0 | 525840 | 2215680 | 9151100 | 952320 | 240890 | 1324800 | 0 | 0 |  | 14273131 | 0 | 5670720 | 0 | 1547520 | 0 | 0 | 0 | 0 | 24704 | 280875 | 0 | 401100 | 0 | 0 | 0 | 0 | 2016 | 0 | 410940 | 0 | 0 | 0 | 12960 | 0 | 514080 | 0 | 215766 | 0 | 0 | 3676700 | 0 | 0 | 0 | 0 | 0 | 0 | 1054178 | 74880 | 4463336 | 0 | 8897200 | 989280 | 0 | 1725888 | 0 | 456960 | 0 | 28054 | 896064 | 10290600 | 444736 | 0 | 638400 |  | 113701412 | 56990088 | 170691500 | 73181707 | 14273131 | 30190909 | 34831706 | 13967300 | 848000 | 962542 | 2031360 | 404845 | 0
Fuel Cost | 0 | 0 | 5746560 | 0 | 7695457.95 | 0 | 0 | 8846985.92 | 7638480 |  | 0 | 0 | 0 | 2972851.2 | 5742952.8 | 1904591.34 | 0 | 0 | 0 | 2725257.6 | 5366062.08 | 3018124.8 | 9352629.7 | 0 | 0 | 0 | 2712096 | 826275.16 | 5180187.64 | 335610 | 450000 | 0 | 0 | 0 | 574630.08 | 0 | 0 | 228960 | 0 | 0 | 798354.73 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2116171.4 | 150126 | 726624 | 4862246.4 | 550428.48 | 1756339.2 | 73156.4 | 0 | 0 | 2920558 | 7538000 | 4120680 | 561032.61 | 1015105 | 337806.72 | 633024 | 0 | 2071907.82 | 0 | 0 | 0 | 544616.64 | 193185 | 1415050 | 373897.5 | 15235200 | 2652586.4 | 2257651.2 | 629244.36 | 177731 | 1174240 | 760704 | 386616 | 359087.04 | 0 | 3412240 | 1309845.12 | 2733897.6 | 0 | 5671216.8 | 0 | 0 | 113832 | 6907390 | 0 | 132620 | 0 | 24962832.72 | 1701277.14 | 0 | 15537600 | 0 | 13932948 | 1286192.25 | 9451392 | 12103392 | 14705524.5 | 0 | 372096 | 8790087.6 | 0 | 0 | 23350503.96 | 10692918.6 | 0 | 0 | 4506448.8 | 14756428.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 82213234.56 | 0 | 5954256 | 0 | 12163507.2 | 0 | 0 | 0 | 0 | 258897.92 | 2926717.5 | 0 | 621705 | 0 | 0 | 0 | 0 | 19837.44 | 0 | 3636819 | 0 | 0 | 0 | 125582.4 | 0 | 987033.6 | 0 | 163334.862 | 0 | 0 | 19927714 | 0 | 0 | 0 | 0 | 0 | 0 | 1581267 | 1273708.8 | 5222103.12 | 0 | 8808228 | 10328083.2 | 0 | 16378677.12 | 0 | 3546009.6 | 0 | 309996.7 | 6621912.96 | 45175734 | 0 | 0 | 0 |  | 304139766.06 | 228244359.982 | 532384126.042 | 69239488.272 | 82213234.56 | 35159839.87 | 254380184.83 | 65103448 | 228960 | 9049850.56 | 15235200 | 1773919.95 | 0
Yesterday Day Peak | 0 | 0 | 330 | 0 | 225 | 0 | 0 | 357 | 327 |  | 0 | 0 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 32 | 17 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 10 | 0 | 0 | 0 | 340 | 270 | 199 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 0 | 19 | 82 | 102 | 8 | 22 | 2 | 30 | 20 | 14 | 5 | 0 | 144 | 20 | 50 | 0 | 129 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 95 | 0 | 0 | 160 | 0 | 77 | 17 | 60 | 68 | 107 | 0 | 0 | 40 | 0 | 3 | 125 | 54 | 0 | 0 | 0 | 100 | 410 | 0 | 43 | 55 | 0 | 0 |  | 579 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 192 | 0 | 351 | 53 | 0 | 50 | 0 | 0 | 0 | 4 | 0 | 410 | 35 | 0 | 0 |  | 7183 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 373 | 354 | 0 | 0 | 0 | 0 | 75 | 70 | 15 | 0 | 0 | 0 | 100 | 50 | 115 | 85 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 32 | 25 | 16 | 24 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 10 | 51 | 50 | 19 | 25 | 0 | 0 | 0 | 0 | 310 | 183 | 36 | 80 | 26 | 49 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 106 | 107 | 40 | 20 | 0 | 30 | 20 | 5 | 5 | 0 | 143 | 33 | 71 | 0 | 163 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 291 | 0 | 0 | 200 | 0 | 123 | 0 | 100 | 50 | 102 | 0 | 8 | 105 | 0 | 0 | 198 | 54 | 0 | 0 | 18 | 100 | 425 | 90 | 0 | 55 | 0 | 0 |  | 817 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 164 | 0 | 370 | 84 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 8921 | EvPeak
Forecast for Evening | 0 | 0 | 300 | 0 | 330 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 20 | 140 |  | 0 | 0 | 360 | 200 | 36 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 21 | 147 | 110 | 95 | 22 | 0 | 50 | 30 | 22 | 20 | 0 | 0 | 33 | 72 | 0 | 200 | 20 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 124 | 100 |  | 833 | 16 | 250 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 36 |  | 0
Forecast for Day | 0 | 0 | 180 | 0 | 330 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 20 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 19 | 10 | 140 |  | 0 | 0 | 360 | 200 | 36 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 135 | 110 | 95 | 22 | 1.6 | 50 | 20 | 11 | 20 | 0 | 0 | 33 | 72 | 0 | 100 | 20 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 124 | 100 |  | 592 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 36 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 370 | 275 | 0 | 0 | 0 | 0 | 55 | 48 | 15 | 0 | 0 | 0 | 7 | 32 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 25 | 24 | 20 |  | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 19 | 14 | 140 | 0 | 0 | 0 | 330 | 205 | 36 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 16 | 76 | 107 | 8 | 22 | 1 | 30 | 20 | 8 | 5 | 0 | 0 | 20 | 30 | 0 | 136 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 278 | 0 | 0 | 84 | 0 | 58 | 6 | 50 | 50 | 102 | 0 | 0 | 17 | 0 | 1 | 160 | 54 | 0 | 0 | 17 | 100 | 427 | 72 | 8 | 55 | 0 | 0 | 0 | 531 | 0 | 265 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 199 | 0 | 335 | 35 | 0 | 35 | 0 | 50 | 0 | 1 | 35 | 310 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5580 | 5:00
| Highest Generation |  | 8921 | 19:00
| Day Peak Generation |  | 7183 | 12:00
| Evening Peak Generation |  | 8921 | 19:00
| HVDC Max Flow |  | 818 | 21:00
| HVDC EvPeak Flow |  | 817 | 19:00
| Load factor L.F |  | 79.72%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7183 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5551 | MW
Evening Peak Generation : |  | 8921 | MW Hour : | 19:00 | Available Max Generation : |  | 13621 | MW
E.P. Demand (at gen end) : |  | 8921 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 8921 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4421 | MW
Total Gen. (MKWH) : |  | 170.6915 | System Load Factor : | 79.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -113 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-05
Actual : | 97.9 | Ft.(MSL) , | Rule curve : | 102.43 | Ft.( MSL )
Gas Consumed : | Total = | 751.92 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104399328.142
: |  | Coal : | 65103448 | Oil : | 263430035.39 | Total : | 432932811.532
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3264.9427 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1105.3094 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 989.4383 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 893.7277 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 807.8215 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 651.8709 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 370.8663 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 168.0079 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 502.7247 |  |  | 0 | 0%
Total | 0 |  | 8754.7094 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Baroaulia-Hathazari 132 kV Ckt-1 was under shut down from 09:03 to 16:15 for A/M.
b) Aminbazar 230/132 kV T03 transformer was under shut down from 09:25 to 18:45 for A/M.
c) Feni-PHP 132 kV Ckt was under shut down from 08:55 to 17:27 for A/M.
d) Baroirhat-PHP 132 kV Ckt was under shut down from 08:55 to 17:27 for A/M.
e) Rampura-Gulshan 132 kV Ckt-1 was under shut down from 08:28 to 16:11 for A/M.
f) Baroaulia-KSRM 132 kV Ckt was under shut down from 09:58 to 17:29 for C/M.
g) Ramganj-Chowmuhani 132 kV Ckt-1 was under shut down from 09:17 to 18:10 for D/W.
h) Mirpur-Aminbazar 132 kV Ckt-2 was under shut down from 08:44 to 19:33 for C/M.
i) Bheramara HVDC 400 kV 10CF15 filter was shutdown at 09:48.
j) Matarbari 132/33 kV T1 transformer was under shut down from 10:22 to 17:25 for A/M.
k) B.Baria-Shahjibazar 132 kV Ckt-1 was under shut down from 09:52 to 17:32 for A/M.
l) Kaliakoir 400/132 kV T01 transformer was under shut down from 10:36 to 17:08 for A/M.
m) Kodda 132 kV main Bus-2 was under shutdown from 08:08 to 16:28 for D/W.
n) Kabirpur 132/33 kV T1 transformer was under shut down from 08:51 to 17:29 for D/W.
o) Ashuganj-Kishoreganj 132 kV Ckt-1 was under shut down from 09:06 to 16:51 for D/W.
p) Madanganj 132 kV Reserve Bus was under shutdown from 09:00 to 20:46 for C/M.
q) Hasnabad-Kamrangichar 132 kV Ckt was under shut down from 08:55 to 11:47 for C/M.
r) HVDC-Rajshahi (N) 230 kV Ckt-1 was under shut down from 09:28 to 20:28 for D/W.
s) Rajshahi 230/132 kV ATR-1 transformer was under shut down from 12:18 to 20:32 for D/W.
t) Kabirpur-Kaliakoir 132 kV Ckt-1 was shut down at 11:48 for Safety.
u) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 09:08 to 14:33 for A/M.
v) Bottail-Bheramara 132 kV Ckt-1 was under shut down from 09:17 to 15:17 for A/M.
w) Kaptai-Chandraghona 132 kV Ckt-2 was under shut down from 09:33 to 17:58 for C/M.
x) Bogra-Mahasthangarh 132 kV Ckt-1 was under shut down from 09:08 to 16:21 for A/M.
y) Rajshahi(Old)-Rajshahi(New) 132 kV Ckt was under shut down from 13:10 to 19:50 for C/M.
z) Mahasthangarh 132/33 kV T1 transformer was under shut down from 08:53 to 11:51 for A/M.
aa) Mahasthangarh 132 kV Bus-1 was under shutdown from 08:53 to 11:50 for A/M.
ab) Mahasthangarh 132/33 kV T2 transformer was under shut down from 12:03 to 16:09 for A/M.
ac) Mahasthangarh 132 kV Bus-2 was under shutdown from 12:07 to 16:04 for A/M.
ad) Barisal(N)-Madaripur 132 kV Ckt-2 was under shut down from 08:39 to 15:26 for A/M.
ae) Bheramara-Kustia 132 kV Ckt-1 was under shut down from 09:17 to 15:17 for A/M.
af) Pabna 132/33 kV, 50/75 MVA T2 transformer was under shut down from 08:34 to 16:38 for A/M.
ag) Gopalganj old-Madhumati P/S 132 kV Ckt was under shut down from 08:04 to 16:27 for C/M.
ah) Gopalganj 132/33 kV,25/41 MVA T2 transformer & 33 kV T2 GCB was shut down at 09:15 for D/W.
ai) Purbasadipur-Thakurgaon 132 kV Ckt-1 was shut down at 10:10 for C/M.
aj) Barishal(South) 132/33 kV T1 transformer was under shut down from 10:05 to 10:32 due to gas leakage.
ak) Gopalganj(Old)-Gopalganj PS 132 kV Ckt was under shut down from 10:40 to 14:17 due to R/H.
al) Bheramara 230 kV-Bheramara GT 132 kV Ckt was shut down at 11:34 for C/M.
am) Rajshahi old 132/33 kV T2 transformer CB was under shut down from 09:35 to 11:55 for C/M.
an) Rangpur-Confidence 132 kV Ckt-1 was under shut down from 08:02 to 18:02 for Breaker & DS replacement.
ao) Ashuganj North tripped at 13:30 with 380 MW load.
ap) Ghorashal Unit-4 tripped at 13:34 with 325 MW load.
aq) Jamalpur-Mymensingh 132 kV Ckt-1 was under shut down from 14:22 to 17:43 for C/M.
ar) Ashuganj Unit-3 was synchronized at 22:04.
as) Shahjibazar 330 MW was shutdown at 06:48(05/01/2021).
at) Hasnabad-APR 230 kV Ckt was shut down at 07:20(05/01/2021) for A/M.
au) Joydevpur-Ghorashal 132 kV Ckt-1 was shut down at 06:44(05/01/2021) for A/M.
ag) Shahmirpur-Sikalbaha 132 kV Ckt-2 was shut down at 07:30(30/12/2020) for D/W.
ah) Goalpara-Bagerhat 132 kV Ckt-1 was shut down at 07:48(30/12/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 3936000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 6932845
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 373 | 8759392 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 354 | 7416000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 75 | 391680 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 70 | 833520 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 225129 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1014385 | High Voltage.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 447480
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 361920
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 588384 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 371520 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 306720 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 106892 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 525374 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1305600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 504700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 581700 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 24 | 59424 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 291 | 3301962
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 100193 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 123 | 1415950 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 930168
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 952320 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 55 | 1324800 | Low demand
| Dhaka area Total |  |  |  | 6057 | 2459 | 42694058
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 85937
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110025
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 613920
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 848000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 218162 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 15720 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1159680
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436848 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 591360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 83520 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 14726
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 198 | 3088691 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1227660
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2215680
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | RRT
| Chattogram area Total |  |  |  | 2266 | 752 | 10709929
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 49430 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4479000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 3946700 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7538000
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 298944 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 452160 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 434909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1211642
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 102 | 2085890
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 882700 | Under maint.
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 50 | 1115520 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 428832 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2031360
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 808600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 498530
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 525840 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1094 | 27045637
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2502440 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 495468
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 40 | 248640 | High Voltage.
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11150
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2988000 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 40800 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 240890
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 209760
| Mymensingh Area Total |  |  |  | 709 | 399 | 6737148
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 475440 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3281000 | Gas shortage & GT-2 under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 217200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 5 | 230184
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 174500
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 664896 | Unit-9 under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1431360 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 3278160
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6839000 | Gas shortage
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 55800 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 425 | 9151100 | On test
| Sylhet Area Total |  |  |  | 1988 | 1186 | 26514640
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 817 | 14273131
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1547520 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 6 | 24704 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 220 | 5670720 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 280875 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 74880 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 84 | 989280 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1226 | 22861110
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 401100 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 64 | 1054178 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 10290600 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 444736 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 54 | 638400 | On test.
| Barisal Area Total |  |  |  | 1676 | 639 | 12829014
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 2016 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 164 | 4463336 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8897200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 514080
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 215766
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 12960 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 105 | 410940
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1725888
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 896064
| Rajshahi Area Total |  |  |  | 2183 | 906 | 17138250
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676700
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 456960
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28054
| Rangpur Area Total |  |  |  | 605 | 260 | 4161714
| Total |  |  |  | 20748 | 8921 | 170691500
| Eastern Grid Total |  |  |  | 14000 | 5890 | 113701412
| Western Grid Total |  |  |  | 6748 | 3031 | 56990088
| National Grid Total |  |  |  | 20748 | 8921 | 170691500
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-04
| (a) ENTIRE EASTERN GRID : |  | 5674 | MW | (b) ENTIRE WESTERN GRID : |  | 2804 | MW
| i) Dhaka area |  | 3027 | MW | i) Khulna area |  | 1085 | MW
| ii) Chittagong area |  | 882 | MW | ii) Rajshahi area |  | 885 | MW
| iii) Comilla area |  | 717 | MW | iii) Barisal area |  | 236 | MW
| iv) Mymensingh area |  | 737 | MW | iv) Rangpur area |  | 598 | MW
| v) Sylhet area |  | 311 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8478 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 96 | 18:00 | Jamalpur | 86 | 18:30 | Benapol | 38 | 19:00
| Munsiganj | 85 | 19:00 | Sherpur | 100 | 19:00 | Jhenida | 86 | 19:00
| Sonargaon | 57 | 10:00 | Srimongal | 26 | 18:30 | Bottail | 80 | 18:00
| Shyampur | 162 | 12:00 | Shahjibazar | 85 | 19:30 | G.K Project | 46 | 19:30
| Bhulta | 154 | 23:00 | Fenchuganj | 26 | 19:30 | Faridpur | 132 | 19:00
| Madanganj | 42 | 11:00 | Kulawara | 29 | 18:00 | Madaripur | 62 | 19:30
| Shitalakhya | 92 | 10:00 | Sylhet | 78 | 18:00 | Sariatpur | 40 | 20:00
| Rahim steel | 18 | 19:00 | Chatak | 21 | 18:00 | Gopalganj | 61 | 18:30
| Matuail | 45 | 10:00 | Sunamganj | 28 | 19:00 | Bagerhat | 80 | 18:30
| Ghorasal | 68 | 6:00 | Biani Bazar | 34 | 19:00 | Mongla | 38 | 12:00
| Narsingdi | 115 | 20:00 | Comilla (S) | 108 | 18:00 | Satkhira | 78 | 18:30
| Haripur (SBU) | 103 | 20:00 | Comilla(N) | 63 | 18:00 | Gallamari | 20 | 13:00
| Ullon | 40 | 18:00 | Chandpur | 62 | 19:30 | Magura | 39 | 19:00
| Hasnabad | 125 | 18:30 | Feni | 78 | 20:00 | Norail | 25 | 18:30
| Magbazar | 67 | 13:00 | Chowmuhani | 114 | 20:00 | Chuadanga | 64 | 18:30
| Maniknagar | 68 | 13:00 | Ashuganj | 38 | 19:30 | Barisal(N) | 29 | 20:00
| Bangabhaban | 15 | 15:00 | Daudkandi | 88 | 20:00 | Barisal (S) | 70 | 20:00
| Narinda | 68 | 13:00 | B.Baria | 96 | 19:30 | Patuakhali | 84 | 19:30
| Dhanmondi | 93 | 13:00 | Ramganj | 66 | 19:30 | Bhandaria | 40 | 18:30
| Lalbag | 68 | 13:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 20:00
| Madartek | 44 | 20:00 | PHP | 2 | 22:00 | Ishurdi | 46 | 18:30
| Dhaka University |  |  | Madunaghat | 48 | 20:00 | Ruppur Paromanobik | 2 | 18:00
| Aftabnagar | 131 | 1 | Hathazari | 64 | 0.75 | Natore | 83 | 0.83333
| Fatullah | 42 | 10:00 | Khulshi | 166 | 12:00 | Bogra | 115 | 19:00
| Mirpur | 70 | 19:00 | Halishahar | 93 | 18:00 | Noagaon | 75 | 18:30
| Kalyanpur | 60 | 19:00 | Baraulia | 72 | 1:00 | Rajshahi | 98 | 20:00
| Gulshan | 78 | 13:00 | Sikalbaha | 21 | 18:00 | Rajshahi New | 9 | 18:00
| Uttara | 66 | 13:00 | Dohazari | 56 | 20:00 | C.Nawabganj | 51 | 19:30
| Uttara New | 24 | 18:00 | Cox'sbazar | 77 | 18:30 | Amnura | 28 | 20:00
| Kamrangirchar | 69 | 18:30 | Chandraghona | 20 | 18:30 | Pabna | 79 | 18:30
| Savar | 112 | 18:30 | Kaptai | 3.6 | 18:00 | Shahjadpur | 78 | 19:00
| Bhasantec | 100 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 65 | 19:00
| Agargaon | 44 | 18:00 | Bakulia | 70 | 18:30 | Niyamatpur | 61 | 19:00
| Satmosjid | 60 | 0.75 | Julda | 19 | 0.5 | Joypurhat | 46 | 0.79167
| Tongi | 52 | 19:00 | TK chemical | 19.5 | 19:00 | Sherpur(Bogura) | 36 | 18:00
| Kabirpur | 178 | 16:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 89 | 18:00 | Shahmirpur | 18 | 8:00 | Rangpur | 106 | 18:30
| Manikganj | 44 | 20:00 | Khagrachhari | 20 | 8:00 | Lalmonirhat | 47 | 18:30
| Joydevpur | 101 | 18:00 | Matarbari | 29 | 18:30 | Saidpur | 80 | 18:00
| New Tongi | 97 | 18:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 80 | 18:30
| Kodda | 182 | 12:00 | Rangamati | 8 | 13:00 | Thakurgaon | 60 | 19:00
| Dhamrai | 72 | 19:00 | Abul Khair 230 | 136 | 6:00 | Palashbari | 85 | 19:30
| Rajendrapur | 78 | 18:30 | BSRM | 149 | 19:30 | Barapukuria | 41 | 20:00
| Valuka | 88 | 18:00 | GPH Ispat | 89 | 4:00 | Panchagar | 42 | 19:00
| Tangail | 135 | 19:00 | Goalpara | 15 | 19:00 | Joldhaka | 24 | 18:30
| Mymensing | 147 | 18:30 | Central s/s | 78 | 18:30 | Kurigram | 40 | 19:00
| Kishorganj | 94 | 19:00 | Noapara | 46 | 19:00
| Netrokona | 96 | 18:30 | Jessore | 89 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 8:00 | 408 | 15:00 | Kaliakoir | 396 | 0.125 | 378 | 0.45833
| Bheramara | 411 | 8:00 | 395 | 18:30 | Bhulta | 389 | 0.33333 | 366 | 0.625
| Ashuganj(N) | 397 | 1:00 | 372 | 14:00 | Gopalganj | 419 | 0.083333 | 395 | 0.77083
| Payra | 422 | 1:00 | 405 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 238 | 1:00 | Comilla (N) | 238 | 8:00 | 229 | 16:00
| Ishurdi | 243 | 4:00 | 230 | 18:00 | Hathazari | 224 | 7:00 | 215 | 2:00
| Ashuganj | 242 | 8:00 | 230 | 14:00 | Megnaghat | 231 | 10:00 | 221 | 13:00
| Serajganj | 235 | 1:00 | 230 | 11:00 | Fenchuganj | 246 | 1:00 | 238 | 19:00
| Baghabari | 248 | 4:00 | 238 | 16:00 | Siddhirganj | 233 | 2:00 | 220 | 24:00
| Barapukuria | 233 | 1:00 | 226 | 12:00 | Maniknagar | 232 | 2:00 | 222 | 14:00
| Bogra | 237 | 5:00 | 227 | 12:00 | Agargaon | 232 | 10:00 | 222 | 15:00
| Rajshahi | 236 | 2:00 | 220 | 12:00 | Barisal | 255 | 8:00 | 245 | 12:00
| Khulna South | 245 | 22:00 | 228 | 17:00 | AKSML | 226 | 8:00 | 216 | 5:00
| Rampura | 231 | 1:00 | 224 | 15:00 | BSRM | 229 | 19:00 | 218 | 5:00
| Haripur | 230 | 1:00 | 222 | 16:00 | Bibiyana | 247 | 5:00 | 237 | 12:00
| Hasnabad | 235 | 1:00 | 224 | 14:00 | Bhulta | 234 | 19:00 | 223 | 17:00
| Shyampur | 231 | 1:00 | 220 | 12:00 | Ashuganj (S) | 239 | 8:00 | 228 | 15:00
| Aminbazar | 232 | 1:00 | 223 | 15:00 | Kaliakoir | 229 | 7:00 | 221 | 14:00
| Tongi | 231 | 4:00 | 220 | 12:00 | GPH | 223 | 7:00 | 216 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 9:00 | 133 | 15:00 | Madanhat | 139 | 0.33333 | 131 | 0.041667
| Munsiganj | 140 | 19:00 | 134 | 12:00 | Hathazari | 137 | 0.77083 | 132 | 0.041667
| Sonargaon | 137 | 5:00 | 132 | 11:00 | Khulshi | 136 | 0.79167 | 128 | 0.041667
| Shyampur | 132 | 1:00 | 127 | 11:00 | Halishahar | 138 | 0.79167 | 130 | 0.041667
| Bhulta | 134 | 4:00 | 127 | 12:00 | Baraulia | 138 | 0.33333 | 130 | 0.041667
| Madanganj | 137 | 5:00 | 132 | 12:00 | Sikalbaha | 138 | 0.77083 | 131 | 0.041667
| Shitalakhya | 140 | 2:00 | 134 | 12:00 | Dohazari | 136 | 0.79167 | 129 | 0.5
| Rahim steal | 138 | 6:00 | 134 | 12:00 | Cox'sbazar | 129 | 0.375 | 122 | 0.041667
| Matuail | 139 | 9:00 | 133 | 15:00 | Chandraghona | 137 | 0.33333 | 130 | 0.16667
| Ghorasal | 140 | 1:00 | 135 | 15:00 | Kaptai | 137 | 0.91667 | 132 | 0.625
| Narsinghdi | 137 | 9:00 | 133 | 11:00 | A. Khaer Stl. | 135 | 0.041667 | 130 | 0.5
| Haripur (SBU) | 139 | 1:00 | 134 | 12:00 | Bakulia | 137 | 0.33333 | 129 | 0.5
| Ullon | 134 | 1:00 | 126 | 16:00 | Julda | 139 | 0.79167 | 130 | 0.041667
| Hasnabad | 141 | 24:00 | 135 | 12:00 | TK Chemical | 138 | 0.79167 | 131 | 0.5
| Magbazar | 135 | 2:00 | 126 | 14:00 | Modern Steel | 136 | 0.77083 | 130 | 0.5
| Maniknagar | 139 | 3:00 | 133 | 15:00 | Shahmirpur | 136 | 0.8125 | 131 | 0.5
| Bangabhaban | 139 | 3:00 | 133 | 15:00 | Khagrachhari | 136 | 0.33333 | 130 | 0.5
| Narinda | 139 | 3:00 | 133 | 15:00 | Matarbari | 132 | 0.375 | 125 | 0.041667
| Dhanmondi | 134 | 1:00 | 126 | 16:00 | Baroiar Hat | 139 | 0.33333 | 132 | 0.5
| Lalbag | 133 | 2:00 | 124 | 12:00 | Rangamati | 137 | 19:00 | 130 | 1:00
| Madartek | 134 | 2:00 | 125 | 15:00 | Goalpara S/S | 139 | 10:00 | 128 | 17:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 10:00 | 127 | 0.70833
| Aftabnagar | 134 | 1:00 | 126 | 21:00 | Noapara | 137 | 14:00 | 124 | 0.75
| Fatuiiah | 133 | 1:00 | 127 | 12:00 | Jessore | 135 | 1:00 | 123 | 0.75
| Mirpur | 136 | 2:00 | 127 | 12:00 | Benapol | 135 | 0.125 | 120 | 0.75
| Kalyanpur | 134 | 2:00 | 126 | 13:00 | Jhenida | 134 | 2:00 | 121 | 0.75
| Gulshan | 133 | 1:00 | 127 | 12:00 | Bottail | 136 | 0.041667 | 130 | 0.5
| Uttara | 133 | 1:00 | 125 | 12:00 | G.K Project | 141 | 0.125 | 135 | 0.75
| Uttara New | 138 | 1:00 | 123 | 12:00 | Faridpur | 139 | 0.041667 | 132 | 0.75
| Kamrangirchar | 141 | 1:00 | 132 | 11:00 | Madaripur | 144 | 0.20833 | 138 | 0.5
| Savar | 135 | 4:00 | 126 | 12:00 | Shariyatpur S/S | 143 | 4:00 | 135 | 0.75
| Bhasantec | 136 | 2:00 | 129 | 12:00 | Gopalganj | 146 | 0.25 | 134 | 0.75
| Agargaon | 137 | 2:00 | 130 | 12:00 | Bagerhat | 138 | 13:00 | 122 | 0.70833
| Satmosjid | 136 | 2:00 | 130 | 12:00 | Mongla | 136 | 10:00 | 122 | 0.75
| Tongi | 142 | 6:00 | 135 | 24:00 | Satkhira | 137 | 10:00 | 126 | 18:00
| Kabirpur | 136 | 5:00 | 126 | 11:00 | Gallamari | 138 | 0.58333 | 128 | 0.70833
| Basundhara | 134 | 2:00 | 126 | 16:00 | Magura | 135 | 2:00 | 123 | 0.75
| Manikganj | 144 | 18:00 | 135 | 22:00 | Norail | 134 | 0.125 | 122 | 0.75
| Joydevpur | 142 | 18:00 | 134 | 17:00 | Chuadanga | 133 | 3:00 | 116 | 0.75
| New Tongi | 139 | 19:30 | 133 | 22:00 | Barisal(N) | 144 | 10:00 | 137 | 20:00
| Kodda | 140 | 18:30 | 130 | 22:00 | Barisal (S) | 142 | 0.375 | 136 | 0.8125
| Dhamrai | 135 | 8:00 | 125 | 11:00 | Patuakhali(S) | 142 | 0.41667 | 137 | 0.79167
| Rajendrapur | 137 | 18:30 | 131 | 12:00 | Bhandaria | 141 | 0.41667 | 133 | 0.8125
| Valuka | 129 | 10:00 | 121 | 23:00 | Ishurdi | 140 | 3:00 | 134 | 12:00
| Tangail | 135 | 1:00 | 126 | 11:00 | Ruppur Paromanobik | 140 | 3:00 | 134 | 13:00
| Mymensing | 132 | 9:00 | 123 | 23:00 | Natore | 141 | 6:00 | 133 | 12:00
| Kishorganj | 132 | 4:00 | 125 | 11:00 | Bogra | 140 | 4:00 | 133 | 12:00
| Netrokona | 131 | 9:00 | 121 | 23:00 | Noagaon | 136 | 4:00 | 127 | 13:00
| Jamalpur | 140 | 9:00 | 123 | 5:00 | Rajshahi | 142 | 5:00 | 134 | 12:00
| Sherpur | 138 | 9:00 | 123 | 5:00 | Rajshahi New | 144 | 4:00 | 134 | 12:00
| Srimongal | 138 | 4:00 | 135 | 15:00 | C.Nawabganj | 142 | 4:00 | 132 | 12:00
| Shahjibazar | 135 | 9:00 | 132 | 15:00 | Amnura | 142 | 2:00 | 133 | 12:00
| Fenchuganj | 138 | 1:00 | 135 | 12:00 | Pabna | 139 | 4:00 | 133 | 12:00
| Khulawara | 137 | 1:00 | 134 | 17:00 | Shahjadpur | 143 | 3:00 | 138 | 8:00
| Sylhet | 135 | 1:00 | 134 | 11:00 | Serajganj | 137 | 2:00 | 132 | 12:00
| Chatak | 135 | 1:00 | 132 | 18:30 | Niyamatpur | 134 | 4:00 | 126 | 12:00
| Sunamganj | 136 | 6:00 | 132 | 18:00 | Joypurhat | 137 | 4:00 | 126 | 12:00
| Biani Bazar | 136 | 1:00 | 133 | 13:00 | Sherpur(Bogura) | 140 | 3:00 | 132 | 12:00
| Comilla(s) | 131 | 4:00 | 125 | 18:00 | Mohastangor | 138 | 4:00 | 128 | 12:00
| Comilla(n) | 143 | 8:00 | 138 | 14:00 | Rangpur | 131 | 2:00 | 120 | 18:00
| Chandpur | 143 | 7:00 | 141 | 19:00 | Lalmonirhat | 131 | 3:00 | 123 | 18:30
| Feni | 140 | 8:00 | 134 | 12:00 | Saidpur | 131 | 7:00 | 122 | 12:00
| Chowmuhani | 135 | 7:00 | 132 | 12:00 | Purbasadipur | 133 | 6:00 | 119 | 18:00
| Ashuganj | 137 | 10:00 | 134 | 17:00 | Thakurgaon | 131 | 2:00 | 115 | 18:00
| Daudkandi | 139 | 8:00 | 133 | 12:00 | Palashbari | 135 | 4:00 | 126 | 12:00
| B.Baria | 134 | 7:00 | 130 | 15:00 | Barapukuria | 133 | 1:00 | 126 | 12:00
| Ramganj | 138 | 9:00 | 134 | 13:00 | Panchagar | 131 | 4:00 | 113 | 18:00
| Chaddagram | 139 | 7:00 | 135 | 17:00 | Joldhaka | 130 | 4:00 | 119 | 18:00
| PHP | 140 | 8:00 | 133 | 5:00 | Kurigram | 131 | 0.25 | 120 | 0.75

## L-Curve
Date | 2021-01-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 317 | 4438 | 2323 | 6761 |  |  |  | QF-LDC-11
0:30 | 215 | 4377.5 | 2016.5 | 6394 | Date: | 2021-01-04
1:00 | 113 | 4317 | 1710 | 6027
1:30 | 93 | 4255 | 1719.5 | 5974.5
2:00 | 73 | 4193 | 1729 | 5922
2:30 | 48 | 4084.5 | 1712 | 5796.5 | [5 empty] | Gen. at Eve. Peak | 8921 | 8921 MW (19:00 )
3:00 | 23 | 3976 | 1695 | 5671 | [6 empty] | 19:00
3:30 | 29 | 3919.5 | 1709.5 | 5629 | [5 empty] | Gen. at Day Peak | 7183 | 7183 MW (12:00 )
4:00 | 35 | 3863 | 1724 | 5587 | [6 empty] | 12:00
4:30 | 66 | 3846 | 1737.5 | 5583.5 | [5 empty] | Highest Generation | 8921
5:00 | 97 | 3829 | 1751 | 5580 | [6 empty] | 19:00
5:30 | 73.5 | 3943 | 1777.5 | 5720.5
6:00 | 50 | 4057 | 1804 | 5861
6:30 | 37 | 4150 | 1843.5 | 5993.5
7:00 | 24 | 4243 | 1883 | 6126
7:30 | 19.5 | 4342.5 | 1983 | 6325.5
8:00 | 15 | 4442 | 2083 | 6525
8:30 | 58.5 | 4535.5 | 2206 | 6741.5
9:00 | 102 | 4629 | 2329 | 6958
9:30 | 192 | 4648.5 | 2342.5 | 6991
10:00 | 282 | 4668 | 2356 | 7024
10:30 | 303 | 4627 | 2343.5 | 6970.5
11:00 | 324 | 4586 | 2331 | 6917
11:30 | 267 | 4736 | 2314 | 7050
12:00 | 210 | 4886 | 2297 | 7183
12:30 | 196.5 | 4961 | 2337 | 7298
13:00 | 183 | 5036 | 2377 | 7413
13:30 | 347.5 | 4807 | 2422 | 7229
14:00 | 512 | 4578 | 2467 | 7045
14:30 | 495 | 4581 | 2406 | 6987
15:00 | 478 | 4584 | 2345 | 6929
15:30 | 420.5 | 4592.5 | 2262 | 6854.5
16:00 | 363 | 4601 | 2179 | 6780
16:30 | 321.5 | 4670 | 2173.5 | 6843.5
17:00 | 280 | 4739 | 2168 | 6907
17:30 | 143 | 5139.5 | 2439.5 | 7579
18:00 | 6 | 5540 | 2711 | 8251
18:30 | 33 | 5715 | 2871 | 8586
19:00 | 60 | 5890 | 3031 | 8921
19:30 | 125 | 5779 | 3086 | 8865
20:00 | 145 | 5716 | 3070 | 8786 |  |  |  | Executive Engineer
20:30 | 208.5 | 5586.5 | 3069 | 8655.5 |  |  |  | Network Operation Division
21:00 | 272 | 5457 | 3068 | 8525
21:30 | 332 | 5248 | 2989.5 | 8237.5
22:00 | 392 | 5039 | 2911 | 7950 |  |  |  |  | Page 6 of 7
22:30 | 396 | 4825.5 | 2783 | 7608.5
23:00 | 400 | 4612 | 2655 | 7267
23:30 | 358.5 | 4525 | 2489 | 7014
24:00 | 317 | 4438 | 2323 | 6761
8921 MW (19:00 )
7183 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-04 |  | Energy | 170691500
[11 empty] | 2021-01-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2825 | 628 | 1249 | 1544 | 600 | 35 | 0 | 0 | 80 | 0
0:30 | 2968.5 | 532 | 1264 | 1102.5 | 515 | 35 | 0 | 0 | 77 | 0 | Date: | 2021-01-04
1:00 | 3112 | 436 | 1279 | 661 | 430 | 35 | 0 | 0 | 74 | 0
1:30 | 3134.5 | 436 | 1271 | 600 | 425 | 35 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 170.6915 | Total Energy Gen 170.692 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.692 MKWHr
2:00 | 3157 | 436 | 1263 | 539 | 420 | 35 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3153 | 436 | 1258 | 423.5 | 420 | 35 | 0 | 0 | 71 | 0 | [7 empty] | Energy Requirement | 170.6915
3:00 | 3149 | 436 | 1253 | 308 | 420 | 35 | 0 | 0 | 70 | 0
3:30 | 3162 | 436 | 1257.5 | 251.5 | 420 | 35 | 0 | 0 | 67 | 0 | [6 empty] | Shortage
4:00 | 3175 | 436 | 1262 | 195 | 420 | 35 | 0 | 0 | 64 | 0
4:30 | 3197 | 436.5 | 1235 | 195 | 420 | 35 | 0 | 0 | 65 | 0
5:00 | 3219 | 437 | 1208 | 195 | 420 | 35 | 0 | 0 | 66 | 0
5:30 | 3250.5 | 436.5 | 1244.5 | 267 | 420 | 35 | 0 | 0 | 67 | 0
6:00 | 3282 | 436 | 1281 | 339 | 420 | 35 | 0 | 0 | 68 | 0
6:30 | 3258 | 436 | 1308.5 | 458 | 430 | 35 | 0 | 0 | 67 | 1 |  |  |  |  | Coal
7:00 | 3234 | 436 | 1336 | 577 | 440 | 35 | 0 | 0 | 66 | 2
7:30 | 3205.5 | 483 | 1263 | 786 | 475 | 35 | 0 | 0 | 70 | 8 |  |  |  | Oil |  |  |  | ,
8:00 | 3177 | 530 | 1190 | 995 | 510 | 35 | 0 | 0 | 74 | 14
8:30 | 3109.5 | 530 | 1155.5 | 1265 | 545 | 35 | 0 | 0 | 76 | 25.5
9:00 | 3042 | 530 | 1121 | 1535 | 580 | 35 | 0 | 0 | 78 | 37
9:30 | 2992.5 | 554 | 1109.5 | 1613.5 | 565 | 35 | 0 | 0 | 77 | 44.5
10:00 | 2943 | 578 | 1098 | 1692 | 550 | 35 | 0 | 0 | 76 | 52
10:30 | 2981.5 | 578 | 1138.5 | 1554.5 | 545 | 35 | 0 | 0 | 79 | 59
11:00 | 3020 | 578 | 1179 | 1417 | 540 | 35 | 0 | 0 | 82 | 66
11:30 | 3153.5 | 578.5 | 1190.5 | 1393 | 550 | 35 | 0 | 0 | 82 | 67.5
12:00 | 3287 | 579 | 1202 | 1369 | 560 | 35 | 0 | 0 | 82 | 69
12:30 | 3308 | 578.5 | 1207.5 | 1441 | 575 | 35 | 0 | 0 | 85 | 68
13:00 | 3329 | 578 | 1213 | 1513 | 590 | 35 | 0 | 0 | 88 | 67
13:30 | 3329 | 578 | 1213 | 1513 | 590 | 35 | 0 | 0 | 88 | 67
14:00 | 3329 | 578 | 1213 | 1513 | 590 | 35 | 0 | 0 | 88 | 67
14:30 | 3044.5 | 578.5 | 1148.5 | 1638.5 | 585 | 35 | 0 | 0 | 90 | 51
15:00 | 2760 | 579 | 1084 | 1764 | 580 | 35 | 0 | 0 | 92 | 35
15:30 | 2752 | 578.5 | 1123 | 1685.5 | 565 | 35 | 0 | 0 | 90 | 25.5
16:00 | 2744 | 578 | 1162 | 1607 | 550 | 35 | 0 | 0 | 88 | 16
16:30 | 2779 | 578 | 1194.5 | 1609.5 | 550.5 | 35 | 0 | 0 | 89 | 8
17:00 | 2814 | 578 | 1227 | 1612 | 551 | 35 | 0 | 0 | 90 | 0
17:30 | 2868 | 650 | 1278 | 1954.5 | 561 | 35 | 133.5 | 0 | 99 | 0
18:00 | 2922 | 722 | 1329 | 2297 | 571 | 35 | 267 | 0 | 108 | 0
18:30 | 2895 | 769.5 | 1341 | 2539 | 610.5 | 35 | 289 | 0 | 107 | 0
19:00 | 2868 | 817 | 1353 | 2781 | 650 | 35 | 311 | 0 | 106 | 0
19:30 | 2914 | 817 | 1415 | 2680 | 650 | 35 | 248 | 0 | 106 | 0
20:00 | 2859 | 817 | 1401 | 2665 | 650 | 35 | 255 | 0 | 104 | 0
20:30 | 2860 | 817.5 | 1404.5 | 2572.5 | 650 | 35 | 215 | 0 | 101 | 0
21:00 | 2861 | 818 | 1408 | 2480 | 650 | 35 | 175 | 0 | 98 | 0
21:30 | 2853 | 818 | 1398 | 2271 | 650 | 35 | 116.5 | 0 | 96 | 0
22:00 | 2845 | 818 | 1388 | 2062 | 650 | 35 | 58 | 0 | 94 | 0
22:30 | 2849.5 | 817.5 | 1333.5 | 1803 | 650 | 35 | 29 | 0 | 91 | 0
23:00 | 2854 | 817 | 1279 | 1544 | 650 | 35 | 0 | 0 | 88 | 0
23:30 | 2839.5 | 722.5 | 1264 | 1544 | 625 | 35 | 0 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 28.2° C
24:00 | 2825 | 628 | 1249 | 1544 | 600 | 35 | 0 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 170.692 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.692 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 2 | 16 |  | 25 | 25 | 25 | 8 |  |  |  | 85937
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 11 | 15 | 17 | 17 | 16 | 14 | 11 | 6 | 0 | [9 empty] | 110025
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 82 |  | 85 | 53 | 61 | 17 |  |  |  | 218162
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 0 |  |  |  |  | 34 | 94 | 145 | 145 | 115 | 95 | 95 | 95 | 168 | 200 | 200 | 273 |  | 291 | 300 | 300 | 300 | 283 | 195 | 130 | 3301962
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 434909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 275 | 276 | 277 | 272 | 278 | 279 | 278 | 278 | 273 | 313 | 311 | 330 | 325 | [13 empty] | 3936000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 270 | 260 | 240 | 225 | 225 | 250 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 6932845
26
28 | Ashuganj TPP Unit- 3 | [24 empty] | 20 | 40 | 49430
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 298944
33 | Ashuganj 225 MW CCPP | 166 | 183 | 189 | 190 | 200 | 190 | 174 | 154 | 147 | 196 | 227 | 199 | 158 | 183 | 183 | 183 | 197 | 201 |  | 183 | 196 | 182 | 183 | 182 | 183 | 181 | 4479000
34 | Ashuganj 450 MW CCPP(South) | 320 | 320 | 320 | 320 | 320 | 355 | 355 | 355 | 350 | 260 | 260 | 270 | 265 | 305 | 285 | 285 | 305 | 335 |  | 310 | 335 | 310 | 310 | 310 | 285 | 280 | 7538000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 265 | 280 | 280 | 275 | 275 | 340 | 385 | [13 empty] | 3946700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 49 | 53 | 52 | 56 | 56 | 57 | 56 | 452160
36 | Chandpur 150 MW CCPP | [11 empty] | 51 | 47 | 47 | 47 | 50 | 70 | 91 |  | 80 | 89 | 90 | 90 | 81 | 91 | 82 | 882700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 363 | 358 | 349 | 350 | 349 | 354 | 361 | 374 | 350 | 349 | 356 | 357 | 371 | 359 | 351 | 352 | 364 | 385 |  | 373 | 373 | 355 | 359 | 349 | 349 | 349 | 8759392
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 355 | 355 | 325 | 288 | 259 | 265 | 327 | 330 | 255 | 244 | 275 | 324 | 334 |  | 354 | 354 | 359 | 353 | 353 | 306 | 290 | 7416000
42 | RPCL 210MW CCPP | 108 | 110 | 110 | 108 | 110 | 110 | 107 | 110 | 109 | 106 | 102 | 102 | 102 | 102 | 103 | 102 | 103 | 103 |  | 107 | 106 | 107 | 107 | 108 | 109 | 107 | 2502440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 7 | 24 | 35 | 43 | 43 | 41 | 29 | 18 | 7 | 0 | [9 empty] | 240890
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475440
46 | Shajibazar 330 MW CCPP | 144 | 144 | 145 | 145 | 145 | 145 | 143 | 144 | 146 | 145 | 145 | 144 | 144 | 144 | 144 | 143 | 144 | 146 |  | 143 | 145 | 145 | 145 | 147 | 144 | 145 | 3281000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 34 | 34 | 34 | 33 | 20 | 20 | 20 | 20 | 20 | 20 | 31 | 20 | 20 | 20 | 32 |  | 33 | 32 | 32 | 33 | 33 | 33 | 20 | 664896
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 72 | 40 | 40 | 71 | 70 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1431360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 129 | 129 | 129 | 129 | 128 | 128 | 128 | 128 | 130 | 130 | 129 | 129 | 130 | 130 | 130 | 131 | 131 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3278160
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [19 empty] | 55800
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 174500
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 14 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 217200
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 270 | 280 | 260 | 275 | 300 | 280 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 285 |  | 280 | 285 | 280 | 280 | 280 | 280 | 280 | 6839000
| Bibiyana South 400 MW | 415 | 415 | 415 | 415 | 415 | 415 | 350 | 280 | 210 | 142 | 250 | 410 | 420 | 420 | 420 | 420 | 418 | 419 |  | 425 | 425 | 425 | 427 | 427 | 426 | 400 | 9151100
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 525374
59 | Tangail Palli Power Gen 22 MW | [13 empty] | 1 | 22 | 24 | 25 | 25 |  | 24 | 24 | 24 | 25 | 25 |  |  | 209760
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436848
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 447480
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 495468
63 | Impoprt (Tripura) | 74 | 72 | 70 | 64 | 66 | 68 | 66 | 74 | 78 | 76 | 82 | 82 | 88 | 88 | 92 | 88 | 90 | 108 |  | 106 | 106 | 104 | 98 | 94 | 88 | 80 | 2031360
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 8 | 8 | 8 | 9 | 10 | 12 | 11 | 5 | 7 | 13 | 15 |  | 25 | 27 | 30 | 35 | 41 | 42 | 42 | 591360
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 428832
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 808600
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 498530
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 29 | 32 | 32 | 32 | 20 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 705600
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 504700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 | 25 | 25 | 8 | 16 | 16 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 581700
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 46 | 46 | 0 |  |  |  |  | 5 | 35 | 35 |  |  |  | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 525840
| Manikgonj 162MW PP(MPGL) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1324800
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 0 | 32 | 28 |  |  |  | 0 | 20 | 16 | 7 | 36 |  | 100 | 100 | 85 | 7 |  |  |  | 361920
78 | Gazipur 52 MW PP | [16 empty] | 5 | 20 |  | 24 | 8 | [5 empty] | 59424
79 | Kodda 150MW PP | [17 empty] | 115 |  | 115 | 84 | 84 | 48 |  |  |  | 306720
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 13 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 248640
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [8 empty] | 4 | 35 | 35 | 40 | 54 | 105 | 105 | 105 | 105 | 105 |  | 105 | 53 | 53 | 17 |  |  |  | 930168
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 |  |  | 3 | 3 | 3 | 2 | 1 | [10 empty] | 14726
| Jodiac Power | 41 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 49 | 54 | 54 | 54 | 35 | 35 | 36 | 49 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1227660
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [8 empty] | 10 | 40 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 55 |  | 70 | 80 | 80 | 80 | 48 | 15 | 15 | 833520
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | 0 | [5 empty] | 2 |  |  |  |  | 26 | 72 | 77 | 50 | 50 | 75 |  | 85 | 85 | 87 | 86 | 85 | 93 | 100 | 1014385
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 10 | 16 |  |  |  |  | 14 | 16 | 16 | 28 |  | 75 | 75 | 75 | 75 | 41 |  |  | 391680
| Meghnaghat 104 MW PP (OPCL) | 53 | 53 | 53 | 0 |  |  | 11 | 34 | 34 | 34 | 22 |  |  |  | 24 | 17 | 17 | 41 |  | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 952320
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 10 | [6 empty] | 15720
92 | Fenchuganj 44MW (Energyprima) | 30 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 230184
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1211642
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 7 | 16 | 16 | 16 | 20 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 588384
95 | Patenga 50MW PP (Baraka) | 32 | 32 | 0 |  | 0 | 1 | 13 | 18 | 19 | 19 | 19 | 19 | 19 | 10 | 22 | 25 | 25 | 37 |  | 50 | 50 | 50 | 50 | 50 | 50 | 31 | 613920
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 14 |  | 51 | 12 | 15 |  |  |  |  | 83520
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 4 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 225129
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 13 | 35 |  | 35 | 17 | 17 |  |  |  |  | 106892
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 11150
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 371520
104 | Keranigonj 300 MW PP (APR) | [13 empty] | 154 | [12 empty] | 100193
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 32 | 8 | 0 |  | 0 | 15 | 58 | 96 | 195 | 200 | 120 | 160 | 168 | 190 | 160 | 160 | 160 | 182 |  | 200 | 200 | 200 | 200 | 160 | 80 | 80 | 2988000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 45 | 40 | 0 | [5 empty] | 22 | 60 | 60 | 77 | 106 | 111 | 118 | 118 | 118 | 124 |  | 123 | 123 | 124 | 110 | 35 |  |  | 1415950
115 | Juldah 100 MW PP Unit-3 (Acorn) |  |  |  |  | 0 | 10 | 32 | 90 | 90 | 90 | 60 | 60 | 60 | 78 | 78 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 50 |  |  | 1159680
116 | Chandpur 200MW (Desh energy) | 34 | 0 |  |  | 0 | 3 | 37 | 68 | 68 | 68 | 68 | 68 | 76 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1115520
117 | Ashuganj 150MW PP (Midland) | 147 | 140 | 70 | 10 | 10 | 16 | 66 | 107 | 128 | 133 | 135 | 107 | 100 | 70 | 10 | 10 | 13 | 60 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2085890
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [8 empty] | 8 | [8 empty] | 8 |  | 8 | 8 | 8 |  |  |  |  | 40800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 66 | 66 | 121 | 123 | 125 | 125 | 125 | 158 | 175 | 198 | 198 | 199 | 198 |  | 198 | 199 | 199 | 199 | 198 | 198 | 198 | 3088691
| Juldah unit-2 (Acorn) | 60 | 60 | 60 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2215680
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4317 | 4193 | 3976 | 3863 | 3829 | 4057 | 4243 | 4442 | 4629 | 4668 | 4586 | 4886 | 5036 | 4578 | 4584 | 4601 | 4739 | 5540 |  | 5890 | 5779 | 5716 | 5457 | 5039 | 4612 | 4438 | 113701412
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) |  |  |  |  | 0 | 16 | 16 | 83 | 99 | 99 | 99 | 99 | 99 | 115 | 115 | 32 | 16 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1547520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 53 | 53 | 53 | 53 | 78 | 105 | 53 | 17 | 17 | 53 |  | 84 | 105 | 105 | 105 | 90 |  |  | 989280
130
131
132 | United Payra Power Ltd. | [12 empty] | 17 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 47 | 638400
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 39 | 27 | 7 | 35 | 35 | 35 | [13 empty] | 444736
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 79 | 89 | 34 | 31 | 31 | 32 | 32 | 31 | 34 | 57 |  | 64 | 63 | 63 | 64 | 62 | 40 | 60 | 1054178
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 14 | 16 | 14 | 13 | 13 | 12 | 13 | 13 | 14 | 14 | 13 | 12 | 13 | 20 |  | 21 | 28 | 28 | 28 | 28 | 26 | 24 | 401100
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 10 | 10 | 10 | 10 | 10 | [12 empty] | 74880
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 24 | [11 empty] | 280875
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 6 | 6 | 6 | 6 | 7 |  |  | 24704
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 436 | 436 | 436 | 436 | 437 | 436 | 436 | 530 | 530 | 578 | 578 | 579 | 578 | 578 | 579 | 578 | 578 | 722 |  | 817 | 817 | 817 | 818 | 818 | 817 | 628 | 14273131
147 | Bheramara 410 MW CCPP | 170 | 190 | 190 | 210 | 230 | 250 | 270 | 255 | 250 | 250 | 220 | 250 | 245 | 240 | 240 | 235 | 230 | 225 |  | 220 | 215 | 215 | 210 | 210 | 215 | 220 | 5670720
148 | Payra 1320 MW | 280 | 270 | 270 | 270 | 270 | 270 | 290 | 360 | 430 | 400 | 390 | 410 | 440 | 430 | 430 | 400 | 400 | 420 |  | 500 | 500 | 500 | 500 | 500 | 500 | 450 | 10290600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 151 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3676700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 2016
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 148 | 161 | 162 | 172 | 180 | 192 | 200 | 198 | 198 | 198 | 197 | 192 | 189 | 182 | 178 | 175 | 173 | 169 |  | 164 | 159 | 158 | 156 | 156 | 157 | 162 | 4463336
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 376 | 376 | 377 | 376 | 376 | 377 | 378 | 322 | 284 | 288 | 388 | 351 | 356 | 390 | 374 | 393 | 399 | 423 |  | 370 | 415 | 399 | 402 | 378 | 338 | 305 | 8897200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 514080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 215766
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | [6 empty] | 12960
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 70 |  | 105 | 105 | 104 | 104 | 51 |  |  | 410940
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 0 |  | 0 | 3 | 35 | 48 | 108 | 113 | 90 | 50 | 60 | 83 | 35 | 35 | 35 | 82 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1725888
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 20 | 35 | 35 |  |  |  | 10 | 35 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 896064
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 35 |  | 110 | 111 | 113 | 113 | 49 |  |  | 456960
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 0 | 1 | 4 | 4 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 28054
178
178