## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-07 | Thursday
|  |  | Date (day): | 2021-01-07 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11964.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13150 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-06 | 2021-01-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 264 | 356 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 255 | 340 | 360
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 350 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 310 | 338 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 12 | 65 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 24 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 67 | 87 | 87 | 87 |  | 13 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 55 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 58 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 7 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 8 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 205 | 280 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 32 | 142 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 35 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1886 | 2577 | 3196 | 3506 | 979 | 1565
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 41 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 22 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 20 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 20 | 10 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 271 | 255 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 539 | 573 | 1230 | 1215 | 930 | 103
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 70 | 70 | 65 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 184 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 150 | 150 | 210 |  | Gas shortage
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 315 | 300 | 300 | 60 |  | Gas shortage
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 56 | 55 | 55
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 100 | 101 | 100 | 100
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 91 | 90 | 91 |  | 72 | Gas shortage
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 34 | 68 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 106 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 22 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 107 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1031 | 1197 | 1763 | 2028 | 804 | 84
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 103 | 105 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 90 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 184 | 182 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 13 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 20 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 446 | 432 | 615.6 | 564 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 45 | 45 | 45
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 20 | 20
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 53 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 49 | 44 | 44
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 68 | 68 | 68
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 70 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 144 | 182 | 200 | 200
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 290 | 330 | 330
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 8 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 421 | 283 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1078 | 1113 | 1284 | 1284 | 330 | 425
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 579 | 811 | 586 | 827
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 325 | 300 | 325 | 85 |  | Gas shortage
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1073 | 1356 | 1401 | 1953 | 85 | 58
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 26 | 24 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 61 | 61 | 60 | 61 | 34 |  | Gas shortage
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 380 | 480 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 30 | 56 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 54 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 491 | 693 | 844 | 853 | 34 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 35 | 35 |  | 15 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 180 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 318 | 336 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 51 | 94 | 94 | 94
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 777 | 880 | 1360 | 1484 | 601 | 15
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 58 | 102 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 212 | 252 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7533 | 9073 | 11964.6 | 13150 | 3979 | 2661
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7169.3437 | 8635 | 11387.0077 | 12515.1824
| A. |  | 2021-01-06 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 9073 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5622 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9073 | MW
| 3 | Day peak Generation : |  |  | 7533 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8635 | MW
| 4 | Evening peak Generation : |  |  | 9073 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 176.2738 | MKWHr | By Solar | 0.34431 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.5256 | MKWHr |  | By Oil: | 40.8014 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.7069 | MKWHr |  | By Hydro: | 0.652 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3979 | MW | Dhaka | 3041 | 3041 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2661 | MW | Chittagong | 991 | 991 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6640 | MW | Khulna | 1091 | 1091 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 792.7 | MMCFD |  |  | Rajshahi | 912 | 912 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 110955867.216 | ii) Oil : | Taka | 307978067.45 | Comilla | 745 | 745 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 68356472 | Total | Taka | 487290406.666 | Mymensingh | 739 | 739 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 226 | MW (E to W) at | 19:30 | hrs | Barisal | 223 | 223 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -24 | MW at | 8:00 | hrs | Rangpur | 577 | 577 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30° C |  |  | Total | 8635 | 8635 |  | 0
| B. |  | 2021-01-07 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 30.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13150 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
| 4 | Reserve(Generation end) |  |  |  | 3950 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 178.7412 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5765 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.2458 | MKWHr. | ii) HVDC Flow at Peak Time |  | 811 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9978 | MKWHr. | iii) Maximum HVDC Flow : |  | 816 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.84 |  | (b) Today: | 97.78 |  | (c) Rule Curve: |  | 101.86
.

## YesterdayGen
2021-01-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 109 | 0 | 330 | 0 | 0 | 357 | 310 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 36 | 0 | 0 | 0 | 0 | 285 | 195 | 8 | 91 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 74 | 108 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 69 | 72 | 0 | 182 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 36 | 100 | 427 | 0 | 0 | 17 | 0 | 0 |  | 434 | 0 | 295 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 389 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 460 | 28 | 0 | 0 |  | 4214 | 2176 | 6390 | 2949 | 434 | 1341 | 936 | 610 | 46 | 0 | 74 | 0 | 0 | 97.85
2:00 | 0 | 0 | 105 | 0 | 330 | 0 | 0 | 356 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 280 | 184 | 8 | 89 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 72 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 69 | 72 | 0 | 182 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 70 | 10 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 36 | 100 | 427 | 0 | 0 | 17 | 0 | 0 |  | 433 | 0 | 295 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 28 | 0 | 0 |  | 4057 | 2025 | 6082 | 2917 | 433 | 1362 | 642 | 610 | 46 | 0 | 72 | 0 | 0 | 97.85
3:00 | 0 | 0 | 104 | 0 | 330 | 0 | 0 | 349 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 275 | 183 | 8 | 81 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 72 | 108 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 70 | 72 | 0 | 182 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 0 | 100 | 360 | 0 | 0 | 17 | 0 | 0 |  | 433 | 0 | 295 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 27 | 0 | 0 |  | 3915 | 1997 | 5912 | 2830 | 433 | 1324 | 596 | 610 | 47 | 0 | 72 | 0 | 0 | 97.84
4:00 | 0 | 0 | 104 | 0 | 330 | 0 | 0 | 351 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 20 | 8 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 275 | 183 | 8 | 91 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 68 | 109 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 70 | 72 | 0 | 182 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 0 | 20 | 360 | 0 | 0 | 17 | 0 | 0 |  | 433 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 28 | 0 | 0 |  | 3694 | 1965 | 5659 | 2822 | 433 | 1324 | 355 | 610 | 47 | 0 | 68 | 0 | 0 | 97.84
5:00 | 0 | 0 | 101 | 0 | 330 | 0 | 0 | 353 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 280 | 183 | 8 | 91 | 5 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 68 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 69 | 72 | 0 | 182 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 0 | 20 | 360 | 0 | 0 | 17 | 0 | 0 |  | 433 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 27 | 0 | 0 |  | 3676 | 1946 | 5622 | 2847 | 433 | 1349 | 355 | 570 | 0 | 0 | 68 | 0 | 0 | 97.84
6:00 | 0 | 0 | 101 | 0 | 330 | 0 | 0 | 370 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 16 | 20 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 320 | 209 | 8 | 91 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 70 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 68 | 73 | 0 | 182 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 69 | 1 | 0 | 0 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 0 | 20 | 360 | 0 | 0 | 17 | 0 | 0 |  | 434 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 180 | 0 | 377 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 420 | 17 | 0 | 0 |  | 3793 | 1986 | 5779 | 2931 | 434 | 1376 | 363 | 570 | 35 | 0 | 70 | 0 | 0 | 97.84
7:00 | 0 | 0 | 103 | 0 | 330 | 0 | 0 | 406 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 16 | 20 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 19 | 34 | 0 | 0 | 0 | 0 | 345 | 217 | 8 | 91 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 68 | 108 | 0 | 22 | 0 | 30 | 20 | 8 | 5 | 0 | 0 | 68 | 73 | 0 | 182 | 0 | 0 | 0 | 330 | 0 | 11 | 0 | 2 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 68 | 33 | 0 | 0 | 0 | 0 | 0 | 196 | 54 | 0 | 0 | 0 | 60 | 360 | 7 | 1 | 17 | 0 | 0 |  | 433 | 0 | 315 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 180 | 0 | 422 | 17 | 0 | 55 | 0 | 0 | 0 | 0 | 25 | 420 | 9 | 0 | 0 |  | 4051 | 2139 | 6190 | 2998 | 433 | 1422 | 638 | 570 | 35 | 25 | 68 | 1 | 0 | 97.83
8:00 | 0 | 0 | 97 | 0 | 330 | 0 | 0 | 410 | 356 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 16 | 20 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 7 | 0 | 0 | 0 | 0 | 330 | 201 | 8 | 88 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 74 | 108 | 0 | 22 | 1 | 30 | 20 | 8 | 5 | 0 | 0 | 68 | 74 | 0 | 182 | 0 | 0 | 0 | 330 | 0 | 11 | 0 | 40 | 0 | 0 | 117 | 0 | 0 | 4 | 0 | 68 | 68 | 0 | 0 | 0 | 0 | 1 | 234 | 54 | 0 | 0 | 8 | 100 | 360 | 21 | 9 | 17 | 0 | 0 |  | 528 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 180 | 0 | 416 | 35 | 0 | 70 | 0 | 0 | 0 | 1 | 35 | 460 | 21 | 0 | 0 |  | 4281 | 2463 | 6744 | 2947 | 528 | 1438 | 1037 | 610 | 35 | 59 | 74 | 16 | 0 | 97.83
9:00 | 0 | 0 | 103 | 0 | 330 | 0 | 0 | 373 | 309 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 6 | 24 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 33 | 19 | 6 | 0 | 0 | 0 | 0 | 290 | 190 | 8 | 82 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 80 | 107 | 22 | 22 | 1 | 30 | 20 | 8 | 5 | 0 | 0 | 67 | 73 | 0 | 182 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 131 | 0 | 0 | 190 | 0 | 0 | 0 | 40 | 68 | 100 | 0 | 0 | 0 | 0 | 2 | 268 | 54 | 0 | 0 | 55 | 100 | 427 | 53 | 25 | 17 | 0 | 0 |  | 529 | 0 | 300 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 34 | 195 | 0 | 344 | 105 | 0 | 87 | 0 | 35 | 0 | 2 | 70 | 400 | 21 | 0 | 0 |  | 4625 | 2567 | 7192 | 2925 | 529 | 1294 | 1649 | 551 | 35 | 99 | 80 | 30 | 0 | 97.83
10:00 | 0 | 0 | 106 | 0 | 330 | 0 | 0 | 351 | 279 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 0 | 24 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 40 | 17 | 5 | 0 | 0 | 0 | 0 | 285 | 193 | 8 | 84 | 5 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 80 | 106 | 61 | 22 | 2 | 0 | 20 | 8 | 5 | 0 | 0 | 66 | 72 | 0 | 144 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 198 | 0 | 0 | 190 | 0 | 30 | 0 | 40 | 50 | 102 | 0 | 0 | 0 | 0 | 3 | 268 | 54 | 0 | 0 | 55 | 100 | 427 | 53 | 35 | 17 | 0 | 0 |  | 575 | 0 | 295 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 150 | 0 | 340 | 105 | 0 | 112 | 0 | 40 | 0 | 3 | 113 | 400 | 21 | 0 | 0 |  | 4625 | 2585 | 7210 | 2778 | 575 | 1229 | 1821 | 550 | 35 | 99 | 80 | 43 | 0 | 97.83
11:00 | 0 | 0 | 174 | 0 | 330 | 0 | 0 | 353 | 311 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 48 | 60 | 0 | 0 | 0 | 0 | 35 | 0 | 22 | 25 | 0 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 40 | 17 | 4 | 0 | 0 | 0 | 0 | 270 | 230 | 8 | 89 | 13 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 80 | 106 | 72 | 22 | 2 | 0 | 20 | 8 | 5 | 0 | 0 | 65 | 71 | 0 | 145 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 200 | 0 | 0 | 194 | 0 | 32 | 0 | 10 | 34 | 100 | 0 | 0 | 0 | 0 | 4 | 268 | 54 | 0 | 0 | 55 | 100 | 427 | 53 | 41 | 17 | 0 | 0 |  | 579 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 150 | 0 | 306 | 105 | 0 | 113 | 0 | 42 | 0 | 4 | 113 | 400 | 21 | 0 | 0 |  | 4808 | 2532 | 7340 | 2881 | 579 | 1224 | 1841 | 550 | 35 | 99 | 80 | 51 | 0 | 97.82
12:00 | 0 | 0 | 264 | 0 | 330 | 0 | 0 | 353 | 310 |  | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 0 | 32 | 48 | 67 | 0 | 0 | 0 | 0 | 35 | 8 | 22 | 25 | 0 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 41 | 20 | 4 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 88 | 103 | 72 | 22 | 2 | 30 | 20 | 8 | 5 | 0 | 0 | 61 | 71 | 0 | 144 | 18 | 0 | 5 | 270 | 14 | 11 | 0 | 205 | 0 | 0 | 184 | 0 | 32 | 0 | 10 | 34 | 100 | 0 | 0 | 0 | 0 | 4 | 271 | 54 | 0 | 0 | 55 | 100 | 421 | 53 | 42 | 17 | 0 | 0 |  | 579 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 150 | 0 | 318 | 105 | 0 | 113 | 0 | 58 | 0 | 4 | 113 | 380 | 30 | 0 | 0 |  | 4980 | 2553 | 7533 | 2997 | 579 | 1238 | 1915 | 530 | 35 | 99 | 88 | 52 | 0 | 97.82
13:00 | 0 | 0 | 327 | 0 | 330 | 0 | 0 | 356 | 275 |  | 0 | 0 | 0 | 1 | 15 | 30 | 0 | 0 | 0 | 0 | 65 | 82 | 70 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 25 | 0 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 43 | 20 | 2 | 0 | 0 | 0 | 0 | 265 | 186 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 88 | 103 | 72 | 22 | 2 | 33 | 20 | 50 | 18 | 0 | 0 | 61 | 71 | 0 | 169 | 18 | 0 | 5 | 260 | 14 | 11 | 0 | 245 | 0 | 0 | 194 | 0 | 32 | 0 | 40 | 42 | 100 | 0 | 0 | 0 | 0 | 4 | 272 | 54 | 0 | 0 | 55 | 100 | 182 | 61 | 42 | 17 | 0 | 0 |  | 579 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 150 | 0 | 330 | 105 | 0 | 113 | 0 | 70 | 0 | 3 | 113 | 370 | 29 | 0 | 0 |  | 5034 | 2601 | 7635 | 2846 | 579 | 1258 | 2125 | 520 | 35 | 133 | 88 | 51 | 7635 | 97.82
14:00 | 0 | 0 | 328 | 0 | 300 | 0 | 0 | 353 | 245 |  | 0 | 0 | 0 | 24 | 25 | 30 | 0 | 0 | 0 | 0 | 65 | 82 | 60 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 40 | 20 | 2 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 81 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 90 | 103 | 48 | 22 | 2 | 40 | 20 | 53 | 49 | 0 | 0 | 61 | 71 | 0 | 169 | 18 | 0 | 5 | 260 | 14 | 11 | 0 | 280 | 0 | 0 | 194 | 0 | 32 | 0 | 40 | 50 | 100 | 0 | 0 | 0 | 0 | 3 | 213 | 54 | 0 | 0 | 55 | 100 | 30 | 75 | 35 | 17 | 0 | 0 |  | 579 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 130 | 0 | 292 | 105 | 0 | 113 | 0 | 70 | 0 | 3 | 70 | 370 | 53 | 0 | 0 |  | 4844 | 2524 | 7368 | 2644 | 579 | 1248 | 2076 | 520 | 35 | 133 | 90 | 43 | 0 | 97.82
15:00 | 0 | 0 | 330 | 0 | 255 | 0 | 0 | 370 | 242 |  | 0 | 0 | 0 | 24 | 15 | 30 | 0 | 0 | 0 | 0 | 65 | 64 | 60 | 0 | 0 | 0 | 0 | 35 | 17 | 16 | 25 | 0 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 40 | 17 | 2 | 0 | 0 | 0 | 0 | 355 | 188 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 90 | 100 | 32 | 22 | 1 | 45 | 20 | 50 | 49 | 0 | 0 | 62 | 70 | 0 | 150 | 18 | 0 | 8 | 260 | 14 | 11 | 0 | 250 | 0 | 0 | 194 | 0 | 17 | 11 | 10 | 50 | 100 | 0 | 0 | 0 | 0 | 2 | 180 | 54 | 0 | 0 | 55 | 100 | 30 | 53 | 25 | 17 | 0 | 0 |  | 578 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 130 | 0 | 342 | 90 | 0 | 113 | 0 | 36 | 0 | 2 | 70 | 370 | 27 | 0 | 0 |  | 4714 | 2460 | 7174 | 2659 | 578 | 1266 | 1870 | 520 | 35 | 115 | 90 | 41 | 0 | 97.81
16:00 | 0 | 0 | 368 | 0 | 255 | 0 | 0 | 357 | 242 |  | 0 | 0 | 0 | 24 | 15 | 30 | 0 | 0 | 0 | 0 | 40 | 64 | 60 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 25 | 0 | 25 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 40 | 17 | 2 | 0 | 0 | 0 | 0 | 360 | 185 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 86 | 102 | 32 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 62 | 70 | 0 | 150 | 18 | 0 | 8 | 290 | 15 | 11 | 0 | 250 | 0 | 0 | 194 | 0 | 16 | 6 | 10 | 50 | 100 | 0 | 0 | 0 | 0 | 1 | 180 | 54 | 0 | 0 | 55 | 100 | 80 | 53 | 11 | 17 | 0 | 0 |  | 571 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 130 | 0 | 327 | 53 | 0 | 113 | 0 | 35 | 0 | 1 | 70 | 370 | 29 | 0 | 0 |  | 4769 | 2362 | 7131 | 2737 | 571 | 1286 | 1762 | 520 | 35 | 115 | 86 | 19 | 0 | 97.81
17:00 | 0 | 0 | 365 | 0 | 255 | 0 | 0 | 363 | 242 |  | 0 | 0 | 0 | 28 | 15 | 30 | 0 | 0 | 0 | 0 | 50 | 84 | 61 | 0 | 0 | 0 | 0 | 35 | 20 | 22 | 25 | 0 | 25 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 41 | 17 | 5 | 0 | 0 | 0 | 0 | 315 | 185 | 8 | 89 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 86 | 103 | 32 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 67 | 70 | 0 | 150 | 18 | 0 | 8 | 300 | 15 | 11 | 0 | 250 | 0 | 0 | 194 | 0 | 19 | 0 | 10 | 50 | 100 | 0 | 0 | 2 | 0 | 0 | 220 | 54 | 0 | 0 | 55 | 100 | 80 | 53 | 1 | 54 | 0 | 0 |  | 578 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 130 | 0 | 338 | 53 | 0 | 113 | 0 | 35 | 0 | 0 | 70 | 370 | 48 | 0 | 0 |  | 4842 | 2399 | 7241 | 2697 | 578 | 1331 | 1858 | 520 | 35 | 135 | 86 | 1 | 0 | 97.81
18:00 | 0 | 0 | 381 | 0 | 235 | 0 | 0 | 353 | 261 |  | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 26 | 58 | 84 | 62 | 0 | 0 | 7 | 54 | 35 | 35 | 22 | 25 | 0 | 25 | 17 | 46 | 0 | 0 | 35 | 0 | 0 | 21 | 0 | 0 | 0 | 0 |  | 14 | 0 | 77 | 0 | 56 | 46 | 17 | 7 | 0 | 0 | 0 | 0 | 315 | 184 | 8 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 14 | 18 | 8 | 33 | 22 | 110 | 104 | 44 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 68 | 71 | 0 | 150 | 18 | 0 | 8 | 270 | 16 | 11 | 0 | 265 | 0 | 0 | 194 | 0 | 62 | 0 | 50 | 50 | 100 | 0 | 13 | 100 | 0 | 0 | 265 | 54 | 0 | 34 | 55 | 100 | 278 | 69 | 0 | 54 | 0 | 0 |  | 816 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 130 | 0 | 389 | 105 | 0 | 113 | 0 | 97 | 0 | 0 | 113 | 420 | 55 | 0 | 54 |  | 5708 | 2980 | 8688 | 2841 | 816 | 1384 | 2677 | 570 | 35 | 255 | 110 | 0 | 0 | 97.81
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 252 | 0 | 255 | 0 | 0 | 366 | 358 |  | 0 | 0 | 0 | 54 | 64 | 0 | 0 | 0 | 0 | 50 | 58 | 84 | 87 | 0 | 0 | 12 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 61 | 0 | 18 | 48 | 17 | 16 | 0 | 0 | 0 | 0 | 310 | 184 | 8 | 81 | 26 | 56 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 22 | 106 | 106 | 89 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 69 | 73 | 0 | 182 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 182 | 0 | 137 | 0 | 50 | 64 | 100 | 0 | 16 | 70 | 0 | 0 | 255 | 54 | 0 | 0 | 73 | 100 | 285 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 162 | 0 | 310 | 105 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 470 | 55 | 0 | 54 |  | 5926 | 3127 | 9053 | 2973 | 811 | 1435 | 2835 | 619 | 35 | 239 | 106 | 0 | 0 | 97.8
19:30 | 0 | 0 | 356 | 0 | 255 | 0 | 0 | 350 | 338 |  | 0 | 0 | 0 | 100 | 65 | 0 | 0 | 0 | 0 | 55 | 58 | 32 | 87 | 0 | 0 | 7 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 22 | 0 | 0 | 50 | 17 | 20 | 0 | 0 | 0 | 0 | 315 | 184 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 106 | 105 | 90 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 68 | 70 | 0 | 182 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 182 | 0 | 142 | 0 | 20 | 68 | 101 | 0 | 13 | 35 | 0 | 0 | 255 | 54 | 0 | 0 | 107 | 100 | 283 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 336 | 105 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 480 | 56 | 0 | 54 |  | 5892 | 3181 | 9073 | 3093 | 811 | 1443 | 2807 | 630 | 35 | 148 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 380 | 0 | 255 | 0 | 0 | 351 | 338 |  | 0 | 0 | 0 | 97 | 64 | 2 | 0 | 0 | 0 | 60 | 58 | 32 | 86 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 5 | 0 | 0 | 50 | 17 | 26 | 0 | 0 | 0 | 0 | 315 | 184 | 8 | 88 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 108 | 106 | 90 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 69 | 73 | 0 | 182 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 185 | 0 | 141 | 0 | 20 | 68 | 100 | 0 | 0 | 35 | 0 | 0 | 255 | 54 | 0 | 0 | 106 | 100 | 285 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 323 | 105 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 470 | 56 | 0 | 54 |  | 5898 | 3129 | 9027 | 3121 | 811 | 1441 | 2760 | 620 | 35 | 131 | 108 | 0 | 0 | 97.8
21:00 | 0 | 0 | 375 | 0 | 255 | 0 | 0 | 360 | 338 |  | 0 | 0 | 0 | 68 | 52 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 85 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 26 | 0 | 0 | 0 | 0 | 325 | 194 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 104 | 105 | 49 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 69 | 70 | 0 | 216 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 280 | 0 | 0 | 185 | 0 | 115 | 0 | 20 | 68 | 100 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 108 | 100 | 282 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 423 | 105 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 470 | 57 | 0 | 54 |  | 5562 | 3177 | 8739 | 3172 | 811 | 1558 | 2348 | 621 | 35 | 90 | 104 | 0 | 0 | 97.8
22:00 | 0 | 0 | 384 | 0 | 255 | 0 | 0 | 353 | 338 |  | 0 | 0 | 0 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 35 | 0 | 0 | 0 | 0 | 315 | 184 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 98 | 108 | 0 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 69 | 72 | 0 | 215 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 250 | 0 | 0 | 180 | 0 | 46 | 0 | 20 | 68 | 100 | 0 | 0 | 0 | 0 | 0 | 253 | 54 | 0 | 0 | 107 | 100 | 270 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 390 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 70 | 470 | 57 | 0 | 54 |  | 5253 | 2990 | 8243 | 3134 | 811 | 1526 | 1975 | 621 | 35 | 43 | 98 | 0 | 0 | 97.8
23:00 | 0 | 0 | 30 | 0 | 340 | 0 | 0 | 355 | 354 |  | 0 | 0 | 0 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 40 | 0 | 0 | 0 | 20 | 300 | 184 | 8 | 86 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 92 | 107 | 0 | 22 | 0 | 30 | 20 | 53 | 50 | 0 | 0 | 69 | 73 | 0 | 216 | 19 | 0 | 9 | 290 | 16 | 11 | 0 | 145 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 68 | 100 | 0 | 0 | 0 | 0 | 0 | 269 | 54 | 0 | 0 | 84 | 100 | 270 | 59 | 0 | 54 | 0 | 0 |  | 813 | 0 | 305 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 185 | 0 | 358 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 35 | 460 | 64 | 0 | 54 |  | 4744 | 2874 | 7618 | 2854 | 813 | 1484 | 1687 | 610 | 35 | 43 | 92 | 0 | 0 | 97.79
24:00 | 0 | 0 | 40 | 0 | 340 | 0 | 0 | 348 | 320 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 25 | 17 | 34 | 0 | 0 | 0 | 20 | 275 | 184 | 8 | 82 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 84 | 107 | 0 | 22 | 0 | 30 | 20 | 50 | 50 | 0 | 0 | 69 | 74 | 0 | 216 | 19 | 0 | 9 | 280 | 16 | 11 | 0 | 145 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 68 | 100 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 36 | 100 | 270 | 53 | 0 | 54 | 0 | 0 |  | 624 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 193 | 0 | 337 | 53 | 0 | 113 | 0 | 0 | 0 | 0 | 35 | 440 | 61 | 0 | 54 |  | 4437 | 2561 | 6998 | 2838 | 624 | 1406 | 1413 | 590 | 35 | 8 | 84 | 0 | 0 | 97.79
KWH | 0 | 0 | 4952000 | 0 | 7240691 | 0 | 0 | 8803330 | 7482000 |  | 0 | 0 | 0 | 408000 | 445800 | 266000 | 0 | 0 | 0 | 144864 | 558432 | 811200 | 1209174 | 0 | 0 | 33456 | 183960 | 363357 | 354056 | 517644 | 600000 | 489420 | 593100 | 528800 | 76164 | 0 | 0 | 652000 | 0 | 0 | 52106 | 0 | 0 | 0 | 0 |  | 297120 | 0 | 150962 | 0 | 82560 | 691680 | 433344 | 509280 | 69202 | 0 | 0 | 35300 | 7324000 | 4625000 | 200727 | 2093980 | 382104 | 1345440 | 0 | 1231464 | 0 | 0 | 32294 | 441324 | 197820 | 820600 | 473930 | 1997760 | 2482280 | 761280 | 509364 | 12300 | 800000 | 478680 | 702600 | 685584 | 0 | 0 | 1601184 | 1723200 | 0 | 4214440 | 221000 | 0 | 91620 | 7316500 | 184752 | 264000 | 0 | 3916689 | 0 | 0 | 3532800 | 0 | 728780 | 18630 | 365760 | 1548000 | 1831636 | 0 | 42000 | 252216 | 0 | 26160 | 5612836 | 1299311 | 0 | 34200 | 1293600 | 2130240 | 7172900 | 1098240 | 264930 | 698400 | 0 | 0 |  | 14245818 | 0 | 7206624 | 0 | 1875840 | 0 | 0 | 0 | 0 | 0 | 212625 | 0 | 517300 | 33700 | 0 | 0 | 0 | 0 | 0 | 940848 | 31520 | 0 | 0 | 0 | 0 | 505920 | 0 | 232038 | 0 | 0 | 3682700 | 0 | 0 | 0 | 0 | 0 | 0 | 1231177 | 48000 | 4377882 | 0 | 8687727 | 1612800 | 0 | 2017753 | 0 | 787200 | 0 | 22293 | 1549920 | 11024200 | 928363 | 0 | 384000 |  | 114117557 | 62156248 | 176273805 | 70366733 | 14245818 | 33158902 | 38898369 | 14706900 | 652000 | 1903010 | 1997760 | 344313 | 0
Fuel Cost | 0 | 0 | 7229920 | 0 | 8037167.01 | 0 | 0 | 8891363.3 | 7706460 |  | 0 | 0 | 0 | 3096720 | 3071562 | 2250360 | 0 | 0 | 0 | 1090825.92 | 5092899.84 | 7982208 | 11148584.28 | 0 | 0 | 304115.04 | 1342908 | 2808749.61 | 3490992.16 | 388233 | 450000 | 0 | 0 | 0 | 736505.88 | 0 | 0 | 176040 | 0 | 0 | 484064.74 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1464331.4 | 0 | 718272 | 5478105.6 | 546013.44 | 1512561.6 | 102418.96 | 0 | 0 | 26122 | 7324000 | 4255000 | 258937.83 | 2408077 | 431777.52 | 1883616 | 0 | 2105803.44 | 0 | 0 | 308407.7 | 560481.48 | 148365 | 1436050 | 355447.5 | 14983200 | 2631216.8 | 6912422.4 | 646892.28 | 196062 | 1312000 | 765888 | 1250628 | 1069511.04 | 0 | 0 | 3154332.48 | 3291312 | 0 | 7290981.2 | 483990 | 0 | 186904.8 | 7389665 | 138564 | 200640 | 0 | 29610168.84 | 0 | 0 | 18370560 | 0 | 7171195.2 | 217784.7 | 2980944 | 16795800 | 12913033.8 | 0 | 383040 | 2383441.2 | 0 | 0 | 42433040.16 | 11316998.81 | 0 | 341316 | 11086152 | 14187398.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 82055911.68 | 0 | 7566955.2 | 0 | 14744102.4 | 0 | 0 | 0 | 0 | 0 | 2215552.5 | 0 | 801815 | 328912 | 0 | 0 | 0 | 0 | 0 | 8326504.8 | 242704 | 0 | 0 | 0 | 0 | 971366.4 | 0 | 175652.766 | 0 | 0 | 19960234 | 0 | 0 | 0 | 0 | 0 | 0 | 1846765.5 | 816480 | 5122121.94 | 0 | 8600849.73 | 16837632 | 0 | 19148475.97 | 0 | 6108672 | 0 | 246337.65 | 11453908.8 | 48396238 | 0 | 0 | 0 |  | 329198550.36 | 255967192.336 | 585165742.696 | 72079670.876 | 82055911.68 | 38876196.34 | 290205023.25 | 68356472 | 176040 | 17773044.2 | 14983200 | 660184.35 | 0
Yesterday Day Peak | 0 | 0 | 264 | 0 | 330 | 0 | 0 | 353 | 310 |  | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 0 | 32 | 48 | 67 | 0 | 0 | 0 | 0 | 35 | 8 | 22 | 25 | 0 | 24 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 41 | 20 | 4 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 88 | 103 | 72 | 22 | 2 | 30 | 20 | 8 | 5 | 0 | 0 | 61 | 71 | 0 | 144 | 18 | 0 | 5 | 270 | 14 | 11 | 0 | 205 | 0 | 0 | 184 | 0 | 32 | 0 | 10 | 34 | 100 | 0 | 0 | 0 | 0 | 4 | 271 | 54 | 0 | 0 | 55 | 100 | 421 | 53 | 42 | 17 | 0 | 0 |  | 579 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 150 | 0 | 318 | 105 | 0 | 113 | 0 | 58 | 0 | 4 | 113 | 380 | 30 | 0 | 0 |  | 7533 | DayPeak
Yesterday Evening Peak | 0 | 0 | 356 | 0 | 255 | 0 | 0 | 350 | 338 | 0 | 0 | 0 | 0 | 100 | 65 | 0 | 0 | 0 | 0 | 55 | 58 | 32 | 87 | 0 | 0 | 7 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 22 | 0 | 0 | 50 | 17 | 20 | 0 | 0 | 0 | 0 | 315 | 184 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 106 | 105 | 90 | 22 | 0 | 45 | 20 | 53 | 49 | 0 | 0 | 68 | 70 | 0 | 182 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 182 | 0 | 142 | 0 | 20 | 68 | 101 | 0 | 13 | 35 | 0 | 0 | 255 | 54 | 0 | 0 | 107 | 100 | 283 | 90 | 0 | 54 | 0 | 0 |  | 811 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 336 | 105 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 480 | 56 | 0 | 54 |  | 9073 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 87 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 20 | 70 | 0 | 0 | 150 | 300 | 225 | 8 | 91 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 22 | 147 | 110 | 95 | 22 | 0 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 100 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 0 | 0 |  | 827 | 16 | 325 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 94 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 0
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 87 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 10 | 70 | 0 | 0 | 150 | 300 | 225 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 135 | 110 | 95 | 22 | 1.6 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 100 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 0 | 0 |  | 586 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 357 | 354 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 25 | 33 | 25 |  | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 2 | 17 | 10 | 70 | 0 | 0 | 125 | 235 | 125 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 70 | 94 | 10 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 73 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 120 | 0 | 0 | 150 | 0 | 14 | 6 | 50 | 68 | 75 | 0 | 0 | 0 | 0 | 8 | 286 | 54 | 0 | 0 | 4 | 100 | 272 | 44 | 6 | 54 | 0 | 0 | 0 | 529 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 11 | 180 | 0 | 349 | 70 | 0 | 68 | 0 | 65 | 0 | 1 | 25 | 380 | 45 | 0 | 41 | 0
199
| Minimum Generation |  | 5622 | 5:00
| Highest Generation |  | 9073 | 19:30
| Day Peak Generation |  | 7533 | 12:00
| Evening Peak Generation |  | 9073 | 19:30
| HVDC Max Flow |  | 816 | 18:00
| HVDC EvPeak Flow |  | 811 | 19:30
| Load factor L.F |  | 80.95%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-07
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7533 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5765 | MW
Evening Peak Generation : |  | 9073 | MW Hour : | 19:30 | Available Max Generation : |  | 13150 | MW
E.P. Demand (at gen end) : |  | 9073 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9073 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3950 | MW
Total Gen. (MKWH) : |  | 176.2738 | System Load Factor : | 80.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -24 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-07
Actual : | 97.78 | Ft.(MSL) , | Rule curve : | 101.86 | Ft.( MSL )
Gas Consumed : | Total = | 792.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 110955867.216
: |  | Coal : | 68356472 | Oil : | 307978067.45 | Total : | 487290406.666
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3269.4904 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1106.8889 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 990.8593 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 895.0137 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 808.9826 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 652.8079 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 371.3478 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 168.248 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 503.4476 |  |  | 0 | 0%
Total | 0 |  | 8767.086 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari-Kaptai 132 kV Ckt-2 was under shut down from 08:52 to 16:28 for A/M.
b) Bakulia-Khulsi 132 kV Ckt-1 was under shut down from 08:28 to 15:06 for A/M.
c) Cumilla(N)-Ashuganj 230 kV Ckt-2 was under shut down from 10:02 to 16:21 for A/M.
d) Kaliakoir 400/132 kV TR-2 transformer was under shut down from 08:40 to 15:25 for A/M.
e) Hasnabad 230 kV Bus-2 was under shut down from 08:44 to 13:37 for A/M.
f) Feni-Chowmuhani 132 kV Ckt-2 was under shut down from 09:16 to 16:49 for C/M.
g) Ashuganj-Kishorganj 132 kV Ckt-1 & 2 were under shut down from 08:59 to 17:16 for D/W.
h) Ramganj-Chowmuhani 132 kV Ckt-1 was under shut down from 09:04 to 20:33 for A/M.
i) Kabirpur 132/33 kV T-1 & T-2 were under shut down from 08:33 to 16:58 for D/W.
j) Cox'sbazar 132/33 kV T-3 transformer was under shut down from 08:05 to 11:18 for A/M.
k) Bogura-Mohastanghor 132 kV Ckt-2 was under shut down from 10:17 to 15:05 for A/M.
l) Barisal(N)-Madaripur 132 kV Ckt-2 was under shut down from 08:45 to 14:36 for A/M.
m) Faridpur-Faridpur-150 MW 132 kV Ckt was under shut down from 08:19 to 14:15 for A/M.
n) Bheramara-Kustia 132 kV Ckt-2 was under shut down from 08:50 to 14:15 for A/M.
o) Ishurdi 132/33 kV T-1 transformer was under shut down from 08:28 to 16:40 for A/M.
p) Shahjadpur 132/33 kV T-1 transformer was under shut down from 08:13 to 15:04 for A/M.
q) Baghabari-Shahjadpur 132 kV Ckt-1 was under shut down from 09:36 to 13:56 for A/M.
r) Aminbazar 230/132 kV T-3 transformer was under shut down from 09:58 to 17:48 for A/M.
s) HVDC-Rajshahi 230 kV Ckt-2 was under shut down from 09:22 to 20:33 for D/W.
t) Siddirganj 132 kV main Bus-2 was under shut down from 12:41 to 16:28 for A/M.
u) Kaliakoir-Dhamrai 132 kV Ckt-1 was under shut down from 13:13 to 14:45 for A/M.
v) Pabna 132/33 kV T-1 transformer was under shut down from 16:29 to 10:06(7/1/21) for breaker maint.
w) Kulaura 132/33 kV T-2 transformer was under shut down from 20:33 to 20:57 for red hot maintenance |  |  |  |  | About 9 MW power interruption occurred under Kulaura S/S area
at 33 kV R-phase CT. |  |  |  |  | from 20:33 to 20:57.
x) Ghorasal #4 CCPP ST & GT tripped at 22:15 & 22:19 due to high vibration & problem with excitation.
y) Ashuganj(N)-360 MW CCPP GT & ST was synchronized at 22:52 & 01:47(7/1/21) respectively.
z) Ashuganj #3 was synchronized at 00:05(7/1/21).
aa) Rajshahi(O)-NPSL P/S 132 kV Ckt tripped at 04:11(7/1/21) due to R-phase PT burst at Rajshahi end
ab) Rajshahi(N) 230/132 kV T-1 & T-2 transformers tripped at 04:11(7/1/21) showing E/F & O/C relay
and were switched on at 04:58(7/1/21).
ac) Rajshahi(O)-Natore 132 kV Ckt-1 tripped at 04:11(7/1/21) showing dist.relay at Rajshahi end and
was switched on at 05:02(7/1/21).
ad) Rampura-Gulshan 132 kV Ckt-2 is under shut down since 07:36(7/1/21) for A/M.
ae) Bheramara-Bottail 132 kV Ckt-2 is under shut down since 07:49(7/1/21) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 356 | 4952000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 255 | 7240691 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8803330 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 338 | 7482000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 408000
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 65 | 445800 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 266000 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 87 | 1209174 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 517644
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 55 | 144864 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 558432 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 7 | 33456 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 183960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 811200 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 363357 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 354056
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1089420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 593100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 528800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 76164 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 3916689 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 142 | 728780 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 35 | 252216 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1098240 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 698400 | Low demand
| Dhaka area Total |  |  |  | 6057 | 2577 | 42755773
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 52106 | Reserve.
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 18630
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 691680
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 652000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 22 | 150962 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 20 | 365760 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 433344
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 509280
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 82560 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26160
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 255 | 5612836 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299311
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2130240
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 573 | 12024869
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 69202 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4625000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 35300 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7324000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 382104 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1345440
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1231464
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 101 | 1831636 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2093980
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 1548000 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 441324 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 197820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 1997760
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 32294 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 473930 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 34200 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 1293600 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1197 | 25978381
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2482280 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509364
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 761280
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12300
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 3532800 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 13 | 42000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 264930
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 20 | 297120
| Mymensingh Area Total |  |  |  | 709 | 432 | 7902074
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 45 | 800000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 478680 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 702600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 685584
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1601184 | Unit-9 under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 70 | 1723200 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 182 | 4214440
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 221000 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 184752 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7316500 | Gas shortage
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 91620 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 283 | 7172900 | On test
| Sylhet Area Total |  |  |  | 1988 | 1113 | 25456460
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 811 | 14245818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1875840
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 325 | 7206624 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 212625 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 48000 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1612800
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1356 | 25201707
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 33700 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 517300 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 61 | 1231177
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 11024200 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 56 | 928363 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 54 | 384000 | On test.
| Barisal Area Total |  |  |  | 1676 | 693 | 14118740
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Low demand
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 31520 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4377882 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 336 | 8687727 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 505920
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232038
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 940848
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2017753
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1549920
| Rajshahi Area Total |  |  |  | 2183 | 880 | 18343608
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682700
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 102 | 787200 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22293
| Rangpur Area Total |  |  |  | 605 | 252 | 4492193
| Total |  |  |  | 20748 | 9073 | 176273805
| Eastern Grid Total |  |  |  | 14000 | 5892 | 114117557
| Western Grid Total |  |  |  | 6748 | 3181 | 62156248
| National Grid Total |  |  |  | 20748 | 9073 | 176273805
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-06
| (a) ENTIRE EASTERN GRID : |  | 5832 | MW | (b) ENTIRE WESTERN GRID : |  | 2803 | MW
| i) Dhaka area |  | 3041 | MW | i) Khulna area |  | 1091 | MW
| ii) Chittagong area |  | 991 | MW | ii) Rajshahi area |  | 912 | MW
| iii) Comilla area |  | 745 | MW | iii) Barisal area |  | 223 | MW
| iv) Mymensingh area |  | 739 | MW | iv) Rangpur area |  | 577 | MW
| v) Sylhet area |  | 316 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8635 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 92 | 17:00 | Jamalpur | 82 | 19:30 | Benapol | 38 | 18:30
| Munsiganj | 86 | 20:00 | Sherpur | 98 | 19:00 | Jhenida | 86 | 18:30
| Sonargaon | 57 | 1:00 | Srimongal | 27 | 19:30 | Bottail | 94 | 18:30
| Shyampur | 164 | 12:00 | Shahjibazar | 87 | 18:30 | G.K Project | 36 | 18:30
| Bhulta | 157 | 19:00 | Fenchuganj | 25 | 18:30 | Faridpur | 130 | 18:00
| Madanganj | 40 | 1:00 | Kulawara | 28 | 18:00 | Madaripur | 63 | 20:00
| Shitalakhya | 103 | 12:00 | Sylhet | 74 | 18:00 | Sariatpur | 42 | 19:30
| Rahim steel | 18 | 12:00 | Chatak | 20 | 19:00 | Gopalganj | 59 | 19:00
| Matuail | 48 | 10:00 | Sunamganj | 29 | 20:00 | Bagerhat | 85 | 18:30
| Ghorasal | 57 | 19:00 | Biani Bazar | 38 | 18:30 | Mongla | 40 | 18:00
| Narsingdi | 121 | 20:00 | Comilla (S) | 110 | 18:00 | Satkhira | 76 | 18:30
| Haripur (SBU) | 101 | 8:00 | Comilla(N) | 69 | 19:30 | Gallamari | 22 | 13:00
| Ullon | 40 | 13:00 | Chandpur | 63 | 20:00 | Magura | 38 | 18:30
| Hasnabad | 139 | 19:00 | Feni | 79 | 20:00 | Norail | 24 | 18:30
| Magbazar | 69 | 13:00 | Chowmuhani | 124 | 20:00 | Chuadanga | 65 | 18:30
| Maniknagar | 72 | 13:00 | Ashuganj | 38 | 19:00 | Barisal(N) | 29 | 19:00
| Bangabhaban | 17 | 12:00 | Daudkandi | 88 | 19:00 | Barisal (S) | 72 | 19:00
| Narinda | 68 | 14:00 | B.Baria | 98 | 19:30 | Patuakhali | 77 | 18:00
| Dhanmondi | 102 | 13:00 | Ramganj | 72 | 23:00 | Bhandaria | 40 | 18:30
| Lalbag | 72 | 18:30 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 19:00
| Madartek | 45 | 19:00 | PHP | 9 | 5:00 | Ishurdi | 47 | 19:00
| Dhaka University | 0 | #NUM! | Madunaghat | 45 | 18:30 | Ruppur Paromanobik | 3 | 15:00
| Aftabnagar | 6 | 0.5 | Hathazari | 65 | 0.79167 | Natore | 82 | 0.79167
| Fatullah | 47 | 10:00 | Khulshi | 167 | 17:00 | Bogra | 118 | 19:00
| Mirpur | 71 | 18:00 | Halishahar | 98 | 18:00 | Noagaon | 74 | 19:00
| Kalyanpur | 63 | 18:00 | Baraulia | 145 | 9:00 | Rajshahi | 96 | 19:00
| Gulshan | 80 | 13:00 | Sikalbaha | 22 | 18:30 | Rajshahi New | 10 | 19:30
| Uttara | 69 | 18:00 | Dohazari | 54 | 19:30 | C.Nawabganj | 51 | 18:30
| Uttara New | 22 | 15:00 | Cox'sbazar | 62 | 21:00 | Amnura | 30 | 20:00
| Kamrangirchar | 70 | 18:00 | Chandraghona | 20 | 18:30 | Pabna | 78 | 18:30
| Savar | 100 | 18:00 | Kaptai | 3.6 | 18:00 | Shahjadpur | 81 | 19:30
| Bhasantec | 106 | 14:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 86 | 19:30
| Agargaon | 48 | 13:00 | Bakulia | 75 | 18:00 | Niyamatpur | 67 | 19:00
| Satmosjid | 67 | 0.54167 | Julda | 18 | 0.041667 | Joypurhat | 42 | 0.83333
| Tongi | 58 | 12:00 | TK chemical | 19.3 | 18:30 | Sherpur(Bogura) | 37 | 18:30
| Kabirpur | 178 | 16:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 89 | 18:00 | Shahmirpur | 20.4 | 18:00 | Rangpur | 117 | 18:30
| Manikganj | 44 | 20:00 | Khagrachhari | 20 | 3:00 | Lalmonirhat | 46 | 18:30
| Joydevpur | 101 | 18:00 | Matarbari | 27 | 18:00 | Saidpur | 79 | 18:00
| New Tongi | 99 | 18:00 | Baroiar Hat | 26 | 18:00 | Purbasadipur | 80 | 18:30
| Kodda | 174 | 12:00 | Rangamati | 8 | 12:00 | Thakurgaon | 59 | 18:30
| Dhamrai | 76 | 18:00 | Abul Khair 230 | 136 | 1:00 | Palashbari | 92 | 18:00
| Rajendrapur | 78 | 19:30 | BSRM | 154 | 19:30 | Barapukuria | 38 | 18:30
| Valuka | 86 | 12:00 | GPH Ispat | 84 | 2:00 | Panchagar | 42 | 18:30
| Tangail | 142 | 19:30 | Goalpara | 16 | 21:00 | Joldhaka | 24 | 18:00
| Mymensing | 170 | 18:00 | Central s/s | 78 | 18:30 | Kurigram | 40 | 19:00
| Kishorganj | 88 | 19:30 | Noapara | 52 | 19:00
| Netrokona | 102 | 18:30 | Jessore | 78 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 414 | 7:00 | 406 | 11:00 | Kaliakoir | 387 | 0.20833 | 367 | 0.5
| Bheramara | 415 | 3:00 | 397 | 13:00 | Bhulta | 382 | 0.79167 | 362 | 0.45833
| Ashuganj(N) | 381 | 5:00 | 367 | 10:00 | Gopalganj | 408 | 0.66667 | 395 | 0.77083
| Payra | 414 | 18:00 | 405 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 230 | 15:00 | Comilla (N) | 235 | 18:00 | 224 | 11:00
| Ishurdi | 241 | 3:00 | 227 | 7:00 | Hathazari | 223 | 19:00 | 206 | 15:00
| Ashuganj | 236 | 19:00 | 230 | 9:00 | Megnaghat | 230 | 18:00 | 221 | 11:00
| Serajganj | 234 | 14:00 | 229 | 21:00 | Fenchuganj | 243 | 17:00 | 236 | 10:00
| Baghabari | 246 | 4:00 | 240 | 11:00 | Siddhirganj | 229 | 20:00 | 219 | 11:00
| Barapukuria | 232 | 3:00 | 227 | 8:00 | Maniknagar | 227 | 19:00 | 218 | 11:00
| Bogra | 236 | 14:00 | 228 | 8:00 | Agargaon | 227 | 4:00 | 216 | 11:00
| Rajshahi | 232 | 2:00 | 224 | 8:00 | Barisal | 250 | 19:00 | 246 | 7:00
| Khulna South | 244 | 2:00 | 233 | 18:30 | AKSML | 226 | 19:00 | 207 | 15:00
| Rampura | 228 | 18:00 | 221 | 10:00 | BSRM | 227 | 18:00 | 211 | 15:00
| Haripur | 226 | 18:00 | 217 | 11:00 | Bibiyana | 245 | 19:00 | 238 | 9:00
| Hasnabad | 227 | 18:00 | 218 | 11:00 | Bhulta | 231 | 19:00 | 220 | 17:00
| Shyampur | 227 | 18:00 | 220 | 10:00 | Ashuganj (S) | 233 | 18:00 | 227 | 10:00
| Aminbazar | 228 | 19:00 | 216 | 11:00 | Kaliakoir | 225 | 17:00 | 215 | 9:00
| Tongi | 225 | 18:00 | 212 | 11:00 | GPH | 223 | 17:00 | 203 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 18:00 | 130 | 10:00 | Madanhat | 137 | 0.75 | 129 | 0.5
| Munsiganj | 139 | 19:00 | 129 | 10:00 | Hathazari | 136 | 0.79167 | 128 | 0.625
| Sonargaon | 135 | 20:00 | 130 | 1:00 | Khulshi | 134 | 0.79167 | 124 | 0.625
| Shyampur | 130 | 19:00 | 123 | 10:00 | Halishahar | 135 | 0.20833 | 128 | 0.29167
| Bhulta | 130 | 18:00 | 124 | 12:00 | Baraulia | 135 | 0.75 | 125 | 0.625
| Madanganj | 139 | 19:30 | 128 | 11:00 | Sikalbaha | 136 | 0.75 | 126 | 0.625
| Shitalakhya | 141 | 14:00 | 129 | 10:00 | Dohazari | 136 | 0.75 | 125 | 0.5
| Rahim steal | 137 | 18:00 | 130 | 11:00 | Cox'sbazar | 131 | 0.375 | 120 | 0.54167
| Matuail | 137 | 18:00 | 130 | 10:00 | Chandraghona | 136 | 0.75 | 128 | 0.66667
| Ghorasal | 138 | 1:00 | 135 | 15:00 | Kaptai | 135 | 0.20833 | 131 | 0.41667
| Narsinghdi | 136 | 18:00 | 128 | 12:00 | A. Khaer Stl. | 133 | 0.79167 | 126 | 0.54167
| Haripur (SBU) | 138 | 18:00 | 132 | 9:00 | Bakulia | 135 | 0.77083 | 126 | 0.66667
| Ullon | 130 | 3:00 | 124 | 11:00 | Julda | 135 | 0.29167 | 125 | 0.58333
| Hasnabad | 136 | 3:00 | 130 | 10:00 | TK Chemical | 138 | 0.77083 | 130 | 0.5
| Magbazar | 132 | 2:00 | 123 | 12:00 | Modern Steel | 133 | 0.375 | 129 | 0.66667
| Maniknagar | 136 | 20:00 | 130 | 10:00 | Shahmirpur | 135 | 0.375 | 129 | 0.5
| Bangabhaban | 136 | 20:00 | 130 | 10:00 | Khagrachhari | 134 | 0.125 | 127 | 0.66667
| Narinda | 136 | 20:00 | 130 | 10:00 | Matarbari | 132 | 0.375 | 119 | 0.625
| Dhanmondi | 130 | 3:00 | 124 | 11:00 | Baroiar Hat | 137 | 0.79167 | 130 | 0.625
| Lalbag | 129 | 3:00 | 120 | 12:00 | Rangamati | 135 | 18:00 | 127 | 15:00
| Madartek | 130 | 3:00 | 124 | 10:00 | Goalpara S/S | 139 | 14:00 | 133 | 18:30
| Dhaka University | 130 | 3:00 | 124 | 10:00 | Khulna Central S/S | 139 | 22:00 | 129 | 0.29167
| Aftabnagar | 131 | 19:00 | 123 | 11:00 | Noapara | 136 | 13:00 | 130 | 0.77083
| Fatuiiah | 130 | 19:00 | 124 | 10:00 | Jessore | 134 | 23:00 | 125 | 0.77083
| Mirpur | 129 | 21:00 | 124 | 11:00 | Benapol | 133 | 0.083333 | 126 | 0.77083
| Kalyanpur | 131 | 19:00 | 124 | 12:00 | Jhenida | 133 | 4:00 | 123 | 0.77083
| Gulshan | 129 | 20:00 | 123 | 11:00 | Bottail | 136 | 0.16667 | 130 | 0.5
| Uttara | 130 | 20:00 | 122 | 11:00 | G.K Project | 141 | 0.083333 | 138 | 0.33333
| Uttara New | 138 | 18:30 | 127 | 12:00 | Faridpur | 137 | 0.125 | 131 | 0.33333
| Kamrangirchar | 140 | 19:00 | 130 | 11:00 | Madaripur | 142 | 0.25 | 138 | 0.8125
| Savar | 131 | 20:00 | 122 | 10:00 | Shariyatpur S/S | 140 | 3:00 | 136 | 0.77083
| Bhasantec | 132 | 3:00 | 124 | 11:00 | Gopalganj | 141 | 0.5 | 135 | 0.79167
| Agargaon | 133 | 3:00 | 126 | 11:00 | Bagerhat | 140 | 9:00 | 131 | 0.20833
| Satmosjid | 133 | 3:00 | 124 | 11:00 | Mongla | 138 | 14:00 | 126 | 0.29167
| Tongi | 139 | 19:00 | 129 | 12:00 | Satkhira | 137 | 15:00 | 131 | 18:30
| Kabirpur | 137 | 5:00 | 125 | 11:00 | Gallamari | 138 | 0.875 | 132 | 0.79167
| Basundhara | 137 | 2:00 | 126 | 16:00 | Magura | 135 | 3:00 | 123 | 0.77083
| Manikganj | 143 | 7:00 | 131 | 15:00 | Norail | 131 | 0.16667 | 122 | 0.77083
| Joydevpur | 142 | 18:00 | 134 | 17:00 | Chuadanga | 131 | 3:00 | 119 | 0.77083
| New Tongi | 138 | 19:30 | 127 | 12:00 | Barisal(N) | 142 | 9:00 | 138 | 21:00
| Kodda | 138 | 18:30 | 126 | 23:00 | Barisal (S) | 141 | 0.375 | 138 | 0.75
| Dhamrai | 137 | 20:00 | 124 | 9:00 | Patuakhali(S) | 139 | 0.66667 | 135 | 0.95833
| Rajendrapur | 137 | 20:00 | 129 | 11:00 | Bhandaria | 140 | 0.375 | 135 | 0.77083
| Valuka | 129 | 14:00 | 121 | 7:00 | Ishurdi | 139 | 1:00 | 135 | 18:30
| Tangail | 134 | 17:00 | 126 | 9:00 | Ruppur Paromanobik | 138 | 1:00 | 135 | 11:00
| Mymensing | 131 | 14:00 | 123 | 7:00 | Natore | 139 | 1:00 | 133 | 10:00
| Kishorganj | 131 | 13:00 | 126 | 21:00 | Bogra | 139 | 14:00 | 134 | 8:00
| Netrokona | 129 | 13:00 | 120 | 3:00 | Noagaon | 134 | 3:00 | 130 | 18:30
| Jamalpur | 139 | 10:00 | 125 | 6:00 | Rajshahi | 140 | 1:00 | 130 | 10:00
| Sherpur | 138 | 10:00 | 122 | 6:00 | Rajshahi New | 142 | 2:00 | 129 | 12:00
| Srimongal | 136 | 1:00 | 135 | 12:00 | C.Nawabganj | 138 | 19:30 | 128 | 12:00
| Shahjibazar | 135 | 14:00 | 133 | 1:00 | Amnura | 141 | 3:00 | 129 | 10:00
| Fenchuganj | 138 | 18:00 | 135 | 5:00 | Pabna | 138 | 1:00 | 134 | 7:00
| Khulawara | 137 | 17:00 | 135 | 1:00 | Shahjadpur | 140 | 1:00 | 137 | 11:00
| Sylhet | 136 | 18:00 | 133 | 11:00 | Serajganj | 136 | 18:00 | 134 | 16:00
| Chatak | 135 | 22:00 | 132 | 11:00 | Niyamatpur | 134 | 14:00 | 124 | 8:00
| Sunamganj | 134 | 3:00 | 132 | 9:00 | Joypurhat | 136 | 1:00 | 129 | 8:00
| Biani Bazar | 136 | 24:00 | 133 | 10:00 | Sherpur(Bogura) | 139 | 14:00 | 134 | 10:00
| Comilla(s) | 130 | 1:00 | 125 | 12:00 | Mohastangor | 138 | 1:00 | 131 | 8:00
| Comilla(n) | 141 | 19:00 | 133 | 12:00 | Rangpur | 130 | 14:00 | 123 | 8:00
| Chandpur | 143 | 7:00 | 140 | 11:00 | Lalmonirhat | 130 | 4:00 | 123 | 18:00
| Feni | 138 | 18:00 | 130 | 12:00 | Saidpur | 131 | 5:00 | 124 | 18:00
| Chowmuhani | 137 | 18:00 | 134 | 10:00 | Purbasadipur | 130 | 3:00 | 121 | 8:00
| Ashuganj | 136 | 17:00 | 134 | 0:00 | Thakurgaon | 129 | 4:00 | 115 | 18:00
| Daudkandi | 138 | 18:00 | 131 | 10:00 | Palashbari | 135 | 14:00 | 128 | 8:00
| B.Baria | 133 | 14:00 | 130 | 21:00 | Barapukuria | 132 | 3:00 | 127 | 8:00
| Ramganj | 137 | 19:00 | 135 | 16:00 | Panchagar | 130 | 3:00 | 114 | 18:00
| Chaddagram | 139 | 19:00 | 133 | 12:00 | Joldhaka | 129 | 4:00 | 121 | 18:00
| PHP | 138 | 18:00 | 129 | 12:00 | Kurigram | 131 | 0.58333 | 121 | 0.33333

## L-Curve
Date | 2021-01-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 451 | 4437 | 2561 | 6998 |  |  |  | QF-LDC-11
0:30 | 352.5 | 4325.5 | 2368.5 | 6694 | Date: | 2021-01-06
1:00 | 254 | 4214 | 2176 | 6390
1:30 | 251.5 | 4135.5 | 2100.5 | 6236
2:00 | 249 | 4057 | 2025 | 6082
2:30 | 260.5 | 3986 | 2011 | 5997 | [5 empty] | Gen. at Eve. Peak | 9073 | 9073 MW (19:30 )
3:00 | 272 | 3915 | 1997 | 5912 | [6 empty] | 19:30
3:30 | 269 | 3804.5 | 1981 | 5785.5 | [5 empty] | Gen. at Day Peak | 7533 | 7533 MW (12:00 )
4:00 | 266 | 3694 | 1965 | 5659 | [6 empty] | 12:00
4:30 | 262 | 3685 | 1955.5 | 5640.5 | [5 empty] | Highest Generation | 9073
5:00 | 258 | 3676 | 1946 | 5622 | [6 empty] | 19:30
5:30 | 265.5 | 3734.5 | 1966 | 5700.5
6:00 | 273 | 3793 | 1986 | 5779
6:30 | 229.5 | 3922 | 2062.5 | 5984.5
7:00 | 186 | 4051 | 2139 | 6190
7:30 | 105 | 4166 | 2301 | 6467
8:00 | 24 | 4281 | 2463 | 6744
8:30 | 227 | 4453 | 2515 | 6968
9:00 | 430 | 4625 | 2567 | 7192
9:30 | 471.5 | 4625 | 2576 | 7201
10:00 | 513 | 4625 | 2585 | 7210
10:30 | 486.5 | 4716.5 | 2558.5 | 7275
11:00 | 460 | 4808 | 2532 | 7340
11:30 | 402.5 | 4894 | 2542.5 | 7436.5
12:00 | 345 | 4980 | 2553 | 7533
12:30 | 318.5 | 5007 | 2577 | 7584
13:00 | 292 | 5034 | 2601 | 7635
13:30 | 365 | 4939 | 2562.5 | 7501.5
14:00 | 438 | 4844 | 2524 | 7368
14:30 | 489 | 4779 | 2492 | 7271
15:00 | 540 | 4714 | 2460 | 7174
15:30 | 536 | 4741.5 | 2411 | 7152.5
16:00 | 532 | 4769 | 2362 | 7131
16:30 | 463 | 4805.5 | 2380.5 | 7186
17:00 | 394 | 4842 | 2399 | 7241
17:30 | 271.5 | 5275 | 2689.5 | 7964.5
18:00 | 149 | 5708 | 2980 | 8688
18:30 | 182.5 | 5817 | 3053.5 | 8870.5
19:00 | 216 | 5926 | 3127 | 9053
19:30 | 226 | 5892 | 3181 | 9073
20:00 | 192 | 5898 | 3129 | 9027 |  |  |  | Executive Engineer
20:30 | 281 | 5730 | 3153 | 8883 |  |  |  | Network Operation Division
21:00 | 370 | 5562 | 3177 | 8739
21:30 | 414 | 5407.5 | 3083.5 | 8491
22:00 | 458 | 5253 | 2990 | 8243 |  |  |  |  | Page 6 of 7
22:30 | 475 | 4998.5 | 2932 | 7930.5
23:00 | 492 | 4744 | 2874 | 7618
23:30 | 471.5 | 4590.5 | 2717.5 | 7308
24:00 | 451 | 4437 | 2561 | 6998
9073 MW (19:30 )
7533 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-06 |  | Energy | 176273805
[11 empty] | 2021-01-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2838 | 624 | 1406 | 1687 | 590 | 35 | 8 | 0 | 84 | 0
0:30 | 2893.5 | 529 | 1373.5 | 1311.5 | 600 | 40.5 | 4 | 0 | 79 | 0 | Date: | 2021-01-06
1:00 | 2949 | 434 | 1341 | 936 | 610 | 46 | 0 | 0 | 74 | 0
1:30 | 2933 | 433.5 | 1351.5 | 789 | 610 | 46 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 176.2738 | Total Energy Gen 176.274 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.274 MKWHr
2:00 | 2917 | 433 | 1362 | 642 | 610 | 46 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2873.5 | 433 | 1343 | 619 | 610 | 46.5 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 176.2738
3:00 | 2830 | 433 | 1324 | 596 | 610 | 47 | 0 | 0 | 72 | 0
3:30 | 2826 | 433 | 1324 | 475.5 | 610 | 47 | 0 | 0 | 70 | 0 | [6 empty] | Shortage
4:00 | 2822 | 433 | 1324 | 355 | 610 | 47 | 0 | 0 | 68 | 0
4:30 | 2834.5 | 433 | 1336.5 | 355 | 590 | 23.5 | 0 | 0 | 68 | 0
5:00 | 2847 | 433 | 1349 | 355 | 570 | 0 | 0 | 0 | 68 | 0
5:30 | 2889 | 433.5 | 1362.5 | 359 | 570 | 17.5 | 0 | 0 | 69 | 0
6:00 | 2931 | 434 | 1376 | 363 | 570 | 35 | 0 | 0 | 70 | 0
6:30 | 2964.5 | 433.5 | 1399 | 500.5 | 570 | 35 | 12.5 | 0 | 69 | 0.5 |  |  |  |  | Coal
7:00 | 2998 | 433 | 1422 | 638 | 570 | 35 | 25 | 0 | 68 | 1
7:30 | 2972.5 | 480.5 | 1430 | 837.5 | 590 | 35 | 42 | 0 | 71 | 8.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2947 | 528 | 1438 | 1037 | 610 | 35 | 59 | 0 | 74 | 16
8:30 | 2936 | 528.5 | 1366 | 1343 | 580.5 | 35 | 79 | 0 | 77 | 23
9:00 | 2925 | 529 | 1294 | 1649 | 551 | 35 | 99 | 0 | 80 | 30
9:30 | 2851.5 | 552 | 1261.5 | 1735 | 550.5 | 35 | 99 | 0 | 80 | 36.5
10:00 | 2778 | 575 | 1229 | 1821 | 550 | 35 | 99 | 0 | 80 | 43
10:30 | 2829.5 | 577 | 1226.5 | 1831 | 550 | 35 | 99 | 0 | 80 | 47
11:00 | 2881 | 579 | 1224 | 1841 | 550 | 35 | 99 | 0 | 80 | 51
11:30 | 2939 | 579 | 1231 | 1878 | 540 | 35 | 99 | 0 | 84 | 51.5
12:00 | 2997 | 579 | 1238 | 1915 | 530 | 35 | 99 | 0 | 88 | 52
12:30 | 2921.5 | 579 | 1248 | 2020 | 525 | 35 | 116 | 0 | 88 | 51.5
13:00 | 2846 | 579 | 1258 | 2125 | 520 | 35 | 133 | 0 | 88 | 51
13:30 | 2846 | 579 | 1258 | 2125 | 520 | 35 | 133 | 0 | 88 | 51
14:00 | 2846 | 579 | 1258 | 2125 | 520 | 35 | 133 | 0 | 88 | 51
14:30 | 2752.5 | 578.5 | 1262 | 1997.5 | 520 | 35 | 124 | 0 | 89 | 46
15:00 | 2659 | 578 | 1266 | 1870 | 520 | 35 | 115 | 0 | 90 | 41
15:30 | 2698 | 574.5 | 1276 | 1816 | 520 | 35 | 115 | 0 | 88 | 30
16:00 | 2737 | 571 | 1286 | 1762 | 520 | 35 | 115 | 0 | 86 | 19
16:30 | 2717 | 574.5 | 1308.5 | 1810 | 520 | 35 | 125 | 0 | 86 | 10
17:00 | 2697 | 578 | 1331 | 1858 | 520 | 35 | 135 | 0 | 86 | 1
17:30 | 2769 | 697 | 1357.5 | 2267.5 | 545 | 35 | 195 | 0 | 98 | 0.5
18:00 | 2841 | 816 | 1384 | 2677 | 570 | 35 | 255 | 0 | 110 | 0
18:30 | 2907 | 813.5 | 1409.5 | 2756 | 594.5 | 35 | 247 | 0 | 108 | 0
19:00 | 2973 | 811 | 1435 | 2835 | 619 | 35 | 239 | 0 | 106 | 0
19:30 | 3093 | 811 | 1443 | 2807 | 630 | 35 | 148 | 0 | 106 | 0
20:00 | 3121 | 811 | 1441 | 2760 | 620 | 35 | 131 | 0 | 108 | 0
20:30 | 3146.5 | 811 | 1499.5 | 2554 | 620.5 | 35 | 110.5 | 0 | 106 | 0
21:00 | 3172 | 811 | 1558 | 2348 | 621 | 35 | 90 | 0 | 104 | 0
21:30 | 3153 | 811 | 1542 | 2161.5 | 621 | 35 | 66.5 | 0 | 101 | 0
22:00 | 3134 | 811 | 1526 | 1975 | 621 | 35 | 43 | 0 | 98 | 0
22:30 | 2994 | 812 | 1505 | 1831 | 615.5 | 35 | 43 | 0 | 95 | 0
23:00 | 2854 | 813 | 1484 | 1687 | 610 | 35 | 43 | 0 | 92 | 0
23:30 | 2846 | 718.5 | 1445 | 1687 | 600 | 35 | 25.5 | 0 | 88 | 0 | Max Temp. in Dhaka |  | 30° C
24:00 | 2838 | 624 | 1406 | 1687 | 590 | 35 | 8 | 0 | 84 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 176.274 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.274 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 47 | 47
2 | Karnaphuli Hydro PP Unit-4 & 5 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 652000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 21 |  | 25 | [5 empty] | 0 | 52106
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 4 | [6 empty] | 11 | 6 | [10 empty] | 18630
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 77 |  | 61 | 22 | 5 |  |  |  |  | 150962
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 50 | [5 empty] | 2 | 40 | 131 | 198 | 200 | 205 | 245 | 280 | 250 | 250 | 250 | 265 |  | 280 | 280 | 280 | 280 | 250 | 145 | 145 | 3916689
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 109 | 105 | 104 | 104 | 101 | 101 | 103 | 97 | 103 | 106 | 174 | 264 | 327 | 328 | 330 | 368 | 365 | 381 |  | 252 | 356 | 380 | 375 | 384 | 30 | 40 | 4952000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 255 | 255 | 255 | 235 |  | 255 | 255 | 255 | 255 | 255 | 340 | 340 | 7240691
26
28 | Ashuganj TPP Unit- 3 | [25 empty] | 0 | 69202
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 13 | 26 | 26 | 26 | 26 | 26 | 23 | 23 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 382104
33 | Ashuganj 225 MW CCPP | 195 | 184 | 183 | 183 | 183 | 209 | 217 | 201 | 190 | 193 | 230 | 184 | 186 | 184 | 188 | 185 | 185 | 184 |  | 184 | 184 | 184 | 194 | 184 | 184 | 184 | 4625000
34 | Ashuganj 450 MW CCPP(South) | 285 | 280 | 275 | 275 | 280 | 320 | 345 | 330 | 290 | 285 | 270 | 270 | 265 | 270 | 355 | 360 | 315 | 315 |  | 310 | 315 | 315 | 325 | 315 | 300 | 275 | 7324000
| Ashuganj 450 MW CCPP(North) | [24 empty] | 20 | 20 | 35300
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1345440
36 | Chandpur 150 MW CCPP | 91 | 89 | 81 | 91 | 91 | 91 | 91 | 88 | 82 | 84 | 89 | 92 | 90 | 81 | 90 | 90 | 89 | 90 |  | 81 | 91 | 88 | 90 | 90 | 86 | 82 | 2093980
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 357 | 356 | 349 | 351 | 353 | 370 | 406 | 410 | 373 | 351 | 353 | 353 | 356 | 353 | 370 | 357 | 363 | 353 |  | 366 | 350 | 351 | 360 | 353 | 355 | 348 | 8803330
40 | Meghnaghat 450 MW CCPP(MPL) | [25 empty] | 0
41 | Haripur 360MW CCPP(HPL) | 310 | 353 | 353 | 353 | 353 | 353 | 353 | 356 | 309 | 279 | 311 | 310 | 275 | 245 | 242 | 242 | 242 | 261 |  | 358 | 338 | 338 | 338 | 338 | 354 | 320 | 7482000
42 | RPCL 210MW CCPP | 108 | 107 | 108 | 109 | 107 | 107 | 108 | 108 | 107 | 106 | 106 | 103 | 103 | 103 | 100 | 102 | 103 | 104 |  | 106 | 105 | 106 | 105 | 108 | 107 | 107 | 2482280
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 25 | 35 | 41 | 42 | 42 | 35 | 25 | 11 | 1 | [9 empty] | 264930
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 33 | 40 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 30 | 30 | 800000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478680
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 70 | 70 | 69 | 68 | 68 | 68 | 67 | 66 | 65 | 61 | 61 | 61 | 62 | 62 | 67 | 68 |  | 69 | 68 | 69 | 69 | 69 | 69 | 69 | 1601184
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 72 | 72 | 73 | 73 | 74 | 73 | 72 | 71 | 71 | 71 | 71 | 70 | 70 | 70 | 71 |  | 73 | 70 | 73 | 70 | 72 | 73 | 74 | 1723200
| Shahjibazar 100 MW GTPP | [26 empty] | 0
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 144 | 145 | 144 | 169 | 169 | 150 | 150 | 150 | 150 |  | 182 | 182 | 182 | 216 | 215 | 216 | 216 | 4214440
51 | Sylhet 20 MW GTPP | [11 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 221000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [11 empty] | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 7 | 7 | 9 | 9 | 91620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 50 | 53 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 702600
56 | Shahjahanulla 25 MW PP | [11 empty] | 14 | 14 | 14 | 14 | 15 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 184752
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 290 | 290 | 310 | 310 | 330 | 330 | 310 | 280 | 280 | 270 | 260 | 260 | 260 | 290 | 300 | 270 |  | 290 | 290 | 290 | 310 | 300 | 290 | 280 | 7316500
| Bibiyana South 400 MW | 427 | 427 | 360 | 360 | 360 | 360 | 360 | 360 | 427 | 427 | 427 | 421 | 182 | 30 | 30 | 80 | 80 | 278 |  | 285 | 283 | 285 | 282 | 270 | 270 | 270 | 7172900
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 8 | 17 | 17 | 17 | 17 | 20 | 35 |  | 55 | 55 | 55 | 17 |  |  | 0 | 354056
59 | Tangail Palli Power Gen 22 MW | [8 empty] | 1 | 22 | 21 | 21 | 25 | 25 | 24 | 20 | 15 | 14 |  | 18 | 20 | 22 | 24 | 24 |  | 14 | 297120
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433344
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 517644
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509364
63 | Impoprt (Tripura) | 74 | 72 | 72 | 68 | 68 | 70 | 68 | 74 | 80 | 80 | 80 | 88 | 88 | 90 | 90 | 86 | 86 | 110 |  | 106 | 106 | 108 | 104 | 98 | 92 | 84 | 1997760
64 | Malancha, Ctg. EPZ (United) | 36 | 42 | 42 | 42 | 42 | 42 | 34 | 7 | 6 | 5 | 4 | 4 | 2 | 2 | 2 | 2 | 5 | 7 |  | 16 | 20 | 26 | 26 | 35 | 40 | 34 | 509280
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 441324
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  |  |  |  | 5 | 5 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 197820
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820600
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 473930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 28 | 28 | 24 | 24 | 16 | 16 | 16 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 489420
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 593100
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 |  | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 528800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 34 | [7 empty] | 0 | 34200
| Chowmuhani 113 MW | 36 | 36 | [5 empty] | 8 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 73 | 107 | 106 | 108 | 107 | 84 | 36 | 1293600
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 698400
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 26 |  | 50 | 55 | 60 |  |  |  | 0 | 144864
78 | Gazipur 52 MW PP | [17 empty] | 46 | [8 empty] | 76164
79 | Kodda 150MW PP | [6 empty] | 25 | 32 | 48 | 48 | 48 | 48 | 82 | 82 | 64 | 64 | 84 | 84 |  | 84 | 32 | 32 | 16 |  |  | 0 | 811200
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 22 | 61 | 72 | 72 | 72 | 48 | 32 | 32 | 32 | 44 |  | 89 | 90 | 90 | 49 |  |  | 0 | 761280
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 14 |  | 16 | [6 empty] | 32294
| Gazipur 100 MW PP | [16 empty] | 2 | 100 |  | 70 | 35 | 35 |  |  |  | 0 | 252216
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299311
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [11 empty] | 12 | 15 | 25 | 15 | 15 | 15 | 35 |  | 64 | 65 | 64 | 52 | 30 | 30 | 15 | 445800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [5 empty] | 3 | 20 | 29 | 57 | 56 | 60 | 67 | 70 | 60 | 60 | 60 | 61 | 62 |  | 87 | 87 | 86 | 85 | 86 | 81 | 60 | 1209174
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 1 | 24 | 24 | 24 | 28 | 50 |  | 54 | 100 | 97 | 68 |  |  | 0 | 408000
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 7 | 21 | 53 | 53 | 53 | 53 | 61 | 75 | 53 | 53 | 53 | 69 |  | 90 | 90 | 90 | 90 | 90 | 59 | 53 | 1098240
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 18 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 685584
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1231464
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 24 | 32 | 65 | 65 | 65 | 40 | 50 | 58 |  | 58 | 58 | 58 | 16 | 16 | 16 | 0 | 558432
95 | Patenga 50MW PP (Baraka) | 25 | [5 empty] | 9 | 18 | 33 | 40 | 40 | 41 | 43 | 40 | 40 | 40 | 41 | 46 |  | 48 | 50 | 50 | 25 | 25 | 25 | 25 | 691680
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 56 |  | 18 | [5 empty] | 0 | 82560
97 | katpotti 52 MW | [17 empty] | 7 |  | 12 | 7 |  |  |  |  | 0 | 33456
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 24 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 2 | 15 | 15 | 15 | 0 | 266000
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 363357
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12300
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 54 |  | 54 | 54 | 54 |  |  |  | 0 | 183960
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 70 | 70 | 35 | 35 | 35 | 43 | 117 | 190 | 190 | 194 | 184 | 194 | 194 | 194 | 194 | 194 | 194 |  | 182 | 182 | 185 | 185 | 180 | 180 | 65 | 3532800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 30 | 32 | 32 | 32 | 32 | 17 | 16 | 19 | 62 |  | 137 | 142 | 141 | 115 | 46 |  | 0 | 728780
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 40 | 40 | 10 | 10 | 40 | 40 | 10 | 10 | 10 | 50 |  | 50 | 20 | 20 | 20 | 20 |  | 0 | 365760
116 | Chandpur 200MW (Desh energy) | 100 | 70 | 70 | 69 | 69 | 69 | 68 | 68 | 68 | 50 | 34 | 34 | 42 | 50 | 50 | 50 | 50 | 50 |  | 64 | 68 | 68 | 68 | 68 | 68 | 68 | 1548000
117 | Ashuganj 150MW PP (Midland) | 50 | 10 |  |  |  | 1 | 33 | 68 | 100 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 1831636
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 13 |  | 16 | 13 |  |  |  |  | 0 | 42000
| Anwara 300 MW PP (United) | 253 | 253 | 253 | 160 | 160 | 160 | 196 | 234 | 268 | 268 | 268 | 271 | 272 | 213 | 180 | 180 | 220 | 265 |  | 255 | 255 | 255 | 253 | 253 | 269 | 270 | 5612836
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 20 | 20 | 20 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2130240
| Anlima Energy Ltd. | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4214 | 4057 | 3915 | 3694 | 3676 | 3793 | 4051 | 4281 | 4625 | 4625 | 4808 | 4980 | 5034 | 4844 | 4714 | 4769 | 4842 | 5708 |  | 5926 | 5892 | 5898 | 5562 | 5253 | 4744 | 4437 | 114117557
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 66 | 32 | 32 |  |  |  | 32 | 83 | 89 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 115 | 115 | 115 | 115 | 115 | 115 | 99 | 1875840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | [5 empty] | 17 | 35 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 53 | 53 | 105 |  | 105 | 105 | 105 | 105 | 105 | 90 | 53 | 1612800
130
131
132 | United Payra Power Ltd. | [17 empty] | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 384000
133 | Bhola Nutan Biddut BD LTD (GAS) | 28 | 28 | 27 | 28 | 27 | 17 | 9 | 21 | 21 | 21 | 21 | 30 | 29 | 53 | 27 | 29 | 48 | 55 |  | 55 | 56 | 56 | 57 | 57 | 64 | 61 | 928363
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 |  |  |  |  | 0 | 33700
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 60 | 62 | 62 | 60 |  | 61 | 61 | 61 | 61 | 61 | 32 | 31 | 1231177
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 24 | 22 | 22 | 20 | 21 | 22 | 21 | 21 | 18 | 19 | 20 | 20 | 21 | 21 | 20 | 19 | 20 | 25 |  | 26 | 26 | 27 | 27 | 27 | 25 | 24 | 517300
141 | Noapara 100 MW PP (Bangla Trac) | [8 empty] | 34 | [16 empty] | 0 | 48000
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 40 | 40 | 16 |  |  | 40 | 40 | 40 | [10 empty] | 0 | 212625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 434 | 433 | 433 | 433 | 433 | 434 | 433 | 528 | 529 | 575 | 579 | 579 | 579 | 579 | 578 | 571 | 578 | 816 |  | 811 | 811 | 811 | 811 | 811 | 813 | 624 | 14245818
147 | Bheramara 410 MW CCPP | 295 | 295 | 295 | 295 | 310 | 320 | 315 | 300 | 300 | 295 | 285 | 290 | 285 | 285 | 250 | 250 | 250 | 200 |  | 330 | 325 | 325 | 320 | 310 | 305 | 310 | 7206624
148 | Payra 1320 MW | 460 | 460 | 460 | 460 | 420 | 420 | 420 | 460 | 400 | 400 | 400 | 380 | 370 | 370 | 370 | 370 | 370 | 420 |  | 470 | 480 | 470 | 470 | 470 | 460 | 440 | 11024200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 149 | 150 | 150 | 151 | 151 | 150 | 150 | 3682700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 195 | 150 | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 130 |  | 162 | 180 | 180 | 180 | 180 | 185 | 193 | 4377882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 389 | 363 | 336 | 337 | 343 | 377 | 422 | 416 | 344 | 340 | 306 | 318 | 330 | 292 | 342 | 327 | 338 | 389 |  | 310 | 336 | 323 | 423 | 390 | 358 | 337 | 8687727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 21 | 21 | 505920
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 232038
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 12 |  |  |  |  | 0 | 31520
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 27 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 94 |  | 94 | 94 | 94 | 74 | 43 | 43 | 8 | 940848
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 |  |  |  |  | 4 | 55 | 70 | 87 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2017753
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 25 | 35 | 70 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 113 |  | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 1549920
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 35 | 40 | 42 | 58 | 70 | 70 | 36 | 35 | 35 | 97 |  | 99 | 102 | 99 | 70 |  |  | 0 | 787200
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 22293
178
178