## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-08 | Friday
|  |  | Date (day): | 2021-01-08 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12056.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13273 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-07 | 2021-01-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 41 | 100 | 100 | 80 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 340
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 50 | 53 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 358 | 351 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 313 | 357 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 93 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 55 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 25 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 84 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 32 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 84 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 49 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 284 | 275 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 50 | 126 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1977 | 2481 | 3319 | 3649 | 1009 | 1372
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 40 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 20 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 20 | 25 | 35
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 309 | 175 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 39 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 597 | 653 | 1255 | 1240 | 920 | 103
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 157 | 164 | 150 | 160
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 385 | 360 | 360
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 235 | 235 | 300 | 300 | 60 |  | Gas shortage
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 102 | 100 | 100 | 100
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 80 | 90 | 91 |  | 72 | Gas shortage
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 68 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 108 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1216 | 1447 | 1757 | 2032 | 735 | 84
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 108 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 82 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 140 | 185 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 55 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 34 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 372 | 470 | 615.6 | 564 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 45 | 45
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 20 | 20
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 31 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 69 | 68 | 68
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 69 | 73 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 171 | 200 | 200
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 330 | 330
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 270 | 270 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1001 | 1068 | 1284 | 1284 | 330 | 425
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 577 | 812 | 482 | 724
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 220 | 300 | 325 | 85 |  | Gas shortage
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 70 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1035 | 1221 | 1297 | 1850 | 85 | 58
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 24 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 31 | 62 | 60 | 61 | 34 |  | Gas shortage
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 470 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 30 | 0 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 54 | 54 | 54 | 54
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 485 | 627 | 898 | 907 | 34 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 149 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 415 | 391 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 52 | 94 | 94 | 94
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 847 | 893 | 1360 | 1484 | 601 | 15
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 68 | 106 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 222 | 256 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7752 | 9116 | 12056.6 | 13273 | 3930 | 2468
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7443.3146 | 8753 | 11576.505 | 12744.4679
| A. |  | 2021-01-07 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 9116 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5765 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9116 | MW
| 3 | Day peak Generation : |  |  | 7752 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8753 | MW
| 4 | Evening peak Generation : |  |  | 9116 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 186.6112 | MKWHr | By Solar | 0.36087 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 109.3605 | MKWHr |  | By Oil: | 45.3332 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.2554 | MKWHr |  | By Hydro: | 0.92617 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3930 | MW | Dhaka | 3108 | 3108 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2468 | MW | Chittagong | 1039 | 1039 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6398 | MW | Khulna | 1088 | 1088 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 796.53 | MMCFD |  |  | Rajshahi | 883 | 883 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 106976460.616 | ii) Oil : | Taka | 330214588.08 | Comilla | 743 | 743 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 66378404 | Total | Taka | 503569452.696 | Mymensingh | 750 | 750 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 324 | 324 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 73 | MW (E to W) at | 19:00 | hrs | Barisal | 233 | 233 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 73 | MW at | 19:00 | hrs | Rangpur | 585 | 585 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 8753 | 8753 |  | 0
| B. |  | 2021-01-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13273 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6800 | MW
| 4 | Reserve(Generation end) |  |  |  | 4873 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 171.9542 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5922 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.384 | MKWHr. | ii) HVDC Flow at Peak Time |  | 812 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.991 | MKWHr. | iii) Maximum HVDC Flow : |  | 813 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.78 |  | (b) Today: | 97.72 |  | (c) Rule Curve: |  | 101.86
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 348 | 320 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 34 | 75 | 0 | 0 | 30 | 275 | 183 | 8 | 88 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 78 | 106 | 0 | 22 | 0 | 30 | 20 | 47 | 50 | 0 | 0 | 68 | 75 | 0 | 216 | 19 | 0 | 9 | 280 | 15 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 9 | 100 | 271 | 0 | 0 | 54 | 0 | 0 |  | 437 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 193 | 0 | 354 | 17 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 410 | 58 | 0 | 54 |  | 4188 | 2284 | 6472 | 2888 | 437 | 1418 | 1056 | 560 | 35 | 0 | 78 | 0 | 0 | 97.79
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 354 | 320 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 37 | 75 | 0 | 0 | 45 | 280 | 180 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 108 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 68 | 75 | 0 | 209 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 54 | 0 | 0 |  | 437 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 193 | 0 | 377 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 390 | 58 | 0 | 54 |  | 3942 | 2223 | 6165 | 2826 | 437 | 1349 | 906 | 540 | 35 | 0 | 72 | 0 | 0 | 97.79
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 353 | 320 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 75 | 0 | 0 | 90 | 275 | 135 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 74 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 75 | 0 | 209 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 68 | 30 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 60 | 269 | 0 | 0 | 54 | 0 | 0 |  | 437 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 193 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 57 | 0 | 54 |  | 3833 | 2107 | 5940 | 2824 | 437 | 1359 | 691 | 520 | 35 | 0 | 74 | 0 | 0 | 97.78
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 351 | 320 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 75 | 0 | 0 | 105 | 250 | 115 | 8 | 86 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 108 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 60 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 60 | 270 | 0 | 0 | 54 | 0 | 0 |  | 437 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 193 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 57 | 0 | 53 |  | 3731 | 2079 | 5810 | 2786 | 437 | 1317 | 643 | 520 | 35 | 0 | 72 | 0 | 0 | 97.78
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 360 | 290 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 75 | 0 | 0 | 120 | 250 | 121 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 72 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 60 | 0 | 209 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 10 | 270 | 0 | 0 | 54 | 0 | 0 |  | 437 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 160 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 57 | 0 | 54 |  | 3694 | 2071 | 5765 | 2786 | 437 | 1321 | 594 | 520 | 35 | 0 | 72 | 0 | 0 | 97.78
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 384 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 75 | 0 | 0 | 120 | 250 | 122 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 72 | 107 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 73 | 0 | 209 | 0 | 0 | 0 | 320 | 0 | 11 | 0 | 2 | 0 | 0 | 26 | 0 | 0 | 0 | 20 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 60 | 270 | 6 | 0 | 54 | 0 | 0 |  | 437 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 181 | 0 | 340 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 0 | 380 | 34 | 0 | 53 |  | 3933 | 2114 | 6047 | 2839 | 437 | 1357 | 777 | 530 | 35 | 0 | 72 | 0 | 0 | 97.78
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 348 | 353 |  | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 70 | 0 | 0 | 120 | 235 | 125 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 74 | 101 | 0 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 73 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 44 | 0 | 0 | 106 | 0 | 0 | 1 | 30 | 68 | 60 | 0 | 0 | 0 | 0 | 0 | 270 | 54 | 0 | 0 | 0 | 100 | 270 | 34 | 0 | 54 | 0 | 0 |  | 437 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 180 | 0 | 368 | 17 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 370 | 34 | 0 | 54 |  | 4182 | 2201 | 6383 | 2765 | 437 | 1336 | 1215 | 520 | 35 | 0 | 74 | 1 | 0 | 97.79
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 357 | 354 |  | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 2 | 17 | 10 | 70 | 0 | 0 | 125 | 235 | 125 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 70 | 94 | 10 | 22 | 0 | 30 | 20 | 8 | 50 | 0 | 0 | 69 | 73 | 0 | 210 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 120 | 0 | 0 | 150 | 0 | 14 | 6 | 50 | 68 | 75 | 0 | 0 | 0 | 0 | 8 | 286 | 54 | 0 | 0 | 4 | 100 | 272 | 44 | 6 | 54 | 0 | 0 |  | 529 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 11 | 180 | 0 | 349 | 70 | 0 | 68 | 0 | 65 | 0 | 1 | 25 | 380 | 45 | 0 | 41 |  | 4438 | 2486 | 6924 | 2769 | 529 | 1314 | 1631 | 530 | 35 | 25 | 70 | 21 | 0 | 97.79
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 363 | 320 |  | 0 | 0 | 0 | 3 | 30 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 85 | 0 | 0 | 0 | 17 | 0 | 55 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 28 | 17 | 5 | 70 | 0 | 0 | 125 | 235 | 125 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 68 | 92 | 25 | 22 | 1 | 30 | 30 | 31 | 50 | 0 | 0 | 40 | 73 | 0 | 209 | 0 | 0 | 0 | 295 | 0 | 2 | 0 | 190 | 0 | 0 | 170 | 0 | 17 | 8 | 78 | 68 | 100 | 0 | 0 | 4 | 0 | 2 | 288 | 54 | 0 | 0 | 20 | 100 | 267 | 75 | 16 | 54 | 0 | 0 |  | 530 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 180 | 0 | 332 | 105 | 0 | 110 | 0 | 92 | 0 | 1 | 80 | 400 | 33 | 0 | 54 |  | 4712 | 2631 | 7343 | 2730 | 530 | 1274 | 2085 | 550 | 35 | 43 | 68 | 28 | 0 | 97.78
10:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 348 | 252 |  | 0 | 0 | 0 | 47 | 30 | 14 | 0 | 0 | 0 | 14 | 32 | 0 | 87 | 0 | 0 | 0 | 17 | 0 | 53 | 0 | 25 | 32 | 25 | 25 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 32 | 14 | 7 | 70 | 0 | 0 | 225 | 235 | 139 | 8 | 84 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 74 | 123 | 16 | 22 | 1 | 30 | 30 | 31 | 50 | 0 | 0 | 40 | 71 | 0 | 143 | 0 | 0 | 0 | 250 | 0 | 5 | 0 | 250 | 0 | 0 | 140 | 0 | 42 | 11 | 50 | 68 | 102 | 0 | 0 | 17 | 0 | 3 | 307 | 54 | 0 | 0 | 45 | 100 | 270 | 90 | 26 | 90 | 0 | 0 |  | 576 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 163 | 0 | 354 | 105 | 0 | 113 | 0 | 71 | 0 | 2 | 50 | 370 | 38 | 0 | 44 |  | 4885 | 2519 | 7404 | 2682 | 576 | 1185 | 2248 | 518 | 35 | 43 | 74 | 43 | 0 | 97.78
11:00 | 0 | 0 | 0 | 0 | 300 | 28 | 0 | 348 | 252 |  | 0 | 0 | 0 | 50 | 30 | 15 | 0 | 0 | 0 | 7 | 58 | 0 | 90 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 25 | 30 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 32 | 17 | 7 | 70 | 0 | 0 | 230 | 235 | 125 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 74 | 145 | 8 | 22 | 1 | 30 | 30 | 31 | 50 | 0 | 0 | 40 | 70 | 0 | 143 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 284 | 0 | 0 | 140 | 0 | 49 | 18 | 50 | 68 | 102 | 0 | 0 | 17 | 0 | 4 | 308 | 54 | 0 | 0 | 45 | 100 | 270 | 72 | 33 | 90 | 0 | 0 |  | 576 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 164 | 0 | 330 | 105 | 0 | 113 | 0 | 70 | 0 | 3 | 50 | 360 | 38 | 0 | 45 |  | 4997 | 2459 | 7456 | 2706 | 576 | 1210 | 2243 | 510 | 35 | 43 | 74 | 59 | 0 | 97.78
12:00 | 0 | 0 | 0 | 0 | 300 | 50 | 0 | 358 | 313 |  | 0 | 0 | 0 | 50 | 30 | 15 | 0 | 0 | 0 | 7 | 58 | 0 | 100 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 25 | 30 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 32 | 17 | 8 | 0 | 0 | 0 | 290 | 235 | 157 | 8 | 92 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 78 | 144 | 8 | 22 | 2 | 30 | 30 | 31 | 50 | 0 | 0 | 40 | 69 | 0 | 162 | 0 | 0 | 8 | 290 | 16 | 5 | 0 | 284 | 0 | 0 | 140 | 0 | 50 | 18 | 20 | 68 | 102 | 0 | 0 | 17 | 0 | 4 | 309 | 54 | 0 | 0 | 45 | 100 | 270 | 90 | 34 | 72 | 0 | 0 |  | 577 | 0 | 270 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 188 | 0 | 415 | 105 | 0 | 113 | 0 | 68 | 0 | 4 | 50 | 350 | 30 | 0 | 54 |  | 5163 | 2589 | 7752 | 2827 | 577 | 1397 | 2224 | 500 | 35 | 52 | 78 | 62 | 0 | 97.78
13:00 | 0 | 0 | 20 | 0 | 300 | 53 | 0 | 359 | 356 |  | 0 | 0 | 0 | 50 | 37 | 15 | 0 | 0 | 0 | 7 | 58 | 0 | 86 | 0 | 0 | 0 | 17 | 0 | 36 | 19 | 25 | 22 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 32 | 17 | 8 | 0 | 0 | 0 | 380 | 235 | 157 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 82 | 106 | 8 | 22 | 2 | 30 | 30 | 31 | 50 | 0 | 0 | 64 | 68 | 0 | 172 | 18 | 0 | 9 | 285 | 16 | 5 | 0 | 284 | 0 | 0 | 140 | 0 | 50 | 18 | 20 | 68 | 100 | 0 | 0 | 17 | 0 | 4 | 307 | 35 | 0 | 0 | 45 | 100 | 264 | 90 | 30 | 72 | 0 | 0 |  | 577 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 169 | 0 | 385 | 105 | 0 | 113 | 0 | 70 | 0 | 4 | 50 | 360 | 0 | 0 | 54 |  | 5306 | 2583 | 7889 | 2936 | 577 | 1383 | 2256 | 510 | 35 | 52 | 82 | 58 | 7889 | 97.78
14:00 | 0 | 0 | 20 | 0 | 300 | 53 | 0 | 350 | 285 |  | 0 | 0 | 0 | 50 | 52 | 15 | 0 | 0 | 0 | 7 | 58 | 0 | 85 | 0 | 0 | 0 | 17 | 0 | 36 | 19 | 25 | 26 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 32 | 17 | 7 | 0 | 0 | 0 | 325 | 235 | 164 | 8 | 88 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 84 | 105 | 8 | 22 | 1 | 30 | 30 | 31 | 50 | 0 | 0 | 63 | 69 | 0 | 171 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 284 | 0 | 0 | 70 | 0 | 20 | 15 | 10 | 68 | 100 | 0 | 0 | 17 | 0 | 3 | 307 | 35 | 0 | 0 | 45 | 60 | 270 | 90 | 28 | 74 | 0 | 0 |  | 577 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 162 | 0 | 314 | 105 | 0 | 113 | 0 | 36 | 0 | 4 | 35 | 320 | 0 | 0 | 54 |  | 5039 | 2416 | 7455 | 2860 | 577 | 1256 | 2070 | 470 | 35 | 52 | 84 | 51 | 0 | 97.77
15:00 | 0 | 0 | 127 | 0 | 300 | 53 | 0 | 351 | 285 |  | 0 | 0 | 0 | 45 | 48 | 15 | 0 | 0 | 0 | 0 | 40 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 26 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 17 | 5 | 0 | 0 | 0 | 310 | 235 | 194 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 76 | 106 | 8 | 22 | 1 | 30 | 30 | 31 | 50 | 0 | 0 | 62 | 68 | 0 | 171 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 283 | 0 | 0 | 70 | 0 | 17 | 12 | 10 | 68 | 103 | 0 | 0 | 17 | 0 | 2 | 252 | 53 | 0 | 0 | 45 | 60 | 270 | 90 | 16 | 72 | 0 | 0 |  | 576 | 0 | 245 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 163 | 0 | 300 | 105 | 0 | 113 | 0 | 35 | 0 | 3 | 35 | 320 | 0 | 0 | 54 |  | 5007 | 2402 | 7409 | 2984 | 576 | 1246 | 1936 | 470 | 35 | 52 | 76 | 34 | 0 | 97.77
16:00 | 0 | 0 | 20 | 0 | 300 | 53 | 0 | 367 | 325 |  | 0 | 0 | 0 | 7 | 48 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 60 | 0 | 0 | 0 | 0 | 6 | 17 | 22 | 25 | 28 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 32 | 17 | 5 | 0 | 0 | 0 | 350 | 235 | 188 | 8 | 88 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 78 | 104 | 0 | 22 | 0 | 30 | 30 | 34 | 50 | 0 | 0 | 65 | 69 | 0 | 171 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 245 | 0 | 0 | 89 | 0 | 16 | 0 | 10 | 68 | 102 | 0 | 0 | 17 | 0 | 1 | 250 | 41 | 0 | 0 | 45 | 60 | 270 | 90 | 6 | 72 | 0 | 0 |  | 577 | 0 | 245 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 171 | 0 | 343 | 70 | 0 | 70 | 0 | 0 | 0 | 2 | 35 | 320 | 0 | 0 | 54 |  | 4908 | 2340 | 7248 | 2936 | 577 | 1353 | 1722 | 470 | 35 | 68 | 78 | 9 | 0 | 97.77
17:00 | 0 | 0 | 30 | 0 | 300 | 53 | 0 | 360 | 307 |  | 0 | 0 | 0 | 7 | 48 | 15 | 0 | 0 | 0 | 1 | 58 | 48 | 70 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 28 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 13 | 0 | 0 | 32 | 17 | 6 | 0 | 0 | 0 | 377 | 235 | 178 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 2 | 18 | 11 | 33 | 21 | 92 | 107 | 2 | 22 | 0 | 30 | 30 | 34 | 50 | 0 | 0 | 67 | 10 | 0 | 171 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 250 | 0 | 0 | 113 | 0 | 16 | 0 | 40 | 70 | 93 | 0 | 0 | 17 | 0 | 0 | 250 | 54 | 0 | 0 | 45 | 100 | 270 | 90 | 1 | 72 | 0 | 0 |  | 576 | 0 | 240 | 0 | 99 | 0 | 0 | 0 | 2 | 0 | 40 | 0 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 140 | 0 | 334 | 70 | 0 | 82 | 0 | 35 | 0 | 0 | 50 | 330 | 0 | 0 | 54 |  | 5109 | 2380 | 7489 | 2930 | 576 | 1255 | 1993 | 480 | 35 | 127 | 92 | 1 | 0 | 97.76
18:00 | 0 | 0 | 35 | 0 | 300 | 53 | 0 | 351 | 357 |  | 0 | 0 | 0 | 25 | 48 | 15 | 0 | 0 | 0 | 24 | 58 | 115 | 85 | 0 | 0 | 0 | 54 | 35 | 30 | 22 | 25 | 22 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 23 | 0 | 82 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 380 | 235 | 172 | 8 | 88 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 102 | 108 | 24 | 22 | 0 | 30 | 30 | 31 | 50 | 0 | 0 | 67 | 69 | 0 | 171 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 260 | 0 | 0 | 146 | 0 | 70 | 0 | 18 | 90 | 97 | 0 | 6 | 66 | 0 | 0 | 0 | 6 | 0 | 52 | 66 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 813 | 0 | 235 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 40 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 18 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 140 | 0 | 396 | 70 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 370 | 0 | 0 | 54 |  | 5388 | 2950 | 8338 | 2909 | 813 | 1437 | 2227 | 520 | 35 | 295 | 102 | 0 | 0 | 97.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 41 | 0 | 300 | 53 | 0 | 351 | 357 |  | 0 | 0 | 0 | 93 | 55 | 25 | 0 | 0 | 0 | 84 | 32 | 84 | 85 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 24 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 102 | 0 | 0 | 40 | 17 | 20 | 0 | 0 | 0 | 385 | 235 | 164 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 21 | 108 | 108 | 82 | 22 | 0 | 30 | 30 | 31 | 50 | 0 | 0 | 69 | 73 | 0 | 171 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 275 | 0 | 0 | 185 | 0 | 126 | 0 | 100 | 68 | 100 | 0 | 55 | 105 | 0 | 0 | 175 | 39 | 0 | 17 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 812 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 149 | 0 | 391 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 470 | 0 | 0 | 54 |  | 6119 | 2997 | 9116 | 2907 | 812 | 1447 | 2903 | 620 | 35 | 284 | 108 | 0 | 0 | 97.74
19:30 | 0 | 0 | 70 | 0 | 300 | 53 | 0 | 351 | 357 |  | 0 | 0 | 0 | 50 | 81 | 15 | 0 | 0 | 0 | 60 | 32 | 84 | 85 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 30 | 25 | 25 | 0 | 0 | 45 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 102 | 0 | 0 | 50 | 17 | 33 | 0 | 0 | 0 | 380 | 235 | 163 | 8 | 88 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 102 | 109 | 90 | 22 | 0 | 30 | 0 | 31 | 50 | 0 | 0 | 68 | 73 | 0 | 171 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 284 | 0 | 0 | 185 | 0 | 128 | 0 | 100 | 68 | 100 | 0 | 25 | 70 | 0 | 0 | 198 | 54 | 0 | 0 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 812 | 0 | 210 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 155 | 0 | 417 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 6049 | 3051 | 9100 | 2910 | 812 | 1498 | 2764 | 650 | 80 | 284 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 85 | 0 | 300 | 53 | 0 | 350 | 359 |  | 0 | 0 | 0 | 58 | 80 | 0 | 0 | 0 | 0 | 50 | 32 | 84 | 85 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 45 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 0 | 0 | 50 | 17 | 34 | 0 | 0 | 0 | 380 | 235 | 162 | 8 | 84 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 109 | 90 | 22 | 0 | 30 | 0 | 31 | 50 | 0 | 0 | 69 | 73 | 0 | 171 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 285 | 0 | 0 | 185 | 0 | 127 | 0 | 100 | 68 | 102 | 0 | 25 | 35 | 0 | 0 | 195 | 54 | 0 | 0 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 813 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 153 | 0 | 398 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 500 | 0 | 0 | 54 |  | 6004 | 3021 | 9025 | 2911 | 813 | 1472 | 2713 | 650 | 80 | 284 | 102 | 0 | 0 | 97.74
21:00 | 0 | 0 | 92 | 0 | 300 | 53 | 0 | 358 | 359 |  | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 85 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 38 | 0 | 0 | 0 | 383 | 235 | 155 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 108 | 91 | 22 | 0 | 30 | 0 | 31 | 50 | 0 | 0 | 69 | 70 | 0 | 190 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 283 | 0 | 0 | 185 | 0 | 117 | 0 | 100 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 195 | 54 | 0 | 0 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 813 | 0 | 195 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 149 | 0 | 397 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 520 | 0 | 0 | 54 |  | 5759 | 3066 | 8825 | 2930 | 813 | 1482 | 2520 | 670 | 45 | 265 | 100 | 0 | 0 | 97.74
22:00 | 0 | 0 | 102 | 0 | 300 | 53 | 0 | 350 | 320 |  | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 0 | 50 | 17 | 39 | 0 | 0 | 0 | 395 | 235 | 145 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 96 | 109 | 25 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 69 | 70 | 0 | 190 | 18 | 0 | 9 | 270 | 16 | 11 | 0 | 245 | 0 | 0 | 185 | 0 | 81 | 0 | 50 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 813 | 0 | 190 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 147 | 0 | 365 | 70 | 0 | 113 | 0 | 67 | 0 | 0 | 70 | 520 | 0 | 0 | 54 |  | 5271 | 2881 | 8152 | 2898 | 813 | 1382 | 2031 | 670 | 43 | 219 | 96 | 0 | 0 | 97.74
23:00 | 0 | 0 | 103 | 0 | 300 | 52 | 0 | 350 | 300 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 0 | 50 | 17 | 39 | 0 | 0 | 0 | 365 | 265 | 146 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 88 | 108 | 8 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 69 | 70 | 0 | 190 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 145 | 0 | 0 | 195 | 0 | 28 | 0 | 20 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 55 | 100 | 270 | 53 | 0 | 72 | 0 | 0 |  | 813 | 0 | 185 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 148 | 0 | 296 | 53 | 0 | 70 | 0 | 36 | 0 | 0 | 70 | 520 | 0 | 0 | 54 |  | 4928 | 2668 | 7596 | 2903 | 813 | 1310 | 1599 | 670 | 41 | 172 | 88 | 0 | 0 | 97.73
24:00 | 0 | 0 | 102 | 0 | 300 | 52 | 0 | 352 | 300 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 0 | 25 | 17 | 40 | 0 | 0 | 0 | 335 | 295 | 146 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 82 | 140 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 69 | 70 | 0 | 190 | 19 | 0 | 9 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 170 | 0 | 0 | 0 | 20 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 55 | 100 | 270 | 53 | 0 | 72 | 0 | 0 |  | 670 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 149 | 0 | 294 | 53 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 480 | 0 | 0 | 54 |  | 4753 | 2407 | 7160 | 2942 | 670 | 1308 | 1363 | 630 | 42 | 123 | 82 | 0 | 0 | 97.73
KWH | 0 | 0 | 758000 | 0 | 7580827 | 690000 | 0 | 8660990 | 7690000 |  | 0 | 0 | 0 | 590400 | 838416 | 183353 | 0 | 0 | 0 | 231360 | 530784 | 505920 | 1507884 | 0 | 0 | 0 | 227520 | 164319 | 642599 | 264240 | 600000 | 680040 | 600700 | 618700 | 265788 | 0 | 214167 | 712000 | 0 | 0 | 32155 | 0 | 0 | 0 | 0 |  | 331440 | 0 | 627456 | 0 | 0 | 613440 | 368160 | 454560 | 780994 | 0 | 0 | 6087000 | 6007000 | 3683000 | 200727 | 2071090 | 166032 | 219840 | 0 | 1232202 | 0 | 0 | 48014 | 437200 | 253260 | 820600 | 497240 | 1991040 | 2564920 | 501120 | 512748 | 9050 | 628000 | 501720 | 594600 | 1204632 | 0 | 0 | 1539072 | 1619520 | 0 | 4405960 | 228000 | 0 | 116820 | 7230000 | 202944 | 205500 | 0 | 4303089 | 0 | 0 | 2868000 | 0 | 860832 | 106785 | 673200 | 1718880 | 2107636 | 0 | 92400 | 416460 | 0 | 25561 | 5823600 | 1188004 | 0 | 71820 | 1152480 | 2031360 | 13690900 | 1474560 | 196020 | 1612800 | 0 | 0 |  | 14384000 | 0 | 6634656 | 0 | 2364480 | 0 | 0 | 0 | 23060 | 0 | 397875 | 0 | 513100 | 84768 | 0 | 0 | 0 | 0 | 0 | 973704 | 32600 | 0 | 0 | 0 | 0 | 501840 | 0 | 216918 | 0 | 0 | 3686600 | 0 | 0 | 0 | 0 | 0 | 0 | 1059832 | 49920 | 4323082 | 0 | 8876327 | 1528320 | 0 | 2064358 | 0 | 1130880 | 0 | 23458 | 1194528 | 10568800 | 567054 | 0 | 1251600 |  | 124159450 | 62451760 | 186611210 | 76589493 | 14384000 | 32771054 | 43203042 | 14255400 | 926167 | 2130140 | 1991040 | 360874 | 0
Fuel Cost | 0 | 0 | 1106680 | 0 | 8414717.97 | 910800 | 0 | 8747599.9 | 7920700 |  | 0 | 0 | 0 | 4481136 | 5776686.24 | 1551166.38 | 0 | 0 | 0 | 1742140.8 | 4840750.08 | 4978252.8 | 13902690.48 | 0 | 0 | 0 | 1660896 | 1270185.87 | 6336026.14 | 198180 | 450000 | 0 | 0 | 0 | 2570169.96 | 0 | 57825.09 | 192240 | 0 | 0 | 298719.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6086323.2 | 0 | 0 | 4858444.8 | 463881.6 | 1350043.2 | 1155871.12 | 0 | 0 | 4504380 | 6007000 | 3388360 | 258937.83 | 2381753.5 | 187616.16 | 307776 | 0 | 2107065.42 | 0 | 0 | 458533.7 | 555244 | 189945 | 1436050 | 372930 | 14932800 | 2718815.2 | 4550169.6 | 651189.96 | 144257 | 1029920 | 802752 | 1058388 | 1879225.92 | 0 | 0 | 3031971.84 | 3093283.2 | 0 | 7622310.8 | 499320 | 0 | 238312.8 | 7302300 | 152208 | 156180 | 0 | 32531352.84 | 0 | 0 | 14913600 | 0 | 8470586.88 | 1248316.65 | 5486580 | 18649848 | 14858833.8 | 0 | 842688 | 3935547 | 0 | 0 | 44026416 | 10347514.84 | 0 | 716763.6 | 9876753.6 | 13528857.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 82851840 | 0 | 6966388.8 | 0 | 18584812.8 | 0 | 0 | 0 | 241899.4 | 0 | 4145857.5 | 0 | 795305 | 827335.68 | 0 | 0 | 0 | 0 | 0 | 8617280.4 | 251020 | 0 | 0 | 0 | 0 | 963532.8 | 0 | 164206.926 | 0 | 0 | 19981372 | 0 | 0 | 0 | 0 | 0 | 0 | 1589748 | 849139.2 | 5058005.94 | 0 | 8787563.73 | 15955660.8 | 0 | 19590757.42 | 0 | 8775628.8 | 0 | 259210.9 | 8827561.92 | 46397032 | 0 | 0 | 0 |  | 342774782.32 | 260481160.016 | 603255942.336 | 68413478.716 | 82851840 | 38562981.9 | 310290832.28 | 66378404 | 250065.09 | 19923755.8 | 14932800 | 1651784.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 50 | 0 | 358 | 313 |  | 0 | 0 | 0 | 50 | 30 | 15 | 0 | 0 | 0 | 7 | 58 | 0 | 100 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 25 | 30 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 32 | 17 | 8 | 0 | 0 | 0 | 290 | 235 | 157 | 8 | 92 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 78 | 144 | 8 | 22 | 2 | 30 | 30 | 31 | 50 | 0 | 0 | 40 | 69 | 0 | 162 | 0 | 0 | 8 | 290 | 16 | 5 | 0 | 284 | 0 | 0 | 140 | 0 | 50 | 18 | 20 | 68 | 102 | 0 | 0 | 17 | 0 | 4 | 309 | 54 | 0 | 0 | 45 | 100 | 270 | 90 | 34 | 72 | 0 | 0 |  | 577 | 0 | 270 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 188 | 0 | 415 | 105 | 0 | 113 | 0 | 68 | 0 | 4 | 50 | 350 | 30 | 0 | 54 |  | 7752 | DayPeak
Yesterday Evening Peak | 0 | 0 | 41 | 0 | 300 | 53 | 0 | 351 | 357 | 0 | 0 | 0 | 0 | 93 | 55 | 25 | 0 | 0 | 0 | 84 | 32 | 84 | 85 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 24 | 25 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 102 | 0 | 0 | 40 | 17 | 20 | 0 | 0 | 0 | 385 | 235 | 164 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 21 | 108 | 108 | 82 | 22 | 0 | 30 | 30 | 31 | 50 | 0 | 0 | 69 | 73 | 0 | 171 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 275 | 0 | 0 | 185 | 0 | 126 | 0 | 100 | 68 | 100 | 0 | 55 | 105 | 0 | 0 | 175 | 39 | 0 | 17 | 113 | 100 | 270 | 90 | 0 | 72 | 0 | 0 |  | 812 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 149 | 0 | 391 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 470 | 0 | 0 | 54 |  | 9116 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 340 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 35 | 0 | 0 | 0 | 360 | 300 | 160 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 22 | 147 | 110 | 95 | 22 | 0 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 100 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 0 | 0 |  | 724 | 16 | 325 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 94 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 54
Forecast for Day | 0 | 0 | 100 | 0 | 300 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 25 | 0 | 0 | 0 | 360 | 300 | 150 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 135 | 110 | 95 | 22 | 1.6 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 100 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 0 | 0 |  | 482 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 54
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 300 | 52 | 0 | 356 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 |  | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 300 | 320 | 148 | 8 | 73 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 0 | 68 | 165 | 0 | 22 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 69 | 72 | 0 | 170 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 30 | 0 | 0 | 60 | 0 | 0 | 6 | 0 | 68 | 65 | 0 | 0 | 0 | 0 | 1 | 215 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 6 | 72 | 0 | 0 | 0 | 440 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 363 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 34 | 0
199
| Minimum Generation |  | 5765 | 5:00
| Highest Generation |  | 9116 | 19:00
| Day Peak Generation |  | 7752 | 12:00
| Evening Peak Generation |  | 9116 | 19:00
| HVDC Max Flow |  | 813 | 18:00
| HVDC EvPeak Flow |  | 812 | 19:00
| Load factor L.F |  | 85.29%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-08
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7752 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5922 | MW
Evening Peak Generation : |  | 9116 | MW Hour : | 19:00 | Available Max Generation : |  | 13273 | MW
E.P. Demand (at gen end) : |  | 9116 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8400 | MW
Maximum Generation : |  | 9116 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4873 | MW
Total Gen. (MKWH) : |  | 186.6112 | System Load Factor : | 85.29% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 73 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-08
Actual : | 97.72 | Ft.(MSL) , | Rule curve : | 101.86 | Ft.( MSL )
Gas Consumed : | Total = | 796.53 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106976460.616
: |  | Coal : | 66378404 | Oil : | 330214588.08 | Total : | 503569452.696
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3015.0763 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1018.5295 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 911.3635 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 823.0659 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 744.0287 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 600.3878 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 344.4106 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 154.814 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 463.0072 |  |  | 0 | 0%
Total | 0 |  | 8074.6837 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari-Raozan 230 kV Ckt-1 was under shut down from 09:53 to 15:27 for A/M.
b) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 08:22 to 14:45 for A/M.
c) Aminbazar 230/132 kV T03 transformer was under shut down from 09:18 to 17:38 for A/M.
d) B.Baria-Narshingdi 132 kV Ckt-1 was under shut down from 08:49 to 20:12 for A/M.
e) Kaliakoir 400/132 kV TR-2 transformer was under shut down from 09:18 to 16:00 for A/M.
f) Dohazari-Sikalbaha 132 kV Ckt-1 was under shut down from 08:15 to 16:55 for D/W.
g) Shahmirpur-Sikalbaha 132 kV Ckt-2 was under shut down from 08:17 to 17:00 for D/W.
h) Feni-Chowmuhani 132 kV Ckt-2 was under shut down from 08:51 to 20:05 for C/M.
i) Ramganj-Chowmuhani 132 kV Ckt-1 was under shut down from 09:42 to 16:26 for D/W.
j) Dohazari-Cox's Bazar 132 kV Ckt-2 was shut down at 08:42 for D/W.
k) Kulaura 132/33 kV T2 transformer was under shut down from 08:35 to 11:18 for C/M.
l) Sonargaon 132/33 kV T2 transformer was under shut down from 08:52 to 16:06 for C/M.
m) Bheramara HVDC-Rajshahi(New) 230 kV Ckt-2 & & Bay 20D05C were under shut down from
10:15 to 20:38 for A/M.
n) Bogura-Mohastanghor 132 kV Ckt-2 was under shut down from 09:46 to 14:53 for A/M.
o) Barisal(N)-Madaripur 132 kV Ckt-2 was under shut down from 09:01 to 12:31 for A/M.
p) Faridpur-Faridpur-150 MW PS 132 kV Ckt was under shut down from 08:14 to 12:53 for A/M.
q) Khulna(Central) - NWPGCL 132 kV Ckt-1 was under shut down from 08:04 to 15:14 for A/M.
r) Ishurdi 132/33 kV T1 transformer was under shut down from 09:24 to 15:50 for A/M.
s) Keraniganj 230 kV Bus-2 was under shutdown from 10:00 to 17:15 for C/M.
t) Siddhirganj-Matuail 132 kV Ckt tripped at 10:12 from Siddhirganj end showing Dist. O/C and was |  |  |  |  | About 55 MW power interruption occurred under Matuail S/S area
switched on at 10:36. |  |  |  |  | from 10:12 to 10:36.
u) Ashuganj Unit-3 was shutdown at 11:12 due to gas shortage.
v) Kabirpur 132/33 kV T1 transformer was under shut down from 08:39 to 12:35 for A/M.
w) Ghorashal Unit-4 GT & ST were synchronized at 12:09 & 17:21 respectively.
x) Kodda 132/33 kV T5 transformer was under shut down from 09:26 to 16:39 for A/M.
y) Baghabari 230 KV main Bus-1 was under shut down from 13:13 to 15:44 for A/M.
z) Netrokona 132/33 kV T4 transformer was switched on at 15:19.
aa) Hathazari-Madunaghat 132 kV Ckt tripped at 17:05 from Hathazari end showing Backup protection
trip, under voltage and was switched on at 17:52.
ab) Kaptai Unit-5 was synchronized at 17:27 and again shutdown at 20:32.
ac) Kaptai Unit-3 was synchronized at 19:28.
ad) Fenchuganj GT-2 was shutdown at 21:09 for Bus-Bar maintenance work.
ae) Cantonment 132/33 kV T2 transformer is under shut down since 07:05(08/01/2021) for A/M.
af) Gopalganj (Old)-Gopalganj (New) 132 kV Ckt is under shut down since 07:11(08/01/2021) for D/W. |  |  |  |  | About 35 MW power interruption has been occurring under Gopalganj(New)
S/S area since 07:11(08/01/2021).
ag) Rajshahi 132/33 kV T3 transformer is under shut down since 07:02(08/01/2021) for C/M. |  |  |  |  | About 08 MW power interruption has been occurring under Rajshahi
S/S area since 07:02(08/01/2021).
ah) Shariatpur 132/33 kV T1 transformer is under shut down since 06:29(08/01/2021) for C/M. |  |  |  |  | About 15 MW power interruption has been occurring under Shariatpur
S/S area since 06:29(08/01/2021).
ai) Shahmirpur-Sikalbaha 132 kV Ckt-2 is under shut down since 07:13(08/01/2021) for D/W.
aj) Siddhirganj 132/33 kV T1 transformer is under shut down since 07:28(08/01/2021) for A/M.
ak) Rampura 230/132 kV T03 transformer is under shut down since 07:28(08/01/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 41 | 758000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7580827 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 53 | 690000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8660990 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 357 | 7690000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 590400 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 55 | 838416 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 25 | 183353 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1507884 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 264240
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 84 | 231360 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 530784 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 227520 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 84 | 505920 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 164319 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 642599
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1280040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 600700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 618700 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 265788 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 4303089 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 126 | 860832 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 416460
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1474560 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1612800 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2481 | 42499581
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 32155
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 106785
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 613440 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 926167 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 627456
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 673200
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 368160
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 454560
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25561
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 175 | 5823600 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 39 | 1188004 | Engine problem
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2031360
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 653 | 12870448
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 780994 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 164 | 3683000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 385 | 6087000
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 235 | 6007000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 166032 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 219840 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1232202
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 2107636 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2071090
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 1718880 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 437200 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 253260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 1991040
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 48014 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 497240 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 71820 | Low demand
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1152480
| Cumilla Area Total |  |  |  | 2980 | 1447 | 29546055
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 2564920 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512748
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 82 | 501120 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9050
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 185 | 2868000 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 55 | 92400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 196020
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 331440
| Mymensingh Area Total |  |  |  | 709 | 470 | 7075698
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 628000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 501720 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 31 | 594600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1204632
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 205500
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1539072
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1619520 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4405960
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 228000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 202944 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7230000 | Gas shortage
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 116820
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 270 | 13690900 | On test
| Sylhet Area Total |  |  |  | 1988 | 1068 | 32167668
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 812 | 14384000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2364480
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 23060 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 220 | 6634656 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 397875 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 49920 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1528320 | Low demand
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1221 | 25382311
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 84768 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 513100 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 62 | 1059832
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 10568800 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 567054 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 54 | 1251600 | On test.
| Barisal Area Total |  |  |  | 1676 | 627 | 14045154
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 32600 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 149 | 4323082 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 391 | 8876327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 501840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216918
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 973704 | Engine problem
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2064358
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1194528
| Rajshahi Area Total |  |  |  | 2183 | 893 | 18183357
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3686600
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 106 | 1130880 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23458
| Rangpur Area Total |  |  |  | 605 | 256 | 4840938
| Total |  |  |  | 20748 | 9116 | 186611210
| Eastern Grid Total |  |  |  | 14000 | 6119 | 124159450
| Western Grid Total |  |  |  | 6748 | 2997 | 62451760
| National Grid Total |  |  |  | 20748 | 9116 | 186611210
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-07
| (a) ENTIRE EASTERN GRID : |  | 5964 | MW | (b) ENTIRE WESTERN GRID : |  | 2789 | MW
| i) Dhaka area |  | 3108 | MW | i) Khulna area |  | 1088 | MW
| ii) Chittagong area |  | 1039 | MW | ii) Rajshahi area |  | 883 | MW
| iii) Comilla area |  | 743 | MW | iii) Barisal area |  | 233 | MW
| iv) Mymensingh area |  | 750 | MW | iv) Rangpur area |  | 585 | MW
| v) Sylhet area |  | 324 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8753 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 9:00 | Jamalpur | 86 | 18:30 | Benapol | 38 | 18:30
| Munsiganj | 86 | 21:00 | Sherpur | 100 | 18:30 | Jhenida | 84 | 18:30
| Sonargaon | 71 | 18:30 | Srimongal | 25 | 19:00 | Bottail | 91 | 18:00
| Shyampur | 170 | 11:00 | Shahjibazar | 88 | 19:30 | G.K Project | 34 | 18:30
| Bhulta | 169 | 12:00 | Fenchuganj | 26 | 18:00 | Faridpur | 132 | 18:30
| Madanganj | 36 | 10:00 | Kulawara | 28 | 18:00 | Madaripur | 65 | 480:00
| Shitalakhya | 97 | 15:00 | Sylhet | 73 | 18:30 | Sariatpur | 40 | 19:30
| Rahim steel | 19 | 16:00 | Chatak | 22 | 18:00 | Gopalganj | 62 | 18:30
| Matuail | 54 | 9:00 | Sunamganj | 29 | 19:00 | Bagerhat | 83 | 19:00
| Ghorasal | 62 | 18:30 | Biani Bazar | 38 | 18:00 | Mongla | 36 | 9:00
| Narsingdi | 123 | 19:30 | Comilla (S) | 108 | 19:00 | Satkhira | 76 | 19:00
| Haripur (SBU) | 104 | 9:00 | Comilla(N) | 69 | 20:00 | Gallamari | 21 | 13:00
| Ullon | 40 | 13:00 | Chandpur | 63 | 20:00 | Magura | 40 | 18:30
| Hasnabad | 151 | 19:00 | Feni | 78 | 21:00 | Norail | 24 | 18:00
| Magbazar | 70 | 12:00 | Chowmuhani | 118 | 20:00 | Chuadanga | 66 | 18:30
| Maniknagar | 78 | 12:00 | Ashuganj | 38 | 21:00 | Barisal(N) | 29 | 19:30
| Bangabhaban | 17 | 12:00 | Daudkandi | 94 | 22:00 | Barisal (S) | 70 | 20:00
| Narinda | 68 | 18:00 | B.Baria | 100 | 19:30 | Patuakhali | 79 | 19:30
| Dhanmondi | 100 | 13:00 | Ramganj | 64 | 19:30 | Bhandaria | 40 | 18:00
| Lalbag | 72 | 13:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 25 | 22:00
| Madartek | 46 | 18:30 | PHP | 10 | 15:00 | Ishurdi | 49 | 18:00
| Dhaka University |  |  | Madunaghat | 46 | 18:30 | Ruppur Paromanobik | 2 | 18:00
| Aftabnagar | 6 | 0.41667 | Hathazari | 65 | 0.75 | Natore | 89 | 0.75
| Fatullah | 44 | 11:00 | Khulshi | 177 | 12:00 | Bogra | 122 | 18:30
| Mirpur | 73 | 18:00 | Halishahar | 99 | 19:00 | Noagaon | 77 | 19:00
| Kalyanpur | 60 | 18:00 | Baraulia | 141 | 13:00 | Rajshahi | 94 | 20:00
| Gulshan | 78 | 18:00 | Sikalbaha | 20 | 19:00 | Rajshahi New | 9 | 20:00
| Uttara | 70 | 13:00 | Dohazari | 70 | 18:30 | C.Nawabganj | 51 | 13:00
| Uttara New | 22 | 18:00 | Cox'sbazar | 81 | 18:30 | Amnura | 32 | 19:30
| Kamrangirchar | 72 | 18:30 | Chandraghona | 22 | 19:00 | Pabna | 76 | 19:00
| Savar | 112 | 12:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 75 | 18:00
| Bhasantec | 104 | 18:00 | A. Khaer Stl. | 8 | 21:00 | Serajganj | 58 | 19:00
| Agargaon | 46 | 18:00 | Bakulia | 74 | 18:00 | Niyamatpur | 70 | 19:00
| Satmosjid | 67 | 0.54167 | Julda | 21 | 0.625 | Joypurhat | 41 | 0.375
| Tongi | 61 | 18:00 | TK chemical | 14.5 | 1:00 | Sherpur(Bogura) | 36 | 18:00
| Kabirpur | 158 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 30 | 19:00
| Basundhara | 93 | 18:00 | Shahmirpur | 18 | 17:00 | Bangura | 4 | 18:00
| Manikganj | 44 | 19:30 | Khagrachhari | 18 | 21:00 | Rangpur | 102 | 19:00
| Joydevpur | 120 | 20:00 | Matarbari | 29.5 | 19:00 | Lalmonirhat | 44 | 18:00
| New Tongi | 103 | 12:00 | Baroiar Hat | 26 | 18:00 | Saidpur | 83 | 18:30
| Kodda | 178 | 18:30 | Rangamati | 8 | 12:00 | Purbasadipur | 80 | 18:30
| Dhamrai | 80 | 19:30 | Abul Khair 230 | 161 | 2:00 | Thakurgaon | 60 | 18:30
| Rajendrapur | 76 | 21:00 | BSRM | 150 | 17:00 | Palashbari | 90 | 18:00
| Valuka | 80 | 18:00 | GPH Ispat | 76 | 3:00 | Barapukuria | 37 | 19:00
| Tangail | 147 | 18:00 | Goalpara | 16 | 13:00 | Panchagar | 42 | 18:30
| Mymensing | 165 | 18:00 | Central s/s | 78 | 18:30 | Joldhaka | 26 | 19:00
| Kishorganj | 96 | 20:00 | Noapara | 53 | 19:00 | Kurigram | 39 | 19:00
| Netrokona | 103 | 18:30 | Jessore | 78 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 21:00 | 410 | 1:00 | Kaliakoir | 392 | 0.66667 | 370 | 0.625
| Bheramara | 411 | 20:00 | 394 | 18:00 | Bhulta | 390 | 0.79167 | 367 | 0.041667
| Ashuganj(N) | 396 | 19:00 | 373 | 1:00 | Gopalganj | 409 | 0.25 | 392 | 0.875
| Payra | 413 | 19:00 | 404 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 18:00 | 230 | 15:00 | Comilla (N) | 239 | 20:00 | 229 | 1:00
| Ishurdi | 242 | 22:00 | 233 | 11:00 | Hathazari | 225 | 19:30 | 209 | 15:00
| Ashuganj | 241 | 19:00 | 231 | 16:00 | Megnaghat | 235 | 19:00 | 225 | 9:00
| Serajganj | 235 | 21:00 | 230 | 12:00 | Fenchuganj | 244 | 18:30 | 238 | 3:00
| Baghabari | 245 | 4:00 | 230 | 13:00 | Siddhirganj | 232 | 19:00 | 222 | 11:00
| Barapukuria | 233 | 4:00 | 230 | 9:00 | Maniknagar | 231 | 19:00 | 220 | 12:00
| Bogra | 237 | 21:00 | 230 | 8:00 | Agargaon | 230 | 2:00 | 219 | 16:00
| Rajshahi | 240 | 22:00 | 224 | 5:00 | Barisal | 252 | 20:00 | 242 | 18:30
| Khulna South | 245 | 24:00 | 233 | 12:00 | AKSML | 228 | 19:30 | 210 | 15:00
| Rampura | 230 | 18:30 | 223 | 1:00 | BSRM | 228 | 22:00 | 213 | 15:00
| Haripur | 231 | 19:00 | 220 | 16:00 | Bibiyana | 246 | 19:00 | 240 | 1:00
| Hasnabad | 232 | 18:30 | 223 | 17:00 | Bhulta | 233 | 19:00 | 223 | 17:00
| Shyampur | 231 | 19:00 | 220 | 16:00 | Ashuganj (S) | 238 | 19:00 | 227 | 1:00
| Aminbazar | 231 | 20:00 | 221 | 15:00 | Kaliakoir | 229 | 19:30 | 217 | 3:00
| Tongi | 228 | 19:30 | 215 | 1:00 | GPH | 227 | 19:30 | 209 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 18:00 | 132 | 15:00 | Madanhat | 138 | 0.875 | 127 | 0.625
| Munsiganj | 140 | 18:30 | 132 | 1:00 | Hathazari | 138 | 0.8125 | 130 | 0.5
| Sonargaon | 137 | 18:00 | 131 | 3:00 | Khulshi | 134 | 0.79167 | 126 | 0.625
| Shyampur | 132 | 18:30 | 124 | 16:00 | Halishahar | 137 | 0.875 | 126 | 0.625
| Bhulta | 130 | 6:00 | 120 | 22:00 | Baraulia | 135 | 0.83333 | 127 | 0.58333
| Madanganj | 138 | 20:00 | 130 | 12:00 | Sikalbaha | 137 | 0.875 | 130 | 0.5
| Shitalakhya | 142 | 19:00 | 133 | 1:00 | Dohazari | 135 | 0.75 | 120 | 0.79167
| Rahim steal | 139 | 18:30 | 133 | 1:00 | Cox'sbazar | 124 | 0.041667 | 110 | 0.77083
| Matuail | 138 | 18:00 | 132 | 15:00 | Chandraghona | 137 | 0.875 | 127 | 0.625
| Ghorasal | 138 | 21:00 | 134 | 1:00 | Kaptai | 135 | 0.29167 | 130 | 0.45833
| Narsinghdi | 136 | 21:00 | 128 | 12:00 | A. Khaer Stl. | 136 | 0.83333 | 126 | 0.45833
| Haripur (SBU) | 139 | 19:00 | 132 | 16:00 | Bakulia | 137 | 0.91667 | 128 | 0.45833
| Ullon | 132 | 19:00 | 125 | 15:00 | Julda | 136 | 0.29167 | 128 | 0.58333
| Hasnabad | 138 | 18:00 | 134 | 15:00 | TK Chemical | 136 | 0.875 | 129 | 0.66667
| Magbazar | 132 | 19:00 | 125 | 11:00 | Modern Steel | 135 | 0.8125 | 127 | 0.45833
| Maniknagar | 137 | 19:00 | 132 | 11:00 | Shahmirpur | 136 | 0.83333 | 127 | 0.625
| Bangabhaban | 137 | 19:00 | 132 | 11:00 | Khagrachhari | 136 | 0.875 | 128 | 0.625
| Narinda | 137 | 19:00 | 132 | 11:00 | Matarbari | 136 | 0.75 | 110 | 0.77083
| Dhanmondi | 132 | 19:00 | 125 | 15:00 | Baroiar Hat | 138 | 0.75 | 131 | 0.625
| Lalbag | 130 | 19:00 | 122 | 12:00 | Rangamati | 136 | 21:00 | 126 | 16:00
| Madartek | 131 | 19:00 | 125 | 12:00 | Goalpara S/S | 140 | 23:00 | 133 | 12:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 140 | 23:00 | 133 | 0.79167
| Aftabnagar | 131 | 18:00 | 126 | 11:00 | Noapara | 137 | 23:00 | 130 | 0.5
| Fatuiiah | 132 | 18:30 | 126 | 12:00 | Jessore | 134 | 23:00 | 126 | 0.5
| Mirpur | 131 | 20:00 | 120 | 11:00 | Benapol | 134 | 0.083333 | 125 | 0.5
| Kalyanpur | 133 | 20:00 | 125 | 12:00 | Jhenida | 133 | 2:00 | 124 | 0.5
| Gulshan | 131 | 20:00 | 126 | 12:00 | Bottail | 135 | 0.041667 | 128 | 0.5
| Uttara | 130 | 20:00 | 124 | 12:00 | G.K Project | 140 | 0.16667 | 137 | 0.5
| Uttara New | 138 | 19:00 | 130 | 12:00 | Faridpur | 137 | 0.16667 | 132 | 0.875
| Kamrangirchar | 141 | 19:00 | 136 | 12:00 | Madaripur | 141 | 0.125 | 136 | 0.79167
| Savar | 133 | 20:00 | 124 | 12:00 | Shariyatpur S/S | 140 | 1:00 | 134 | 0.875
| Bhasantec | 134 | 20:00 | 127 | 16:00 | Gopalganj | 143 | 0.25 | 135 | 0.8125
| Agargaon | 135 | 20:00 | 128 | 12:00 | Bagerhat | 140 | 13:00 | 130 | 0.79167
| Satmosjid | 134 | 20:00 | 128 | 12:00 | Mongla | 138 | 17:00 | 141 | 0.5
| Tongi | 140 | 20:00 | 131 | 7:00 | Satkhira | 139 | 23:00 | 132 | 12:00
| Kabirpur | 139 | 21:00 | 131 | 16:00 | Gallamari | 139 | 0.91667 | 133 | 0.5
| Basundhara | 132 | 24:00 | 127 | 1:00 | Magura | 135 | 4:00 | 125 | 0.375
| Manikganj | 144 | 19:00 | 133 | 16:00 | Narail | 133 | 0.125 | 122 | 0.77083
| Joydevpur | 139 | 21:00 | 131 | 17:00 | Chuadanga | 131 | 4:00 | 120 | 0.77083
| New Tongi | 140 | 18:30 | 131 | 16:00 | Barisal(N) | 133 | 2:00 | 137 | 18:30
| Kodda | 140 | 18:30 | 126 | 6:00 | Barisal (S) | 142 | 0.25 | 137 | 0.77083
| Dhamrai | 138 | 22:00 | 127 | 16:00 | Patuakhali(S) | 140 | 0.70833 | 135 | 0.45833
| Rajendrapur | 137 | 20:00 | 129 | 8:00 | Bhandaria | 141 | 0.625 | 134 | 0.79167
| Valuka | 128 | 21:00 | 119 | 15:00 | Ishurdi | 138 | 18:00 | 135 | 12:00
| Tangail | 135 | 6:00 | 126 | 15:00 | Ruppur Paromanobik | 138 | 6:00 | 135 | 12:00
| Mymensing | 130 | 11:00 | 121 | 14:00 | Natore | 137 | 18:00 | 133 | 4:00
| Kishorganj | 130 | 11:00 | 124 | 14:00 | Bogra | 139 | 5:00 | 134 | 8:00
| Netrokona | 129 | 21:00 | 117 | 15:00 | Noagaon | 134 | 5:00 | 129 | 12:00
| Jamalpur | 139 | 18:30 | 125 | 1:00 | Rajshahi | 140 | 1:00 | 132 | 12:00
| Sherpur | 138 | 20:00 | 121 | 1:00 | Rajshahi New | 140 | 1:00 | 130 | 5:00
| Srimongal | 136 | 1:00 | 134 | 17:00 | C.Nawabganj | 138 | 4:00 | 130 | 8:00
| Shahjibazar | 134 | 6:00 | 132 | 3:00 | Amnura | 140 | 1:00 | 131 | 7:00
| Fenchuganj | 138 | 1:00 | 136 | 2:00 | Pabna | 138 | 6:00 | 134 | 12:00
| Khulawara | 137 | 9:00 | 136 | 1:00 | Shahjadpur | 141 | 1:00 | 137 | 18:00
| Sylhet | 136 | 1:00 | 135 | 7:00 | Serajganj | 136 | 1:00 | 132 | 12:00
| Chatak | 135 | 1:00 | 133 | 12:00 | Niyamatpur | 133 | 3:00 | 126 | 12:00
| Sunamganj | 136 | 17:00 | 133 | 12:00 | Joypurhat | 136 | 5:00 | 129 | 12:00
| Biani Bazar | 135 | 1:00 | 134 | 11:00 | Sherpur(Bogura) | 138 | 20:00 | 135 | 12:00
| Comilla(s) | 131 | 2:00 | 126 | 17:00 | Mohastangor | 137 | 1:00 | 133 | 12:00
| Comilla(n) | 142 | 21:00 | 137 | 10:00 | Bangura | 141 | 6:00 | 137 | 7:00
| Chandpur | 145 | 18:00 | 142 | 11:00 | Rangpur | 130 | 6:00 | 126 | 16:00
| Feni | 141 | 18:00 | 132 | 11:00 | Lalmonirhat | 130 | 6:00 | 126 | 16:00
| Chowmuhani | 138 | 18:00 | 132 | 14:00 | Saidpur | 132 | 6:00 | 124 | 18:30
| Ashuganj | 135 | 18:00 | 133 | 3:00 | Purbasadipur | 129 | 5:00 | 123 | 18:00
| Daudkandi | 140 | 19:00 | 134 | 15:00 | Thakurgaon | 130 | 6:00 | 120 | 18:00
| B.Baria | 131 | 20:00 | 129 | 17:00 | Palashbari | 135 | 4:00 | 129 | 7:00
| Ramganj | 139 | 9:00 | 135 | 18:00 | Barapukuria | 133 | 6:00 | 130 | 18:00
| Chaddagram | 140 | 18:00 | 133 | 15:00 | Panchagar | 129 | 6:00 | 117 | 18:30
| PHP | 138 | 18:00 | 131 | 11:00 | Joldhaka | 132 | 0.25 | 123 | 0.77083

## L-Curve
Date | 2021-01-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 4753 | 2407 | 7160 |  |  |  | QF-LDC-11
0:30 | 298 | 4470.5 | 2345.5 | 6816 | Date: | 2021-01-07
1:00 | 326 | 4188 | 2284 | 6472
1:30 | 356 | 4065 | 2253.5 | 6318.5
2:00 | 386 | 3942 | 2223 | 6165
2:30 | 388 | 3887.5 | 2165 | 6052.5 | [5 empty] | Gen. at Eve. Peak | 9116 | 9116 MW (19:00 )
3:00 | 390 | 3833 | 2107 | 5940 | [6 empty] | 19:00
3:30 | 386.5 | 3782 | 2093 | 5875 | [5 empty] | Gen. at Day Peak | 7752 | 7752 MW (12:00 )
4:00 | 383 | 3731 | 2079 | 5810 | [6 empty] | 12:00
4:30 | 376.5 | 3712.5 | 2075 | 5787.5 | [5 empty] | Highest Generation | 9116
5:00 | 370 | 3694 | 2071 | 5765 | [6 empty] | 19:00
5:30 | 371.5 | 3813.5 | 2092.5 | 5906
6:00 | 373 | 3933 | 2114 | 6047
6:30 | 306 | 4057.5 | 2157.5 | 6215
7:00 | 239 | 4182 | 2201 | 6383
7:30 | 244.5 | 4310 | 2343.5 | 6653.5
8:00 | 250 | 4438 | 2486 | 6924
8:30 | 288 | 4575 | 2558.5 | 7133.5
9:00 | 326 | 4712 | 2631 | 7343
9:30 | 361 | 4798.5 | 2575 | 7373.5
10:00 | 396 | 4885 | 2519 | 7404
10:30 | 387 | 4941 | 2489 | 7430
11:00 | 378 | 4997 | 2459 | 7456
11:30 | 372.5 | 5080 | 2524 | 7604
12:00 | 367 | 5163 | 2589 | 7752
12:30 | 342.5 | 5234.5 | 2586 | 7820.5
13:00 | 318 | 5306 | 2583 | 7889
13:30 | 344 | 5172.5 | 2499.5 | 7672
14:00 | 370 | 5039 | 2416 | 7455
14:30 | 422.5 | 5023 | 2409 | 7432
15:00 | 475 | 5007 | 2402 | 7409
15:30 | 450.5 | 4957.5 | 2371 | 7328.5
16:00 | 426 | 4908 | 2340 | 7248
16:30 | 449.5 | 5008.5 | 2360 | 7368.5
17:00 | 473 | 5109 | 2380 | 7489
17:30 | 314 | 5248.5 | 2665 | 7913.5
18:00 | 155 | 5388 | 2950 | 8338
18:30 | 114 | 5753.5 | 2973.5 | 8727
19:00 | 73 | 6119 | 2997 | 9116
19:30 | 92 | 6049 | 3051 | 9100
20:00 | 92 | 6004 | 3021 | 9025 |  |  |  | Executive Engineer
20:30 | 179.5 | 5881.5 | 3043.5 | 8925 |  |  |  | Network Operation Division
21:00 | 267 | 5759 | 3066 | 8825
21:30 | 324.5 | 5515 | 2973.5 | 8488.5
22:00 | 382 | 5271 | 2881 | 8152 |  |  |  |  | Page 6 of 7
22:30 | 365 | 5099.5 | 2774.5 | 7874
23:00 | 348 | 4928 | 2668 | 7596
23:30 | 309 | 4840.5 | 2537.5 | 7378
24:00 | 270 | 4753 | 2407 | 7160
9116 MW (19:00 )
7752 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-07 |  | Energy | 186611210
[11 empty] | 2021-01-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2942 | 670 | 1308 | 1599 | 630 | 42 | 123 | 0 | 82 | 0
0:30 | 2915 | 553.5 | 1363 | 1327.5 | 595 | 38.5 | 61.5 | 0 | 80 | 0 | Date: | 2021-01-07
1:00 | 2888 | 437 | 1418 | 1056 | 560 | 35 | 0 | 0 | 78 | 0
1:30 | 2857 | 437 | 1383.5 | 981 | 550 | 35 | 0 | 0 | 75 | 0 | [7 empty] | Total Energy | 186.6112 | Total Energy Gen 186.611 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 186.611 MKWHr
2:00 | 2826 | 437 | 1349 | 906 | 540 | 35 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2825 | 437 | 1354 | 798.5 | 530 | 35 | 0 | 0 | 73 | 0 | [7 empty] | Energy Requirement | 186.6112
3:00 | 2824 | 437 | 1359 | 691 | 520 | 35 | 0 | 0 | 74 | 0
3:30 | 2805 | 437 | 1338 | 667 | 520 | 35 | 0 | 0 | 73 | 0 | [6 empty] | Shortage
4:00 | 2786 | 437 | 1317 | 643 | 520 | 35 | 0 | 0 | 72 | 0
4:30 | 2786 | 437 | 1319 | 618.5 | 520 | 35 | 0 | 0 | 72 | 0
5:00 | 2786 | 437 | 1321 | 594 | 520 | 35 | 0 | 0 | 72 | 0
5:30 | 2812.5 | 437 | 1339 | 685.5 | 525 | 35 | 0 | 0 | 72 | 0
6:00 | 2839 | 437 | 1357 | 777 | 530 | 35 | 0 | 0 | 72 | 0
6:30 | 2802 | 437 | 1346.5 | 996 | 525 | 35 | 0 | 0 | 73 | 0.5 |  |  |  |  | Coal
7:00 | 2765 | 437 | 1336 | 1215 | 520 | 35 | 0 | 0 | 74 | 1
7:30 | 2767 | 483 | 1325 | 1423 | 525 | 35 | 12.5 | 0 | 72 | 11 |  |  |  | Oil |  |  |  | ,
8:00 | 2769 | 529 | 1314 | 1631 | 530 | 35 | 25 | 0 | 70 | 21
8:30 | 2749.5 | 529.5 | 1294 | 1858 | 540 | 35 | 34 | 0 | 69 | 24.5
9:00 | 2730 | 530 | 1274 | 2085 | 550 | 35 | 43 | 0 | 68 | 28
9:30 | 2706 | 553 | 1229.5 | 2166.5 | 534 | 35 | 43 | 0 | 71 | 35.5
10:00 | 2682 | 576 | 1185 | 2248 | 518 | 35 | 43 | 0 | 74 | 43
10:30 | 2694 | 576 | 1197.5 | 2245.5 | 514 | 35 | 43 | 0 | 74 | 51
11:00 | 2706 | 576 | 1210 | 2243 | 510 | 35 | 43 | 0 | 74 | 59
11:30 | 2766.5 | 576.5 | 1303.5 | 2233.5 | 505 | 35 | 47.5 | 0 | 76 | 60.5
12:00 | 2827 | 577 | 1397 | 2224 | 500 | 35 | 52 | 0 | 78 | 62
12:30 | 2881.5 | 577 | 1390 | 2240 | 505 | 35 | 52 | 0 | 80 | 60
13:00 | 2936 | 577 | 1383 | 2256 | 510 | 35 | 52 | 0 | 82 | 58
13:30 | 2936 | 577 | 1383 | 2256 | 510 | 35 | 52 | 0 | 82 | 58
14:00 | 2936 | 577 | 1383 | 2256 | 510 | 35 | 52 | 0 | 82 | 58
14:30 | 2960 | 576.5 | 1314.5 | 2096 | 490 | 35 | 52 | 0 | 79 | 46
15:00 | 2984 | 576 | 1246 | 1936 | 470 | 35 | 52 | 0 | 76 | 34
15:30 | 2960 | 576.5 | 1299.5 | 1829 | 470 | 35 | 60 | 0 | 77 | 21.5
16:00 | 2936 | 577 | 1353 | 1722 | 470 | 35 | 68 | 0 | 78 | 9
16:30 | 2933 | 576.5 | 1304 | 1857.5 | 475 | 35 | 97.5 | 0 | 85 | 5
17:00 | 2930 | 576 | 1255 | 1993 | 480 | 35 | 127 | 0 | 92 | 1
17:30 | 2919.5 | 694.5 | 1346 | 2110 | 500 | 35 | 211 | 0 | 97 | 0.5
18:00 | 2909 | 813 | 1437 | 2227 | 520 | 35 | 295 | 0 | 102 | 0
18:30 | 2908 | 812.5 | 1442 | 2565 | 570 | 35 | 289.5 | 0 | 105 | 0
19:00 | 2907 | 812 | 1447 | 2903 | 620 | 35 | 284 | 0 | 108 | 0
19:30 | 2910 | 812 | 1498 | 2764 | 650 | 80 | 284 | 0 | 102 | 0
20:00 | 2911 | 813 | 1472 | 2713 | 650 | 80 | 284 | 0 | 102 | 0
20:30 | 2920.5 | 813 | 1477 | 2616.5 | 660 | 62.5 | 274.5 | 0 | 101 | 0
21:00 | 2930 | 813 | 1482 | 2520 | 670 | 45 | 265 | 0 | 100 | 0
21:30 | 2914 | 813 | 1432 | 2275.5 | 670 | 44 | 242 | 0 | 98 | 0
22:00 | 2898 | 813 | 1382 | 2031 | 670 | 43 | 219 | 0 | 96 | 0
22:30 | 2900.5 | 813 | 1346 | 1815 | 670 | 42 | 195.5 | 0 | 92 | 0
23:00 | 2903 | 813 | 1310 | 1599 | 670 | 41 | 172 | 0 | 88 | 0
23:30 | 2922.5 | 741.5 | 1309 | 1599 | 650 | 41.5 | 147.5 | 0 | 85 | 0 | Max Temp. in Dhaka |  | 30.2° C
24:00 | 2942 | 670 | 1308 | 1599 | 630 | 42 | 123 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 186.611 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 186.611 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [19 empty] | 0 | 45 | 45 | 45 | 43 | 41 | 42 | 214167
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 0 |  |  |  | 712000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 25 | [5 empty] | 0 | 32155
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 8 | 11 | 18 | 18 | 18 | 15 | 12 |  | 0 | [9 empty] | 106785
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 13 | 82 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 627456
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 |  |  |  |  | 2 | 44 | 120 | 190 | 250 | 284 | 284 | 284 | 284 | 283 | 245 | 250 | 260 |  | 275 | 284 | 285 | 283 | 245 | 145 | 95 | 4303089
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [12 empty] | 20 | 20 | 127 | 20 | 30 | 35 |  | 41 | 70 | 85 | 92 | 102 | 103 | 102 | 758000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7580827
26
28 | Ashuganj TPP Unit- 3 | 75 | 75 | 75 | 75 | 75 | 75 | 70 | 70 | 70 | 70 | 70 | [14 empty] | 0 | 780994
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 166032
33 | Ashuganj 225 MW CCPP | 183 | 180 | 135 | 115 | 121 | 122 | 125 | 125 | 125 | 139 | 125 | 157 | 157 | 164 | 194 | 188 | 178 | 172 |  | 164 | 163 | 162 | 155 | 145 | 146 | 146 | 3683000
34 | Ashuganj 450 MW CCPP(South) | 275 | 280 | 275 | 250 | 250 | 250 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 |  | 235 | 235 | 235 | 235 | 235 | 265 | 295 | 6007000
| Ashuganj 450 MW CCPP(North) | 30 | 45 | 90 | 105 | 120 | 120 | 120 | 125 | 125 | 225 | 230 | 290 | 380 | 325 | 310 | 350 | 377 | 380 |  | 385 | 380 | 380 | 383 | 395 | 365 | 335 | 6087000
35 | Ashuganj 55 MW PP (Precision) | 56 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 219840
36 | Chandpur 150 MW CCPP | 88 | 90 | 90 | 86 | 91 | 91 | 91 | 91 | 81 | 84 | 91 | 92 | 90 | 88 | 90 | 88 | 90 | 88 |  | 80 | 88 | 84 | 82 | 82 | 90 | 81 | 2071090
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 348 | 354 | 353 | 351 | 360 | 384 | 348 | 357 | 363 | 348 | 348 | 358 | 359 | 350 | 351 | 367 | 360 | 351 |  | 351 | 351 | 350 | 358 | 350 | 350 | 352 | 8660990
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 320 | 320 | 320 | 320 | 290 | 353 | 353 | 354 | 320 | 252 | 252 | 313 | 356 | 285 | 285 | 325 | 307 | 357 |  | 357 | 357 | 359 | 359 | 320 | 300 | 300 | 7690000
42 | RPCL 210MW CCPP | 106 | 108 | 107 | 108 | 107 | 107 | 101 | 94 | 92 | 123 | 145 | 144 | 106 | 105 | 106 | 104 | 107 | 108 |  | 108 | 109 | 109 | 108 | 109 | 108 | 140 | 2564920
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 6 | 16 | 26 | 33 | 34 | 30 | 28 | 16 | 6 | 1 | [9 empty] | 196020
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 |  |  |  | 628000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 0 | [5 empty] | 501720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 68 | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 40 | 40 | 40 | 40 | 64 | 63 | 62 | 65 | 67 | 67 |  | 69 | 68 | 69 | 69 | 69 | 69 | 69 | 1539072
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 60 | 60 | 73 | 73 | 73 | 73 | 71 | 70 | 69 | 68 | 69 | 68 | 69 | 10 | 69 |  | 73 | 73 | 73 | 70 | 70 | 70 | 70 | 1619520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 216 | 209 | 209 | 210 | 209 | 209 | 210 | 210 | 209 | 143 | 143 | 162 | 172 | 171 | 171 | 171 | 171 | 171 |  | 171 | 171 | 171 | 190 | 190 | 190 | 190 | 4405960
51 | Sylhet 20 MW GTPP | 19 | [11 empty] | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 228000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | [10 empty] | 8 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 116820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 2 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 205500
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 34 | 34 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 594600
56 | Shahjahanulla 25 MW PP | 15 | [10 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 202944
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 290 | 290 | 300 | 320 | 290 | 290 | 295 | 250 | 270 | 290 | 285 | 280 | 280 | 300 | 290 | 300 |  | 290 | 300 | 290 | 300 | 270 | 290 | 290 | 7230000
| Bibiyana South 400 MW | 271 | 270 | 269 | 270 | 270 | 270 | 270 | 272 | 267 | 270 | 270 | 270 | 264 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 13690900
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 45 | 55 | 55 | 53 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 30 |  | 55 | 55 | 55 | 55 |  |  | 0 | 642599
59 | Tangail Palli Power Gen 22 MW | [5 empty] | 1 | 21 | 22 | 24 | 23 | 22 | 22 | 26 | 23 |  | 7 | 19 | 23 |  | 18 | 20 | 23 | 24 |  |  | 0 | 331440
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 368160
61 | Narshingdi 22 MW PP (Doreen) | 22 | [11 empty] | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 264240
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512748
63 | Impoprt (Tripura) | 78 | 72 | 74 | 72 | 72 | 72 | 74 | 70 | 68 | 74 | 74 | 78 | 82 | 84 | 76 | 78 | 92 | 102 |  | 108 | 102 | 102 | 100 | 96 | 88 | 82 | 1991040
64 | Malancha, Ctg. EPZ (United) | 34 | 37 | 40 | 40 | 40 | 40 | 25 | 10 | 5 | 7 | 7 | 8 | 8 | 7 | 5 | 5 | 6 | 0 |  | 20 | 33 | 34 | 38 | 39 | 39 | 40 | 454560
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 437200
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820600
68 | Cumilla 25 MW PP (Summit) | 22 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 497240
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 33 | 28 | 28 | 28 | 33 | 33 | 33 | 32 | 30 | 30 | 22 | 26 | 26 | 28 | 28 | 22 |  | 24 | 30 | 32 | 33 | 33 | 33 | 33 | 680040
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 618700
73 | Ghorashal 108MW PP (Regent) | [10 empty] | 28 | 50 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 52 | 52 | 690000
| Feni Lanka Power | [17 empty] | 52 |  | 17 | [6 empty] | 71820
| Chowmuhani 113 MW | 9 | [6 empty] | 4 | 20 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 66 |  | 113 | 113 | 113 | 113 | 113 | 55 | 55 | 1152480
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 | 90 | 72 | 72 | 74 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1612800
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 4 | 14 | 7 | 7 | 7 | 7 |  |  | 1 | 24 |  | 84 | 60 | 50 |  |  |  | 0 | 231360
78 | Gazipur 52 MW PP | [9 empty] | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | [6 empty] | 265788
79 | Kodda 150MW PP | [15 empty] | 16 | 48 | 115 |  | 84 | 84 | 84 | 65 | 48 | 32 | 0 | 505920
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 10 | 25 | 16 | 8 | 8 | 8 | 8 | 8 |  | 2 | 24 |  | 82 | 90 | 90 | 91 | 25 | 8 | 0 | 501120
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 8 |  | 25 | [6 empty] | 48014
| Gazipur 100 MW PP | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 66 |  | 105 | 70 | 35 |  |  |  | 0 | 416460
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 8 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25561
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 53 | 41 | 54 | 6 |  | 39 | 54 | 54 | 54 | 54 | 54 | 54 | 1188004
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [6 empty] | 3 | 28 | 30 | 30 | 30 | 30 | 37 | 52 | 48 | 48 | 48 | 48 |  | 55 | 81 | 80 | 64 | 48 | 30 | 30 | 838416
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 41 |  |  |  |  | 11 | 50 | 60 | 85 | 87 | 90 | 100 | 86 | 85 | 85 | 60 | 70 | 85 |  | 85 | 85 | 85 | 85 | 82 | 60 | 30 | 1507884
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 3 | 47 | 50 | 50 | 50 | 50 | 45 | 7 | 7 | 25 |  | 93 | 50 | 58 | 50 |  |  | 0 | 590400
| Meghnaghat 104 MW PP (OPCL) | [5 empty] | 6 | 34 | 44 | 75 | 90 | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 53 | 53 | 1474560
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1204632
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1232202
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 16 | 32 | 58 | 58 | 58 | 58 | 40 | 32 | 58 | 58 |  | 32 | 32 | 32 |  |  |  | 0 | 530784
95 | Patenga 50MW PP (Baraka) | 25 | [6 empty] | 2 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 4 |  | 40 | 50 | 50 | 50 | 50 | 50 | 25 | 613440
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 25 | 15 |  |  |  |  | 0 | 183353
100 | Manikganj 55 MW PP (Northern) | [15 empty] | 6 | 35 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 164319
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [8 empty] | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 9050
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 54 |  | 17 | 17 | 17 |  |  |  | 0 | 227520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 35 | 35 | 35 | 8 | 8 | 26 | 106 | 150 | 170 | 140 | 140 | 140 | 140 | 70 | 70 | 89 | 113 | 146 |  | 185 | 185 | 185 | 185 | 185 | 195 | 170 | 2868000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 14 | 17 | 42 | 49 | 50 | 50 | 20 | 17 | 16 | 16 | 70 |  | 126 | 128 | 127 | 117 | 81 | 28 | 0 | 860832
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 20 | 30 | 50 | 78 | 50 | 50 | 20 | 20 | 10 | 10 | 10 | 40 | 18 |  | 100 | 100 | 100 | 100 | 50 | 20 | 20 | 673200
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 90 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1718880
117 | Ashuganj 150MW PP (Midland) | 102 | 102 | 30 | 10 | 10 | 23 | 60 | 75 | 100 | 102 | 102 | 102 | 100 | 100 | 103 | 102 | 93 | 97 |  | 100 | 100 | 102 | 102 | 102 | 102 | 102 | 2107636
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 6 |  | 55 | 25 | 25 |  |  |  | 0 | 92400
| Anwara 300 MW PP (United) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 286 | 288 | 307 | 308 | 309 | 307 | 307 | 252 | 250 | 250 |  |  | 175 | 198 | 195 | 195 | 161 | 161 | 162 | 5823600
| Juldah unit-2 (Acorn) | 100 | 100 | 60 | 60 | 10 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2031360
| Anlima Energy Ltd. | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4188 | 3942 | 3833 | 3731 | 3694 | 3933 | 4182 | 4438 | 4712 | 4885 | 4997 | 5163 | 5306 | 5039 | 5007 | 4908 | 5109 | 5388 |  | 6119 | 6049 | 6004 | 5759 | 5271 | 4928 | 4753 | 124159450
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 66 | 66 | 66 | 99 | 115 | 115 | 99 | 83 | 83 | 83 | 99 | 99 | 99 | 99 | 99 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2364480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 2 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 23060
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [5 empty] | 17 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 |  | 70 | 70 | 70 | 105 | 70 | 53 | 53 | 1528320
130
131
132 | United Payra Power Ltd. | 54 | 54 | 54 | 53 | 54 | 53 | 54 | 41 | 54 | 44 | 45 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1251600
133 | Bhola Nutan Biddut BD LTD (GAS) | 58 | 58 | 57 | 57 | 57 | 34 | 34 | 45 | 33 | 38 | 38 | 30 | [14 empty] | 567054
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 5 | 16 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 84768
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 33 | 31 | 31 | 51 | 60 | 60 | 62 | 61 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1059832
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 21 | 21 | 22 | 18 | 18 | 18 | 18 | 19 | 20 | 21 | 21 | 19 | 19 | 14 | 25 |  | 25 | 27 | 27 | 27 | 27 | 25 | 24 | 513100
141 | Noapara 100 MW PP (Bangla Trac) | [7 empty] | 11 | [17 empty] | 0 | 49920
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 40 | 40 | 40 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | [8 empty] | 397875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 437 | 437 | 437 | 437 | 437 | 437 | 437 | 529 | 530 | 576 | 576 | 577 | 577 | 577 | 576 | 577 | 576 | 813 |  | 812 | 812 | 813 | 813 | 813 | 813 | 670 | 14384000
147 | Bheramara 410 MW CCPP | 315 | 315 | 320 | 320 | 320 | 330 | 310 | 310 | 300 | 240 | 240 | 270 | 270 | 250 | 245 | 245 | 240 | 235 |  | 220 | 210 | 200 | 195 | 190 | 185 | 200 | 6634656
148 | Payra 1320 MW | 410 | 390 | 370 | 370 | 370 | 380 | 370 | 380 | 400 | 370 | 360 | 350 | 360 | 320 | 320 | 320 | 330 | 370 |  | 470 | 500 | 500 | 520 | 520 | 520 | 480 | 10568800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 148 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3686600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 193 | 193 | 193 | 193 | 160 | 181 | 180 | 180 | 180 | 163 | 164 | 188 | 169 | 162 | 163 | 171 | 140 | 140 |  | 149 | 155 | 153 | 149 | 147 | 148 | 149 | 4323082
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 354 | 377 | 380 | 354 | 378 | 340 | 368 | 349 | 332 | 354 | 330 | 415 | 385 | 314 | 300 | 343 | 334 | 396 |  | 391 | 417 | 398 | 397 | 365 | 296 | 294 | 8876327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 216918
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 18 |  |  | 0 |  |  |  |  | 0 | 32600
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 25 | 43 | 43 | 43 | 52 | 52 | 52 | 52 | 52 | 64 | 94 |  | 94 | 94 | 94 | 94 | 65 | 34 | 17 | 973704
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 |  |  |  | 10 | 50 | 68 | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 82 | 113 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 2064358
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 25 | 80 | 50 | 50 | 50 | 50 | 35 | 35 | 35 | 50 | 113 |  | 113 | 113 | 113 | 113 | 70 | 70 | 35 | 1194528
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [5 empty] | 20 | 40 | 65 | 92 | 71 | 70 | 68 | 70 | 36 | 35 |  | 35 | 90 |  | 106 | 106 | 106 | 106 | 67 | 36 | 0 | 1130880
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 23458
178
178