## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-09 | Saturday
|  |  | Date (day): | 2021-01-09 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12412.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13677 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-08 | 2021-01-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 101 | 0 | 100 | 100 | 80 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 330 | 300 | 340
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 98 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 351 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 307 | 359 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 60 | 245 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 17 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 4 | 53 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1398 | 1830 | 3319 | 3649 | 1009 | 1372
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 46 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 40 | 25 | 35
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 215 | 124 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 507 | 633 | 1255 | 1240 | 920 | 103
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 173 | 185 | 180 | 180
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 325 | 300 | 360
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 330 | 300 | 330 | 30 |  | Gas shortage
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 26 | 5 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 53 | 5 | 50 | 5 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 149 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 91 |  | 72 | Gas shortage
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 68 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 98 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1257 | 1491 | 1777 | 2198 | 639 | 84
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 137 | 161 | 150 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 40 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 182 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 300 | 429 | 655.6 | 604 | 52 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 45 | 45
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 20 | 20
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 44 | 44 | 44
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 40 | 68 | 68
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 100 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 164 | 200 | 200
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 330 | 330
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 130 | 130 | 400 | 400 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 792 | 952 | 1384 | 1384 | 330 | 425
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 470 | 707 | 678 | 822
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 275 | 260 | 300 | 325 | 85 |  | Gas shortage
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 877 | 1121 | 1493 | 1948 | 85 | 58
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 26 | 24 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 30 | 60 | 60 | 61 | 34 |  | Gas shortage
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 360 | 420 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 28 | 55 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 35 | 55 | 54 | 54
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 473 | 616 | 898 | 907 | 34 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 180 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 407 | 317 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 20 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 69 | 94 | 94
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 728 | 823 | 1360 | 1484 | 601 | 15
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 153 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 6485 | 8158 | 12412.6 | 13677 | 3794 | 2468
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6236.9833 | 7846 | 11937.8842 | 13153.9277
| A. |  | 2021-01-08 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 8158 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5922 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8158 | MW
| 3 | Day peak Generation : |  |  | 6485 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7846 | MW
| 4 | Evening peak Generation : |  |  | 8158 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 162.4615 | MKWHr | By Solar | 0.4007 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.3588 | MKWHr |  | By Oil: | 29.9836 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.1007 | MKWHr |  | By Hydro: | 1.0551 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3794 | MW | Dhaka | 2560 | 2560 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2468 | MW | Chittagong | 929 | 929 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6262 | MW | Khulna | 1006 | 1006 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 772.42 | MMCFD |  |  | Rajshahi | 826 | 826 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 109417766.182 | ii) Oil : | Taka | 210825004.02 | Comilla | 709 | 709 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 65697623 | Total | Taka | 385940393.202 | Mymensingh | 714 | 714 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.037 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 63 | MW (E to W) at | 19:30 | hrs | Barisal | 231 | 231 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -37 | MW at | 18:30 | hrs | Rangpur | 557 | 557 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.4° C |  |  | Total | 7846 | 7846 |  | 0
| B. |  | 2021-01-09 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 28.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13677 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
| 4 | Reserve(Generation end) |  |  |  | 4577 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 181.2208 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5529 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.68 | MKWHr. | ii) HVDC Flow at Peak Time |  | 707 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8826 | MKWHr. | iii) Maximum HVDC Flow : |  | 708 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.72 |  | (b) Today: | 97.66 |  | (c) Rule Curve: |  | 101.48
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 0 | 300 | 52 | 0 | 372 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 25 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 151 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 78 | 161 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 69 | 70 | 0 | 190 | 19 | 0 | 9 | 310 | 14 | 11 | 0 | 95 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 68 | 102 | 0 | 0 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 72 | 0 | 0 |  | 439 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 154 | 0 | 360 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 54 |  | 4474 | 2103 | 6577 | 2992 | 439 | 1392 | 984 | 610 | 44 | 38 | 78 | 0 | 0 | 97.73
2:00 | 0 | 0 | 102 | 0 | 300 | 52 | 0 | 362 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 6 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 153 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 163 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 69 | 71 | 0 | 190 | 19 | 0 | 9 | 310 | 14 | 11 | 0 | 15 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 50 | 270 | 0 | 0 | 72 | 0 | 0 |  | 440 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 158 | 0 | 329 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 54 |  | 4203 | 2073 | 6276 | 3012 | 440 | 1362 | 733 | 590 | 46 | 17 | 76 | 0 | 0 | 97.73
3:00 | 0 | 0 | 102 | 0 | 300 | 52 | 0 | 354 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 153 | 8 | 83 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 74 | 162 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 68 | 71 | 0 | 190 | 19 | 0 | 9 | 290 | 14 | 11 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 131 | 54 | 0 | 0 | 0 | 20 | 270 | 0 | 0 | 72 | 0 | 0 |  | 439 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 168 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 36 |  | 4016 | 2008 | 6024 | 3007 | 439 | 1342 | 526 | 590 | 46 | 0 | 74 | 0 | 0 | 97.73
4:00 | 0 | 0 | 102 | 0 | 300 | 52 | 0 | 377 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 153 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 74 | 162 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 68 | 71 | 0 | 190 | 19 | 0 | 9 | 320 | 14 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 135 | 54 | 0 | 0 | 0 | 20 | 270 | 0 | 0 | 72 | 0 | 0 |  | 345 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 177 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 30 |  | 4051 | 1915 | 5966 | 3040 | 345 | 1360 | 512 | 590 | 45 | 0 | 74 | 0 | 0 | 97.72
5:00 | 0 | 0 | 105 | 0 | 300 | 52 | 0 | 366 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 153 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 70 | 162 | 0 | 22 | 0 | 0 | 0 | 31 | 25 | 0 | 0 | 68 | 71 | 0 | 190 | 19 | 0 | 9 | 310 | 14 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 125 | 54 | 0 | 0 | 0 | 20 | 270 | 0 | 0 | 72 | 0 | 0 |  | 345 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 184 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 21 |  | 3984 | 1938 | 5922 | 3044 | 345 | 1335 | 493 | 590 | 45 | 0 | 70 | 0 | 0 | 97.72
6:00 | 0 | 0 | 101 | 0 | 300 | 52 | 0 | 375 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 335 | 300 | 153 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 70 | 166 | 0 | 22 | 0 | 0 | 0 | 31 | 25 | 0 | 0 | 68 | 72 | 0 | 190 | 19 | 0 | 9 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 195 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 72 | 0 | 0 |  | 345 | 0 | 255 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 176 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 27 |  | 4161 | 1984 | 6145 | 3049 | 345 | 1374 | 671 | 590 | 46 | 0 | 70 | 0 | 0 | 97.72
7:00 | 0 | 0 | 101 | 0 | 300 | 52 | 0 | 349 | 290 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 335 | 320 | 142 | 8 | 79 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 70 | 164 | 0 | 22 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 69 | 72 | 0 | 170 | 18 | 0 | 9 | 275 | 16 | 5 | 0 | 19 | 0 | 0 | 55 | 0 | 0 | 1 | 0 | 68 | 38 | 0 | 0 | 0 | 0 | 0 | 215 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 72 | 0 | 0 |  | 329 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 378 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 28 |  | 4151 | 1919 | 6070 | 2934 | 329 | 1257 | 863 | 570 | 46 | 0 | 70 | 1 | 0 | 97.71
8:00 | 0 | 0 | 100 | 0 | 300 | 52 | 0 | 356 | 290 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 300 | 320 | 148 | 8 | 73 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 0 | 68 | 165 | 0 | 22 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 69 | 72 | 0 | 170 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 30 | 0 | 0 | 60 | 0 | 0 | 6 | 0 | 68 | 65 | 0 | 0 | 0 | 0 | 1 | 215 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 6 | 72 | 0 | 0 |  | 440 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 363 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 34 |  | 4182 | 2007 | 6189 | 2887 | 440 | 1265 | 930 | 540 | 46 | 0 | 68 | 13 | 0 | 97.71
9:00 | 0 | 0 | 102 | 0 | 300 | 52 | 0 | 354 | 257 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 300 | 320 | 142 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 64 | 164 | 0 | 22 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 67 | 72 | 0 | 170 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 12 | 0 | 68 | 122 | 0 | 0 | 0 | 0 | 2 | 215 | 54 | 0 | 0 | 0 | 100 | 130 | 0 | 19 | 72 | 0 | 0 |  | 472 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 339 | 0 | 0 | 112 | 0 | 0 | 0 | 1 | 0 | 360 | 0 | 0 | 30 |  | 4188 | 2002 | 6190 | 2759 | 472 | 1205 | 1100 | 510 | 45 | 0 | 64 | 35 | 0 | 97.71
10:00 | 0 | 0 | 130 | 0 | 300 | 52 | 0 | 367 | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 17 | 8 | 0 | 0 | 44 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 270 | 300 | 146 | 8 | 70 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 70 | 140 | 0 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 74 | 0 | 170 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 68 | 123 | 0 | 0 | 0 | 0 | 3 | 215 | 54 | 0 | 0 | 0 | 100 | 120 | 0 | 29 | 72 | 0 | 0 |  | 475 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 300 | 0 | 0 | 113 | 0 | 0 | 0 | 2 | 0 | 360 | 25 | 0 | 28 |  | 4213 | 1992 | 6205 | 2685 | 475 | 1248 | 1123 | 510 | 44 | 0 | 70 | 50 | 0 | 97.71
11:00 | 0 | 0 | 104 | 0 | 300 | 52 | 0 | 354 | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 17 | 8 | 0 | 0 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 270 | 300 | 160 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 70 | 142 | 0 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 74 | 0 | 171 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 18 | 0 | 68 | 130 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 0 | 100 | 120 | 0 | 37 | 72 | 0 | 0 |  | 472 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 381 | 0 | 0 | 113 | 0 | 0 | 0 | 3 | 0 | 360 | 27 | 0 | 30 |  | 4197 | 2101 | 6298 | 2701 | 472 | 1308 | 1132 | 510 | 42 | 0 | 70 | 63 | 0 | 97.71
12:00 | 0 | 0 | 101 | 0 | 300 | 52 | 0 | 368 | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 12 | 17 | 8 | 0 | 0 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 30 | 0 | 0 | 0 | 270 | 300 | 173 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 74 | 137 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 72 | 0 | 170 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 18 | 0 | 68 | 132 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 0 | 100 | 130 | 4 | 41 | 72 | 0 | 0 |  | 470 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 407 | 17 | 0 | 113 | 0 | 0 | 0 | 3 | 35 | 360 | 28 | 0 | 35 |  | 4254 | 2231 | 6485 | 2773 | 470 | 1351 | 1197 | 510 | 42 | 0 | 74 | 68 | 0 | 97.7
13:00 | 0 | 0 | 101 | 0 | 330 | 52 | 0 | 368 | 353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 11 | 17 | 8 | 0 | 0 | 43 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 17 | 36 | 0 | 0 | 0 | 270 | 300 | 179 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 22 | 82 | 140 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 73 | 0 | 170 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 95 | 0 | 0 | 100 | 0 | 0 | 18 | 10 | 68 | 132 | 0 | 0 | 0 | 0 | 4 | 250 | 54 | 0 | 0 | 35 | 100 | 130 | 39 | 33 | 72 | 0 | 0 |  | 471 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 160 | 0 | 414 | 53 | 0 | 113 | 0 | 34 | 0 | 3 | 70 | 360 | 21 | 0 | 35 |  | 4524 | 2350 | 6874 | 2815 | 471 | 1407 | 1486 | 510 | 43 | 0 | 82 | 60 | 6874 | 97.7
14:00 | 0 | 0 | 101 | 0 | 330 | 52 | 0 | 329 | 277 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 11 | 17 | 8 | 0 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 17 | 35 | 0 | 0 | 0 | 270 | 270 | 195 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 74 | 139 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 136 | 18 | 0 | 9 | 270 | 16 | 5 | 0 | 120 | 0 | 0 | 70 | 0 | 0 | 15 | 10 | 68 | 70 | 0 | 0 | 0 | 0 | 3 | 181 | 54 | 0 | 0 | 17 | 50 | 130 | 53 | 23 | 72 | 0 | 0 |  | 471 | 0 | 250 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 160 | 0 | 334 | 35 | 0 | 35 | 0 | 36 | 0 | 3 | 35 | 340 | 43 | 0 | 35 |  | 4052 | 2065 | 6117 | 2698 | 471 | 1193 | 1101 | 489 | 45 | 0 | 74 | 46 | 0 | 0
15:00 | 0 | 0 | 130 | 0 | 330 | 53 | 0 | 305 | 277 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 11 | 17 | 8 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 25 | 17 | 35 | 0 | 0 | 0 | 270 | 270 | 184 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 0 | 33 | 21 | 66 | 156 | 0 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 138 | 18 | 0 | 9 | 310 | 8 | 5 | 0 | 120 | 0 | 0 | 70 | 0 | 0 | 11 | 10 | 34 | 0 | 0 | 0 | 0 | 0 | 2 | 142 | 54 | 0 | 0 | 17 | 50 | 130 | 53 | 14 | 72 | 0 | 100 |  | 471 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 160 | 0 | 326 | 17 | 0 | 35 | 0 | 36 | 0 | 2 | 35 | 340 | 49 | 0 | 35 |  | 3975 | 2018 | 5993 | 2792 | 471 | 1232 | 867 | 490 | 45 | 0 | 66 | 30 | 0 | 0
16:00 | 0 | 0 | 125 | 0 | 330 | 53 | 0 | 304 | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 25 | 11 | 17 | 8 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 25 | 17 | 28 | 0 | 0 | 0 | 290 | 290 | 188 | 8 | 91 | 12 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 64 | 155 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 20 | 0 | 138 | 18 | 0 | 9 | 300 | 8 | 5 | 0 | 65 | 0 | 0 | 32 | 0 | 0 | 7 | 10 | 20 | 1 | 0 | 0 | 0 | 0 | 1 | 106 | 54 | 0 | 0 | 17 | 30 | 130 | 53 | 5 | 54 | 0 | 100 |  | 471 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 320 | 17 | 0 | 44 | 0 | 36 | 0 | 1 | 35 | 310 | 51 | 0 | 0 |  | 3838 | 1906 | 5744 | 2817 | 471 | 1216 | 657 | 460 | 45 | 0 | 64 | 14 | 0 | 0
17:00 | 0 | 0 | 105 | 0 | 330 | 53 | 0 | 288 | 307 |  | 0 | 0 | 0 | 7 | 10 | 2 | 0 | 0 | 0 | 2 | 0 | 16 | 20 | 0 | 0 | 0 | 17 | 0 | 17 | 15 | 25 | 11 | 17 | 8 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 68 | 0 | 11 | 25 | 17 | 30 | 0 | 0 | 0 | 290 | 290 | 184 | 8 | 82 | 26 | 5 | 0 | 51 | 0 | 0 | 1 | 19 | 8 | 33 | 21 | 70 | 157 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 20 | 0 | 138 | 18 | 0 | 9 | 285 | 8 | 5 | 0 | 65 | 0 | 0 | 32 | 0 | 11 | 1 | 10 | 34 | 97 | 0 | 0 | 6 | 0 | 0 | 160 | 54 | 0 | 0 | 17 | 10 | 130 | 53 | 2 | 54 | 0 | 100 |  | 471 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 301 | 17 | 0 | 70 | 0 | 38 | 0 | 0 | 35 | 320 | 51 | 0 | 0 |  | 4082 | 2007 | 6089 | 2788 | 471 | 1188 | 901 | 470 | 45 | 153 | 70 | 3 | 0 | 0
18:00 | 0 | 0 | 97 | 0 | 330 | 53 | 0 | 313 | 359 |  | 0 | 0 | 0 | 24 | 46 | 15 | 0 | 0 | 0 | 10 | 24 | 16 | 59 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 11 | 17 | 8 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 85 | 0 | 11 | 28 | 17 | 30 | 0 | 0 | 0 | 355 | 330 | 184 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 21 | 92 | 160 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 77 | 0 | 164 | 18 | 0 | 9 | 310 | 8 | 5 | 0 | 83 | 0 | 0 | 65 | 0 | 20 | 0 | 50 | 40 | 133 | 0 | 17 | 17 | 0 | 0 | 162 | 54 | 0 | 0 | 28 | 50 | 130 | 53 | 0 | 72 | 0 | 100 |  | 707 | 0 | 250 | 0 | 96 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 159 | 0 | 304 | 35 | 0 | 79 | 0 | 85 | 0 | 0 | 90 | 350 | 55 | 0 | 54 |  | 4886 | 2572 | 7458 | 2973 | 707 | 1335 | 1631 | 500 | 46 | 174 | 92 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 25 | 0 | 330 | 98 | 0 | 351 | 359 |  | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 85 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 0 | 0 | 50 | 17 | 40 | 0 | 0 | 0 | 335 | 330 | 185 | 8 | 90 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 94 | 160 | 40 | 22 | 0 | 0 | 0 | 18 | 10 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 280 | 8 | 8 | 0 | 240 | 0 | 0 | 147 | 0 | 48 | 0 | 100 | 68 | 133 | 0 | 0 | 0 | 0 | 0 | 123 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 707 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 178 | 0 | 323 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 420 | 55 | 0 | 54 |  | 5249 | 2808 | 8057 | 2976 | 707 | 1456 | 2017 | 570 | 46 | 191 | 94 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 0 | 330 | 98 | 0 | 351 | 359 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 85 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 40 | 0 | 0 | 0 | 325 | 330 | 185 | 8 | 91 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 98 | 161 | 40 | 22 | 0 | 0 | 0 | 53 | 44 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 245 | 0 | 0 | 182 | 0 | 17 | 0 | 100 | 68 | 149 | 0 | 0 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 707 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 180 | 0 | 317 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 55 | 0 | 55 |  | 5335 | 2823 | 8158 | 2958 | 707 | 1568 | 2020 | 570 | 46 | 191 | 98 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 330 | 98 | 0 | 351 | 359 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 28 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 40 | 0 | 0 | 0 | 330 | 330 | 184 | 8 | 91 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 100 | 161 | 40 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 245 | 0 | 0 | 182 | 0 | 21 | 0 | 100 | 68 | 148 | 0 | 0 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 707 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 180 | 0 | 313 | 35 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 420 | 55 | 0 | 55 |  | 5334 | 2817 | 8151 | 2965 | 707 | 1567 | 2021 | 570 | 46 | 175 | 100 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 0 | 330 | 95 | 0 | 352 | 358 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 28 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 42 | 0 | 0 | 0 | 330 | 290 | 184 | 8 | 86 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 98 | 161 | 16 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 305 | 8 | 5 | 0 | 245 | 0 | 0 | 184 | 0 | 0 | 0 | 100 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 708 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 180 | 0 | 321 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 470 | 55 | 0 | 55 |  | 5226 | 2878 | 8104 | 2920 | 708 | 1579 | 1958 | 620 | 46 | 175 | 98 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 0 | 330 | 95 | 0 | 350 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 28 | 20 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 42 | 0 | 0 | 0 | 300 | 290 | 184 | 8 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 94 | 162 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 150 | 0 | 0 | 0 | 50 | 68 | 150 | 0 | 0 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 452 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 180 | 0 | 367 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 470 | 54 | 0 | 55 |  | 4993 | 2636 | 7629 | 2904 | 452 | 1552 | 1830 | 620 | 45 | 132 | 94 | 0 | 0 | 97.68
23:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 350 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 25 | 17 | 40 | 0 | 0 | 0 | 300 | 300 | 192 | 8 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 90 | 162 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 280 | 8 | 11 | 0 | 195 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 50 | 150 | 0 | 0 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 8 | 100 | 130 | 35 | 0 | 72 | 0 | 100 |  | 423 | 0 | 265 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 180 | 0 | 362 | 17 | 0 | 113 | 0 | 72 | 0 | 0 | 35 | 450 | 55 | 0 | 55 |  | 4645 | 2421 | 7066 | 2923 | 423 | 1535 | 1421 | 599 | 45 | 30 | 90 | 0 | 0 | 97.67
24:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 354 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 42 | 0 | 0 | 0 | 300 | 295 | 185 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 82 | 162 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 0 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 100 | 130 | 0 | 0 | 72 | 0 | 100 |  | 424 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 180 | 0 | 368 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 400 | 56 | 0 | 54 |  | 4360 | 2160 | 6520 | 2929 | 424 | 1566 | 920 | 550 | 45 | 4 | 82 | 0 | 0 | 97.67
KWH | 0 | 0 | 2006000 | 0 | 7534282 | 1544136 | 0 | 8500220 | 7418000 |  | 0 | 0 | 0 | 48000 | 226632 | 26570 | 0 | 0 | 0 | 21120 | 27216 | 48960 | 979449 | 0 | 0 | 0 | 110160 | 0 | 301020 | 451116 | 600000 | 554760 | 463400 | 491100 | 0 | 0 | 1055127 | 0 | 0 | 0 | 138189 | 0 | 0 | 0 | 0 |  | 169680 | 0 | 654638 | 0 | 31680 | 603360 | 396384 | 932640 | 0 | 0 | 0 | 7759000 | 7336000 | 4102000 | 217454 | 1975980 | 281880 | 399360 | 0 | 1238720 | 0 | 0 | 13613 | 414676 | 224460 | 820300 | 490700 | 1882560 | 3687080 | 135360 | 502884 | 9200 | 0 | 0 | 447600 | 564120 | 0 | 0 | 1324224 | 1580160 | 0 | 4101000 | 437000 | 0 | 204120 | 7386300 | 261120 | 153000 | 0 | 2473963 | 0 | 0 | 2200800 | 0 | 104976 | 121095 | 465600 | 1498080 | 2301672 | 0 | 39600 | 27096 | 0 | 26159 | 3899127 | 1299404 | 0 | 0 | 367920 | 1830720 | 4293600 | 619200 | 224520 | 1720800 | 0 | 920000 |  | 11680000 | 0 | 6006816 | 0 | 2375040 | 0 | 0 | 0 | 30240 | 0 | 0 | 0 | 495600 | 0 | 0 | 0 | 0 | 0 | 0 | 385080 | 0 | 0 | 0 | 0 | 0 | 491760 | 0 | 229176 | 0 | 0 | 3685000 | 0 | 0 | 0 | 0 | 0 | 0 | 1098196 | 0 | 4212018 | 0 | 8127363 | 490560 | 0 | 1729440 | 0 | 805440 | 0 | 19727 | 885600 | 10415700 | 683100 | 0 | 897600 |  | 107718042 | 54743456 | 162461498 | 70530176 | 11680000 | 32828629 | 28864687 | 14100700 | 1055127 | 1118918 | 1882560 | 400701 | 0
Fuel Cost | 0 | 0 | 2928760 | 0 | 8363053.02 | 2038259.52 | 0 | 8585222.2 | 7640540 |  | 0 | 0 | 0 | 364320 | 1561494.48 | 224782.2 | 0 | 0 | 0 | 159033.6 | 248209.92 | 481766.4 | 9030519.78 | 0 | 0 | 0 | 804168 | 0 | 2968057.2 | 338337 | 450000 | 0 | 0 | 0 | 0 | 0 | 284884.29 | 0 | 0 | 0 | 1283775.81 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6349988.6 | 0 | 275616 | 4778611.2 | 499443.84 | 2769940.8 | 0 | 0 | 0 | 5741660 | 7336000 | 3773840 | 280515.66 | 2272377 | 318524.4 | 559104 | 0 | 2118211.2 | 0 | 0 | 130004.15 | 526638.52 | 168345 | 1435525 | 368025 | 14119200 | 3908304.8 | 1229068.8 | 638662.68 | 146648 | 0 | 0 | 796728 | 880027.2 | 0 | 0 | 2608721.28 | 3018105.6 | 0 | 7094730 | 957030 | 0 | 416404.8 | 7460163 | 195840 | 116280 | 0 | 18703160.28 | 0 | 0 | 11444160 | 0 | 1032963.84 | 1415600.55 | 3794640 | 16254168 | 16226787.6 | 0 | 361152 | 256057.2 | 0 | 0 | 29477400.12 | 11317808.84 | 0 | 0 | 3153074.4 | 12192595.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 67276800 | 0 | 6307156.8 | 0 | 18667814.4 | 0 | 0 | 0 | 317217.6 | 0 | 0 | 0 | 768180 | 0 | 0 | 0 | 0 | 0 | 0 | 3407958 | 0 | 0 | 0 | 0 | 0 | 944179.2 | 0 | 173486.232 | 0 | 0 | 19972700 | 0 | 0 | 0 | 0 | 0 | 0 | 1647294 | 0 | 4928061.06 | 0 | 8046089.37 | 5121446.4 | 0 | 16412385.6 | 0 | 6250214.4 | 0 | 217983.35 | 6544584 | 45724923 | 0 | 0 | 0 |  | 256673035.98 | 212728473.412 | 469401509.392 | 70034023.832 | 67276800 | 39383742.35 | 200268073.42 | 65697623 | 284884.29 | 10556930.6 | 14119200 | 1780231.9 | 0
Yesterday Day Peak | 0 | 0 | 101 | 0 | 300 | 52 | 0 | 368 | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 12 | 17 | 8 | 0 | 0 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 30 | 0 | 0 | 0 | 270 | 300 | 173 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 74 | 137 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 72 | 0 | 170 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 18 | 0 | 68 | 132 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 0 | 100 | 130 | 4 | 41 | 72 | 0 | 0 |  | 470 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 407 | 17 | 0 | 113 | 0 | 0 | 0 | 3 | 35 | 360 | 28 | 0 | 35 |  | 6485 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 330 | 98 | 0 | 351 | 359 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 85 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | 0 | 50 | 17 | 40 | 0 | 0 | 0 | 325 | 330 | 185 | 8 | 91 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 98 | 161 | 40 | 22 | 0 | 0 | 0 | 53 | 44 | 0 | 0 | 40 | 75 | 0 | 164 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 245 | 0 | 0 | 182 | 0 | 17 | 0 | 100 | 68 | 149 | 0 | 0 | 0 | 0 | 0 | 124 | 54 | 0 | 0 | 26 | 100 | 130 | 53 | 0 | 72 | 0 | 100 |  | 707 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 180 | 0 | 317 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 55 | 0 | 55 |  | 8158 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 340 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 35 | 0 | 0 | 0 | 360 | 330 | 180 | 8 | 91 | 26 | 50 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 22 | 147 | 150 | 95 | 22 | 0 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 0 | 100 |  | 822 | 16 | 325 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 94 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 54
Forecast for Day | 0 | 0 | 100 | 0 | 300 | 50 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 25 | 0 | 0 | 0 | 300 | 300 | 180 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 135 | 150 | 95 | 22 | 1.6 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 0 | 100 |  | 678 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 54
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 330 | 106 | 0 | 356 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 20 |  | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 13 | 0 | 0 | 0 | 260 | 270 | 193 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 80 | 157 | 0 | 22 | 0 | 0 | 0 | 11 | 50 | 0 | 0 | 40 | 40 | 0 | 163 | 18 | 0 | 0 | 300 | 0 | 8 | 0 | 61 | 0 | 0 | 108 | 0 | 0 | 6 | 0 | 50 | 73 | 0 | 0 | 0 | 0 | 1 | 142 | 54 | 0 | 0 | 17 | 100 | 130 | 28 | 2 | 72 | 0 | 100 | 0 | 567 | 0 | 350 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 159 | 0 | 334 | 53 | 0 | 60 | 0 | 0 | 0 | 0 | 35 | 350 | 54 | 0 | 18 | 0
199
| Minimum Generation |  | 5922 | 5:00
| Highest Generation |  | 8158 | 19:30
| Day Peak Generation |  | 6485 | 12:00
| Evening Peak Generation |  | 8158 | 19:30
| HVDC Max Flow |  | 708 | 21:00
| HVDC EvPeak Flow |  | 707 | 19:30
| Load factor L.F |  | 82.98%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-09
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6485 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5529 | MW
Evening Peak Generation : |  | 8158 | MW Hour : | 19:30 | Available Max Generation : |  | 13677 | MW
E.P. Demand (at gen end) : |  | 8158 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 8158 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4577 | MW
Total Gen. (MKWH) : |  | 162.4615 | System Load Factor : | 82.98% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -37 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-09
Actual : | 97.66 | Ft.(MSL) , | Rule curve : | 101.48 | Ft.( MSL )
Gas Consumed : | Total = | 772.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 109417766.182
: |  | Coal : | 65697623 | Oil : | 210825004.02 | Total : | 385940393.202
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3267.1378 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1106.0718 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 990.1242 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 894.3485 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 808.382 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 652.3232 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 371.0987 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 168.1238 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 503.0736 |  |  | 0 | 0%
Total | 0 |  | 8760.6835 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Madunaghat 132/33 kV T1 transformer and its associated Bay were under shut down from 08:48 to
13:57 for A/M.
b) Haripur-Fatullah 132 kV Ckt was shut down at 09:58 for A/M.
c) Maniknagar 132/33 kV T1 transformer was under shut down from 09:07 to 14:53 for A/M.
d) Bhulta-Haripur 132 kV Ckt was shut down at 09:09 for C/M.
e) Fenchuganj Power Station 132 kV main Bus was under shut down from 09:20 to 17:54 for C/M.
f) Ramganj 132/33 kV T1 transformer was under shut down from 09:20 to 18:01 for C/M.
g) Pabna 132 kV main Bus was under shut down from 09:20 to 13:56 for A/M.
h) Faridpur 132/33 kV T1 transformer (33 kV side) was under shut down from 08:50 to 10:28 for C/M. |  |  |  |  | About 20 MW power interruption occurred under Faridpur S/S area
from 08:50 to 10:28.
i) Barishal(N) 33 kV Bus was under shut down from 08:53 to 16:18 for C/M.
j) Naogaon S/S-Shantahar P/S 132 kV Ckt was shutdown at 11:30 for safety of power transformer work.
k) Ashuganj-Sirajganj 230 kV Ckt-2 tripped at 12:17 from both end showing Dist. 67-N, GT at Ashuganj
end & Dist. 67-N, GT, 64.8 km at Sirajganj end and was switched on at 13:11.
l) Kabirpur 132/33 kV T3 transformer was under shut down from 09:11 to 17:19 for D/W.
m) Thakurgaon-Purbasadipur 132 kV Ckt-2 tripped at 15:13 from Thakurgaon end due to PT MCB trip |  |  |  |  | About 50 MW power interruption occurred under Thakurgaon and
and was switched on at 15:30. Other Ckt was under shutdown. |  |  |  |  | Panchagar S/S area from 15:13 to 15:30.
n) Ghorashal unit-4 was force shutdown at 19:01 for maintenance.
o) Gopalganj (Old)-Gopalganj (New) 132 kV Ckt-2 is under shut down since 07:07(09/01/2021) for D/W.
p) Sylhet 132/33 kV T1 transformer is under shut down since 07:30(09/01/2021) for C/M.
q) Dohazari-Sikalbaha 132 kV Ckt-1 is under shut down since 07:17(09/01/2021) for D/W.
r) Khulna(Central)-NWPGCL 132 kV Ckt-2 is under shut down since 07:58(09/01/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 2006000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7534282
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 1544136
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8500220
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 359 | 7418000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 48000 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 226632 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 26570 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 979449 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 451116
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 21120 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 27216 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 110160 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 48960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 301020
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1154760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 463400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 491100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 2473963 | High Voltage.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 17 | 104976 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 27096 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 619200 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1720800 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 1830 | 36298176
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 138189
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 121095
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 603360
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1055127 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 654638
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 465600
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 396384 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 932640
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 31680 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26159
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 124 | 3899127 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299404
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1830720
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 633 | 11454123
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 185 | 4102000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7759000
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7336000
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 281880 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 399360
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1238720
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 149 | 2301672
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 1975980
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 1498080 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 414676 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 224460 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 98 | 1882560
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 13613 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 490700 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 367920 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1491 | 31324375
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 161 | 3687080 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502884
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 40 | 135360 | Low demand
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 2200800 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 39600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 224520
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 169680
| Mymensingh Area Total |  |  |  | 709 | 429 | 6969124
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 447600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 564120
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 153000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1324224 | Low demand
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1580160 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 920000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 4101000
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 437000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 261120 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7386300 | Gas shortage
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 204120
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 130 | 4293600 | On test
| Sylhet Area Total |  |  |  | 1988 | 952 | 21672244
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 707 | 11680000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2375040
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 30240 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 6006816 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 490560 | Low demand
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1121 | 20582656
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 495600 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 60 | 1098196
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 420 | 10415700 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 55 | 683100 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 55 | 897600 | On test.
| Barisal Area Total |  |  |  | 1676 | 616 | 13590196
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4212018 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 317 | 8127363 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 491760
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 229176
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 69 | 385080 | Low demand
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1729440
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 885600
| Rajshahi Area Total |  |  |  | 2183 | 823 | 16060437
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3685000
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 805440
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19727
| Rangpur Area Total |  |  |  | 605 | 263 | 4510167
| Total |  |  |  | 20748 | 8158 | 162461498
| Eastern Grid Total |  |  |  | 14000 | 5335 | 107718042
| Western Grid Total |  |  |  | 6748 | 2823 | 54743456
| National Grid Total |  |  |  | 20748 | 8158 | 162461498
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-08
| (a) ENTIRE EASTERN GRID : |  | 5226 | MW | (b) ENTIRE WESTERN GRID : |  | 2620 | MW
| i) Dhaka area |  | 2560 | MW | i) Khulna area |  | 1006 | MW
| ii) Chittagong area |  | 929 | MW | ii) Rajshahi area |  | 826 | MW
| iii) Comilla area |  | 709 | MW | iii) Barisal area |  | 231 | MW
| iv) Mymensingh area |  | 714 | MW | iv) Rangpur area |  | 557 | MW
| v) Sylhet area |  | 314 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7846 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 72 | 21:00 | Jamalpur | 89 | 19:00 | Benapol | 36 | 18:30
| Munsiganj | 80 | 21:00 | Sherpur | 106 | 18:30 | Jhenida | 80 | 18:30
| Sonargaon | 61 | 1:00 | Srimongal | 26 | 19:00 | Bottail | 74 | 18:30
| Shyampur | 220 | 15:00 | Shahjibazar | 90 | 21:00 | G.K Project | 36 | 21:00
| Bhulta | 146 | 1:00 | Fenchuganj | 24 | 18:00 | Faridpur | 120 | 21:00
| Madanganj | 33 | 5:00 | Kulawara | 26 | 18:00 | Madaripur | 62 | 21:00
| Shitalakhya | 77 | 10:00 | Sylhet | 70 | 18:00 | Sariatpur | 42 | 20:00
| Rahim steel | 4 | 1:00 | Chatak | 21 | 18:30 | Gopalganj | 64 | 18:30
| Matuail | 40 | 1:00 | Sunamganj | 28 | 19:30 | Bagerhat | 76 | 18:30
| Ghorasal | 55 | 22:00 | Biani Bazar | 37 | 18:30 | Mongla | 32 | 1:00
| Narsingdi | 114 | 23:00 | Comilla (S) | 100 | 20:00 | Satkhira | 72 | 19:00
| Haripur (SBU) | 89 | 4:00 | Comilla(N) | 63 | 18:30 | Gallamari | 23 | 13:00
| Ullon | 73 | 18:00 | Chandpur | 63 | 20:00 | Magura | 40 | 18:00
| Hasnabad | 111 | 18:00 | Feni | 73 | 19:30 | Norail | 24 | 18:30
| Magbazar | 58 | 18:00 | Chowmuhani | 114 | 19:30 | Chuadanga | 61 | 18:30
| Maniknagar | 56 | 18:00 | Ashuganj | 36 | 23:00 | Barisal(N) | 32 | 20:00
| Bangabhaban | 9 | 15:00 | Daudkandi | 86 | 20:00 | Barisal (S) | 60 | 19:30
| Narinda | 52 | 13:00 | B.Baria | 94 | 19:00 | Patuakhali | 78 | 19:30
| Dhanmondi | 70 | 13:00 | Ramganj | 66 | 20:00 | Bhandaria | 40 | 19:00
| Lalbag | 53 | 1:00 | Chaddagram | 22 | 19:00 | Borhan Uddin | 25 | 19:30
| Madartek | 44 | 13:00 | PHP | 11 | 9:00 | Ishurdi | 41 | 18:00
| Dhaka University |  |  | Madunaghat | 41 | 18:00 | Ruppur Paromanobik | 2 | 9:00
| Aftabnagar | 6 | 0.5 | Hathazari | 67 | 0.54167 | Natore | 75 | 0.77083
| Fatullah | 41 | 1:00 | Khulshi | 142 | 21:00 | Bogra | 107 | 19:30
| Mirpur | 64 | 18:00 | Halishahar | 90 | 21:00 | Noagaon | 75 | 19:30
| Kalyanpur | 57 | 18:00 | Baraulia | 126 | 1:00 | Rajshahi | 89 | 20:00
| Gulshan | 64 | 18:00 | Sikalbaha | 19 | 18:30 | Rajshahi New | 9 | 18:00
| Uttara | 62 | 18:00 | Dohazari | 56 | 18:30 | C.Nawabganj | 49 | 12:00
| Uttara New | 22 | 13:00 | Cox'sbazar | 159 | 13:00 | Amnura | 30 | 18:00
| Kamrangirchar | 51 | 19:30 | Chandraghona | 20 | 18:30 | Pabna | 61 | 18:30
| Savar | 76 | 18:30 | Kaptai | 3.5 | 18:00 | Shahjadpur | 66 | 18:30
| Bhasantec | 88 | 18:00 | A. Khaer Stl. | 10 | 10:00 | Serajganj | 45 | 19:00
| Agargaon | 42 | 13:00 | Bakulia | 62 | 18:30 | Niyamatpur | 75 | 18:30
| Satmosjid | 65 | 0.54167 | Julda | 18 | 0.041667 | Joypurhat | 39 | 0.77083
| Tongi | 45 | 12:00 | TK chemical | 17.9 | 20:00 | Sherpur(Bogura) | 35 | 18:00
| Kabirpur | 131 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 30 | 18:30
| Basundhara | 83 | 18:00 | Shahmirpur | 13 | 6:00 | Bangura | 15 | 18:00
| Manikganj | 42 | 19:30 | Khagrachhari | 18 | 9:00 | Rangpur | 96 | 19:30
| Joydevpur | 79 | 18:00 | Matarbari | 24.5 | 19:30 | Lalmonirhat | 46 | 18:00
| New Tongi | 68 | 18:00 | Baroiar Hat | 24 | 18:00 | Saidpur | 67 | 19:30
| Kodda | 126 | 21:00 | Rangamati | 9 | 18:30 | Purbasadipur | 78 | 20:00
| Dhamrai | 60 | 20:00 | Abul Khair 230 | 155 | 5:00 | Thakurgaon | 54 | 18:30
| Rajendrapur | 62 | 18:30 | BSRM | 154 | 7:00 | Palashbari | 83 | 19:00
| Valuka | 70 | 19:00 | GPH Ispat | 79 | 18:00 | Barapukuria | 39 | 20:00
| Tangail | 123 | 21:00 | Goalpara | 14 | 21:00 | Panchagar | 42 | 18:30
| Mymensing | 163 | 18:00 | Central s/s | 69 | 18:30 | Joldhaka | 25 | 18:30
| Kishorganj | 98 | 19:30 | Noapara | 47 | 18:30 | Kurigram | 39 | 18:30
| Netrokona | 101 | 19:00 | Jessore | 72 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 418 | 18:30 | 410 | 2:00 | Kaliakoir | 398 | 0.41667 | 378 | 0.5
| Bheramara | 410 | 18:30 | 393 | 18:30 | Bhulta | 392 | 0.75 | 377 | 0.5
| Ashuganj(N) | 398 | 24:00 | 381 | 12:00 | Gopalganj | 410 | 0.41667 | 398 | 0.83333
| Payra | 413 | 22:00 | 406 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 234 | 1:00 | Comilla (N) | 239 | 18:30 | 228 | 12:00
| Ishurdi | 242 | 14:00 | 237 | 12:00 | Hathazari | 225 | 18:30 | 216 | 24:00
| Ashuganj | 243 | 18:00 | 236 | 16:00 | Megnaghat | 238 | 17:00 | 232 | 4:00
| Serajganj | 235 | 13:00 | 231 | 9:00 | Fenchuganj | 246 | 18:30 | 241 | 11:00
| Baghabari | 248 | 17:00 | 244 | 4:00 | Siddhirganj | 234 | 18:00 | 225 | 12:00
| Barapukuria | 234 | 22:00 | 230 | 8:00 | Maniknagar | 232 | 18:30 | 224 | 12:00
| Bogra | 238 | 22:00 | 230 | 9:00 | Agargaon | 231 | 5:00 | 219 | 12:00
| Rajshahi | 241 | 17:00 | 232 | 9:00 | Barisal | 254 | 8:00 | 246 | 19:30
| Khulna South | 245 | 4:00 | 234 | 8:00 | AKSML | 228 | 9:00 | 210 | 5:00
| Rampura | 232 | 18:00 | 228 | 11:00 | BSRM | 228 | 8:00 | 210 | 12:00
| Haripur | 232 | 21:00 | 226 | 7:00 | Bibiyana | 245 | 17:00 | 240 | 12:00
| Hasnabad | 231 | 18:30 | 225 | 11:00 | Bhulta | 235 | 19:00 | 227 | 17:00
| Shyampur | 230 | 22:00 | 220 | 12:00 | Ashuganj (S) | 241 | 18:30 | 231 | 12:00
| Aminbazar | 232 | 18:00 | 223 | 11:00 | Kaliakoir | 231 | 18:00 | 220 | 12:00
| Tongi | 228 | 21:00 | 215 | 12:00 | GPH | 226 | 18:00 | 208 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 17:00 | 134 | 12:00 | Madanhat | 139 | 0.375 | 130 | 0.5
| Munsiganj | 142 | 18:00 | 133 | 12:00 | Hathazari | 138 | 0.77083 | 131 | 0
| Sonargaon | 138 | 18:00 | 133 | 7:00 | Khulshi | 136 | 0.91667 | 125 | 0.5
| Shyampur | 131 | 8:00 | 122 | 12:00 | Halishahar | 138 | 0.77083 | 126 | 0.66667
| Bhulta | 132 | 14:00 | 121 | 2:00 | Baraulia | 136 | 0.875 | 130 | 0.66667
| Madanganj | 138 | 15:00 | 134 | 5:00 | Sikalbaha | 138 | 0.77083 | 127 | 0.5
| Shitalakhya | 142 | 18:00 | 132 | 12:00 | Dohazari | 134 | 0.77083 | 127 | 0.083333
| Rahim steal | 140 | 18:00 | 135 | 12:00 | Cox'sbazar | 126 | 0.91667 | 116 | 0.5
| Matuail | 140 | 17:00 | 134 | 12:00 | Chandraghona | 137 | 0.33333 | 132 | 0.16667
| Ghorasal | 140 | 18:30 | 136 | 8:00 | Kaptai | 137 | 0.33333 | 132 | 0.41667
| Narsinghdi | 137 | 9:00 | 131 | 12:00 | A. Khaer Stl. | 136 | 0.041667 | 128 | 0.5
| Haripur (SBU) | 140 | 14:00 | 130 | 4:00 | Bakulia | 137 | 0.375 | 128 | 0.5
| Ullon | 133 | 7:00 | 131 | 1:00 | Julda | 137 | 0.77083 | 128 | 0.125
| Hasnabad | 140 | 19:00 | 134 | 12:00 | TK Chemical | 136 | 0.91667 | 128 | 0.5
| Magbazar | 133 | 3:00 | 128 | 12:00 | Modern Steel | 135 | 0.125 | 129 | 0.95833
| Maniknagar | 140 | 18:30 | 135 | 12:00 | Shahmirpur | 137 | 0.33333 | 129 | 0.66667
| Bangabhaban | 140 | 18:30 | 135 | 12:00 | Khagrachhari | 135 | 0.375 | 128 | 0.20833
| Narinda | 140 | 18:30 | 135 | 12:00 | Matarbari | 130 | 0.91667 | 120 | 0.66667
| Dhanmondi | 133 | 7:00 | 131 | 1:00 | Baroiar Hat | 138 | 0.29167 | 132 | 0.041667
| Lalbag | 132 | 18:30 | 124 | 12:00 | Rangamati | 138 | 9:00 | 130 | 4:00
| Madartek | 133 | 8:00 | 127 | 12:00 | Goalpara S/S | 140 | 13:00 | 132 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 3:00 | 132 | 0.33333
| Aftabnagar | 133 | 20:00 | 128 | 12:00 | Noapara | 137 | 1:00 | 129 | 0.29167
| Fatuiiah | 132 | 8:00 | 123 | 12:00 | Jessore | 135 | 1:00 | 126 | 0.33333
| Mirpur | 133 | 6:00 | 129 | 15:00 | Benapol | 135 | 0.041667 | 125 | 0.33333
| Kalyanpur | 134 | 20:00 | 127 | 12:00 | Jhenida | 134 | 1:00 | 126 | 0.77083
| Gulshan | 133 | 18:30 | 126 | 12:00 | Bottail | 137 | 0.20833 | 133 | 0.29167
| Uttara | 134 | 18:30 | 126 | 12:00 | G.K Project | 141 | 0.20833 | 138 | 0.77083
| Uttara New | 137 | 18:30 | 132 | 13:00 | Faridpur | 138 | 0.375 | 134 | 0.875
| Kamrangirchar | 140 | 20:00 | 134 | 12:00 | Madaripur | 143 | 0.33333 | 138 | 0.875
| Savar | 133 | 18:30 | 126 | 12:00 | Shariyatpur S/S | 142 | 5:00 | 136 | 0.83333
| Bhasantec | 134 | 20:00 | 127 | 12:00 | Gopalganj | 142 | 0.16667 | 137 | 0.83333
| Agargaon | 135 | 18:30 | 128 | 12:00 | Bagerhat | 140 | 2:00 | 129 | 0.33333
| Satmosjid | 135 | 18:30 | 127 | 12:00 | Mongla | 136 | 1:00 | 130 | 0.33333
| Tongi | 138 | 21:00 | 133 | 132:00 | Satkhira | 139 | 2:00 | 131 | 8:00
| Kabirpur | 139 | 17:00 | 132 | 19:00 | Gallamari | 139 | 0.041667 | 133 | 0.33333
| Basundhara | 134 | 18:30 | 127 | 12:00 | Magura | 135 | 1:00 | 125 | 0.77083
| Manikganj | 144 | 18:30 | 135 | 13:00 | Narail | 134 | 0.20833 | 124 | 0.77083
| Joydevpur | 140 | 17:00 | 133 | 12:00 | Chuadanga | 132 | 3:00 | 122 | 0.77083
| New Tongi | 140 | 18:00 | 131 | 12:00 | Barisal(N) | 143 | 2:00 | 139 | 20:00
| Kodda | 136 | 18:00 | 126 | 12:00 | Barisal (S) | 142 | 0.29167 | 137 | 0.83333
| Dhamrai | 139 | 20:07 | 127 | 20:00 | Patuakhali(S) | 141 | 0.041667 | 136 | 0.83333
| Rajendrapur | 138 | 18:30 | 135 | 12:00 | Bhandaria | 142 | 0.41667 | 134 | 0.83333
| Valuka | 129 | 5:00 | 122 | 16:00 | Ishurdi | 139 | 1:00 | 136 | 8:00
| Tangail | 135 | 24:00 | 132 | 9:00 | Ruppur Paromanobik | 139 | 14:00 | 137 | 8:00
| Mymensing | 131 | 18:30 | 122 | 16:00 | Natore | 138 | 6:00 | 134 | 8:00
| Kishorganj | 132 | 2:00 | 127 | 13:00 | Bogra | 139 | 13:00 | 134 | 8:00
| Netrokona | 129 | 1:00 | 120 | 7:00 | Noagaon | 135 | 4:00 | 128 | 9:00
| Jamalpur | 138 | 18:30 | 121 | 7:00 | Rajshahi | 137 | 17:00 | 133 | 8:00
| Sherpur | 136 | 18:30 | 120 | 16:00 | Rajshahi New | 137 | 17:00 | 132 | 8:00
| Srimongal | 138 | 24:00 | 134 | 22:00 | C.Nawabganj | 136 | 18:00 | 130 | 8:00
| Shahjibazar | 135 | 22:00 | 133 | 1:00 | Amnura | 136 | 3:00 | 131 | 8:00
| Fenchuganj | 139 | 24:00 | 135 | 11:00 | Pabna | 139 | 15:00 | 136 | 5:00
| Khulawara | 138 | 23:00 | 134 | 12:00 | Shahjadpur | 140 | 1:00 | 138 | 7:00
| Sylhet | 137 | 21:00 | 135 | 3:00 | Serajganj | 137 | 15:00 | 134 | 8:00
| Chatak | 135 | 1:00 | 133 | 12:00 | Niyamatpur | 134 | 13:00 | 127 | 8:00
| Sunamganj | 136 | 1:00 | 133 | 15:00 | Joypurhat | 136 | 1:00 | 129 | 9:00
| Biani Bazar | 136 | 5:00 | 133 | 12:00 | Sherpur(Bogura) | 140 | 13:00 | 135 | 9:00
| Comilla(s) | 131 | 3:00 | 127 | 18:00 | Mohastangor | 138 | 19:00 | 133 | 9:00
| Comilla(n) | 141 | 22:00 | 137 | 22:00 | Bangura | 142 | 1:00 | 139 | 7:00
| Chandpur | 143 | 19:00 | 141 | 15:00 | Rangpur | 133 | 15:00 | 124 | 9:00
| Feni | 138 | 7:00 | 133 | 15:00 | Lalmonirhat | 131 | 15:00 | 124 | 9:00
| Chowmuhani | 135 | 7:00 | 132 | 19:00 | Saidpur | 133 | 15:00 | 123 | 9:00
| Ashuganj | 136 | 7:00 | 134 | 16:00 | Purbasadipur | 132 | 15:00 | 124 | 9:00
| Daudkandi | 139 | 17:00 | 134 | 12:00 | Thakurgaon | 130 | 5:00 | 121 | 9:00
| B.Baria | 133 | 12:00 | 130 | 22:00 | Palashbari | 135 | 13:00 | 130 | 8:00
| Ramganj | 138 | 18:30 | 134 | 23:00 | Barapukuria | 133 | 13:00 | 130 | 8:00
| Chaddagram | 138 | 7:00 | 136 | 15:00 | Panchagar | 129 | 4:00 | 121 | 9:00
| PHP | 138 | 8:00 | 133 | 23:00 | Joldhaka | 130 | 0.16667 | 122 | 0.375

## L-Curve
Date | 2021-01-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 227 | 4360 | 2160 | 6520 |  |  |  | QF-LDC-11
0:30 | 190.5 | 4417 | 2131.5 | 6548.5 | Date: | 2021-01-08
1:00 | 154 | 4474 | 2103 | 6577
1:30 | 180 | 4338.5 | 2088 | 6426.5
2:00 | 206 | 4203 | 2073 | 6276
2:30 | 211 | 4109.5 | 2040.5 | 6150 | [5 empty] | Gen. at Eve. Peak | 8158 | 8158 MW (19:30 )
3:00 | 216 | 4016 | 2008 | 6024 | [6 empty] | 19:30
3:30 | 228 | 4033.5 | 1961.5 | 5995 | [5 empty] | Gen. at Day Peak | 6485 | 6485 MW (12:00 )
4:00 | 240 | 4051 | 1915 | 5966 | [6 empty] | 12:00
4:30 | 246.5 | 4017.5 | 1926.5 | 5944 | [5 empty] | Highest Generation | 8158
5:00 | 253 | 3984 | 1938 | 5922 | [6 empty] | 19:30
5:30 | 236.5 | 4072.5 | 1961 | 6033.5
6:00 | 220 | 4161 | 1984 | 6145
6:30 | 133.5 | 4156 | 1951.5 | 6107.5
7:00 | 47 | 4151 | 1919 | 6070
7:30 | 41 | 4166.5 | 1963 | 6129.5
8:00 | 35 | 4182 | 2007 | 6189
8:30 | 60 | 4185 | 2004.5 | 6189.5
9:00 | 85 | 4188 | 2002 | 6190
9:30 | 133.5 | 4200.5 | 1997 | 6197.5
10:00 | 182 | 4213 | 1992 | 6205
10:30 | 239.5 | 4205 | 2046.5 | 6251.5
11:00 | 297 | 4197 | 2101 | 6298
11:30 | 340.5 | 4225.5 | 2166 | 6391.5
12:00 | 384 | 4254 | 2231 | 6485
12:30 | 400.5 | 4389 | 2290.5 | 6679.5
13:00 | 417 | 4524 | 2350 | 6874
13:30 | 397.5 | 4288 | 2207.5 | 6495.5
14:00 | 378 | 4052 | 2065 | 6117
14:30 | 371.5 | 4013.5 | 2041.5 | 6055
15:00 | 365 | 3975 | 2018 | 5993
15:30 | 363 | 3906.5 | 1962 | 5868.5
16:00 | 361 | 3838 | 1906 | 5744
16:30 | 266.5 | 3960 | 1956.5 | 5916.5
17:00 | 172 | 4082 | 2007 | 6089
17:30 | 136.5 | 4484 | 2289.5 | 6773.5
18:00 | 101 | 4886 | 2572 | 7458
18:30 | 81 | 5067.5 | 2690 | 7757.5
19:00 | 61 | 5249 | 2808 | 8057
19:30 | 63 | 5335 | 2823 | 8158
20:00 | 96 | 5334 | 2817 | 8151 |  |  |  | Executive Engineer
20:30 | 158 | 5280 | 2847.5 | 8127.5 |  |  |  | Network Operation Division
21:00 | 220 | 5226 | 2878 | 8104
21:30 | 202 | 5109.5 | 2757 | 7866.5
22:00 | 184 | 4993 | 2636 | 7629 |  |  |  |  | Page 6 of 7
22:30 | 219.5 | 4819 | 2528.5 | 7347.5
23:00 | 255 | 4645 | 2421 | 7066
23:30 | 241 | 4502.5 | 2290.5 | 6793
24:00 | 227 | 4360 | 2160 | 6520
8158 MW (19:30 )
6485 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-08 |  | Energy | 162461498
[11 empty] | 2021-01-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2929 | 424 | 1566 | 1421 | 550 | 45 | 4 | 0 | 82 | 0
0:30 | 2960.5 | 431.5 | 1479 | 1202.5 | 580 | 44.5 | 21 | 0 | 80 | 0 | Date: | 2021-01-08
1:00 | 2992 | 439 | 1392 | 984 | 610 | 44 | 38 | 0 | 78 | 0
1:30 | 3002 | 439.5 | 1377 | 858.5 | 600 | 45 | 27.5 | 0 | 77 | 0 | [7 empty] | Total Energy | 162.4615 | Total Energy Gen 162.461 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.461 MKWHr
2:00 | 3012 | 440 | 1362 | 733 | 590 | 46 | 17 | 0 | 76 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3009.5 | 439.5 | 1352 | 629.5 | 590 | 46 | 8.5 | 0 | 75 | 0 | [7 empty] | Energy Requirement | 162.4615
3:00 | 3007 | 439 | 1342 | 526 | 590 | 46 | 0 | 0 | 74 | 0
3:30 | 3023.5 | 392 | 1351 | 519 | 590 | 45.5 | 0 | 0 | 74 | 0 | [6 empty] | Shortage
4:00 | 3040 | 345 | 1360 | 512 | 590 | 45 | 0 | 0 | 74 | 0
4:30 | 3042 | 345 | 1347.5 | 502.5 | 590 | 45 | 0 | 0 | 72 | 0
5:00 | 3044 | 345 | 1335 | 493 | 590 | 45 | 0 | 0 | 70 | 0
5:30 | 3046.5 | 345 | 1354.5 | 582 | 590 | 45.5 | 0 | 0 | 70 | 0
6:00 | 3049 | 345 | 1374 | 671 | 590 | 46 | 0 | 0 | 70 | 0
6:30 | 2991.5 | 337 | 1315.5 | 767 | 580 | 46 | 0 | 0 | 70 | 0.5 |  |  |  |  | Coal
7:00 | 2934 | 329 | 1257 | 863 | 570 | 46 | 0 | 0 | 70 | 1
7:30 | 2910.5 | 384.5 | 1261 | 896.5 | 555 | 46 | 0 | 0 | 69 | 7 |  |  |  | Oil |  |  |  | ,
8:00 | 2887 | 440 | 1265 | 930 | 540 | 46 | 0 | 0 | 68 | 13
8:30 | 2823 | 456 | 1235 | 1015 | 525 | 45.5 | 0 | 0 | 66 | 24
9:00 | 2759 | 472 | 1205 | 1100 | 510 | 45 | 0 | 0 | 64 | 35
9:30 | 2722 | 473.5 | 1226.5 | 1111.5 | 510 | 44.5 | 0 | 0 | 67 | 42.5
10:00 | 2685 | 475 | 1248 | 1123 | 510 | 44 | 0 | 0 | 70 | 50
10:30 | 2693 | 473.5 | 1278 | 1127.5 | 510 | 43 | 0 | 0 | 70 | 56.5
11:00 | 2701 | 472 | 1308 | 1132 | 510 | 42 | 0 | 0 | 70 | 63
11:30 | 2737 | 471 | 1329.5 | 1164.5 | 510 | 42 | 0 | 0 | 72 | 65.5
12:00 | 2773 | 470 | 1351 | 1197 | 510 | 42 | 0 | 0 | 74 | 68
12:30 | 2794 | 470.5 | 1379 | 1341.5 | 510 | 42.5 | 0 | 0 | 78 | 64
13:00 | 2815 | 471 | 1407 | 1486 | 510 | 43 | 0 | 0 | 82 | 60
13:30 | 2815 | 471 | 1407 | 1486 | 510 | 43 | 0 | 0 | 82 | 60
14:00 | 2815 | 471 | 1407 | 1486 | 510 | 43 | 0 | 0 | 82 | 60
14:30 | 2803.5 | 471 | 1319.5 | 1176.5 | 500 | 44 | 0 | 0 | 74 | 45
15:00 | 2792 | 471 | 1232 | 867 | 490 | 45 | 0 | 0 | 66 | 30
15:30 | 2804.5 | 471 | 1224 | 762 | 475 | 45 | 0 | 0 | 65 | 22
16:00 | 2817 | 471 | 1216 | 657 | 460 | 45 | 0 | 0 | 64 | 14
16:30 | 2802.5 | 471 | 1202 | 779 | 465 | 45 | 76.5 | 0 | 67 | 8.5
17:00 | 2788 | 471 | 1188 | 901 | 470 | 45 | 153 | 0 | 70 | 3
17:30 | 2880.5 | 589 | 1261.5 | 1266 | 485 | 45.5 | 163.5 | 0 | 81 | 1.5
18:00 | 2973 | 707 | 1335 | 1631 | 500 | 46 | 174 | 0 | 92 | 0
18:30 | 2974.5 | 707 | 1395.5 | 1824 | 535 | 46 | 182.5 | 0 | 93 | 0
19:00 | 2976 | 707 | 1456 | 2017 | 570 | 46 | 191 | 0 | 94 | 0
19:30 | 2958 | 707 | 1568 | 2020 | 570 | 46 | 191 | 0 | 98 | 0
20:00 | 2965 | 707 | 1567 | 2021 | 570 | 46 | 175 | 0 | 100 | 0
20:30 | 2942.5 | 707.5 | 1573 | 1989.5 | 595 | 46 | 175 | 0 | 99 | 0
21:00 | 2920 | 708 | 1579 | 1958 | 620 | 46 | 175 | 0 | 98 | 0
21:30 | 2912 | 580 | 1565.5 | 1894 | 620 | 45.5 | 153.5 | 0 | 96 | 0
22:00 | 2904 | 452 | 1552 | 1830 | 620 | 45 | 132 | 0 | 94 | 0
22:30 | 2913.5 | 437.5 | 1543.5 | 1625.5 | 609.5 | 45 | 81 | 0 | 92 | 0
23:00 | 2923 | 423 | 1535 | 1421 | 599 | 45 | 30 | 0 | 90 | 0
23:30 | 2926 | 423.5 | 1550.5 | 1421 | 574.5 | 45 | 17 | 0 | 86 | 0 | Max Temp. in Dhaka |  | 29.4° C
24:00 | 2929 | 424 | 1566 | 1421 | 550 | 45 | 4 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 162.461 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.461 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 46 | 46 | 45 | 45 | 46 | 46 | 46 | 45 | 44 | 42 | 42 | 43 | 45 | 45 | 45 | 45 | 46 |  | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 1055127
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 5 | 25 | 25 | 25 | 25 | 25 | [11 empty] | 0 | 138189
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 12 | 15 | 18 | 18 | 18 | 15 | 11 | 7 | 1 | [9 empty] | 121095
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 17 | [14 empty] | 68 | 85 |  | 102 | 102 | 102 | 102 | 102 |  |  | 654638
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 15 |  |  |  |  | 19 | 30 | 60 | 60 | 60 | 60 | 95 | 120 | 120 | 65 | 65 | 83 |  | 240 | 245 | 245 | 245 | 245 | 195 | 145 | 2473963
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 102 | 102 | 102 | 105 | 101 | 101 | 100 | 102 | 130 | 104 | 101 | 101 | 101 | 130 | 125 | 105 | 97 |  | 25 | [5 empty] | 0 | 2006000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7534282
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 281880
33 | Ashuganj 225 MW CCPP | 151 | 153 | 153 | 153 | 153 | 153 | 142 | 148 | 142 | 146 | 160 | 173 | 179 | 195 | 184 | 188 | 184 | 184 |  | 185 | 185 | 184 | 184 | 184 | 192 | 185 | 4102000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 270 | 270 | 290 | 290 | 330 |  | 330 | 330 | 330 | 290 | 290 | 300 | 295 | 7336000
| Ashuganj 450 MW CCPP(North) | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 290 | 355 |  | 335 | 325 | 330 | 330 | 300 | 300 | 300 | 7759000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 25 | 53 | 52 | 52 | 53 | 53 | 56 | 399360
36 | Chandpur 150 MW CCPP | 80 | 80 | 83 | 80 | 80 | 80 | 79 | 73 | 80 | 70 | 80 | 90 | 81 | 90 | 90 | 91 | 82 | 90 |  | 90 | 91 | 91 | 86 | 90 | 90 | 90 | 1975980
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 362 | 354 | 377 | 366 | 375 | 349 | 356 | 354 | 367 | 354 | 368 | 368 | 329 | 305 | 304 | 288 | 313 |  | 351 | 351 | 351 | 352 | 350 | 350 | 354 | 8500220
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 290 | 257 | 307 | 307 | 307 | 353 | 277 | 277 | 307 | 307 | 359 |  | 359 | 359 | 359 | 358 | 300 | 300 | 300 | 7418000
42 | RPCL 210MW CCPP | 161 | 163 | 162 | 162 | 162 | 166 | 164 | 165 | 164 | 140 | 142 | 137 | 140 | 139 | 156 | 155 | 157 | 160 |  | 160 | 161 | 161 | 161 | 162 | 162 | 162 | 3687080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 6 | 19 | 29 | 37 | 41 | 33 | 23 | 14 | 5 | 2 | [9 empty] | 224520
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 68 | 68 | 68 | 68 | 69 | 69 | 67 | 67 | 65 | 62 | 64 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1324224
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 71 | 71 | 71 | 71 | 72 | 72 | 72 | 72 | 74 | 74 | 72 | 73 | 40 | 40 | 20 | 20 | 77 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1580160
| Shahjibazar 100 MW GTPP | [14 empty] | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 920000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 190 | 170 | 170 | 170 | 170 | 171 | 170 | 170 | 136 | 138 | 138 | 138 | 164 |  | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 4101000
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 437000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 204120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 11 | 11 | 5 | 11 | 11 | 11 | 153000
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 31 | 31 | 31 | 31 | 5 | 5 | [11 empty] | 18 | 53 | 50 | 50 | 50 | 50 | 50 | 447600
56 | Shahjahanulla 25 MW PP | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 261120
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 310 | 290 | 320 | 310 | 310 | 275 | 300 | 300 | 310 | 290 | 310 | 310 | 270 | 310 | 300 | 285 | 310 |  | 280 | 300 | 300 | 305 | 290 | 280 | 300 | 7386300
| Bibiyana South 400 MW | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 130 | 120 | 120 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4293600
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 5 | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 |  | 0 | 301020
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 0 | 6 | 10 | 10 | 10 | 12 |  | 22 | 24 | 24 | 24 | 24 | 22 | 0 | 169680
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 396384
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 451116
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502884
63 | Impoprt (Tripura) | 78 | 76 | 74 | 74 | 70 | 70 | 70 | 68 | 64 | 70 | 70 | 74 | 82 | 74 | 66 | 64 | 70 | 92 |  | 94 | 98 | 100 | 98 | 94 | 90 | 82 | 1882560
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 34 | 35 | 30 | 36 | 35 | 35 | 28 | 30 | 30 |  | 40 | 40 | 40 | 42 | 42 | 40 | 42 | 932640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 414676
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 224460
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 21 | 22 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 490700
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 22 | 22 | 12 | 11 | 11 | 11 | 11 | 11 | 11 |  | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 554760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 463400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 491100
73 | Ghorashal 108MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 53 | 53 | 53 | 53 |  | 98 | 98 | 98 | 95 | 95 | 94 | 94 | 1544136
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [12 empty] | 35 | 17 | 17 | 17 | 17 | 28 |  | 26 | 26 | 26 | 26 | 26 | 8 | 0 | 367920
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 54 | 54 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1720800
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 10 | [7 empty] | 0 | 21120
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [16 empty] | 16 | 16 |  | 16 | 16 |  |  |  |  | 0 | 48960
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 22 |  | 40 | 40 | 40 | 16 |  |  | 0 | 135360
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 8 | [8 empty] | 13613
| Gazipur 100 MW PP | [16 empty] | 6 | 17 | [7 empty] | 0 | 27096
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26159
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299404
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | [14 empty] | 10 | 46 |  | 48 | 15 | 15 | 15 | 15 | 15 | 0 | 226632
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [5 empty] | 1 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 59 |  | 85 | 85 | 86 | 85 | 86 | 66 | 0 | 979449
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 7 | 24 | [7 empty] | 0 | 48000
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 4 | 39 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 35 | 0 | 619200
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 25 | 25 | 5 | 5 | 5 | [10 empty] | 10 | 44 | 50 | 50 | 50 | 50 | 50 | 564120
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1238720
94 | Gagnagar 102 MW PP (Digital Power) | [15 empty] | 7 |  | 24 | [7 empty] | 0 | 27216
95 | Patenga 50MW PP (Baraka) | 25 | 6 | [9 empty] | 2 | 36 | 50 | 25 | 25 | 25 | 28 |  | 50 | 50 | 50 | 50 | 50 | 25 | 23 | 603360
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 11 | 11 | [7 empty] | 0 | 31680
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 2 | 15 | [7 empty] | 0 | 26570
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 54 |  | 17 | 17 | 17 |  |  |  | 0 | 110160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 70 | 20 | 20 | 8 | 8 | 29 | 55 | 60 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 32 | 32 | 65 |  | 147 | 182 | 182 | 184 | 150 | 150 | 100 | 2200800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [16 empty] | 11 | 20 |  | 48 | 17 | 21 |  |  |  | 0 | 104976
115 | Juldah 100 MW PP Unit-3 (Acorn) | [12 empty] | 10 | 10 | 10 | 10 | 10 | 50 |  | 100 | 100 | 100 | 100 | 50 |  | 0 | 465600
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 34 | 20 | 34 | 40 |  | 68 | 68 | 68 | 68 | 68 | 50 | 50 | 1498080
117 | Ashuganj 150MW PP (Midland) | 102 | 50 | 10 | 10 | 10 | 10 | 38 | 65 | 122 | 123 | 130 | 132 | 132 | 70 |  | 1 | 97 | 133 |  | 133 | 149 | 148 | 150 | 150 | 150 | 100 | 2301672
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 17 | [7 empty] | 0 | 39600
| Anwara 300 MW PP (United) | 161 | 161 | 131 | 135 | 125 | 195 | 215 | 215 | 215 | 215 | 215 | 215 | 250 | 181 | 142 | 106 | 160 | 162 |  | 123 | 124 | 124 | 124 | 88 | 88 | 88 | 3899127
| Juldah unit-2 (Acorn) | 100 | 50 | 20 | 20 | 20 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 30 | 10 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1830720
| Anlima Energy Ltd. | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4474 | 4203 | 4016 | 4051 | 3984 | 4161 | 4151 | 4182 | 4188 | 4213 | 4197 | 4254 | 4524 | 4052 | 3975 | 3838 | 4082 | 4886 |  | 5249 | 5335 | 5334 | 5226 | 4993 | 4645 | 4360 | 107718042
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 59 | 32 | 16 | 16 | 96 |  | 115 | 115 | 115 | 115 | 115 | 99 | 99 | 2375040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | [15 empty] | 3 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 30240
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 53 | [9 empty] | 17 | 53 | 35 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 0 | 490560
130
131
132 | United Payra Power Ltd. | 54 | 54 | 36 | 30 | 21 | 27 | 28 | 34 | 30 | 28 | 30 | 35 | 35 | 35 | 35 |  |  | 54 |  | 54 | 55 | 55 | 55 | 55 | 55 | 54 | 897600
133 | Bhola Nutan Biddut BD LTD (GAS) | [9 empty] | 25 | 27 | 28 | 21 | 43 | 49 | 51 | 51 | 55 |  | 55 | 55 | 55 | 55 | 54 | 55 | 56 | 683100
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 61 | 61 | 61 | 61 | 61 | 31 | 31 | 31 | 32 | 32 | 30 | 30 | 33 | 33 | 32 | 32 | 32 | 32 |  | 60 | 60 | 61 | 62 | 62 | 63 | 62 | 1098196
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 23 | 21 | 20 | 20 | 23 | 19 | 17 | 18 | 19 | 17 | 20 | 20 | 18 | 17 | 14 | 18 | 22 |  | 25 | 26 | 26 | 26 | 26 | 25 | 25 | 495600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 439 | 440 | 439 | 345 | 345 | 345 | 329 | 440 | 472 | 475 | 472 | 470 | 471 | 471 | 471 | 471 | 471 | 707 |  | 707 | 707 | 707 | 708 | 452 | 423 | 424 | 11680000
147 | Bheramara 410 MW CCPP | 200 | 220 | 220 | 230 | 245 | 255 | 230 | 230 | 200 | 200 | 230 | 275 | 265 | 250 | 250 | 240 | 250 | 250 |  | 250 | 260 | 260 | 265 | 270 | 265 | 275 | 6006816
148 | Payra 1320 MW | 460 | 440 | 440 | 440 | 440 | 440 | 420 | 390 | 360 | 360 | 360 | 360 | 360 | 340 | 340 | 310 | 320 | 350 |  | 420 | 420 | 420 | 470 | 470 | 450 | 400 | 10415700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 3685000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 154 | 158 | 168 | 177 | 184 | 176 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 160 | 160 | 140 | 140 | 159 |  | 178 | 180 | 180 | 180 | 180 | 180 | 180 | 4212018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 329 | 331 | 320 | 330 | 395 | 378 | 363 | 339 | 300 | 381 | 407 | 414 | 334 | 326 | 320 | 301 | 304 |  | 323 | 317 | 313 | 321 | 367 | 362 | 368 | 8127363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 20 | 18 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 491760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 229176
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 66 | 69 |  | 69 | 69 | 69 | 69 | 26 | 26 | 0 | 385080
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 49 | 67 | 112 | 113 | 113 | 113 | 113 | 35 | 35 | 44 | 70 | 79 |  | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 1729440
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 35 | 70 | 35 | 35 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 35 | 0 | 885600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 34 | 36 | 36 | 36 | 38 | 85 |  | 106 | 113 | 110 | 106 | 113 | 72 | 0 | 805440
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 19727
178
178