## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-10 | Sunday
|  |  | Date (day): | 2021-01-10 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12458.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13631 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-09 | 2021-01-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 20 | 0 | 0 | 180 |  | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 380 | 300 | 360
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 102 | 100 | 100 | 8 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 366 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 125 | 307 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 86 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 98 | 60 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 5 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 23 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 38 | 128 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 44 | 104 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1321 | 2544 | 3329 | 3719 | 959 | 1372
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 23 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 22 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 44 | 48 | 45 | 45 | 185 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 38 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 26 | 25 | 35
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 31 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 215 | 268 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 511 | 753 | 1255 | 1240 | 920 | 103
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 70 | 70 | 64 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 193 | 180 | 190
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 320 | 300 | 360
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 385 | 315 | 300 | 330 | 30 |  | Gas shortage
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 56 | 50 | 50 | 5 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 92 | 149 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 90 | 90 | 91 |  | 72 | Gas shortage
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 58 | 50 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 106 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 55 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1397 | 1518 | 1913 | 2278 | 569 | 84
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 135 | 150 | 150 | 52 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 58 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 130 | 195 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 21 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 338 | 431 | 655.6 | 604 | 52 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 45 | 45
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 20 | 20
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Line S/D
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 34 | 53 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 67 | 68 | 68
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 66 | 74 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 100 | 0 | 0 | 0 |  |  | Under maint
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 150 | 200 | 200
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 330 | 330
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 127 | 130 | 400 | 400 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 913 | 882 | 1284 | 1284 | 330 | 425
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 662 | 709 | 678 | 726
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 3 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 260 | 300 | 325 | 85 |  | Gas shortage
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 8 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 40 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 53 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1239 | 1148 | 1493 | 1852 | 85 | 58
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 27 | 24 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 21 | 21 | 60 | 61 | 34 |  | Gas shortage
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 500 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 33 | 42 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 31 | 54 | 54 | 54
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 417 | 644 | 898 | 907 | 34 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 180 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 319 | 425 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 51 | 93 | 94 | 94
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 60 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 690 | 958 | 1360 | 1484 | 601 | 15
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 188 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7014 | 9141 | 12458.6 | 13631 | 3674 | 2468
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6727.0253 | 8767 | 11948.8619 | 13073.2936
| A. |  | 2021-01-09 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9141 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 5529 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9141 | MW
| 3 | Day peak Generation : |  |  | 7014 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8767 | MW
| 4 | Evening peak Generation : |  |  | 9141 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 172.1416 | MKWHr | By Solar | 0.080672 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 105.5079 | MKWHr |  | By Oil: | 35.2689 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6578 | MKWHr |  | By Hydro: | 1.104 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3674 | MW | Dhaka | 3069 | 3069 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2468 | MW | Chittagong | 1053 | 1053 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6142 | MW | Khulna | 1087 | 1087 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 808.62 | MMCFD |  |  | Rajshahi | 913 | 913 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 110842287.74 | ii) Oil : | Taka | 255148334.62 | Comilla | 733 | 733 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 63761635 | Total | Taka | 429752257.36 | Mymensingh | 761 | 761 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.02 | MKWHr. | Sylhet | 329 | 329 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 8 | MW (E to W) at | 19:30 | hrs | Barisal | 243 | 243 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -27 | MW at | 19:00 | hrs | Rangpur | 579 | 579 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.6° C |  |  | Total | 8767 | 8767 |  | 0
| B. |  | 2021-01-10 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13631 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
| 4 | Reserve(Generation end) |  |  |  | 4131 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 178.9022 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5757 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.44 | MKWHr. | ii) HVDC Flow at Peak Time |  | 709 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0822 | MKWHr. | iii) Maximum HVDC Flow : |  | 710 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.66 |  | (b) Today: | 97.59 |  | (c) Rule Curve: |  | 101.29
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 349 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 300 | 295 | 185 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 76 | 163 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 100 | 130 | 0 | 0 | 72 | 0 | 100 |  | 426 | 0 | 275 | 0 | 49 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 180 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 55 | 0 | 55 |  | 4072 | 2025 | 6097 | 2926 | 426 | 1513 | 560 | 550 | 42 | 4 | 76 | 0 | 0 | 97.67
2:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 352 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 300 | 290 | 184 | 8 | 86 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 74 | 164 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 19 | 0 | 9 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 88 | 54 | 0 | 0 | 0 | 50 | 130 | 0 | 0 | 72 | 0 | 100 |  | 427 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 180 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 55 | 0 | 55 |  | 3891 | 1966 | 5857 | 2926 | 427 | 1502 | 337 | 549 | 42 | 0 | 74 | 0 | 0 | 97.67
3:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 351 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 300 | 265 | 184 | 8 | 90 | 26 | 57 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 72 | 164 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 75 | 0 | 164 | 19 | 0 | 9 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 0 | 30 | 130 | 0 | 0 | 0 | 0 | 100 |  | 426 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 180 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 55 | 0 | 55 |  | 3719 | 1942 | 5661 | 2911 | 426 | 1492 | 198 | 520 | 42 | 0 | 72 | 0 | 0 | 97.66
4:00 | 0 | 0 | 0 | 0 | 330 | 94 | 0 | 353 | 300 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 300 | 265 | 184 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 164 | 0 | 22 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 40 | 40 | 0 | 164 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 0 | 30 | 130 | 0 | 0 | 0 | 0 | 100 |  | 427 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 180 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 56 | 0 | 35 |  | 3681 | 1853 | 5534 | 2926 | 427 | 1386 | 178 | 500 | 45 | 0 | 72 | 0 | 0 | 97.66
5:00 | 0 | 0 | 0 | 0 | 330 | 97 | 0 | 354 | 330 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 300 | 265 | 183 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 19 | 72 | 164 | 0 | 22 | 0 | 0 | 0 | 11 | 50 | 0 | 0 | 40 | 10 | 0 | 163 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 0 | 30 | 130 | 0 | 0 | 11 | 0 | 100 |  | 427 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 140 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 57 | 0 | 28 |  | 3655 | 1874 | 5529 | 2877 | 427 | 1408 | 200 | 500 | 45 | 0 | 72 | 0 | 0 | 97.66
6:00 | 0 | 0 | 0 | 0 | 330 | 97 | 0 | 370 | 357 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 42 | 0 | 0 | 0 | 260 | 265 | 186 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 72 | 164 | 0 | 22 | 0 | 0 | 0 | 11 | 50 | 0 | 0 | 40 | 10 | 0 | 165 | 19 | 0 | 9 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 0 | 0 | 0 | 0 | 101 | 54 | 0 | 0 | 4 | 90 | 130 | 0 | 0 | 36 | 0 | 100 |  | 426 | 0 | 335 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 140 | 0 | 315 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 350 | 34 | 0 | 35 |  | 3878 | 1872 | 5750 | 2895 | 426 | 1405 | 407 | 500 | 45 | 0 | 72 | 0 | 0 | 97.66
7:00 | 0 | 0 | 0 | 0 | 330 | 97 | 0 | 360 | 357 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 42 | 0 | 0 | 0 | 260 | 300 | 201 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 19 | 68 | 146 | 0 | 22 | 0 | 0 | 0 | 11 | 50 | 0 | 0 | 40 | 40 | 0 | 165 | 18 | 0 | 9 | 300 | 8 | 2 | 0 | 34 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 142 | 54 | 0 | 0 | 17 | 100 | 130 | 17 | 0 | 70 | 0 | 100 |  | 426 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 150 | 0 | 333 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 350 | 34 | 0 | 18 |  | 4173 | 1941 | 6114 | 2916 | 426 | 1447 | 711 | 500 | 46 | 0 | 68 | 0 | 0 | 97.65
8:00 | 0 | 0 | 0 | 0 | 330 | 106 | 0 | 356 | 357 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 13 | 0 | 0 | 0 | 260 | 270 | 193 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 80 | 157 | 0 | 22 | 0 | 0 | 0 | 11 | 50 | 0 | 0 | 40 | 40 | 0 | 163 | 18 | 0 | 0 | 300 | 0 | 8 | 0 | 61 | 0 | 0 | 108 | 0 | 0 | 6 | 0 | 50 | 73 | 0 | 0 | 0 | 0 | 1 | 142 | 54 | 0 | 0 | 17 | 100 | 130 | 28 | 2 | 72 | 0 | 100 |  | 567 | 0 | 350 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 159 | 0 | 334 | 53 | 0 | 60 | 0 | 0 | 0 | 0 | 35 | 350 | 54 | 0 | 18 |  | 4275 | 2366 | 6641 | 2905 | 567 | 1438 | 1043 | 500 | 48 | 51 | 80 | 9 | 0 | 97.65
9:00 | 0 | 0 | 0 | 0 | 330 | 110 | 0 | 362 | 325 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 20 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 5 | 0 | 0 | 0 | 300 | 270 | 183 | 8 | 82 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 86 | 155 | 0 | 22 | 0 | 0 | 0 | 31 | 50 | 0 | 0 | 40 | 40 | 0 | 163 | 18 | 0 | 0 | 300 | 0 | 2 | 0 | 95 | 0 | 0 | 167 | 0 | 0 | 11 | 0 | 50 | 100 | 0 | 0 | 0 | 0 | 2 | 155 | 54 | 0 | 0 | 17 | 100 | 130 | 34 | 5 | 72 | 0 | 100 |  | 567 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 162 | 0 | 396 | 53 | 0 | 70 | 0 | 0 | 0 | 1 | 35 | 370 | 37 | 0 | 17 |  | 4442 | 2505 | 6947 | 2924 | 567 | 1457 | 1275 | 520 | 48 | 51 | 86 | 19 | 0 | 97.65
10:00 | 0 | 0 | 0 | 0 | 300 | 110 | 0 | 340 | 272 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 23 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 2 | 0 | 0 | 0 | 300 | 270 | 184 | 26 | 90 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 84 | 156 | 12 | 22 | 1 | 0 | 0 | 31 | 50 | 0 | 0 | 40 | 40 | 0 | 163 | 18 | 0 | 0 | 280 | 0 | 5 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 3 | 160 | 54 | 0 | 0 | 17 | 50 | 130 | 34 | 0 | 72 | 0 | 100 |  | 662 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 154 | 0 | 368 | 35 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 320 | 23 | 0 | 12 |  | 4266 | 2392 | 6658 | 2801 | 662 | 1357 | 1180 | 470 | 47 | 51 | 84 | 6 | 0 | 97.64
11:00 | 0 | 0 | 0 | 0 | 300 | 106 | 0 | 322 | 273 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 23 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 4 | 0 | 0 | 0 | 260 | 270 | 182 | 26 | 90 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 86 | 161 | 38 | 22 | 2 | 0 | 0 | 31 | 50 | 0 | 0 | 40 | 40 | 0 | 162 | 18 | 0 | 0 | 310 | 0 | 5 | 0 | 145 | 0 | 0 | 130 | 0 | 30 | 0 | 20 | 50 | 70 | 0 | 0 | 0 | 0 | 4 | 180 | 54 | 0 | 0 | 17 | 50 | 130 | 34 | 0 | 72 | 0 | 100 |  | 662 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 159 | 0 | 362 | 35 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 320 | 23 | 0 | 12 |  | 4312 | 2391 | 6703 | 2750 | 662 | 1379 | 1250 | 470 | 46 | 51 | 86 | 9 | 0 | 97.64
12:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 338 | 125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 5 | 19 | 0 | 23 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 4 | 0 | 0 | 0 | 260 | 385 | 184 | 26 | 80 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 84 | 144 | 40 | 22 | 2 | 0 | 0 | 34 | 50 | 0 | 0 | 40 | 66 | 0 | 163 | 18 | 0 | 0 | 310 | 0 | 5 | 0 | 145 | 0 | 0 | 130 | 0 | 38 | 0 | 38 | 58 | 92 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 17 | 90 | 127 | 44 | 0 | 72 | 0 | 100 |  | 662 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 192 | 0 | 319 | 53 | 0 | 60 | 0 | 34 | 0 | 4 | 50 | 320 | 33 | 0 | 31 |  | 4480 | 2534 | 7014 | 2924 | 662 | 1229 | 1540 | 470 | 44 | 51 | 84 | 10 | 0 | 97.64
13:00 | 0 | 0 | 0 | 0 | 300 | 106 | 0 | 361 | 102 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 14 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 43 | 17 | 12 | 0 | 0 | 0 | 305 | 380 | 184 | 26 | 82 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 80 | 120 | 40 | 20 | 2 | 0 | 0 | 31 | 50 | 0 | 0 | 40 | 71 | 0 | 157 | 18 | 0 | 0 | 290 | 0 | 8 | 0 | 195 | 0 | 0 | 130 | 0 | 80 | 0 | 50 | 68 | 100 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 55 | 90 | 121 | 66 | 0 | 72 | 0 | 100 |  | 662 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 40 | 163 | 0 | 323 | 53 | 0 | 112 | 0 | 34 | 0 | 4 | 70 | 320 | 19 | 0 | 31 |  | 4693 | 2563 | 7256 | 2906 | 662 | 1191 | 1838 | 470 | 45 | 54 | 80 | 10 | 7256 | 97.63
14:00 | 0 | 0 | 0 | 0 | 300 | 106 | 0 | 353 | 183 |  | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 21 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 46 | 17 | 5 | 0 | 0 | 0 | 300 | 265 | 184 | 26 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 120 | 40 | 17 | 1 | 0 | 0 | 34 | 50 | 0 | 0 | 40 | 73 | 0 | 156 | 18 | 0 | 9 | 290 | 0 | 8 | 0 | 195 | 0 | 0 | 130 | 0 | 80 | 0 | 20 | 68 | 100 | 0 | 0 | 0 | 0 | 3 | 181 | 54 | 0 | 0 | 55 | 100 | 130 | 34 | 0 | 35 | 0 | 100 |  | 662 | 0 | 325 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 161 | 0 | 314 | 53 | 0 | 70 | 0 | 36 | 0 | 3 | 35 | 300 | 32 | 0 | 32 |  | 4578 | 2470 | 7048 | 2789 | 662 | 1284 | 1660 | 450 | 45 | 63 | 88 | 7 | 0 | 97.63
15:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 377 | 102 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 21 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 47 | 17 | 4 | 0 | 0 | 0 | 340 | 320 | 206 | 26 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 119 | 40 | 20 | 1 | 0 | 0 | 49 | 50 | 0 | 0 | 40 | 71 | 0 | 156 | 18 | 0 | 9 | 310 | 0 | 8 | 0 | 195 | 0 | 0 | 130 | 0 | 80 | 0 | 20 | 50 | 100 | 0 | 0 | 0 | 0 | 2 | 197 | 54 | 0 | 0 | 26 | 50 | 130 | 17 | 0 | 35 | 0 | 45 |  | 663 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 165 | 0 | 417 | 53 | 0 | 70 | 0 | 35 | 0 | 3 | 35 | 300 | 29 | 0 | 35 |  | 4507 | 2495 | 7002 | 2876 | 663 | 1336 | 1475 | 450 | 46 | 62 | 88 | 6 | 0 | 97.63
16:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 361 | 132 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 22 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 17 | 8 | 0 | 0 | 0 | 300 | 275 | 184 | 26 | 91 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 119 | 40 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 40 | 68 | 0 | 150 | 18 | 0 | 9 | 290 | 0 | 8 | 0 | 195 | 0 | 0 | 130 | 0 | 77 | 0 | 20 | 50 | 100 | 0 | 0 | 0 | 0 | 1 | 197 | 54 | 0 | 0 | 26 | 50 | 130 | 17 | 0 | 35 | 0 | 0 |  | 663 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 156 | 0 | 405 | 53 | 0 | 70 | 0 | 35 | 0 | 2 | 35 | 300 | 56 | 0 | 35 |  | 4437 | 2480 | 6917 | 2765 | 663 | 1365 | 1475 | 450 | 46 | 62 | 88 | 3 | 0 | 97.63
17:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 361 | 239 |  | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 88 | 1 | 7 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 0 | 22 | 25 | 33 | 2 | 0 | 47 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 17 | 11 | 0 | 0 | 0 | 285 | 290 | 192 | 26 | 91 | 26 | 55 | 0 | 51 | 0 | 0 | 1 | 19 | 8 | 33 | 21 | 100 | 140 | 40 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 65 | 71 | 0 | 150 | 18 | 0 | 9 | 300 | 0 | 0 | 0 | 197 | 0 | 0 | 130 | 0 | 80 | 1 | 20 | 50 | 100 | 0 | 1 | 5 | 0 | 0 | 198 | 54 | 0 | 0 | 26 | 50 | 130 | 17 | 0 | 72 | 0 | 0 |  | 662 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 157 | 0 | 399 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 300 | 56 | 0 | 35 |  | 4716 | 2478 | 7194 | 2815 | 662 | 1479 | 1553 | 450 | 47 | 87 | 100 | 1 | 0 | 97.62
18:00 | 0 | 0 | 20 | 0 | 300 | 102 | 0 | 364 | 336 |  | 0 | 0 | 0 | 18 | 38 | 13 | 0 | 0 | 90 | 30 | 7 | 115 | 67 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 8 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 68 | 0 | 13 | 50 | 17 | 11 | 0 | 0 | 0 | 365 | 350 | 219 | 26 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 21 | 112 | 139 | 40 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 65 | 72 | 0 | 150 | 18 | 0 | 9 | 315 | 0 | 0 | 0 | 242 | 0 | 0 | 130 | 0 | 83 | 0 | 64 | 50 | 110 | 0 | 8 | 32 | 0 | 0 | 235 | 54 | 0 | 0 | 26 | 100 | 130 | 48 | 0 | 72 | 0 | 0 |  | 709 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 159 | 0 | 416 | 70 | 0 | 90 | 0 | 90 | 0 | 0 | 90 | 380 | 43 | 0 | 54 |  | 5620 | 2796 | 8416 | 3005 | 709 | 1605 | 2129 | 530 | 47 | 279 | 112 | 0 | 0 | 97.62
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 19 | 0 | 380 | 102 | 0 | 375 | 340 |  | 0 | 0 | 0 | 70 | 52 | 15 | 0 | 0 | 97 | 100 | 16 | 115 | 86 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 23 | 25 | 33 | 12 | 0 | 48 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 21 | 0 | 68 | 0 | 30 | 50 | 17 | 20 | 0 | 0 | 0 | 305 | 300 | 184 | 26 | 82 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 21 | 108 | 133 | 45 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 67 | 73 | 0 | 150 | 18 | 0 | 9 | 290 | 0 | 0 | 0 | 270 | 0 | 0 | 175 | 0 | 126 | 0 | 100 | 50 | 132 | 0 | 8 | 90 | 0 | 0 | 268 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 710 | 0 | 265 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 183 | 0 | 379 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 47 | 0 | 54 |  | 6154 | 2970 | 9124 | 2970 | 710 | 1562 | 2817 | 630 | 48 | 279 | 108 | 0 | 0 | 97.62
19:30 | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 366 | 307 |  | 0 | 0 | 0 | 50 | 80 | 15 | 0 | 0 | 98 | 50 | 16 | 100 | 86 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 25 | 33 | 8 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 0 | 34 | 0 | 31 | 50 | 17 | 26 | 0 | 0 | 0 | 320 | 315 | 193 | 26 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 135 | 58 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 67 | 74 | 0 | 150 | 18 | 0 | 9 | 320 | 0 | 11 | 0 | 270 | 0 | 0 | 195 | 0 | 128 | 0 | 100 | 50 | 149 | 0 | 0 | 90 | 0 | 0 | 268 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 709 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 180 | 0 | 425 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 42 | 0 | 54 |  | 6128 | 3013 | 9141 | 3020 | 709 | 1607 | 2771 | 650 | 48 | 230 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 356 | 320 |  | 0 | 0 | 0 | 40 | 70 | 15 | 0 | 0 | 99 | 50 | 16 | 100 | 86 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 25 | 33 | 8 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 0 | 34 | 0 | 32 | 50 | 17 | 10 | 0 | 0 | 0 | 310 | 300 | 187 | 26 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 134 | 58 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 67 | 74 | 0 | 150 | 19 | 0 | 9 | 280 | 0 | 11 | 0 | 267 | 0 | 0 | 195 | 0 | 126 | 0 | 100 | 50 | 143 | 0 | 0 | 90 | 0 | 0 | 268 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 709 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 178 | 0 | 416 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 42 | 0 | 54 |  | 6042 | 2990 | 9032 | 2994 | 709 | 1557 | 2737 | 650 | 48 | 231 | 106 | 0 | 0 | 97.62
21:00 | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 351 | 292 |  | 0 | 0 | 0 | 7 | 72 | 15 | 0 | 0 | 100 | 50 | 16 | 84 | 86 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 50 | 17 | 27 | 0 | 0 | 0 | 305 | 300 | 184 | 8 | 90 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 100 | 123 | 58 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 67 | 74 | 0 | 150 | 19 | 0 | 9 | 305 | 0 | 11 | 0 | 270 | 0 | 0 | 195 | 0 | 123 | 0 | 100 | 50 | 142 | 0 | 0 | 50 | 0 | 0 | 271 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 710 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 169 | 0 | 419 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 41 | 0 | 54 |  | 5819 | 2953 | 8772 | 2947 | 710 | 1523 | 2595 | 650 | 48 | 199 | 100 | 0 | 0 | 97.62
22:00 | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 352 | 324 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 100 | 0 | 16 | 48 | 86 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 50 | 17 | 38 | 0 | 0 | 0 | 305 | 300 | 184 | 8 | 86 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 98 | 124 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 68 | 73 | 0 | 143 | 19 | 0 | 9 | 310 | 0 | 11 | 0 | 286 | 0 | 0 | 170 | 0 | 55 | 0 | 60 | 50 | 142 | 0 | 0 | 0 | 0 | 0 | 271 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 710 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 163 | 0 | 418 | 53 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 500 | 41 | 0 | 54 |  | 5402 | 2840 | 8242 | 2920 | 710 | 1569 | 2152 | 650 | 47 | 96 | 98 | 0 | 0 | 97.61
23:00 | 0 | 0 | 19 | 0 | 380 | 102 | 0 | 352 | 345 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 100 | 0 | 0 | 16 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 17 | 40 | 0 | 0 | 0 | 320 | 320 | 176 | 8 | 90 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 90 | 124 | 0 | 22 | 0 | 26 | 0 | 53 | 50 | 0 | 0 | 67 | 73 | 0 | 144 | 19 | 0 | 9 | 280 | 0 | 11 | 0 | 205 | 0 | 0 | 140 | 0 | 0 | 0 | 20 | 50 | 142 | 0 | 0 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 25 | 100 | 130 | 90 | 0 | 72 | 0 | 0 |  | 710 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 158 | 0 | 420 | 17 | 0 | 70 | 0 | 36 | 0 | 0 | 35 | 500 | 57 | 0 | 54 |  | 4989 | 2589 | 7578 | 2931 | 710 | 1577 | 1554 | 650 | 46 | 20 | 90 | 0 | 0 | 97.61
24:00 | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 350 | 344 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 25 | 17 | 41 | 0 | 0 | 0 | 295 | 300 | 165 | 8 | 90 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 86 | 124 | 0 | 22 | 0 | 26 | 0 | 53 | 50 | 0 | 0 | 69 | 73 | 0 | 144 | 19 | 0 | 9 | 290 | 0 | 11 | 0 | 130 | 0 | 0 | 140 | 0 | 0 | 0 | 20 | 50 | 142 | 0 | 0 | 0 | 0 | 0 | 197 | 43 | 0 | 0 | 25 | 100 | 130 | 70 | 0 | 47 | 0 | 0 |  | 615 | 0 | 210 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 156 | 0 | 379 | 17 | 0 | 70 | 0 | 19 | 0 | 0 | 35 | 480 | 57 | 0 | 54 |  | 4731 | 2398 | 7129 | 2874 | 615 | 1546 | 1329 | 630 | 45 | 4 | 86 | 0 | 0 | 97.61
KWH | 0 | 0 | 144000 | 0 | 7894709 | 2407681 | 0 | 8650750 | 6530000 |  | 0 | 0 | 0 | 149760 | 387744 | 69842 | 0 | 0 | 869000 | 247680 | 85824 | 478080 | 1025839 | 0 | 0 | 0 | 121680 | 115182 | 257150 | 489996 | 600000 | 572580 | 630300 | 837700 | 36660 | 0 | 1104000 | 0 | 0 | 0 | 232659 | 0 | 0 | 0 | 0 |  | 220560 | 0 | 184803 | 0 | 85440 | 699840 | 401136 | 444000 | 0 | 0 | 0 | 7400000 | 7146000 | 4568000 | 418181 | 2097210 | 598248 | 1248480 | 0 | 1206074 | 0 | 0 | 19046 | 404136 | 175860 | 820600 | 496780 | 2082240 | 3342960 | 505920 | 483192 | 9000 | 128000 | 0 | 939000 | 1210176 | 0 | 0 | 1161312 | 1420800 | 0 | 3785990 | 432000 | 0 | 153900 | 7454700 | 56352 | 168000 | 0 | 3434944 | 0 | 0 | 2829600 | 0 | 998500 | 17010 | 683520 | 1057440 | 2100945 | 0 | 20400 | 322968 | 0 | 25200 | 4109891 | 1289304 | 0 | 0 | 684600 | 1878720 | 3105700 | 1026240 | 7440 | 1380960 | 0 | 1460000 |  | 14440000 | 0 | 7366464 | 0 | 1783680 | 0 | 0 | 0 | 36960 | 0 | 301875 | 0 | 473900 | 0 | 0 | 0 | 0 | 0 | 0 | 999560 | 0 | 0 | 0 | 17760 | 0 | 448560 | 0 | 101790 | 0 | 0 | 3693100 | 0 | 0 | 0 | 0 | 0 | 0 | 547023 | 262080 | 4200836 | 0 | 8875491 | 826080 | 0 | 1493760 | 0 | 794880 | 0 | 22022 | 1079328 | 9964700 | 1140380 | 0 | 931200 |  | 112340134 | 59801429 | 172141563 | 70589601 | 14440000 | 34918346 | 33569501 | 13657800 | 1104000 | 1699403 | 2082240 | 80672 | 0
Fuel Cost | 0 | 0 | 210240 | 0 | 8763126.99 | 3178138.92 | 0 | 8737257.5 | 6725900 |  | 0 | 0 | 0 | 1136678.4 | 2671556.16 | 590863.32 | 0 | 0 | 1503370 | 1865030.4 | 782714.88 | 4704307.2 | 9458235.58 | 0 | 0 | 0 | 888264 | 890356.86 | 2535499 | 367497 | 450000 | 0 | 0 | 0 | 354502.2 | 0 | 298080 | 0 | 0 | 0 | 2161402.11 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1792589.1 | 0 | 743328 | 5542732.8 | 505431.36 | 1318680 | 0 | 0 | 0 | 5476000 | 7146000 | 4202560 | 539453.49 | 2411791.5 | 676020.24 | 1747872 | 0 | 2062386.54 | 0 | 0 | 181889.3 | 513252.72 | 131895 | 1436050 | 372585 | 15616800 | 3543537.6 | 4593753.6 | 613653.84 | 143460 | 209920 | 0 | 1671420 | 1887874.56 | 0 | 0 | 2287784.64 | 2713728 | 0 | 6549762.7 | 946080 | 0 | 313956 | 7529247 | 42264 | 127680 | 0 | 25968176.64 | 0 | 0 | 14713920 | 0 | 9825240 | 198846.9 | 5570688 | 11473224 | 14811662.25 | 0 | 186048 | 3052047.6 | 0 | 0 | 31070775.96 | 11229837.84 | 0 | 0 | 5867022 | 12512275.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83174400 | 0 | 7734787.2 | 0 | 14019724.8 | 0 | 0 | 0 | 387710.4 | 0 | 3145537.5 | 0 | 734545 | 0 | 0 | 0 | 0 | 0 | 0 | 8846106 | 0 | 0 | 0 | 172094.4 | 0 | 861235.2 | 0 | 77055.03 | 0 | 0 | 20016602 | 0 | 0 | 0 | 0 | 0 | 0 | 820534.5 | 4457980.8 | 4914978.12 | 0 | 8786736.09 | 8624275.2 | 0 | 14175782.4 | 0 | 6168268.8 | 0 | 243343.1 | 7976233.92 | 43745033 | 0 | 0 | 0 |  | 290344223.9 | 239082963.46 | 529427187.36 | 69950580.44 | 83174400 | 40891707.3 | 239417621.92 | 63761635 | 298080 | 15730712.7 | 15616800 | 585650 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 338 | 125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 5 | 19 | 0 | 23 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 4 | 0 | 0 | 0 | 260 | 385 | 184 | 26 | 80 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 84 | 144 | 40 | 22 | 2 | 0 | 0 | 34 | 50 | 0 | 0 | 40 | 66 | 0 | 163 | 18 | 0 | 0 | 310 | 0 | 5 | 0 | 145 | 0 | 0 | 130 | 0 | 38 | 0 | 38 | 58 | 92 | 0 | 0 | 0 | 0 | 4 | 215 | 54 | 0 | 0 | 17 | 90 | 127 | 44 | 0 | 72 | 0 | 100 |  | 662 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 192 | 0 | 319 | 53 | 0 | 60 | 0 | 34 | 0 | 4 | 50 | 320 | 33 | 0 | 31 |  | 7014 | DayPeak
Yesterday Evening Peak | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 366 | 307 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 0 | 0 | 98 | 50 | 16 | 100 | 86 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 25 | 33 | 8 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 34 | 0 | 31 | 50 | 17 | 26 | 0 | 0 | 0 | 320 | 315 | 193 | 26 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 135 | 58 | 22 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 67 | 74 | 0 | 150 | 18 | 0 | 9 | 320 | 0 | 11 | 0 | 270 | 0 | 0 | 195 | 0 | 128 | 0 | 100 | 50 | 149 | 0 | 0 | 90 | 0 | 0 | 268 | 54 | 0 | 0 | 55 | 100 | 130 | 104 | 0 | 72 | 0 | 0 |  | 709 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 180 | 0 | 425 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 42 | 0 | 54 |  | 9141 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 360 | 100 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 35 | 0 | 0 | 70 | 360 | 330 | 190 | 8 | 91 | 26 | 50 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 22 | 147 | 150 | 95 | 22 | 0 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 0 | 0 |  | 726 | 16 | 325 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 94 | 35 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 54
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 60 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 17 | 25 | 0 | 0 | 70 | 300 | 300 | 180 | 8 | 90 | 26 | 50 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 135 | 150 | 95 | 22 | 1.6 | 45 | 20 | 51 | 44 | 0 | 0 | 68 | 70 | 0 | 200 | 20 | 0 | 9 | 330 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 0 | 0 |  | 678 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 35 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 54
Generation at 08:00(Today) | 0 | 0 | 20 | 0 | 380 | 102 | 0 | 360 | 309 | 0 | 0 | 0 | 0 | 16 | 35 | 0 | 0 | 0 | 40 | 7 | 16 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 24 | 25 |  | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 20 | 17 | 14 | 0 | 0 | 70 | 285 | 300 | 190 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 78 | 147 | 0 | 22 | 0 | 26 | 0 | 53 | 50 | 0 | 0 | 40 | 40 | 0 | 143 | 0 | 0 | 9 | 300 | 0 | 11 | 0 | 128 | 0 | 0 | 135 | 0 | 56 | 6 | 40 | 34 | 85 | 0 | 0 | 0 | 0 | 1 | 125 | 54 | 0 | 0 | 39 | 50 | 130 | 53 | 4 | 35 | 0 | 0 | 0 | 566 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1 | 150 | 0 | 334 | 17 | 0 | 67 | 0 | 70 | 0 | 0 | 70 | 400 | 45 | 0 | 0 | 0
199
| Minimum Generation |  | 5529 | 5:00
| Highest Generation |  | 9141 | 19:30
| Day Peak Generation |  | 7014 | 12:00
| Evening Peak Generation |  | 9141 | 19:30
| HVDC Max Flow |  | 710 | 19:00
| HVDC EvPeak Flow |  | 709 | 19:30
| Load factor L.F |  | 78.47%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7014 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5757 | MW
Evening Peak Generation : |  | 9141 | MW Hour : | 19:30 | Available Max Generation : |  | 13631 | MW
E.P. Demand (at gen end) : |  | 9141 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9141 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4131 | MW
Total Gen. (MKWH) : |  | 172.1416 | System Load Factor : | 78.47% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -27 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-10
Actual : | 97.59 | Ft.(MSL) , | Rule curve : | 101.29 | Ft.( MSL )
Gas Consumed : | Total = | 808.62 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 110842287.74
: |  | Coal : | 63761635 | Oil : | 255148334.62 | Total : | 429752257.36
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3399.4039 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1152.0085 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1031.4528 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 931.753 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 842.1505 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 679.5756 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 385.1029 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 175.1079 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 524.098 |  |  | 0 | 0%
Total | 0 |  | 9120.6532 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2, 3 ,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Madunaghat 132/33 kV T2 transformer and its associated Bay were under shut down from 08:42 to
14:04 for A/M.
b) Hathazari-Raozan 230 kV Ckt-2 was under shutdown from 08:59 to 15:32 for A/M.
c) New Tongi 132 kV Bus section-2 was under shut down from 09:12 to 12:43 for A/M.
d) Mirpur 132/33 kV T1 transformer was under shut down from 09:20 to 19:30 for A/M.
e) Savar-Manikganj PP 132 kV Ckt was under shutdown from 09:04 to 16:58 for A/M.
f) Comilla(N)-Chandpur 132 kV Ckt-1 was under shutdown from 08:13 to 16:35 for A/M.
g) Rampura 230/132 kV T03 transformer was under shut down from 08:30 to 16:31 for A/M.
h) Comilla(N) 132/33 kV T3 transformer was under shut down from 08:33 to 14:48 for A/M.
i) Maniknagar 132/33 kV GT2 transformer was under shut down from 09:50 to 13:52 for A/M.
j) Kabirpur-Kodda 132 kV Ckt-1 was under shutdown from 10:46 to 16:46 for A/M.
k) Mymensing-Mymensing Solar PP 132 kV Ckt was under shutdown from 09:26 to 17:55 for A/M.
l) Mymensing-Kishorganj 132 kV Ckt-1 was under shutdown from 09:52 to 13:06 for A/M.
m) Mymensing 132 kV Bus-1 was under shut down from 10:40 to 17:15 for A/M.
n) Kishorganj-Ashuganj 132 kV Ckt-1 was under shutdown from 08:43 to 16:21 for A/M.
o) Kabirpur 132/33 kV T3 transformer was under shut down from 08:52 to 16:49 for A/M.
p) Cantonment 132/33 kV T1 transformer was under shut down from 08:03 to 15:06 for A/M.
q) Mymensing-Jamalpur 132 kV Ckt-1 was under shutdown from 08:23 to 18:28 for D/W.
r) Rampura 230 kV Bus-2 was under shut down from 08:45 to 13:25 for D/W.
s) Tongi 132/33 kV T3 transformer was switched on at 10:45.
t) Mirpur-Uttara 3rd phase 132 kV Ckt was under shutdown from 09:58 to 20:45 for C/M.
u) Ramganj 132/33 kV T1 transformer was under shut down from 09:10 to 17:59 for SAS work.
v) B.Baria 132/33 kV T2 transformer was under shut down from 09:02 to 10:53 for C/M. |  |  |  |  | About 15 MW power interruption occurred under B.Baria S/S area
from 09:02 to 10:53.
w) Haripur 132/33 kV T1 transformer is under shutdown since 08:16 for C/M.
x) Natore-Ishurdi 132 kV Ckt-1 was under shutdown from 08:26 to 16:18 for A/M.
y) Sirajganj-Shahjadpur 132 kV Ckt was under shutdown from 08:48 to 15:37 for A/M.
z) Barisal-Bhandaria 132 kV Ckt was under shutdown from 08:07 to 16:34 for A/M.
aa) Bheramara-Bottail 132 kV Ckt-2 was under shutdown from 08:16 to 14:15 for A/M.
ab) Pabna 132/33 kV T3 transformer was under shut down from 08:43 to 16:59 for A/M.
ac) Saidpur-Barapukuria 132 kV Ckt-2 was under shutdown from 10:48 to 17:26 for C/M.
ad) Barishal 132/33 kV T4 & T5 transformer's 33 kV Bus were under shut down from 09:19 to 15:36 for A/M.
ae) Purbasadipur-Thakurgaon 132 kV Ckt-1 switched on at 11:07.
af) Sylhet 132/33 kV T1 transformer was switched on at 10:51.
ag) Haripur 360 MW ST tripped & synchronized at 11:33 & 15:51 respectively.
ah) Mymensing-Kishorganj 132 kV Ckt-2 was under shutdown from 13:08 to 17:28 for A/M.
ai) Rampura-Gulshan 132 kV Ckt-2 was under shutdown from 13:08 to 17:28 for Relay functional test.
aj) Siddhirganj PP GT-2 was synchronized at 15:27.
ak) Shahjibazar 100 MW tripped at 15:56 due to tripping of GBC.
al) Ghorashal Unit-4 GT was synchronized at 17:01.
am) Ashuganj Unit-5 was synchronized at 00:22(10/01/2021).
an) Bheramara-Bottail 132 kV Ckt-2 is under shut down since 07:45(10/01/2021) for A/M.
ao) Rampura 132/33 kV T3 transformer is under shut down since 07:42(10/01/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 20 | 144000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7894709
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2407681
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 366 | 8650750 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 307 | 6530000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 149760 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 387744 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 69842 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 86 | 1025839 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 489996
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 869000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 247680 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 85824 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 121680 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 478080 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 115182 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 257150 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1172580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 630300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 837700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 36660 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 3434944 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 128 | 998500 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 322968 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1026240
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1380960 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2544 | 39765769
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 232659
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 17010
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 699840
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 48 | 1104000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 184803 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 683520
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 401136 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 444000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 31 | 85440 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25200
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 268 | 4109891 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1289304
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1878720
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 753 | 11155523
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 193 | 4568000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7400000
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7146000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 598248 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1248480
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 418181 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1206074
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 149 | 2100945
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2097210
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 50 | 1057440 | Low demand
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 404136 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 175860 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2082240
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 19046 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 496780 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 684600 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1518 | 32523840
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 135 | 3342960 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483192
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 58 | 505920 | Low demand
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9000
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 2829600 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 20400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 7440
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 21 | 220560
| Mymensingh Area Total |  |  |  | 709 | 431 | 7419072
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 128000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Line O/L
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 939000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1210176
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 168000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1161312
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1420800 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 1460000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3785990
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 56352 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7454700
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 153900
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 130 | 3105700 | On test
| Sylhet Area Total |  |  |  | 1988 | 882 | 21475930
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 709 | 14440000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1783680
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 3 | 36960 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7366464 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 8 | 301875 | Low demand
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 262080 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 826080 | Low demand
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1148 | 25017139
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 473900 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 21 | 547023
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 9964700
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 42 | 1140380 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 54 | 931200 | On test.
| Barisal Area Total |  |  |  | 1676 | 644 | 13057203
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4200836 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 425 | 8875491 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 448560
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 101790
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 17760 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 999560
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1493760
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1079328
| Rajshahi Area Total |  |  |  | 2183 | 958 | 17217085
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3693100
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 794880
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22022
| Rangpur Area Total |  |  |  | 605 | 263 | 4510002
| Total |  |  |  | 20748 | 9141 | 172141563
| Eastern Grid Total |  |  |  | 14000 | 6128 | 112340134
| Western Grid Total |  |  |  | 6748 | 3013 | 59801429
| National Grid Total |  |  |  | 20748 | 9141 | 172141563
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-09
| (a) ENTIRE EASTERN GRID : |  | 5945 | MW | (b) ENTIRE WESTERN GRID : |  | 2822 | MW
| i) Dhaka area |  | 3069 | MW | i) Khulna area |  | 1087 | MW
| ii) Chittagong area |  | 1053 | MW | ii) Rajshahi area |  | 913 | MW
| iii) Comilla area |  | 733 | MW | iii) Barisal area |  | 243 | MW
| iv) Mymensingh area |  | 761 | MW | iv) Rangpur area |  | 579 | MW
| v) Sylhet area |  | 329 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8767 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 94 | 18:00 | Jamalpur | 90 | 19:00 | Benapol | 40 | 18:30
| Munsiganj | 76 | 19:00 | Sherpur | 108 | 18:30 | Jhenida | 84 | 18:30
| Sonargaon | 66 | 18:00 | Srimongal | 31 | 10:00 | Bottail | 92 | 18:30
| Shyampur | 174 | 11:00 | Shahjibazar | 90 | 18:30 | G.K Project | 38 | 18:30
| Bhulta | 164 | 19:00 | Fenchuganj | 26 | 18:00 | Faridpur | 134 | 18:30
| Madanganj | 36 | 11:00 | Kulawara | 27 | 18:00 | Madaripur | 67 | 20:00
| Shitalakhya | 97 | 12:00 | Sylhet | 82 | 18:30 | Sariatpur | 42 | 19:00
| Rahim steel | 20 | 13:00 | Chatak | 21 | 18:00 | Gopalganj | 66 | 18:30
| Matuail | 42 | 12:00 | Sunamganj | 29 | 19:30 | Bagerhat | 86 | 18:30
| Ghorasal | 60 | 19:00 | Biani Bazar | 38 | 19:30 | Mongla | 38 | 10:00
| Narsingdi | 124 | 18:30 | Comilla (S) | 112 | 18:00 | Satkhira | 75 | 18:30
| Haripur (SBU) | 104 | 19:00 | Comilla(N) | 53 | 18:00 | Gallamari | 22 | 12:00
| Ullon | 46 | 13:00 | Chandpur | 62 | 19:00 | Magura | 40 | 18:30
| Hasnabad | 140 | 18:30 | Feni | 75 | 18:00 | Norail | 24 | 18:30
| Magbazar | 65 | 12:00 | Chowmuhani | 121 | 18:30 | Chuadanga | 63 | 18:30
| Maniknagar | 68 | 19:00 | Ashuganj | 37 | 20:00 | Barisal(N) | 32 | 19:30
| Bangabhaban | 10 | 11:00 | Daudkandi | 104 | 19:30 | Barisal (S) | 66 | 18:30
| Narinda | 68 | 11:00 | B.Baria | 100 | 19:30 | Patuakhali | 51 | 21:00
| Dhanmondi | 92 | 13:00 | Ramganj | 68 | 20:00 | Bhandaria | 42 | 20:00
| Lalbag | 68 | 12:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 20:00
| Madartek | 46 | 20:00 | PHP | 10 | 13:00 | Ishurdi | 47 | 18:30
| Dhaka University | 0 | #NUM! | Madunaghat | 45 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.16667 | Hathazari | 66 | 0.79167 | Natore | 86 | 0.83333
| Fatullah | 44 | 12:00 | Khulshi | 146 | 19:30 | Bogra | 121 | 19:00
| Mirpur | 74 | 18:30 | Halishahar | 107 | 18:30 | Noagaon | 76 | 19:00
| Kalyanpur | 69 | 18:30 | Baraulia | 145 | 11:00 | Rajshahi | 96 | 19:00
| Gulshan | 70 | 13:00 | Sikalbaha | 18 | 18:00 | Rajshahi New | 10 | 19:00
| Uttara | 65 | 18:30 | Dohazari | 58 | 19:00 | C.Nawabganj | 52 | 20:00
| Uttara New | 27 | 18:30 | Cox'sbazar | 81 | 18:30 | Amnura | 34 | 19:00
| Kamrangirchar | 68 | 18:30 | Chandraghona | 20 | 10:00 | Pabna | 64 | 19:00
| Savar | 108 | 12:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 68 | 18:00
| Bhasantec | 96 | 18:30 | A. Khaer Stl. | 12 | 12:00 | Serajganj | 71 | 19:00
| Agargaon | 47 | 18:30 | Bakulia | 77 | 18:30 | Niyamatpur | 76 | 19:00
| Satmosjid | 54 | 0.77083 | Julda | 19 | 0.5 | Joypurhat | 45 | 0.83333
| Tongi | 68 | 12:00 | TK chemical | 19 | 20:00 | Sherpur(Bogura) | 37 | 18:30
| Kabirpur | 177 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 93 | 18:00 | Shahmirpur | 16.5 | 13:00 | Bangura | 15 | 18:00
| Manikganj | 42 | 20:00 | Khagrachhari | 14 | 7:00 | Rangpur | 107 | 18:00
| Joydevpur | 119 | 18:30 | Matarbari | 27 | 19:00 | Lalmonirhat | 45 | 19:00
| New Tongi | 96 | 18:00 | Baroiar Hat | 24 | 18:00 | Saidpur | 84 | 19:00
| Kodda | 157 | 9:00 | Rangamati | 8 | 18:00 | Purbasadipur | 80 | 18:30
| Dhamrai | 76 | 18:30 | Abul Khair 230 | 148 | 15:00 | Thakurgaon | 58 | 20:00
| Rajendrapur | 76 | 19:00 | BSRM | 155 | 2:00 | Palashbari | 86 | 18:30
| Valuka | 84 | 16:00 | GPH Ispat | 84 | 20:00 | Barapukuria | 41 | 18:30
| Tangail | 139 | 18:30 | Goalpara | 16 | 13:00 | Panchagar | 42 | 18:30
| Mymensing | 166 | 19:00 | Central s/s | 78 | 18:30 | Joldhaka | 25 | 18:30
| Kishorganj | 100 | 18:30 | Noapara | 54 | 19:00 | Kurigram | 42 | 18:30
| Netrokona | 101 | 20:00 | Jessore | 82 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 19:00 | 409 | 17:00 | Kaliakoir | 394 | 0.20833 | 369 | 0.5
| Bheramara | 403 | 4:00 | 392 | 18:30 | Bhulta | 389 | 0.79167 | 368 | 0.625
| Ashuganj(N) | 396 | 6:00 | 375 | 15:00 | Gopalganj | 412 | 0.33333 | 393 | 0.77083
| Payra | 415 | 4:00 | 404 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 19:00 | 230 | 13:00 | Comilla (N) | 238 | 19:00 | 227 | 10:00
| Ishurdi | 240 | 14:00 | 234 | 18:00 | Hathazari | 224 | 6:00 | 207 | 15:00
| Ashuganj | 242 | 21:00 | 230 | 12:00 | Megnaghat | 234 | 14:00 | 222 | 15:00
| Serajganj | 234 | 22:00 | 230 | 8:00 | Fenchuganj | 244 | 5:00 | 239 | 17:00
| Baghabari | 245 | 1:00 | 240 | 11:00 | Siddhirganj | 233 | 7:00 | 220 | 11:00
| Barapukuria | 232 | 1:00 | 228 | 8:00 | Maniknagar | 231 | 4:00 | 219 | 12:00
| Bogra | 236 | 6:00 | 229 | 9:00 | Agargaon | 230 | 9:00 | 215 | 15:00
| Rajshahi | 238 | 14:00 | 231 | 7:00 | Barisal | 252 | 13:00 | 243 | 18:00
| Khulna South | 244 | 14:00 | 230 | 18:00 | AKSML | 224 | 18:30 | 205 | 17:00
| Rampura | 232 | 2:00 | 221 | 14:00 | BSRM | 226 | 14:00 | 206 | 15:00
| Haripur | 231 | 18:30 | 219 | 12:00 | Bibiyana | 245 | 5:00 | 237 | 15:00
| Hasnabad | 230 | 1:00 | 220 | 12:00 | Bhulta | 237 | 19:00 | 220 | 17:00
| Shyampur | 229 | 4:00 | 220 | 15:00 | Ashuganj (S) | 238 | 19:00 | 227 | 15:00
| Aminbazar | 231 | 3:00 | 220 | 12:00 | Kaliakoir | 230 | 20:00 | 211 | 15:00
| Tongi | 227 | 19:30 | 212 | 10:00 | GPH | 224 | 20:00 | 208 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 6:00 | 132 | 10:00 | Madanhat | 137 | 0.58333 | 130 | 0.66667
| Munsiganj | 140 | 18:30 | 130 | 12:00 | Hathazari | 137 | 0.25 | 128 | 0.625
| Sonargaon | 137 | 18:30 | 130 | 12:00 | Khulshi | 134 | 0.20833 | 127 | 0.41667
| Shyampur | 131 | 19:00 | 123 | 10:00 | Halishahar | 136 | 0.77083 | 125 | 0.625
| Bhulta | 130 | 5:00 | 120 | 12:00 | Baraulia | 137 | 0.79167 | 126 | 0.625
| Madanganj | 137 | 4:00 | 134 | 18:30 | Sikalbaha | 137 | 0.29167 | 125 | 0.58333
| Shitalakhya | 140 | 21:00 | 129 | 12:00 | Dohazari | 134 | 0.77083 | 124 | 0.45833
| Rahim steal | 140 | 18:30 | 132 | 12:00 | Cox'sbazar | 127 | 0.77083 | 115 | 0.41667
| Matuail | 139 | 6:00 | 132 | 10:00 | Chandraghona | 136 | 0.8125 | 129 | 0.41667
| Ghorasal | 140 | 1:00 | 134 | 12:00 | Kaptai | 137 | 0.77083 | 129 | 0.375
| Narsinghdi | 132 | 18:00 | 125 | 11:00 | A. Khaer Stl. | 134 | 0.041667 | 126 | 0.70833
| Haripur (SBU) | 140 | 18:00 | 131 | 12:00 | Bakulia | 135 | 0.79167 | 126 | 0.70833
| Ullon | 134 | 3:00 | 124 | 13:00 | Julda | 137 | 0.77083 | 128 | 0.41667
| Hasnabad | 138 | 2:00 | 130 | 11:00 | TK Chemical | 136 | 0.875 | 127 | 0.41667
| Magbazar | 133 | 1:00 | 124 | 15:00 | Modern Steel | 134 | 0.20833 | 128 | 0.375
| Maniknagar | 138 | 2:00 | 128 | 15:00 | Shahmirpur | 137 | 0.77083 | 128 | 0.45833
| Bangabhaban | 138 | 2:00 | 128 | 15:00 | Khagrachhari | 135 | 0.29167 | 126 | 0.70833
| Narinda | 138 | 2:00 | 128 | 15:00 | Matarbari | 129 | 0.29167 | 120 | 0.041667
| Dhanmondi | 134 | 3:00 | 124 | 13:00 | Baroiar Hat | 136 | 0.041667 | 130 | 0.41667
| Lalbag | 131 | 1:00 | 121 | 15:00 | Rangamati | 136 | 21:00 | 124 | 10:00
| Madartek | 133 | 3:00 | 123 | 15:00 | Goalpara S/S | 138 | 9:00 | 128 | 18:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Khulna Central S/S | 138 | 12:00 | 129 | 0.75
| Aftabnagar | 132 | 7:00 | 125 | 14:00 | Noapara | 136 | 9:00 | 128 | 0.75
| Fatuiiah | 132 | 19:00 | 122 | 10:00 | Jessore | 133 | 14:00 | 124 | 0.75
| Mirpur | 133 | 6:00 | 124 | 12:00 | Benapol | 134 | 0.58333 | 124 | 0.75
| Kalyanpur | 134 | 6:00 | 126 | 12:00 | Jhenida | 133 | 4:00 | 123 | 0.75
| Gulshan | 132 | 6:00 | 125 | 12:00 | Bottail | 135 | 0.041667 | 130 | 0.75
| Uttara | 132 | 6:00 | 125 | 12:00 | G.K Project | 140 | 0.375 | 136 | 0.75
| Uttara New | 137 | 20:00 | 128 | 11:00 | Faridpur | 138 | 0.25 | 131 | 0.77083
| Kamrangirchar | 140 | 20:00 | 130 | 20:00 | Madaripur | 142 | 0.125 | 136 | 0.75
| Savar | 133 | 20:00 | 124 | 20:00 | Shariyatpur S/S | 142 | 3:00 | 134 | 0.79167
| Bhasantec | 133 | 20:00 | 126 | 11:00 | Gopalganj | 144 | 0.25 | 134 | 0.77083
| Agargaon | 135 | 6:00 | 127 | 12:00 | Bagerhat | 136 | 17:00 | 127 | 0.75
| Satmosjid | 135 | 6:00 | 127 | 12:00 | Mongla | 136 | 10:00 | 126 | 0.75
| Tongi | 127 | 20:00 | 212 | 10:00 | Satkhira | 137 | 9:00 | 129 | 18:00
| Kabirpur | 134 | 22:00 | 124 | 11:00 | Gallamari | 138 | 0.58333 | 129 | 0.75
| Basundhara | 133 | 19:00 | 124 | 15:00 | Magura | 132 | 1:00 | 120 | 0.75
| Manikganj | 143 | 18:00 | 132 | 10:00 | Narail | 131 | 0.125 | 120 | 0.75
| Joydevpur | 140 | 6:00 | 131 | 15:00 | Chuadanga | 130 | 3:00 | 118 | 0.75
| New Tongi | 139 | 21:00 | 129 | 15:00 | Barisal(N) | 143 | 3:00 | 137 | 18:30
| Kodda | 137 | 21:00 | 125 | 9:00 | Barisal (S) | 142 | 0.58333 | 135 | 0.75
| Dhamrai | 134 | 4:00 | 125 | 12:00 | Patuakhali(S) | 142 | 0.083333 | 136 | 0.75
| Rajendrapur | 137 | 18:30 | 127 | 12:00 | Bhandaria | 140 | 0.041667 | 132 | 0.58333
| Valuka | 128 | 6:00 | 117 | 18:00 | Ishurdi | 138 | 14:00 | 135 | 18:30
| Tangail | 134 | 15:00 | 126 | 18:00 | Ruppur Paromanobik | 138 | 6:00 | 136 | 19:30
| Mymensing | 130 | 6:00 | 119 | 18:00 | Natore | 137 | 4:00 | 133 | 18:00
| Kishorganj | 130 | 4:00 | 124 | 18:00 | Bogra | 137 | 12:00 | 133 | 18:00
| Netrokona | 128 | 5:00 | 116 | 18:00 | Noagaon | 134 | 5:00 | 128 | 9:00
| Jamalpur | 138 | 16:00 | 123 | 2:00 | Rajshahi | 136 | 5:00 | 131 | 18:00
| Sherpur | 138 | 17:00 | 121 | 1:00 | Rajshahi New | 136 | 17:00 | 132 | 18:00
| Srimongal | 138 | 1:00 | 136 | 12:00 | C.Nawabganj | 134 | 17:00 | 131 | 9:00
| Shahjibazar | 135 | 1:00 | 132 | 18:30 | Amnura | 135 | 17:00 | 131 | 6:00
| Fenchuganj | 138 | 6:00 | 136 | 9:00 | Pabna | 139 | 4:00 | 133 | 18:00
| Khulawara | 138 | 1:00 | 136 | 15:00 | Shahjadpur | 140 | 20:00 | 140 | 18:00
| Sylhet | 136 | 1:00 | 134 | 18:00 | Serajganj | 137 | 7:00 | 133 | 18:30
| Chatak | 136 | 1:00 | 133 | 18:00 | Niyamatpur | 132 | 4:00 | 126 | 18:30
| Sunamganj | 136 | 1:00 | 133 | 20:00 | Joypurhat | 135 | 6:00 | 128 | 9:00
| Biani Bazar | 136 | 3:00 | 134 | 18:30 | Sherpur(Bogura) | 138 | 6:00 | 133 | 11:00
| Comilla(s) | 131 | 3:00 | 124 | 18:00 | Mohastangor | 136 | 6:00 | 131 | 11:00
| Comilla(n) | 142 | 7:00 | 136 | 16:00 | Bangura | 140 | 5:00 | 137 | 18:00
| Chandpur | 143 | 14:00 | 140 | 10:00 | Rangpur | 131 | 6:00 | 123 | 18:00
| Feni | 137 | 14:00 | 131 | 10:00 | Lalmonirhat | 133 | 6:00 | 122 | 11:00
| Chowmuhani | 135 | 14:00 | 131 | 16:00 | Saidpur | 131 | 4:00 | 121 | 11:00
| Ashuganj | 137 | 6:00 | 134 | 12:00 | Purbasadipur | 131 | 5:00 | 120 | 11:00
| Daudkandi | 138 | 7:00 | 133 | 19:00 | Thakurgaon | 128 | 6:00 | 117 | 11:00
| B.Baria | 133 | 7:00 | 130 | 14:00 | Palashbari | 132 | 20:00 | 127 | 11:00
| Ramganj | 138 | 7:00 | 133 | 19:00 | Barapukuria | 132 | 6:00 | 128 | 18:00
| Chaddagram | 140 | 14:00 | 131 | 10:00 | Panchagar | 131 | 5:00 | 117 | 11:00
| PHP | 137 | 23:00 | 129 | 15:00 | Joldhaka | 130 | 0.20833 | 121 | 0.45833

## L-Curve
Date | 2021-01-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 153 | 4731 | 2398 | 7129 |  |  |  | QF-LDC-11
0:30 | 177.5 | 4401.5 | 2211.5 | 6613 | Date: | 2021-01-09
1:00 | 202 | 4072 | 2025 | 6097
1:30 | 235.5 | 3981.5 | 1995.5 | 5977
2:00 | 269 | 3891 | 1966 | 5857
2:30 | 283.5 | 3805 | 1954 | 5759 | [5 empty] | Gen. at Eve. Peak | 9141 | 9141 MW (19:30 )
3:00 | 298 | 3719 | 1942 | 5661 | [6 empty] | 19:30
3:30 | 292 | 3700 | 1897.5 | 5597.5 | [5 empty] | Gen. at Day Peak | 7014 | 7014 MW (12:00 )
4:00 | 286 | 3681 | 1853 | 5534 | [6 empty] | 12:00
4:30 | 263 | 3668 | 1863.5 | 5531.5 | [5 empty] | Highest Generation | 9141
5:00 | 240 | 3655 | 1874 | 5529 | [6 empty] | 19:30
5:30 | 200 | 3766.5 | 1873 | 5639.5
6:00 | 160 | 3878 | 1872 | 5750
6:30 | 124 | 4025.5 | 1906.5 | 5932
7:00 | 88 | 4173 | 1941 | 6114
7:30 | 142.5 | 4224 | 2153.5 | 6377.5
8:00 | 197 | 4275 | 2366 | 6641
8:30 | 325.5 | 4358.5 | 2435.5 | 6794
9:00 | 454 | 4442 | 2505 | 6947
9:30 | 491.5 | 4354 | 2448.5 | 6802.5
10:00 | 529 | 4266 | 2392 | 6658
10:30 | 532 | 4289 | 2391.5 | 6680.5
11:00 | 535 | 4312 | 2391 | 6703
11:30 | 571 | 4396 | 2462.5 | 6858.5
12:00 | 607 | 4480 | 2534 | 7014
12:30 | 548 | 4586.5 | 2548.5 | 7135
13:00 | 489 | 4693 | 2563 | 7256
13:30 | 524 | 4635.5 | 2516.5 | 7152
14:00 | 559 | 4578 | 2470 | 7048
14:30 | 619.5 | 4542.5 | 2482.5 | 7025
15:00 | 680 | 4507 | 2495 | 7002
15:30 | 662.5 | 4472 | 2487.5 | 6959.5
16:00 | 645 | 4437 | 2480 | 6917
16:30 | 594.5 | 4576.5 | 2479 | 7055.5
17:00 | 544 | 4716 | 2478 | 7194
17:30 | 294 | 5168 | 2637 | 7805
18:00 | 44 | 5620 | 2796 | 8416
18:30 | 35.5 | 5887 | 2883 | 8770
19:00 | 27 | 6154 | 2970 | 9124
19:30 | 8 | 6128 | 3013 | 9141
20:00 | 34 | 6042 | 2990 | 9032 |  |  |  | Executive Engineer
20:30 | 59 | 5930.5 | 2971.5 | 8902 |  |  |  | Network Operation Division
21:00 | 84 | 5819 | 2953 | 8772
21:30 | 113.5 | 5610.5 | 2896.5 | 8507
22:00 | 143 | 5402 | 2840 | 8242 |  |  |  |  | Page 6 of 7
22:30 | 147.5 | 5195.5 | 2714.5 | 7910
23:00 | 152 | 4989 | 2589 | 7578
23:30 | 152.5 | 4860 | 2493.5 | 7353.5
24:00 | 153 | 4731 | 2398 | 7129
9141 MW (19:30 )
7014 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-09 |  | Energy | 172141563
[11 empty] | 2021-01-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2874 | 615 | 1546 | 1554 | 630 | 45 | 4 | 0 | 86 | 0
0:30 | 2900 | 520.5 | 1529.5 | 1057 | 590 | 43.5 | 4 | 0 | 81 | 0 | Date: | 2021-01-09
1:00 | 2926 | 426 | 1513 | 560 | 550 | 42 | 4 | 0 | 76 | 0
1:30 | 2926 | 426.5 | 1507.5 | 448.5 | 549.5 | 42 | 2 | 0 | 75 | 0 | [7 empty] | Total Energy | 172.1416 | Total Energy Gen 172.142 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.142 MKWHr
2:00 | 2926 | 427 | 1502 | 337 | 549 | 42 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2918.5 | 426.5 | 1497 | 267.5 | 534.5 | 42 | 0 | 0 | 73 | 0 | [7 empty] | Energy Requirement | 172.1416
3:00 | 2911 | 426 | 1492 | 198 | 520 | 42 | 0 | 0 | 72 | 0
3:30 | 2918.5 | 426.5 | 1439 | 188 | 510 | 43.5 | 0 | 0 | 72 | 0 | [6 empty] | Shortage
4:00 | 2926 | 427 | 1386 | 178 | 500 | 45 | 0 | 0 | 72 | 0
4:30 | 2901.5 | 427 | 1397 | 189 | 500 | 45 | 0 | 0 | 72 | 0
5:00 | 2877 | 427 | 1408 | 200 | 500 | 45 | 0 | 0 | 72 | 0
5:30 | 2886 | 426.5 | 1406.5 | 303.5 | 500 | 45 | 0 | 0 | 72 | 0
6:00 | 2895 | 426 | 1405 | 407 | 500 | 45 | 0 | 0 | 72 | 0
6:30 | 2905.5 | 426 | 1426 | 559 | 500 | 45.5 | 0 | 0 | 70 | 0 |  |  |  |  | Coal
7:00 | 2916 | 426 | 1447 | 711 | 500 | 46 | 0 | 0 | 68 | 0
7:30 | 2910.5 | 496.5 | 1442.5 | 877 | 500 | 47 | 25.5 | 0 | 74 | 4.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2905 | 567 | 1438 | 1043 | 500 | 48 | 51 | 0 | 80 | 9
8:30 | 2914.5 | 567 | 1447.5 | 1159 | 510 | 48 | 51 | 0 | 83 | 14
9:00 | 2924 | 567 | 1457 | 1275 | 520 | 48 | 51 | 0 | 86 | 19
9:30 | 2862.5 | 614.5 | 1407 | 1227.5 | 495 | 47.5 | 51 | 0 | 85 | 12.5
10:00 | 2801 | 662 | 1357 | 1180 | 470 | 47 | 51 | 0 | 84 | 6
10:30 | 2775.5 | 662 | 1368 | 1215 | 470 | 46.5 | 51 | 0 | 85 | 7.5
11:00 | 2750 | 662 | 1379 | 1250 | 470 | 46 | 51 | 0 | 86 | 9
11:30 | 2837 | 662 | 1304 | 1395 | 470 | 45 | 51 | 0 | 85 | 9.5
12:00 | 2924 | 662 | 1229 | 1540 | 470 | 44 | 51 | 0 | 84 | 10
12:30 | 2915 | 662 | 1210 | 1689 | 470 | 44.5 | 52.5 | 0 | 82 | 10
13:00 | 2906 | 662 | 1191 | 1838 | 470 | 45 | 54 | 0 | 80 | 10
13:30 | 2906 | 662 | 1191 | 1838 | 470 | 45 | 54 | 0 | 80 | 10
14:00 | 2906 | 662 | 1191 | 1838 | 470 | 45 | 54 | 0 | 80 | 10
14:30 | 2891 | 662.5 | 1263.5 | 1656.5 | 460 | 45.5 | 58 | 0 | 84 | 8
15:00 | 2876 | 663 | 1336 | 1475 | 450 | 46 | 62 | 0 | 88 | 6
15:30 | 2820.5 | 663 | 1350.5 | 1475 | 450 | 46 | 62 | 0 | 88 | 4.5
16:00 | 2765 | 663 | 1365 | 1475 | 450 | 46 | 62 | 0 | 88 | 3
16:30 | 2790 | 662.5 | 1422 | 1514 | 450 | 46.5 | 74.5 | 0 | 94 | 2
17:00 | 2815 | 662 | 1479 | 1553 | 450 | 47 | 87 | 0 | 100 | 1
17:30 | 2910 | 685.5 | 1542 | 1841 | 490 | 47 | 183 | 0 | 106 | 0.5
18:00 | 3005 | 709 | 1605 | 2129 | 530 | 47 | 279 | 0 | 112 | 0
18:30 | 2987.5 | 709.5 | 1583.5 | 2473 | 580 | 47.5 | 279 | 0 | 110 | 0
19:00 | 2970 | 710 | 1562 | 2817 | 630 | 48 | 279 | 0 | 108 | 0
19:30 | 3020 | 709 | 1607 | 2771 | 650 | 48 | 230 | 0 | 106 | 0
20:00 | 2994 | 709 | 1557 | 2737 | 650 | 48 | 231 | 0 | 106 | 0
20:30 | 2970.5 | 709.5 | 1540 | 2666 | 650 | 48 | 215 | 0 | 103 | 0
21:00 | 2947 | 710 | 1523 | 2595 | 650 | 48 | 199 | 0 | 100 | 0
21:30 | 2933.5 | 710 | 1546 | 2373.5 | 650 | 47.5 | 147.5 | 0 | 99 | 0
22:00 | 2920 | 710 | 1569 | 2152 | 650 | 47 | 96 | 0 | 98 | 0
22:30 | 2925.5 | 710 | 1573 | 1853 | 650 | 46.5 | 58 | 0 | 94 | 0
23:00 | 2931 | 710 | 1577 | 1554 | 650 | 46 | 20 | 0 | 90 | 0
23:30 | 2902.5 | 662.5 | 1561.5 | 1554 | 640 | 45.5 | 12 | 0 | 88 | 0 | Max Temp. in Dhaka |  | 27.6° C
24:00 | 2874 | 615 | 1546 | 1554 | 630 | 45 | 4 | 0 | 86 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 172.142 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.142 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 45 | 45 | 45 | 46 | 48 | 48 | 47 | 46 | 44 | 45 | 45 | 46 | 46 | 47 | 47 |  | 48 | 48 | 48 | 48 | 47 | 46 | 45 | 1104000
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 18 | 25 | 25 | 23 | 25 | 25 |  |  | 1 | 8 |  | 17 | 25 | 25 | 8 |  |  |  | 232659
| Teknaf 20MW PP (Solartech) | [7 empty] | 6 | 11 | [7 empty] | 1 | [9 empty] | 17010
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 68 |  | 68 | 34 | 34 | 17 |  |  |  | 184803
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [15 empty] | 85 | 88 | 90 |  | 97 | 98 | 99 | 100 | 100 | 100 | 100 | 869000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 0 |  |  |  |  | 34 | 61 | 95 | 130 | 145 | 145 | 195 | 195 | 195 | 195 | 197 | 242 |  | 270 | 270 | 267 | 270 | 286 | 205 | 130 | 3434944
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [17 empty] | 20 |  | 19 | 20 | 20 | 20 | 20 | 19 | 20 | 144000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 7894709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 598248
33 | Ashuganj 225 MW CCPP | 185 | 184 | 184 | 184 | 183 | 186 | 201 | 193 | 183 | 184 | 182 | 184 | 184 | 184 | 206 | 184 | 192 | 219 |  | 184 | 193 | 187 | 184 | 184 | 176 | 165 | 4568000
34 | Ashuganj 450 MW CCPP(South) | 295 | 290 | 265 | 265 | 265 | 265 | 300 | 270 | 270 | 270 | 270 | 385 | 380 | 265 | 320 | 275 | 290 | 350 |  | 300 | 315 | 300 | 300 | 300 | 320 | 300 | 7146000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 260 | 260 | 260 | 300 | 300 | 260 | 260 | 305 | 300 | 340 | 300 | 285 | 365 |  | 305 | 320 | 310 | 305 | 305 | 320 | 295 | 7400000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 57 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 56 |  | 56 | 56 | 56 | 25 | 25 | 25 | 25 | 1248480
36 | Chandpur 150 MW CCPP | 90 | 86 | 90 | 91 | 90 | 92 | 91 | 90 | 82 | 90 | 90 | 80 | 82 | 90 | 90 | 91 | 91 | 92 |  | 82 | 90 | 91 | 90 | 86 | 90 | 90 | 2097210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 349 | 352 | 351 | 353 | 354 | 370 | 360 | 356 | 362 | 340 | 322 | 338 | 361 | 353 | 377 | 361 | 361 | 364 |  | 375 | 366 | 356 | 351 | 352 | 352 | 350 | 8650750
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 330 | 357 | 357 | 357 | 325 | 272 | 273 | 125 | 102 | 183 | 102 | 132 | 239 | 336 |  | 340 | 307 | 320 | 292 | 324 | 345 | 344 | 6530000
42 | RPCL 210MW CCPP | 163 | 164 | 164 | 164 | 164 | 164 | 146 | 157 | 155 | 156 | 161 | 144 | 120 | 120 | 119 | 119 | 140 | 139 |  | 133 | 135 | 134 | 123 | 124 | 124 | 124 | 3342960
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 5 | [17 empty] | 7440
44 | Fenchugonj CCPP Phase-1 | [21 empty] | 30 | 30 | 30 | 26 | 26 | 128000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 65 |  | 67 | 67 | 67 | 67 | 68 | 67 | 69 | 1161312
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 40 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 66 | 71 | 73 | 71 | 68 | 71 | 72 |  | 73 | 74 | 74 | 74 | 73 | 73 | 73 | 1420800
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 45 | [11 empty] | 1460000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 164 | 164 | 164 | 164 | 163 | 165 | 165 | 163 | 163 | 163 | 162 | 163 | 157 | 156 | 156 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 143 | 144 | 144 | 3785990
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 432000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [6 empty] | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 153900
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 8 | 2 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 168000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 31 | 31 | 31 | 34 | 31 | 34 | 49 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 939000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [19 empty] | 56352
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 295 | 290 | 300 | 305 | 300 | 300 | 300 | 280 | 310 | 310 | 290 | 290 | 310 | 290 | 300 | 315 |  | 290 | 320 | 280 | 305 | 310 | 280 | 290 | 7454700
| Bibiyana South 400 MW | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 127 | 121 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3105700
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 |  |  | 257150
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 9 | 22 | 25 | 25 | 25 | 21 |  | 21 | 21 | 17 | 17 | 16 | 12 | 12 | 220560
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 401136
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 489996
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 17 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 483192
63 | Impoprt (Tripura) | 76 | 74 | 72 | 72 | 72 | 72 | 68 | 80 | 86 | 84 | 86 | 84 | 80 | 88 | 88 | 88 | 100 | 112 |  | 108 | 106 | 106 | 100 | 98 | 90 | 86 | 2082240
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 13 | 5 | 2 | 4 | 4 | 12 | 5 | 4 | 8 | 11 | 11 |  | 20 | 26 | 10 | 27 | 38 | 40 | 41 | 444000
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 404136
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 0 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175860
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820600
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 496780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | [5 empty] | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 28 | 28 | 28 | 28 | 28 | 26 | 29 | 23 | 23 | 23 | 23 | 14 | 21 | 21 | 22 | 22 | 8 |  | 23 | 28 | 28 | 29 | 29 | 29 | 28 | 572580
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 630300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 837700
73 | Ghorashal 108MW PP (Regent) | 94 | 94 | 94 | 94 | 97 | 97 | 97 | 106 | 110 | 110 | 106 | 104 | 106 | 106 | 103 | 103 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2407681
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW |  |  |  |  | 0 | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 26 | 26 | 26 | 26 |  | 55 | 55 | 55 | 55 | 55 | 25 | 25 | 684600
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 0 | 0 | 11 | 36 | 70 | 72 | 72 | 72 | 72 | 72 | 72 | 35 | 35 | 35 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 47 | 1380960
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 1 | 30 |  | 100 | 50 | 50 | 50 |  |  |  | 247680
78 | Gazipur 52 MW PP | [16 empty] | 2 |  |  | 12 | 8 | 8 |  |  |  |  | 36660
79 | Kodda 150MW PP | [16 empty] | 16 | 115 |  | 115 | 100 | 100 | 84 | 48 | 16 |  | 478080
80 | Jamalpur 95 MW PP(Powerpac) | [9 empty] | 12 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 45 | 58 | 58 | 58 |  |  |  | 505920
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 8 |  | 8 | [6 empty] | 19046
| Gazipur 100 MW PP | [16 empty] | 5 | 32 |  | 90 | 90 | 90 | 50 |  |  |  | 322968
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25200
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 43 | 1289304
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [13 empty] | 3 | 15 | 15 | 15 | 38 |  | 52 | 80 | 70 | 72 | 30 | 15 | 0 | 387744
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) |  |  |  |  | 0 | 3 | 10 | 38 | 40 | 31 | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 67 |  | 86 | 86 | 86 | 86 | 86 | 70 | 50 | 1025839
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 18 |  | 70 | 50 | 40 | 7 |  |  |  | 149760
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 17 | 28 | 34 | 34 | 34 | 44 | 66 | 34 | 17 | 17 | 17 | 48 |  | 104 | 104 | 104 | 104 | 104 | 90 | 70 | 1026240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1210176
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1206074
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 7 | 7 |  | 16 | 16 | 16 | 16 | 16 |  |  | 85824
95 | Patenga 50MW PP (Baraka) |  |  |  |  | 0 | 1 | 18 | 18 | 19 | 19 | 19 | 22 | 43 | 46 | 47 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 699840
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 13 |  | 30 | 31 | 32 |  |  |  |  | 85440
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 13 |  | 15 | 15 | 15 | 15 |  |  |  | 69842
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 35 |  | 35 | 17 | 17 | 17 |  |  |  | 115182
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 9000
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 35 | 17 | 17 | 17 |  |  |  | 121680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 35 | 8 | 8 | 8 | 19 | 38 | 65 | 108 | 167 | 160 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 175 | 195 | 195 | 195 | 170 | 140 | 140 | 2829600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 30 | 38 | 80 | 80 | 80 | 77 | 80 | 83 |  | 126 | 128 | 126 | 123 | 55 |  |  | 998500
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 20 | 38 | 50 | 20 | 20 | 20 | 20 | 64 |  | 100 | 100 | 100 | 100 | 60 | 20 | 20 | 683520
116 | Chandpur 200MW (Desh energy) | 17 | 0 |  | 0 | 7 | 20 | 50 | 50 | 50 | 50 | 50 | 58 | 68 | 68 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1057440
117 | Ashuganj 150MW PP (Midland) | 60 | 10 | 0 |  | 0 | 3 | 48 | 73 | 100 | 70 | 70 | 92 | 100 | 100 | 100 | 100 | 100 | 110 |  | 132 | 149 | 143 | 142 | 142 | 142 | 142 | 2100945
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [16 empty] | 1 | 8 |  | 8 | [6 empty] | 20400
| Anwara 300 MW PP (United) | 88 | 88 | 51 | 51 | 51 | 101 | 142 | 142 | 155 | 160 | 180 | 215 | 215 | 181 | 197 | 197 | 198 | 235 |  | 268 | 268 | 268 | 271 | 271 | 198 | 197 | 4109891
| Juldah unit-2 (Acorn) | 100 | 50 | 30 | 30 | 30 | 90 | 100 | 100 | 100 | 50 | 50 | 90 | 90 | 100 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1878720
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4072 | 3891 | 3719 | 3681 | 3655 | 3878 | 4173 | 4275 | 4442 | 4266 | 4312 | 4480 | 4693 | 4578 | 4507 | 4437 | 4716 | 5620 |  | 6154 | 6128 | 6042 | 5819 | 5402 | 4989 | 4731 | 112340134
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | 0 |  |  | 0 | 16 | 16 | 76 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 115 | 115 | 115 | 115 | 99 | 83 | 1783680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 0 | [10 empty] | 3 | 4 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 36960
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 17 | 53 | 53 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 70 |  | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 826080
130
131
132 | United Payra Power Ltd. | 55 | 55 | 55 | 35 | 28 | 35 | 18 | 18 | 17 | 12 | 12 | 31 | 31 | 32 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 931200
133 | Bhola Nutan Biddut BD LTD (GAS) | 55 | 55 | 55 | 56 | 57 | 34 | 34 | 54 | 37 | 23 | 23 | 33 | 19 | 32 | 29 | 56 | 56 | 43 |  | 47 | 42 | 42 | 41 | 41 | 57 | 57 | 1140380
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 23 | 22 | 22 | 22 | 22 | 21 |  | 21 | 21 | 22 | 21 | 22 | 21 | 21 | 547023
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 24 | 21 | 20 | 18 | 17 | 19 | 17 | 16 | 14 | 14 | 15 | 12 | 13 | 13 | 19 | 19 | 17 | 26 |  | 27 | 27 | 28 | 28 | 27 | 25 | 25 | 473900
141 | Noapara 100 MW PP (Bangla Trac) | [8 empty] | 40 | 40 | 40 | 40 | 40 | 40 | [12 empty] | 262080
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | [5 empty] | 24 | 8 | 8 |  |  |  |  | 301875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 426 | 427 | 426 | 427 | 427 | 426 | 426 | 567 | 567 | 662 | 662 | 662 | 662 | 662 | 663 | 663 | 662 | 709 |  | 710 | 709 | 709 | 710 | 710 | 710 | 615 | 14440000
147 | Bheramara 410 MW CCPP | 275 | 285 | 295 | 310 | 330 | 335 | 345 | 350 | 350 | 310 | 310 | 345 | 335 | 325 | 320 | 300 | 300 | 285 |  | 265 | 260 | 245 | 230 | 220 | 210 | 210 | 7366464
148 | Payra 1320 MW | 400 | 400 | 370 | 350 | 350 | 350 | 350 | 350 | 370 | 320 | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 380 |  | 480 | 500 | 500 | 500 | 500 | 500 | 480 | 9964700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3693100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 180 | 180 | 140 | 140 | 150 | 159 | 162 | 154 | 159 | 192 | 163 | 161 | 165 | 156 | 157 | 159 |  | 183 | 180 | 178 | 169 | 163 | 158 | 156 | 4200836
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 357 | 344 | 344 | 280 | 328 | 315 | 333 | 334 | 396 | 368 | 362 | 319 | 323 | 314 | 417 | 405 | 399 | 416 |  | 379 | 425 | 416 | 419 | 418 | 420 | 379 | 8875491
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 448560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | [10 empty] | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 101790
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 17 | 8 | 8 |  |  |  |  | 17760
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 59 | 59 | 59 | 68 | 93 |  | 93 | 93 | 94 | 94 | 44 |  |  | 999560
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 |  |  |  |  | 0 | 6 | 35 | 60 | 70 | 35 | 35 | 60 | 112 | 70 | 70 | 70 | 70 | 90 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 1493760
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 35 | 35 | 35 | 35 | 50 | 70 | 35 | 35 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 1079328
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 34 | 34 | 36 | 35 | 35 | 34 | 90 |  | 113 | 113 | 113 | 113 | 70 | 36 | 19 | 794880
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 0 | [9 empty] | 22022
178
178