## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-18 | Monday
|  |  | Date (day): | 2021-01-18 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11661.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12797 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-17 | 2021-01-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 211 | 200 | 180 | 180
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 300 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 333 | 341 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 242 | 250 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 89 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 75 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 72 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 37 |  | 18 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 49 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 35 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 16 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 64 | 130 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 99 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 71 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2050 | 2763 | 3368 | 3620 | 1074 | 1360
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 0 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 48 | 44 | 43 | 43 | 187 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 10 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 24 | 90 | 90 |  | 18 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 252 | 250 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 639 | 762 | 1099 | 1214 | 922 | 123
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 164 | 174 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 360 | 360
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 3 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 73 | 75 | 75 | 75 |  | 75 | Engine
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maintenance
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 34 | 48 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 76 | 102 | 134 | 146
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52 |  | 0
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 18 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 46 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 999 | 1138 | 1782 | 2046 | 680 | 238
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 86 | 87 | 105 | 105 | 97 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 91 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 190 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 65 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 19 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 394 | 482 | 610.6 | 559 | 97 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 20 | 20 |  | 50
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 130 | 163 | 163
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 8 | 8 | 8
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 20 | 5 | 5
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 20 | 40 | 40
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 70 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 150 | 160 | 160 |  | 71 | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 270 | 266 | 270 | 270 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 985 | 1025 | 1268 | 1268 | 0 | 884
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 726 | 868 | 741 | 885
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 7 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 370 | 0 | 0 |  | 410 | Under maint.
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 90 | 90 |  | 15 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1278 | 1474 | 1241 | 1671 | 0 | 483
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 26 | 24 | 28 |  | 5 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 61 | 80 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 440 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 32 | 45 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 564 | 607 | 879 | 889 | 0 | 199
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 28 | 28 |  | 22 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 369 | 285 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 105 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 622 | 724 | 1143 | 1267 | 821 | 22
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 107 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 266 | 257 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7797 | 9232 | 11661.6 | 12797 | 3718 | 3519
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7446.5066 | 8817 | 11137.3838 | 12221.7449
| A. |  | 2021-01-17 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 9232 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5531 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9232 | MW
| 3 | Day peak Generation : |  |  | 7797 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8817 | MW
| 4 | Evening peak Generation : |  |  | 9232 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 180.2646 | MKWHr | By Solar | 0.31249 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 98.2012 | MKWHr |  | By Oil: | 47.5 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.5398 | MKWHr |  | By Hydro: | 1.0927 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3718 | MW | Dhaka | 3102 | 3102 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3519 | MW | Chittagong | 1002 | 1002 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7237 | MW | Khulna | 986 | 986 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 747.2 | MMCFD |  |  | Rajshahi | 968 | 968 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 100418073.776 | ii) Oil : | Taka | 350228316.01 | Comilla | 751 | 751 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 67591488 | Total | Taka | 518237877.786 | Mymensingh | 780 | 780 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.055 | MKWHr. | Sylhet | 334 | 334 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 76 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 9 | MW at | 20:00 | hrs | Rangpur | 657 | 657 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 23.2° C |  |  | Total | 8817 | 8817 |  | 0
| B. |  | 2021-01-18 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 26.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12797 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7900 | MW
| 4 | Reserve(Generation end) |  |  |  | 3297 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 185.4976 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5746 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6611 | MKWHr. | ii) HVDC Flow at Peak Time |  | 868 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9574 | MKWHr. | iii) Maximum HVDC Flow : |  | 869 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.11 |  | (b) Today: | 97.03 |  | (c) Rule Curve: |  | 99.77
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 280 | 12 | 0 | 331 | 253 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 15 | 36 | 0 | 0 | 0 | 260 | 260 | 160 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 15 | 80 | 110 | 8 | 22 | 0 | 20 | 43 | 8 | 5 | 110 | 0 | 33 | 73 | 0 | 150 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 30 | 0 | 0 | 85 | 0 | 27 | 0 | 0 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 234 | 54 | 0 | 0 | 46 | 100 | 270 | 52 | 0 | 54 | 0 | 100 |  | 445 | 0 | 310 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 333 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 370 | 37 | 0 | 17 |  | 4413 | 1976 | 6389 | 2795 | 445 | 1304 | 1172 | 520 | 47 | 26 | 80 | 0 | 0 | 97.14
2:00 | 0 | 0 | 213 | 0 | 280 | 12 | 0 | 338 | 263 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 36 | 0 | 0 | 0 | 260 | 260 | 164 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 15 | 76 | 110 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 110 | 0 | 34 | 73 | 0 | 135 | 0 | 0 | 9 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 73 | 0 | 0 | 0 | 0 | 0 | 234 | 54 | 0 | 0 | 46 | 100 | 270 | 0 | 0 | 54 | 0 | 100 |  | 444 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 331 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 370 | 37 | 0 | 17 |  | 4205 | 1857 | 6062 | 2791 | 444 | 1326 | 859 | 519 | 47 | 0 | 76 | 0 | 0 | 97.13
3:00 | 0 | 0 | 213 | 0 | 280 | 12 | 0 | 342 | 293 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 40 | 0 | 0 | 0 | 260 | 260 | 168 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 12 | 74 | 110 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 110 | 0 | 33 | 73 | 0 | 120 | 0 | 0 | 9 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 26 | 100 | 270 | 0 | 0 | 54 | 0 | 100 |  | 445 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 327 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 39 | 0 | 0 |  | 4084 | 1801 | 5885 | 2780 | 445 | 1356 | 665 | 518 | 47 | 0 | 74 | 0 | 0 | 97.13
4:00 | 0 | 0 | 213 | 0 | 280 | 12 | 0 | 333 | 313 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 0 | 0 | 260 | 260 | 167 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 12 | 72 | 110 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 110 | 0 | 34 | 73 | 0 | 120 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 73 | 0 | 0 | 0 | 0 | 0 | 180 | 54 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 54 | 0 | 100 |  | 445 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 296 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 37 | 0 | 0 |  | 4006 | 1763 | 5769 | 2771 | 445 | 1332 | 585 | 519 | 45 | 0 | 72 | 0 | 0 | 97.12
5:00 | 0 | 0 | 214 | 0 | 280 | 12 | 0 | 351 | 313 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 12 | 72 | 110 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 110 | 0 | 34 | 43 | 0 | 120 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 143 | 54 | 0 | 0 | 0 | 30 | 270 | 0 | 0 | 54 | 0 | 0 |  | 444 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 341 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 |  | 3760 | 1771 | 5531 | 2670 | 444 | 1337 | 464 | 499 | 45 | 0 | 72 | 0 | 0 | 97.12
6:00 | 0 | 0 | 215 | 0 | 280 | 12 | 0 | 362 | 313 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 18 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 12 | 72 | 111 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 140 | 0 | 33 | 40 | 0 | 120 | 0 | 0 | 9 | 320 | 8 | 11 | 0 | 2 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 141 | 54 | 0 | 0 | 0 | 30 | 270 | 2 | 0 | 54 | 0 | 0 |  | 531 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 410 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 350 | 38 | 0 | 0 |  | 3864 | 1995 | 5859 | 2714 | 531 | 1466 | 532 | 499 | 45 | 0 | 72 | 0 | 0 | 97.11
7:00 | 0 | 0 | 213 | 0 | 280 | 12 | 0 | 363 | 282 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 18 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 28 | 12 | 70 | 110 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 140 | 0 | 34 | 67 | 0 | 120 | 0 | 0 | 9 | 315 | 8 | 11 | 0 | 25 | 0 | 0 | 80 | 0 | 0 | 1 | 40 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 193 | 54 | 0 | 0 | 0 | 100 | 270 | 22 | 0 | 54 | 0 | 0 |  | 633 | 0 | 315 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 377 | 17 | 0 | 89 | 0 | 34 | 0 | 0 | 35 | 380 | 38 | 0 | 0 |  | 4123 | 2209 | 6332 | 2664 | 633 | 1423 | 968 | 530 | 43 | 0 | 70 | 1 | 0 | 97.11
8:00 | 0 | 0 | 213 | 0 | 300 | 12 | 0 | 335 | 261 |  | 0 | 0 | 0 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 25 | 10 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 12 | 64 | 111 | 0 | 22 | 0 | 20 | 43 | 8 | 5 | 140 | 0 | 33 | 67 | 0 | 120 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 120 | 0 | 0 | 141 | 0 | 14 | 4 | 10 | 17 | 74 | 0 | 0 | 0 | 0 | 1 | 210 | 54 | 0 | 0 | 0 | 100 | 270 | 70 | 2 | 54 | 0 | 0 |  | 727 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 416 | 17 | 0 | 113 | 0 | 64 | 0 | 0 | 90 | 420 | 37 | 0 | 0 |  | 4329 | 2524 | 6853 | 2665 | 727 | 1389 | 1387 | 570 | 44 | 0 | 64 | 7 | 0 | 97.1
9:00 | 0 | 0 | 213 | 0 | 300 | 12 | 0 | 356 | 234 |  | 0 | 0 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 86 | 0 | 0 | 0 | 35 | 17 | 34 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 22 | 13 | 4 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 10 | 70 | 110 | 48 | 22 | 0 | 20 | 43 | 37 | 20 | 140 | 0 | 33 | 65 | 0 | 90 | 0 | 0 | 9 | 310 | 8 | 0 | 0 | 175 | 0 | 0 | 194 | 0 | 74 | 9 | 70 | 27 | 75 | 0 | 21 | 0 | 0 | 2 | 213 | 54 | 0 | 0 | 0 | 100 | 270 | 70 | 6 | 54 | 0 | 0 |  | 726 | 0 | 305 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 385 | 53 | 0 | 113 | 0 | 106 | 0 | 1 | 113 | 520 | 35 | 0 | 0 |  | 4844 | 2726 | 7570 | 2654 | 726 | 1413 | 1974 | 670 | 45 | 0 | 70 | 18 | 0 | 97.1
10:00 | 0 | 0 | 213 | 0 | 280 | 12 | 0 | 355 | 224 |  | 0 | 0 | 0 | 24 | 46 | 15 | 0 | 0 | 0 | 24 | 50 | 20 | 76 | 0 | 0 | 0 | 35 | 17 | 35 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 3 | 0 | 0 | 0 | 260 | 260 | 164 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 10 | 74 | 101 | 64 | 22 | 0 | 0 | 43 | 44 | 50 | 140 | 0 | 32 | 65 | 0 | 20 | 0 | 0 | 9 | 310 | 8 | 0 | 0 | 240 | 0 | 0 | 200 | 0 | 92 | 13 | 70 | 34 | 75 | 0 | 35 | 0 | 0 | 3 | 213 | 54 | 0 | 0 | 0 | 100 | 270 | 71 | 10 | 54 | 0 | 0 |  | 726 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 420 | 53 | 0 | 113 | 0 | 107 | 0 | 1 | 113 | 480 | 24 | 0 | 0 |  | 4982 | 2723 | 7705 | 2523 | 726 | 1463 | 2195 | 630 | 47 | 20 | 74 | 27 | 0 | 97.09
11:00 | 0 | 0 | 212 | 0 | 250 | 12 | 0 | 347 | 232 |  | 0 | 0 | 0 | 24 | 48 | 18 | 0 | 0 | 0 | 30 | 50 | 48 | 75 | 0 | 0 | 0 | 35 | 17 | 36 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 2 | 0 | 0 | 0 | 260 | 260 | 164 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 80 | 99 | 32 | 22 | 0 | 0 | 43 | 45 | 50 | 140 | 0 | 32 | 67 | 0 | 20 | 0 | 0 | 7 | 300 | 8 | 8 | 0 | 262 | 0 | 0 | 190 | 0 | 90 | 15 | 100 | 34 | 75 | 0 | 16 | 0 | 0 | 4 | 250 | 54 | 0 | 0 | 0 | 100 | 270 | 71 | 19 | 54 | 0 | 0 |  | 727 | 0 | 325 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 359 | 53 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 450 | 18 | 0 | 0 |  | 4995 | 2647 | 7642 | 2475 | 727 | 1388 | 2238 | 600 | 47 | 48 | 80 | 39 | 0 | 97.09
12:00 | 0 | 0 | 211 | 0 | 250 | 12 | 0 | 333 | 242 |  | 0 | 0 | 0 | 24 | 48 | 30 | 0 | 0 | 0 | 40 | 50 | 48 | 75 | 0 | 0 | 0 | 35 | 17 | 49 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 2 | 0 | 0 | 0 | 260 | 260 | 164 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 76 | 86 | 32 | 22 | 1 | 0 | 43 | 45 | 50 | 140 | 0 | 31 | 70 | 0 | 20 | 0 | 0 | 7 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 64 | 16 | 100 | 34 | 73 | 0 | 16 | 0 | 0 | 4 | 252 | 54 | 0 | 0 | 0 | 100 | 270 | 71 | 35 | 54 | 0 | 0 |  | 726 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 369 | 53 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 450 | 32 | 0 | 0 |  | 5067 | 2730 | 7797 | 2517 | 726 | 1422 | 2301 | 600 | 48 | 48 | 76 | 59 | 0 | 97.09
13:00 | 0 | 0 | 203 | 0 | 280 | 12 | 0 | 343 | 240 |  | 0 | 0 | 0 | 30 | 48 | 30 | 0 | 0 | 0 | 20 | 48 | 64 | 77 | 0 | 0 | 0 | 45 | 35 | 55 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 7 | 0 | 50 | 13 | 3 | 0 | 0 | 0 | 260 | 260 | 153 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 30 | 10 | 80 | 87 | 32 | 22 | 1 | 0 | 43 | 47 | 47 | 140 | 0 | 32 | 70 | 0 | 74 | 0 | 0 | 7 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 28 | 16 | 100 | 43 | 75 | 0 | 8 | 0 | 0 | 4 | 287 | 54 | 0 | 0 | 3 | 100 | 245 | 71 | 33 | 54 | 0 | 0 |  | 727 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 315 | 70 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 450 | 38 | 0 | 0 |  | 5193 | 2723 | 7916 | 2597 | 727 | 1383 | 2359 | 600 | 48 | 64 | 80 | 58 | 7916 | 97.08
14:00 | 0 | 0 | 215 | 0 | 300 | 12 | 0 | 335 | 239 |  | 0 | 0 | 0 | 50 | 47 | 30 | 0 | 0 | 0 | 50 | 48 | 64 | 72 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | 10 | 0 | 50 | 13 | 3 | 0 | 0 | 0 | 260 | 260 | 153 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 30 | 13 | 84 | 84 | 32 | 20 | 1 | 0 | 43 | 47 | 50 | 140 | 0 | 20 | 70 | 0 | 78 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 270 | 0 | 0 | 180 | 0 | 16 | 13 | 60 | 50 | 75 | 0 | 8 | 0 | 0 | 3 | 287 | 54 | 0 | 0 | 25 | 70 | 271 | 84 | 28 | 54 | 0 | 0 |  | 726 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 292 | 70 | 0 | 70 | 0 | 72 | 0 | 4 | 35 | 400 | 18 | 0 | 0 |  | 5185 | 2466 | 7651 | 2637 | 726 | 1333 | 2160 | 550 | 48 | 64 | 84 | 49 | 0 | 97.08
15:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 338 | 244 |  | 0 | 0 | 0 | 50 | 48 | 30 | 0 | 0 | 0 | 24 | 58 | 64 | 74 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 10 | 25 | 16 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 3 | 0 | 0 | 0 | 260 | 260 | 163 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 76 | 71 | 32 | 22 | 1 | 0 | 43 | 8 | 5 | 140 | 0 | 20 | 69 | 0 | 78 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 268 | 0 | 0 | 187 | 0 | 16 | 10 | 60 | 34 | 75 | 0 | 8 | 0 | 0 | 2 | 287 | 54 | 0 | 0 | 25 | 70 | 270 | 90 | 19 | 54 | 0 | 0 |  | 726 | 0 | 350 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 334 | 70 | 0 | 70 | 0 | 70 | 0 | 3 | 35 | 370 | 17 | 0 | 0 |  | 5045 | 2420 | 7465 | 2594 | 726 | 1314 | 2088 | 520 | 48 | 64 | 76 | 35 | 0 | 97.08
16:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 345 | 244 |  | 0 | 0 | 0 | 50 | 48 | 15 | 0 | 0 | 0 | 24 | 24 | 64 | 82 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 25 | 10 | 25 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 50 | 13 | 7 | 0 | 0 | 0 | 260 | 260 | 172 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 74 | 71 | 48 | 20 | 0 | 0 | 43 | 8 | 5 | 140 | 0 | 20 | 69 | 0 | 77 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 248 | 0 | 0 | 200 | 0 | 16 | 5 | 30 | 34 | 75 | 0 | 0 | 0 | 0 | 1 | 287 | 54 | 0 | 0 | 25 | 70 | 270 | 90 | 9 | 54 | 0 | 0 |  | 726 | 0 | 300 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 399 | 35 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 370 | 55 | 0 | 0 |  | 4923 | 2330 | 7253 | 2558 | 726 | 1378 | 1868 | 520 | 48 | 64 | 74 | 17 | 0 | 97.07
17:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 359 | 248 |  | 0 | 0 | 0 | 60 | 54 | 15 | 0 | 0 | 0 | 40 | 32 | 100 | 85 | 0 | 0 | 0 | 54 | 55 | 25 | 22 | 25 | 10 | 25 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 13 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 16 | 94 | 86 | 48 | 20 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 20 | 20 | 0 | 96 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 247 | 0 | 0 | 200 | 0 | 35 | 1 | 60 | 34 | 75 | 0 | 0 | 7 | 0 | 0 | 236 | 54 | 0 | 17 | 42 | 100 | 270 | 90 | 2 | 54 | 0 | 0 |  | 726 | 0 | 250 | 0 | 110 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 341 | 35 | 0 | 45 | 0 | 70 | 0 | 1 | 50 | 350 | 20 | 0 | 0 |  | 5093 | 2234 | 7327 | 2556 | 726 | 1208 | 2091 | 500 | 46 | 102 | 94 | 4 | 0 | 97.07
18:00 | 0 | 0 | 201 | 0 | 280 | 12 | 0 | 301 | 253 |  | 0 | 0 | 0 | 75 | 88 | 15 | 0 | 0 | 0 | 80 | 64 | 100 | 85 | 0 | 0 | 0 | 54 | 55 | 50 | 22 | 25 | 10 | 25 | 17 | 13 | 0 | 45 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 |  | 14 | 0 | 85 | 10 | 25 | 40 | 13 | 15 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 102 | 87 | 91 | 20 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 50 | 0 | 126 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 300 | 34 | 0 | 200 | 0 | 120 | 0 | 100 | 17 | 75 | 0 | 24 | 53 | 0 | 0 | 203 | 54 | 0 | 17 | 46 | 100 | 270 | 90 | 0 | 131 | 0 | 0 |  | 869 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 105 | 24 | 16 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1 | 0 | 0 | 386 | 35 | 0 | 95 | 0 | 106 | 0 | 0 | 100 | 320 | 21 | 0 | 0 |  | 5750 | 2886 | 8636 | 2565 | 869 | 1329 | 2909 | 470 | 45 | 347 | 102 | 0 | 0 | 97.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 341 | 250 |  | 0 | 0 | 0 | 89 | 100 | 15 | 0 | 0 | 0 | 100 | 72 | 149 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 10 | 25 | 25 | 16 | 0 | 44 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 85 | 0 | 24 | 50 | 15 | 15 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 16 | 19 | 8 | 33 | 18 | 102 | 87 | 91 | 20 | 0 | 0 | 43 | 8 | 20 | 130 | 0 | 20 | 70 | 0 | 150 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 48 | 75 | 0 | 65 | 99 | 0 | 0 | 250 | 54 | 0 | 17 | 46 | 100 | 266 | 90 | 0 | 144 | 0 | 0 |  | 868 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 7 | 40 | 0 | 26 | 16 | 0 | 0 | 0 | 50 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 285 | 90 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 440 | 45 | 0 | 0 |  | 6170 | 3062 | 9232 | 2724 | 868 | 1321 | 3187 | 590 | 44 | 396 | 102 | 0 | 0 | 97.06
19:30 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 334 | 250 |  | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 48 | 149 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 86 | 0 | 0 | 50 | 15 | 20 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 104 | 88 | 91 | 20 | 0 | 0 | 43 | 25 | 30 | 130 | 0 | 20 | 70 | 0 | 161 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 50 | 75 | 0 | 25 | 105 | 0 | 0 | 253 | 54 | 0 | 0 | 46 | 100 | 270 | 90 | 0 | 126 | 0 | 0 |  | 868 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 27 | 32 | 0 | 0 | 0 | 50 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 338 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 55 | 0 | 0 |  | 6055 | 3170 | 9225 | 2755 | 868 | 1439 | 2968 | 650 | 44 | 397 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 333 | 250 |  | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 48 | 149 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 0 | 0 | 50 | 15 | 22 | 0 | 0 | 0 | 260 | 260 | 169 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 102 | 87 | 91 | 22 | 0 | 0 | 43 | 34 | 30 | 130 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 275 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 143 | 0 | 50 | 51 | 75 | 0 | 8 | 105 | 0 | 0 | 252 | 54 | 0 | 0 | 46 | 100 | 270 | 90 | 0 | 126 | 0 | 0 |  | 869 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 50 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 296 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 56 | 0 | 0 |  | 6022 | 3149 | 9171 | 2752 | 869 | 1377 | 2963 | 650 | 45 | 413 | 102 | 0 | 0 | 97.06
21:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 334 | 248 |  | 0 | 0 | 0 | 71 | 100 | 0 | 0 | 0 | 0 | 40 | 7 | 130 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 0 | 0 | 46 | 15 | 30 | 0 | 0 | 0 | 260 | 260 | 159 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 100 | 90 | 91 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 69 | 75 | 0 | 0 | 105 | 0 | 0 | 252 | 54 | 0 | 0 | 46 | 100 | 270 | 90 | 0 | 126 | 0 | 0 |  | 869 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 314 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 56 | 0 | 0 |  | 5812 | 3093 | 8905 | 2731 | 869 | 1365 | 2817 | 650 | 46 | 327 | 100 | 0 | 0 | 97.06
22:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 332 | 228 |  | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 84 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 44 | 15 | 36 | 0 | 0 | 0 | 260 | 260 | 160 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 96 | 93 | 91 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 147 | 0 | 20 | 68 | 75 | 0 | 0 | 0 | 0 | 0 | 271 | 54 | 0 | 0 | 8 | 100 | 270 | 90 | 0 | 126 | 0 | 0 |  | 869 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 316 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 57 | 0 | 0 |  | 5279 | 3010 | 8289 | 2738 | 869 | 1344 | 2337 | 630 | 46 | 229 | 96 | 0 | 0 | 97.05
23:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 332 | 228 |  | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 7 | 0 | 0 | 25 | 15 | 42 | 0 | 0 | 0 | 260 | 260 | 160 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 86 | 109 | 40 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 93 | 0 | 0 | 64 | 75 | 0 | 0 | 0 | 0 | 0 | 269 | 54 | 0 | 0 | 8 | 100 | 270 | 90 | 0 | 126 | 0 | 0 |  | 869 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 334 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 460 | 58 | 0 | 0 |  | 4943 | 2815 | 7758 | 2754 | 869 | 1338 | 1944 | 609 | 47 | 111 | 86 | 0 | 0 | 97.05
24:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 340 | 228 |  | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 15 | 34 | 0 | 0 | 0 | 260 | 260 | 172 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 148 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 68 | 76 | 0 | 0 | 0 | 0 | 0 | 234 | 54 | 0 | 0 | 8 | 100 | 270 | 80 | 0 | 162 | 0 | 0 |  | 729 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 343 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 113 | 460 | 57 | 0 | 0 |  | 4470 | 2561 | 7031 | 2767 | 729 | 1329 | 1471 | 609 | 47 | 7 | 72 | 0 | 0 | 97.05
KWH | 0 | 0 | 4981000 | 0 | 6830236 | 290636 | 0 | 8299520 | 6094000 |  | 0 | 0 | 0 | 723840 | 1175400 | 229009 | 0 | 0 | 0 | 655680 | 638208 | 1173120 | 1539039 | 0 | 0 | 0 | 502200 | 567754 | 682669 | 409860 | 600000 | 421920 | 613900 | 591100 | 32904 | 0 | 1092655 | 0 | 0 | 0 | 52266 | 0 | 0 | 0 | 0 |  | 285360 | 0 | 418162 | 36000 | 49920 | 813600 | 378144 | 575040 | 0 | 0 | 0 | 6569700 | 6387000 | 4013000 | 217454 | 0 | 65016 | 0 | 0 | 1251643 | 0 | 0 | 27643 | 449496 | 152100 | 694400 | 391680 | 1957440 | 2282440 | 901440 | 501300 | 5850 | 194000 | 1019040 | 442800 | 505368 | 3259309 | 0 | 658944 | 1574400 | 0 | 2578110 | 0 | 0 | 205020 | 7389000 | 189978 | 239000 | 0 | 4604180 | 31575 | 0 | 3640800 | 0 | 1295710 | 102060 | 1018560 | 871680 | 1798181 | 0 | 261600 | 432336 | 0 | 22887 | 5630400 | 1301769 | 0 | 44460 | 554400 | 2191680 | 6469900 | 1511040 | 162210 | 1913760 | 0 | 453000 |  | 16661090 | 0 | 8090496 | 0 | 1932480 | 0 | 0 | 0 | 0 | 47912 | 308250 | 0 | 515200 | 138432 | 0 | 0 | 0 | 135472 | 0 | 592896 | 75370 | 23016 | 0 | 30720 | 0 | 515760 | 0 | 167878 | 0 | 0 | 3652200 | 0 | 0 | 0 | 0 | 0 | 0 | 1259296 | 22080 | 0 | 0 | 8468200 | 1110240 | 0 | 2166528 | 0 | 1558080 | 0 | 19479 | 1707744 | 10887600 | 945927 | 0 | 44400 |  | 119187901 | 61076746 | 180264647 | 64692158 | 16661090 | 33509053 | 45132403 | 14539800 | 1092655 | 2367562 | 1957440 | 312486 | 0
Fuel Cost | 0 | 0 | 7272260 | 0 | 7581561.96 | 383639.52 | 0 | 8382515.2 | 6276820 |  | 0 | 0 | 0 | 5493945.6 | 8098506 | 1937416.14 | 0 | 0 | 0 | 4937270.4 | 5820456.96 | 11543500.8 | 14189939.58 | 0 | 0 | 0 | 3666060 | 4388738.42 | 6731116.34 | 307395 | 450000 | 0 | 0 | 0 | 318181.68 | 0 | 295016.85 | 0 | 0 | 0 | 485551.14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4056171.4 | 343800 | 434304 | 6443712 | 476461.44 | 1707868.8 | 0 | 0 | 0 | 4861578 | 6387000 | 3691960 | 280515.66 | 0 | 73468.08 | 0 | 0 | 2140309.53 | 0 | 0 | 263990.65 | 570859.92 | 114075 | 1215200 | 293760 | 14680800 | 2419386.4 | 8185075.2 | 636651 | 93249 | 318160 | 1630464 | 788184 | 788374.08 | 3715612.26 | 0 | 1298119.68 | 3007104 | 0 | 4460130.3 | 0 | 0 | 418240.8 | 7462890 | 142483.5 | 181640 | 0 | 34807600.8 | 536143.5 | 0 | 18932160 | 0 | 12749786.4 | 1193081.4 | 8301264 | 9457728 | 12677176.05 | 0 | 2385792 | 4085575.2 | 0 | 0 | 42565824 | 11338407.99 | 0 | 443710.8 | 4751208 | 14596588.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95967878.4 | 0 | 8495020.8 | 0 | 15189292.8 | 0 | 0 | 0 | 0 | 502117.76 | 3211965 | 0 | 798560 | 1351096.32 | 0 | 0 | 0 | 1333044.48 | 0 | 5247129.6 | 580349 | 311176.32 | 0 | 297676.8 | 0 | 990259.2 | 0 | 127083.646 | 0 | 0 | 19794924 | 0 | 0 | 0 | 0 | 0 | 0 | 1888944 | 375580.8 | 0 | 0 | 8383518 | 11590905.6 | 0 | 20560350.72 | 0 | 12090700.8 | 0 | 215242.95 | 12620228.16 | 47796564 | 0 | 0 | 0 |  | 360963537.23 | 269719609.156 | 630683146.386 | 61387233.926 | 95967878.4 | 39030839.85 | 327546351.97 | 67591488 | 295016.85 | 22681964.04 | 14680800 | 1501573.35 | 0
Yesterday Day Peak | 0 | 0 | 211 | 0 | 250 | 12 | 0 | 333 | 242 |  | 0 | 0 | 0 | 24 | 48 | 30 | 0 | 0 | 0 | 40 | 50 | 48 | 75 | 0 | 0 | 0 | 35 | 17 | 49 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 50 | 13 | 2 | 0 | 0 | 0 | 260 | 260 | 164 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 76 | 86 | 32 | 22 | 1 | 0 | 43 | 45 | 50 | 140 | 0 | 31 | 70 | 0 | 20 | 0 | 0 | 7 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 64 | 16 | 100 | 34 | 73 | 0 | 16 | 0 | 0 | 4 | 252 | 54 | 0 | 0 | 0 | 100 | 270 | 71 | 35 | 54 | 0 | 0 |  | 726 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 369 | 53 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 450 | 32 | 0 | 0 |  | 7797 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 341 | 250 | 0 | 0 | 0 | 0 | 89 | 100 | 15 | 0 | 0 | 0 | 100 | 72 | 149 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 10 | 25 | 25 | 16 | 0 | 44 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 85 | 0 | 24 | 50 | 15 | 15 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 16 | 19 | 8 | 33 | 18 | 102 | 87 | 91 | 20 | 0 | 0 | 43 | 8 | 20 | 130 | 0 | 20 | 70 | 0 | 150 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 48 | 75 | 0 | 65 | 99 | 0 | 0 | 250 | 54 | 0 | 17 | 46 | 100 | 266 | 90 | 0 | 144 | 0 | 0 |  | 868 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 7 | 40 | 0 | 26 | 16 | 0 | 0 | 0 | 50 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 285 | 90 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 440 | 45 | 0 | 0 |  | 9232 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 300 | 50 | 0 | 412 | 300 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 37 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 25 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 22 | 146 | 105 | 95 | 22 | 0 | 20 | 43 | 8 | 5 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 75 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 90 | 0 | 144 | 0 | 100 |  | 885 | 16 | 0 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 28 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 28 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 0
Forecast for Day | 0 | 0 | 180 | 0 | 300 | 50 | 0 | 412 | 300 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 10 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 134 | 105 | 95 | 22 | 1.6 | 20 | 43 | 8 | 5 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 75 | 0 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 90 | 50 | 144 | 0 | 100 |  | 741 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 28 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 0
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 280 | 12 | 0 | 350 | 273 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 22 | 3 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 |  | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 260 | 260 | 175 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 78 | 104 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 72 | 0 | 162 | 0 | 0 | 9 | 305 | 8 | 11 | 0 | 136 | 0 | 0 | 125 | 0 | 95 | 5 | 50 | 68 | 75 | 0 | 0 | 0 | 0 | 1 | 283 | 36 | 0 | 0 | 0 | 100 | 270 | 53 | 3 | 72 | 0 | 0 | 0 | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 338 | 70 | 0 | 89 | 0 | 98 | 0 | 1 | 75 | 440 | 26 | 0 | 0 | 0
199
| Minimum Generation |  | 5531 | 5:00
| Highest Generation |  | 9232 | 19:00
| Day Peak Generation |  | 7797 | 12:00
| Evening Peak Generation |  | 9232 | 19:00
| HVDC Max Flow |  | 869 | 18:00
| HVDC EvPeak Flow |  | 868 | 19:00
| Load factor L.F |  | 81.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7797 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5746 | MW
Evening Peak Generation : |  | 9232 | MW Hour : | 19:00 | Available Max Generation : |  | 12797 | MW
E.P. Demand (at gen end) : |  | 9232 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9232 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3297 | MW
Total Gen. (MKWH) : |  | 180.2646 | System Load Factor : | 81.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 9 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-18
Actual : | 97.03 | Ft.(MSL) , | Rule curve : | 99.77 | Ft.( MSL )
Gas Consumed : | Total = | 747.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 100418073.776
: |  | Coal : | 67591488 | Oil : | 350228316.01 | Total : | 518237877.786
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3385.6817 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1147.2428 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1027.1651 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 927.8724 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 838.6471 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 676.7482 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 383.65 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.3833 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 521.9167 |  |  | 0 | 0%
Total | 0 |  | 9083.3074 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-3,4,5
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,3,5
4) Shahjibazar 330 MW
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,3 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Khulshi-Madunaghat 132 kV Ckt-2 was under shut down from 08:49 to 13:29 for A/M.
b) Baraulia-AKSPL 132 kV Ckt was under shut down from 08:56 to 15:40 for Breaker maintenance work.
c) Juldah-Sikalbaha 132 kV Ckt was under shut down from 08:33 to 16:21 for A/M.
d) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 08:26 to 17:03 for A/M.
e) Mirpur 132/33 kV T2 Transformer was under shut down from 08:30 to 20:30 for A/M
f) Kulaura-Fenchuganj 132 kV Ckt-2 was under shut down from 09:11 to 17:07 for A/M.
g) Haripur-Madanganj 132 kV Ckt-2 was under shut down from 08:44 to 16:51 for C/M.
h) Ashuganj 230/132 kV OAT-12 Transformer was under shut down from 08:30 to 20:30 for A/M
i) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 09:18 to 17:18 for D/W.
j) Mymensingh-Jamalpur 132 kV Ckt-2 was under shut down from 10:34 to 15:36 for D/W.
k) Kaliakoir-Tangail 132 kV Ckt-2 was shut down at 09:13 for A/M.
l) Shahzadpur 132/33 kV T-2 transformer was under shut down from 10:10 to 14:51 for A/M.
m) Barishal(N)-Barishal(S) 132 kV Ckt-1 was under shut down from 08:13 to 16:29 for A/M.
n) Madaripur-Shariatpur 132 kV Ckt-2 was under shut down from 08:36 to 15:32 for A/M.
o) Kustia-Jhenaidah 132 kV Ckt-2 was under shut down from 08:17 to 18:33 for A/M.
p) Sirajganj132/33 kV T-4 transformer was under shut down from 11:28 to 12:22 for A/M.
q) Sirajganj132/33 kV T-2 transformer was under shut down from 09:56 to 10:16 for A/M.
r) Rajshahi 230/132 kV ATR-1 transformer was under shut down from 11:20 to 20:09 for D/W.
s) After maintenance work Ashuganj-Sirajganj 230 kV Ckt-1 was switched on at 09:47.
t) Kodda 33 kV Bus was under shut down from 11:50 to 13:56 for Emergency maintenance of Bus-DS |  |  |  |  | About 120 MW power interruption occurred under Kodda S/S area
by PBS. |  |  |  |  | from 11:50 to 13:56.
u) Sylhet 225 MW CCPP STG was synchronized at 12:30.
v) Aminbazar 132 kV Bus-2 under shut down from 10:50 16:28 for PT replacement work.
w) Rajendrapur 132/33 kV ATR transformer was under shut down from 13:44 to 14:35 for relay replacement work.
x) Maniknagar-Narinda 132 kV Ckt-2 was under shut down from 13:26 to 15:01 for CT maint. work .
y) Agargaon 230/132 kV T02 transformer was under shut down from 13:39 to 17:04 for A/M.
z) Rajshahi S/S-PDB Katakhali PP 132 kV Ckt was under shut down from 14:10 to 15:39 for Y-phase oil leakage
at Rajshahi end.
aa) Faridpur 132/33 kV T-1,T-2 transformers, 33 kV side tripped at 18:57 showing HVDC SPS and were |  |  |  |  | About 120 MW power interruption occurred under Kodda S/S area
switched on at 19:07. |  |  |  |  | from 18:57 to 19:07.
ab) Aminbazar-Manikganj 162 MW PP 132 kV Ckt-2 was switched on at 20:22.
ac) Bheramara CCPP ST was shut down at 06:42(18/01/2021) for air filter replacement work and GT
was shut down at 07:03.
ad) Hathazari 230 kV Bus-1 was shut down at 06:46(18/01/2021) for D/W.
ae) Hasnabad-Keraniganj 230 kV Ckt-2 tripped at 06:53(18/01/2021) from both ends showing Dist. Z1,2,3
L/O at Hasnabad and Gen. trip at Keraniganj end and was switched on at 07:37.
af) Aminbazar-Keraniganj 230 kV Ckt-2 tripped at 06:53(18/01/2021) from Keraniganj end showing Gen.
trip and was switched on at 07:30.
ag) Norail-Magura 132 kV Ckt-2 was shut down at 07:14(18/01/2021) for A/M.
ah) kochua 132/33 kV T-1 transformer was charged at 18:05 from 132 kV side and was charged at 18:58
from 33 kV side.
ai) kochua 132/33 kV T-2 transformer was charged at 18:10 from 132 kV side and was charged at 20:23
from 33 kV side.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4981000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6830236 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 290636 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 8299520 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 250 | 6094000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 89 | 723840 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1175400
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 229009 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1539039 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 409860
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 655680
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 638208 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 502200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1173120
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 567754
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 682669
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 1021920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 613900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 591100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 16 | 32904 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4604180
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 31575 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 1295710 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 99 | 432336
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1511040 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1913760
| Dhaka area Total |  |  |  | 6057 | 2763 | 46840596
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 52266
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 102060
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 813600
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 1092655 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 418162 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 36000 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1018560
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 378144 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 575040
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 49920 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22887
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 250 | 5630400 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1301769
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2191680
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 762 | 13683143
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 174 | 4013000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6569700 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6387000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 3 | 65016 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1251643
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 75 | 1798181 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 48 | 871680 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 449496
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 152100 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1957440
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 694400
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 27643 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 391680
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 44460 | High Voltage.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 554400 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1138 | 25445293
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 87 | 2282440 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 501300
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 901440 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5850
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3640800 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 65 | 261600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 162210
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 19 | 285360
| Mymensingh Area Total |  |  |  | 709 | 482 | 8041000
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 194000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1019040 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3259309 | Frequency Control
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 8 | 442800 | Gas shortage
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 20 | 505368 | Gas shortage
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 239000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 658944 | Gas shortage
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 70 | 1574400 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 453000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 2578110
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 189978 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7389000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 205020
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 266 | 6469900 | On test
| Sylhet Area Total |  |  |  | 1988 | 1025 | 25177869
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 868 | 16661090
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1932480 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 7 | 47912 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8090496 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 308250
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 22080 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1110240 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1474 | 28172548
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 138432 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 515200 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 80 | 1259296 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 440 | 10887600 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 45 | 945927 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 44400 | On test.
| Barisal Area Total |  |  |  | 1676 | 607 | 13790855
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 135472
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 75370 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 23016 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 285 | 8468200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 515760
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167878
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 30720 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 105 | 592896
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2166528
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1707744
| Rajshahi Area Total |  |  |  | 2183 | 724 | 13883584
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3652200
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1558080
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19479
| Rangpur Area Total |  |  |  | 605 | 257 | 5229759
| Total |  |  |  | 20748 | 9232 | 180264647
| Eastern Grid Total |  |  |  | 14000 | 6170 | 119187901
| Western Grid Total |  |  |  | 6748 | 3062 | 61076746
| National Grid Total |  |  |  | 20748 | 9232 | 180264647
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-17
| (a) ENTIRE EASTERN GRID : |  | 5969 | MW | (b) ENTIRE WESTERN GRID : |  | 2848 | MW
| i) Dhaka area |  | 3102 | MW | i) Khulna area |  | 986 | MW
| ii) Chittagong area |  | 1002 | MW | ii) Rajshahi area |  | 968 | MW
| iii) Comilla area |  | 751 | MW | iii) Barisal area |  | 237 | MW
| iv) Mymensingh area |  | 780 | MW | iv) Rangpur area |  | 657 | MW
| v) Sylhet area |  | 334 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8817 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 19:00 | Jamalpur | 92 | 18:30 | Benapol | 36 | 7:00
| Munsiganj | 82 | 20:00 | Sherpur | 11 | 18:00 | Jhenida | 84 | 18:30
| Sonargaon | 50 | 19:30 | Srimongal | 29 | 19:00 | Bottail | 96 | 18:30
| Shyampur | 170 | 10:00 | Shahjibazar | 88 | 18:30 | G.K Project | 36 | 18:00
| Bhulta | 157 | 20:00 | Fenchuganj | 27 | 18:00 | Faridpur | 140 | 19:30
| Madanganj | 53 | 1:00 | Kulawara | 28 | 18:00 | Madaripur | 66 | 20:00
| Shitalakhya | 96 | 17:00 | Sylhet | 80 | 19:00 | Sariatpur | 42 | 19:30
| Rahim steel | 18 | 13:00 | Chatak | 19 | 18:30 | Gopalganj | 59 | 19:00
| Matuail | 45 | 12:00 | Sunamganj | 29 | 20:00 | Bagerhat | 82 | 18:30
| Ghorasal | 67 | 18:30 | Biani Bazar | 38 | 18:30 | Mongla | 40 | 18:00
| Narsingdi | 128 | 20:00 | Comilla (S) | 106 | 18:30 | Satkhira | 72 | 18:30
| Haripur (SBU) | 91 | 10:00 | Comilla(N) | 79 | 19:00 | Gallamari | 22 | 13:00
| Ullon | 38 | 19:00 | Chandpur | 54 | 20:00 | Magura | 40 | 18:30
| Hasnabad | 130 | 19:30 | Feni | 76 | 18:30 | Norail | 24 | 18:30
| Magbazar | 65 | 14:00 | Chowmuhani | 120 | 18:00 | Chuadanga | 65 | 18:30
| Maniknagar | 62 | 13:00 | Ashuganj | 39 | 13:00 | Barisal(N) | 27 | 20:00
| Bangabhaban | 14 | 12:00 | Daudkandi | 92 | 20:00 | Barisal (S) | 76 | 21:00
| Narinda | 64 | 12:00 | B.Baria | 102 | 18:30 | Patuakhali | 70 | 21:00
| Dhanmondi | 91 | 13:00 | Ramganj | 74 | 19:30 | Bhandaria | 40 | 19:30
| Lalbag | 74 | 14:00 | Chaddagram | 32 | 14:00 | Borhan Uddin
| Madartek | 47 | 13:00 | PHP | 8 | 18:30 | Ishurdi | 46 | 19:00
| Dhaka University |  |  | Madunaghat | 45 | 19:00 | Ruppur Paromanobik | 2 | 19:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 63 | 0.75 | Natore | 91 | 0.77083
| Fatullah | 46 | 10:00 | Khulshi | 139 | 22:00 | Bogra | 121 | 19:30
| Mirpur | 72 | 18:00 | Halishahar | 91 | 18:00 | Noagaon | 84 | 18:30
| Kalyanpur | 69 | 18:00 | Baraulia | 134 | 8:00 | Rajshahi | 94 | 20:00
| Gulshan | 70 | 18:00 | Sikalbaha | 21 | 18:30 | Rajshahi New | 11 | 20:00
| Uttara | 57 | 18:00 | Dohazari | 58 | 19:30 | C.Nawabganj | 62 | 20:0
| Uttara New | 27 | 18:00 | Cox'sbazar | 79 | 19:00 | Amnura | 44 | 18:30
| Kamrangirchar | 67 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 64 | 19:00
| Savar | 122 | 18:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 78 | 19:00
| Bhasantec | 95 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 69 | 9:00
| Agargaon | 43 | 18:00 | Bakulia | 73 | 12:00 | Niyamatpur | 77 | 18:30
| Satmosjid | 56 | 0.54167 | Julda | 22 | 0.45833 | Joypurhat | 53 | 0.83333
| Tongi | 76 | 11:00 | TK chemical | 19.2 | 18:30 | Sherpur(Bogura) | 42 | 19:00
| Kabirpur | 181 | 16:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 19:00
| Basundhara | 89 | 13:00 | Shahmirpur | 18 | 18:00 | Bangura | 15 | 19:00
| Manikganj | 64 | 21:00 | Khagrachhari | 18 | 19:00 | Rangpur | 112 | 18:00
| Joydevpur | 128 | 18:30 | Matarbari | 26 | 19:00 | Lalmonirhat | 50 | 19:30
| New Tongi | 89 | 18:00 | Baroiar Hat | 26 | 18:00 | Saidpur | 92 | 19:00
| Kodda | 167 | 18:00 | Rangamati | 9 | 18:00 | Purbasadipur | 88 | 20:00
| Dhamrai | 50 | 9:00 | Abul Khair 230 | 148 | 16:00 | Thakurgaon | 63 | 20:00
| Rajendrapur | 80 | 15:00 | BSRM | 150 | 19:00 | Palashbari | 104 | 18:00
| Valuka | 88 | 18:00 | GPH Ispat | 88 | 4:00 | Barapukuria | 44 | 20:00
| Tangail | 137 | 20:"00 | Goalpara | 17 | 13:00 | Panchagar | 45 | 19:30
| Mymensing | 163 | 18:30 | Central s/s | 81 | 18:30 | Joldhaka | 31 | 18:30
| Kishorganj | 104 | 19:00 | Noapara | 57 | 18:30 | Kurigram | 45 | 19:00
| Netrokona | 127 | 22:00 | Jessore | 84 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 17:00 | 394 | 19:00 | Kaliakoir | 399 | 0.83333 | 388 | 0.66667
| Bheramara | 235 | 3:00 | 222 | 12:00 | Bhulta | 415 | 0.875 | 408 | 0.54167
| Ashuganj(N) | 393 | 20:00 | 382 | 10:00 | Gopalganj | 405 | 0.041667 | 386 | 0.33333
| Payra | 412 | 4:00 | 392 | 9:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 23:00 | 235 | 1:00 | Hathazari | 230 | 5:00 | 215 | 7:00
| Ishurdi | 242 | 4:00 | 233 | 9:00 | Megnaghat | 236 | 13:00 | 228 | 13:00
| Ashuganj | 243 | 1:00 | 236 | 14:00 | Fenchuganj | 245 | 21:00 | 238 | 8:00
| Serajganj | 234 | 1:00 | 228 | 10:00 | Siddhirganj | 237 | 18:30 | 228 | 11:00
| Baghabari | 248 | 1:00 | 238 | 12:00 | Maniknagar | 235 | 19:00 | 228 | 12:00
| Barapukuria | 233 | 1:00 | 228 | 13:00 | Agargaon | 236 | 2:00 | 226 | 12:00
| Bogra | 236 | 1:00 | 229 | 16:00 | Barisal | 252 | 2:00 | 245 | 13:00
| Rajshahi | 242 | 18:30 | 229 | 9:00 | Bhola 225 MW | 254 | 2:00 | 248 | 18:00
| Khulna South | 244 | 4:00 | 235 | 8:00 | AKSML | 254 | 2:00 | 252 | 4:00
| Rampura | 233 | 17:00 | 229 | 12:00 | BSRM | 231 | 7:00 | 218 | 8:00
| Haripur | 236 | 19:30 | 228 | 12:00 | Bibiyana | 230 | 4:00 | 218 | 5:00
| Hasnabad | 234 | 18:00 | 227 | 11:00 | Bhulta | 245 | 3:00 | 239 | 24:00
| Shyampur | 418 | 4:00 | 220 | 9:00 | Ashuganj (S) | 238 | 21:00 | 230 | 16:00
| Aminbazar | 237 | 18:30 | 227 | 12:00 | Kaliakoir | 240 | 18:30 | 235 | 16:00
| Tongi | 232 | 18:00 | 223 | 15:00 | GPH | 230 | 7:00 | 220 | 6:00
| Comilla (N) | 241 | 19:00 | 233 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 17:00 | 134 | 10:00 | Madanhat | 140 | 0.25 | 132 | 0.33333
| Munsiganj | 141 | 13:00 | 134 | 16:00 | Hathazari | 140 | 0.25 | 132 | 0.29167
| Sonargaon | 137 | 17:00 | 133 | 12:00 | Khulshi | 137 | 0.16667 | 132 | 0.41667
| Shyampur | 135 | 18:30 | 129 | 10:00 | Halishahar | 141 | 0.29167 | 131 | 0.33333
| Bhulta | 136 | 18:00 | 127 | 12:00 | Baraulia | 137 | 0.375 | 129 | 0.77083
| Madanganj | 137 | 10:00 | 133 | 1:00 | Sikalbaha | 142 | 0.77083 | 134 | 0.45833
| Shitalakhya | 141 | 13:00 | 132 | 0:00 | Dohazari | 138 | 0.77083 | 128 | 0.33333
| Rahim steal | 138 | 17:00 | 134 | 12:00 | Cox'sbazar | 128 | 0.29167 | 116 | 0.75
| Matuail | 139 | 17:00 | 134 | 10:00 | Chandraghona | 139 | 0.041667 | 134 | 0.20833
| Ghorasal | 140 | 1:00 | 140 | 1:00 | Kaptai | 137 | 0.8125 | 132 | 0.29167
| Narsinghdi | 136 | 17:00 | 132 | 12:00 | A. Khaer Stl. | 136 | 0.875 | 130 | 0.58333
| Haripur (SBU) | 137 | 7:00 | 134 | 1:00 | Bakulia | 139 | 0.77083 | 131 | 0.25
| Ullon | 134 | 17:00 | 129 | 12:00 | Julda | 139 | 0.79167 | 131 | 0.29167
| Hasnabad | 138 | 16:00 | 135 | 3:00 | TK Chemical | 141 | 0.77083 | 131 | 0.25
| Magbazar | 134 | 1:00 | 130 | 5:00 | Modern Steel | 139 | 0.77083 | 133 | 0.20833
| Maniknagar | 140 | 1:00 | 135 | 12:00 | Shahmirpur | 139 | 0.79167 | 134 | 0.25
| Bangabhaban | 140 | 1:00 | 135 | 12:00 | Khagrachhari | 138 | 0.79167 | 132 | 0.41667
| Narinda | 140 | 1:00 | 135 | 12:00 | Matarbari | 128 | 0.41667 | 115 | 0.75
| Dhanmondi | 134 | 17:00 | 129 | 12:00 | Baroiar Hat | 140 | 0.79167 | 132 | 0.33333
| Lalbag | 135 | 19:00 | 128 | 12:00 | Rangamati | 138 | 18:30 | 133 | 10:00
| Madartek | 133 | 1:00 | 129 | 10:00 | Goalpara S/S | 139 | 22:00 | 134 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 15:00 | 133 | 0.33333
| Aftabnagar | 134 | 20:00 | 129 | 12:00 | Noapara | 136 | 1:00 | 130 | 0.29167
| Fatuiiah | 135 | 18:30 | 128 | 12:00 | Jessore | 134 | 1:00 | 125 | 0.41667
| Mirpur | 135 | 20:00 | 128 | 12:00 | Benapol | 134 | 0.041667 | 126 | 0.33333
| Kalyanpur | 135 | 20:00 | 130 | 12:00 | Jhenida | 135 | 1:00 | 124 | 0.375
| Gulshan | 133 | 20:00 | 129 | 12:00 | Bottail | 138 | 0.083333 | 131 | 0.375
| Uttara | 135 | 20:00 | 130 | 12:00 | G.K Project | 142 | 0.083333 | 137 | 0.375
| Uttara New | 138 | 20:00 | 134 | 12:00 | Faridpur | 140 | 0.125 | 130 | 0.375
| Kamrangirchar | 139 | 20:00 | 135 | 12:00 | Madaripur | 141 | 0.125 | 137 | 0.29167
| Savar | 138 | 20:00 | 128 | 12:00 | Shariyatpur S/S | 143 | 3:00 | 137 | 0.375
| Bhasantec | 137 | 20:00 | 131 | 12:00 | Gopalganj | 145 | 0.041667 | 137 | 0.375
| Agargaon | 138 | 20:00 | 135 | 12:00 | Bagerhat | 140 | 15:00 | 131 | 0.33333
| Satmosjid | 138 | 20:00 | 133 | 12:00 | Mongla | 136 | 1:00 | 130 | 0.33333
| Tongi | 141 | 18:00 | 134 | 15:00 | Satkhira | 138 | 1:00 | 131 | 8:00
| Kabirpur | 135 | 23:00 | 125 | 12:00 | Gallamari | 139 | 0.16667 | 133 | 0.33333
| Basundhara | 138 | 22:00 | 128 | 16:00 | Magura | 135 | 3:00 | 123 | 0.375
| Manikganj | 144 | 17:00 | 138 | 0:00 | Narail | 133 | 0.16667 | 124 | 0.75
| Joydevpur | 141 | 17:00 | 134 | 8:00 | Chuadanga | 132 | 1:00 | 122 | 0.375
| New Tongi | 140 | 18:00 | 133 | 16:00 | Barisal(N) | 143 | 2:00 | 139 | 9:00
| Kodda | 140 | 18:00 | 130 | 14:00 | Barisal (S) | 143 | 0.16667 | 137 | 0.41667
| Dhamrai | 134 | 23:00 | 125 | 16:00 | Patuakhali(S) | 140 | 0.041667 | 134 | 0.5
| Rajendrapur | 139 | 18:00 | 134 | 10:00 | Bhandaria | 141 | 0.29167 | 134 | 0.79167
| Valuka | 129 | 22:00 | 117 | 14:00 | Ishurdi | 140 | 4:00 | 135 | 12:00
| Tangail | 134 | 1:00 | 125 | 8:00 | Ruppur Paromanobik | 139 | 6:00 | 135 | 12:00
| Mymensing | 130 | 1:00 | 118 | 13:00 | Natore | 138 | 18:00 | 132 | 12:00
| Kishorganj | 129 | 9:00 | 123 | 8:00 | Bogra | 140 | 1:00 | 134 | 13:00
| Netrokona | 127 | 22:00 | 114 | 13:00 | Noagaon | 134 | 1:00 | 127 | 9:00
| Jamalpur | 139 | 10:00 | 127 | 3:00 | Rajshahi | 137 | 18:00 | 130 | 9:00
| Sherpur | 137 | 20:00 | 121 | 4:00 | Rajshahi New | 139 | 18:00 | 129 | 12:00
| Srimongal | 138 | 3:00 | 135 | 10:00 | C.Nawabganj | 137 | 18:00 | 126 | 9:00
| Shahjibazar | 135 | 1:00 | 132 | 8:00 | Amnura | 139 | 18:00 | 127 | 12:00
| Fenchuganj | 137 | 1:00 | 134 | 8:00 | Pabna | 140 | 1:00 | 134 | 12:00
| Khulawara | 137 | 1:00 | 135 | 15:00 | Shahjadpur | 144 | 6:00 | 137 | 17:00
| Sylhet | 135 | 4:00 | 133 | 16:00 | Serajganj | 138 | 4:00 | 134 | 12:00
| Chatak | 135 | 1:00 | 133 | 10:00 | Niyamatpur | 132 | 4:00 | 123 | 9:00
| Sunamganj | 135 | 3:00 | 132 | 12:00 | Joypurhat | 136 | 4:00 | 125 | 12:00
| Biani Bazar | 135 | 1:00 | 133 | 11:00 | Sherpur(Bogura) | 139 | 6:00 | 132 | 16:00
| Comilla(s) | 130 | 1:00 | 125 | 18:00 | Mohastangor | 137 | 1:00 | 131 | 16:00
| Comilla(n) | 144 | 19:00 | 138 | 11:00 | Bangura | 141 | 1:00 | 137 | 17:00
| Chandpur | 143 | 16:00 | 140 | 19:00 | Rangpur | 131 | 6:00 | 124 | 19:00
| Feni | 139 | 18:30 | 133 | 10:00 | Lalmonirhat | 131 | 1:00 | 123 | 19:00
| Chowmuhani | 136 | 18:00 | 132 | 18:00 | Saidpur | 130 | 6:00 | 121 | 7:00
| Ashuganj | 136 | 1:00 | 134 | 16:00 | Purbasadipur | 130 | 5:00 | 121 | 18:30
| Daudkandi | 140 | 17:00 | 136 | 9:00 | Thakurgaon | 130 | 6:00 | 123 | 19:00
| B.Baria | 132 | 18:00 | 130 | 8:00 | Palashbari | 135 | 5:00 | 127 | 16:00
| Ramganj | 138 | 7:00 | 133 | 19:30 | Barapukuria | 133 | 5:00 | 128 | 13:00
| Chaddagram | 140 | 17:00 | 134 | 10:00 | Panchagar | 131 | 4:00 | 122 | 18:30

## L-Curve
Date | 2021-01-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 410 | 4470 | 2561 | 7031 |  |  |  | QF-LDC-11
0:30 | 213.5 | 4441.5 | 2268.5 | 6710 | Date: | 2021-01-17
1:00 | 17 | 4413 | 1976 | 6389
1:30 | 22 | 4309 | 1916.5 | 6225.5
2:00 | 27 | 4205 | 1857 | 6062
2:30 | 26 | 4144.5 | 1829 | 5973.5 | [5 empty] | Gen. at Eve. Peak | 9232 | 9500 MW (19:30 )
3:00 | 25 | 4084 | 1801 | 5885 | [6 empty] | 19:00
3:30 | 31 | 4045 | 1782 | 5827 | [5 empty] | Gen. at Day Peak | 7797 | 7952.5 MW (12:00 )
4:00 | 37 | 4006 | 1763 | 5769 | [6 empty] | 12:00
4:30 | 58 | 3883 | 1767 | 5650 | [5 empty] | Highest Generation | 9232
5:00 | 79 | 3760 | 1771 | 5531 | [6 empty] | 19:00
5:30 | 115.5 | 3812 | 1883 | 5695
6:00 | 152 | 3864 | 1995 | 5859
6:30 | 174 | 3993.5 | 2102 | 6095.5
7:00 | 196 | 4123 | 2209 | 6332
7:30 | 168.5 | 4226 | 2366.5 | 6592.5
8:00 | 141 | 4329 | 2524 | 6853
8:30 | 154 | 4586.5 | 2625 | 7211.5
9:00 | 167 | 4844 | 2726 | 7570
9:30 | 250.5 | 4913 | 2724.5 | 7637.5
10:00 | 334 | 4982 | 2723 | 7705
10:30 | 306 | 4988.5 | 2685 | 7673.5
11:00 | 278 | 4995 | 2647 | 7642
11:30 | 307.5 | 5031 | 2688.5 | 7719.5
12:00 | 337 | 5067 | 2730 | 7797
12:30 | 245 | 5130 | 2726.5 | 7856.5
13:00 | 153 | 5193 | 2723 | 7916
13:30 | 161.5 | 5189 | 2594.5 | 7783.5
14:00 | 170 | 5185 | 2466 | 7651
14:30 | 247.5 | 5115 | 2443 | 7558
15:00 | 325 | 5045 | 2420 | 7465
15:30 | 332 | 4984 | 2375 | 7359
16:00 | 339 | 4923 | 2330 | 7253
16:30 | 229.5 | 5008 | 2282 | 7290
17:00 | 120 | 5093 | 2234 | 7327
17:30 | 89 | 5421.5 | 2560 | 7981.5
18:00 | 58 | 5750 | 2886 | 8636
18:30 | 67 | 5960 | 2974 | 8934
19:00 | 76 | 6170 | 3062 | 9232
19:30 | 62 | 6055 | 3170 | 9225
20:00 | 9 | 6022 | 3149 | 9171 |  |  |  | Executive Engineer
20:30 | 65 | 5917 | 3121 | 9038 |  |  |  | Network Operation Division
21:00 | 121 | 5812 | 3093 | 8905
21:30 | 207.5 | 5545.5 | 3051.5 | 8597
22:00 | 294 | 5279 | 3010 | 8289 |  |  |  |  | Page 6 of 7
22:30 | 335.5 | 5111 | 2912.5 | 8023.5
23:00 | 377 | 4943 | 2815 | 7758
23:30 | 393.5 | 4706.5 | 2688 | 7394.5
24:00 | 410 | 4470 | 2561 | 7031
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-17 |  | Energy | 180264647
[11 empty] | 2021-01-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2767 | 729 | 1329 | 1944 | 609 | 47 | 7 | 0 | 72 | 0
0:30 | 2781 | 587 | 1316.5 | 1558 | 564.5 | 47 | 16.5 | 0 | 76 | 0 | Date: | 2021-01-17
1:00 | 2795 | 445 | 1304 | 1172 | 520 | 47 | 26 | 0 | 80 | 0
1:30 | 2793 | 444.5 | 1315 | 1015.5 | 519.5 | 47 | 13 | 0 | 78 | 0 | [7 empty] | Total Energy | 180.2646 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2791 | 444 | 1326 | 859 | 519 | 47 | 0 | 0 | 76 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2785.5 | 444.5 | 1341 | 762 | 518.5 | 47 | 0 | 0 | 75 | 0 | [7 empty] | Energy Requirement | 180.2646
3:00 | 2780 | 445 | 1356 | 665 | 518 | 47 | 0 | 0 | 74 | 0
3:30 | 2775.5 | 445 | 1344 | 625 | 518.5 | 46 | 0 | 0 | 73 | 0 | [6 empty] | Shortage
4:00 | 2771 | 445 | 1332 | 585 | 519 | 45 | 0 | 0 | 72 | 0
4:30 | 2720.5 | 444.5 | 1334.5 | 524.5 | 509 | 45 | 0 | 0 | 72 | 0
5:00 | 2670 | 444 | 1337 | 464 | 499 | 45 | 0 | 0 | 72 | 0
5:30 | 2692 | 487.5 | 1401.5 | 498 | 499 | 45 | 0 | 0 | 72 | 0
6:00 | 2714 | 531 | 1466 | 532 | 499 | 45 | 0 | 0 | 72 | 0
6:30 | 2689 | 582 | 1444.5 | 750 | 514.5 | 44 | 0 | 0 | 71 | 0.5 |  |  |  |  | Coal
7:00 | 2664 | 633 | 1423 | 968 | 530 | 43 | 0 | 0 | 70 | 1
7:30 | 2664.5 | 680 | 1406 | 1177.5 | 550 | 43.5 | 0 | 0 | 67 | 4 |  |  |  | Oil |  |  |  | ,
8:00 | 2665 | 727 | 1389 | 1387 | 570 | 44 | 0 | 0 | 64 | 7
8:30 | 2659.5 | 726.5 | 1401 | 1680.5 | 620 | 44.5 | 0 | 0 | 67 | 12.5
9:00 | 2654 | 726 | 1413 | 1974 | 670 | 45 | 0 | 0 | 70 | 18
9:30 | 2588.5 | 726 | 1438 | 2084.5 | 650 | 46 | 10 | 0 | 72 | 22.5
10:00 | 2523 | 726 | 1463 | 2195 | 630 | 47 | 20 | 0 | 74 | 27
10:30 | 2499 | 726.5 | 1425.5 | 2216.5 | 615 | 47 | 34 | 0 | 77 | 33
11:00 | 2475 | 727 | 1388 | 2238 | 600 | 47 | 48 | 0 | 80 | 39
11:30 | 2496 | 726.5 | 1405 | 2269.5 | 600 | 47.5 | 48 | 0 | 78 | 49
12:00 | 2517 | 726 | 1422 | 2301 | 600 | 48 | 48 | 0 | 76 | 59
12:30 | 2557 | 726.5 | 1402.5 | 2330 | 600 | 48 | 56 | 0 | 78 | 58.5
13:00 | 2597 | 727 | 1383 | 2359 | 600 | 48 | 64 | 0 | 80 | 58
13:30 | 2597 | 727 | 1383 | 2359 | 600 | 48 | 64 | 0 | 80 | 58
14:00 | 2597 | 727 | 1383 | 2359 | 600 | 48 | 64 | 0 | 80 | 58
14:30 | 2595.5 | 726.5 | 1348.5 | 2223.5 | 560 | 48 | 64 | 0 | 78 | 46.5
15:00 | 2594 | 726 | 1314 | 2088 | 520 | 48 | 64 | 0 | 76 | 35
15:30 | 2576 | 726 | 1346 | 1978 | 520 | 48 | 64 | 0 | 75 | 26
16:00 | 2558 | 726 | 1378 | 1868 | 520 | 48 | 64 | 0 | 74 | 17
16:30 | 2557 | 726 | 1293 | 1979.5 | 510 | 47 | 83 | 0 | 84 | 10.5
17:00 | 2556 | 726 | 1208 | 2091 | 500 | 46 | 102 | 0 | 94 | 4
17:30 | 2560.5 | 797.5 | 1268.5 | 2500 | 485 | 45.5 | 224.5 | 0 | 98 | 2
18:00 | 2565 | 869 | 1329 | 2909 | 470 | 45 | 347 | 0 | 102 | 0
18:30 | 2644.5 | 868.5 | 1325 | 3048 | 530 | 44.5 | 371.5 | 0 | 102 | 0
19:00 | 2724 | 868 | 1321 | 3187 | 590 | 44 | 396 | 0 | 102 | 0
19:30 | 2755 | 868 | 1439 | 2968 | 650 | 44 | 397 | 0 | 104 | 0
20:00 | 2752 | 869 | 1377 | 2963 | 650 | 45 | 413 | 0 | 102 | 0
20:30 | 2741.5 | 869 | 1371 | 2890 | 650 | 45.5 | 370 | 0 | 101 | 0
21:00 | 2731 | 869 | 1365 | 2817 | 650 | 46 | 327 | 0 | 100 | 0
21:30 | 2734.5 | 869 | 1354.5 | 2577 | 640 | 46 | 278 | 0 | 98 | 0
22:00 | 2738 | 869 | 1344 | 2337 | 630 | 46 | 229 | 0 | 96 | 0
22:30 | 2746 | 869 | 1341 | 2140.5 | 619.5 | 46.5 | 170 | 0 | 91 | 0
23:00 | 2754 | 869 | 1338 | 1944 | 609 | 47 | 111 | 0 | 86 | 0
23:30 | 2760.5 | 799 | 1333.5 | 1944 | 609 | 47 | 59 | 0 | 79 | 0 | Max Temp. in Dhaka |  | 23.2° C
24:00 | 2767 | 729 | 1329 | 1944 | 609 | 47 | 7 | 0 | 72 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 47 | 47 | 47 | 45 | 45 | 45 | 43 | 44 | 45 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 46 | 45 |  | 44 | 44 | 45 | 46 | 46 | 47 | 47 | 1092655
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 22 |  | 25 | [6 empty] | 52266
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 9 | 13 | 15 | 16 | 16 | 13 | 10 | 5 | 1 | [9 empty] | 102060
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 86 | 102 | 85 | 17 | 7 |  | 418162
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 |  |  |  |  | 2 | 25 | 120 | 175 | 240 | 262 | 300 | 300 | 270 | 268 | 248 | 247 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 148 | 4604180
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 213 | 213 | 213 | 214 | 215 | 213 | 213 | 213 | 213 | 212 | 211 | 203 | 215 | 200 | 200 | 200 | 201 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4981000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 280 | 250 | 250 | 280 | 300 | 300 | 300 | 300 | 280 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6830236
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 65016
33 | Ashuganj 225 MW CCPP | 160 | 164 | 168 | 167 | 169 | 169 | 169 | 169 | 169 | 164 | 164 | 164 | 153 | 153 | 163 | 172 | 174 | 174 |  | 174 | 174 | 169 | 159 | 160 | 160 | 172 | 4013000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6387000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6569700
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 331 | 338 | 342 | 333 | 351 | 362 | 363 | 335 | 356 | 355 | 347 | 333 | 343 | 335 | 338 | 345 | 359 | 301 |  | 341 | 334 | 333 | 334 | 332 | 332 | 340 | 8299520
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 253 | 263 | 293 | 313 | 313 | 313 | 282 | 261 | 234 | 224 | 232 | 242 | 240 | 239 | 244 | 244 | 248 | 253 |  | 250 | 250 | 250 | 248 | 228 | 228 | 228 | 6094000
42 | RPCL 210MW CCPP | 110 | 110 | 110 | 110 | 110 | 111 | 110 | 111 | 110 | 101 | 99 | 86 | 87 | 84 | 71 | 71 | 86 | 87 |  | 87 | 88 | 87 | 90 | 93 | 109 | 108 | 2282440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 6 | 10 | 19 | 35 | 33 | 28 | 19 | 9 | 2 | [9 empty] | 162210
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | [16 empty] | 194000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1019040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 34 | 33 | 34 | 34 | 33 | 34 | 33 | 33 | 32 | 32 | 31 | 32 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 658944
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 73 | 73 | 43 | 40 | 67 | 67 | 65 | 65 | 67 | 70 | 70 | 70 | 69 | 69 | 20 | 50 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1574400
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | [22 empty] | 453000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 90 | 20 | 20 | 20 | 74 | 78 | 78 | 77 | 96 | 126 |  | 150 | 161 | 162 | 162 | 162 | 162 | 162 | 2578110
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 205020
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 37 | 44 | 45 | 45 | 47 | 47 | 8 | 8 | 8 | 8 |  | 8 | 25 | 34 | 8 | 8 | 8 | 8 | 442800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189978
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 305 | 305 | 300 | 290 | 320 | 315 | 290 | 310 | 310 | 300 | 290 | 300 | 290 | 310 | 300 | 290 | 270 |  | 290 | 310 | 275 | 290 | 280 | 280 | 290 | 7389000
| Bibiyana South 400 MW | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 245 | 271 | 270 | 270 | 270 | 270 |  | 266 | 270 | 270 | 270 | 270 | 270 | 270 | 6469900
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 21 | 34 | 35 | 36 | 49 | 55 | 55 | 55 | 17 | 25 | 50 |  | 55 | 55 | 55 | 55 | 17 |  |  | 682669
59 | Tangail Palli Power Gen 22 MW | 25 | [6 empty] | 3 | 11 | 12 | 12 | 12 | 11 | 7 | 12 | 9 | 12 | 14 |  | 19 | 22 | 24 | 24 | 24 | 25 | 25 | 285360
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 378144
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 409860
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 20 | 20 | 20 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 501300
63 | Impoprt (Tripura) | 80 | 76 | 74 | 72 | 72 | 72 | 70 | 64 | 70 | 74 | 80 | 76 | 80 | 84 | 76 | 74 | 94 | 102 |  | 102 | 104 | 102 | 100 | 96 | 86 | 72 | 1957440
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 40 | 40 | 40 | 40 | 38 | 12 | 4 | 3 | 2 | 2 | 3 | 3 | 3 | 7 | 13 | 15 |  | 15 | 20 | 22 | 30 | 36 | 42 | 34 | 575040
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 449496
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 152100
67 | Jangalia 33MW PP (Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 |  | 33 | 30 | 30 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 694400
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 13 | 18 | 18 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 391680
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 28 | 28 | 28 | 28 | 10 | 6 | 10 | 10 | 10 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 32 | 33 | 33 | 33 | 33 | 26 | 421920
71 | Maona 33 MW PP(Summit) | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 613900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 17 | 17 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 591100
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 290636
| Feni Lanka Power | [16 empty] | 17 | 17 |  | 17 | [6 empty] | 44460
| Chowmuhani 113 MW | 46 | 46 | 26 | [9 empty] | 3 | 25 | 25 | 25 | 42 | 46 |  | 46 | 46 | 46 | 46 | 8 | 8 | 8 | 554400
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 131 |  | 144 | 126 | 126 | 126 | 126 | 126 | 162 | 1913760
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 20 | 24 | 30 | 40 | 20 | 50 | 24 | 24 | 40 | 80 |  | 100 | 100 | 100 | 40 |  |  |  | 655680
78 | Gazipur 52 MW PP | [17 empty] | 13 |  | 16 | [6 empty] | 32904
79 | Kodda 150MW PP | [9 empty] | 20 | 48 | 48 | 64 | 64 | 64 | 64 | 100 | 100 |  | 149 | 149 | 149 | 130 | 100 | 64 | 0 | 1173120
80 | Jamalpur 95 MW PP(Powerpac) | 8 | [7 empty] | 48 | 64 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 91 |  | 91 | 91 | 91 | 91 | 91 | 40 |  | 901440
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 8 |  | 16 | [6 empty] | 27643
| Gazipur 100 MW PP | [16 empty] | 7 | 53 |  | 99 | 105 | 105 | 105 |  |  |  | 432336
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 22887
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1301769
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 | 46 | 48 | 48 | 48 | 47 | 48 | 48 | 54 | 88 |  | 100 | 100 | 100 | 100 | 80 | 64 | 30 | 1175400
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 86 | 70 | 27 |  |  | 17 | 52 | 77 | 86 | 76 | 75 | 75 | 77 | 72 | 74 | 82 | 85 | 85 |  | 85 | 85 | 85 | 85 | 84 |  |  | 1539039
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 6 | 24 | 24 | 24 | 24 | 30 | 50 | 50 | 50 | 60 | 75 |  | 89 | 100 | 100 | 71 |  |  |  | 723840
| Meghnaghat 104 MW PP (OPCL) | 52 |  |  |  |  | 2 | 22 | 70 | 70 | 71 | 71 | 71 | 71 | 84 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 1511040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 7 | 10 |  |  |  | 10 | [8 empty] | 36000
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 50 | 50 | 50 | 47 | 50 | 5 | 5 | 5 | 5 |  | 20 | 30 | 30 | 5 | 5 | 5 | 5 | 505368
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1251643
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 10 | 32 | 50 | 50 | 50 | 48 | 48 | 58 | 24 | 32 | 64 |  | 72 | 48 | 48 | 7 |  |  |  | 638208
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | [5 empty] | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 |  | 50 | 50 | 50 | 46 | 44 | 25 | 25 | 813600
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 25 |  | 24 | [6 empty] | 49920
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 15 | 18 | 30 | 30 | 30 | 30 | 15 | 15 | 15 |  | 15 | [6 empty] | 229009
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 |  |  | 567754
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 110 | 130 |  | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 3259309
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 5850
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 35 | 35 | 35 | 35 | 45 | 35 | 17 | 17 | 54 | 54 |  | 54 | 54 | 54 | 35 |  |  |  | 502200
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 34 | [8 empty] | 31575
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 85 | 35 | 8 | 8 | 8 | 32 | 80 | 141 | 194 | 200 | 190 | 190 | 200 | 180 | 187 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 120 | 3640800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 27 | [6 empty] | 14 | 74 | 92 | 90 | 64 | 28 | 16 | 16 | 16 | 35 | 120 |  | 130 | 149 | 143 | 149 | 147 | 93 |  | 1295710
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 10 | 40 | 10 | 70 | 70 | 100 | 100 | 100 | 60 | 60 | 30 | 60 | 100 |  | 100 | 50 | 50 | 50 | 20 |  |  | 1018560
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 34 | 34 | 34 | 43 | 50 | 34 | 34 | 34 | 17 |  | 48 | 50 | 51 | 69 | 68 | 64 | 68 | 871680
117 | Ashuganj 150MW PP (Midland) | 75 | 73 | 75 | 73 | 75 | 75 | 75 | 74 | 75 | 75 | 75 | 73 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 1798181
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [8 empty] | 21 | 35 | 16 | 16 | 8 | 8 | 8 |  |  | 24 |  | 65 | 25 | 8 |  |  |  |  | 261600
| Anwara 300 MW PP (United) | 234 | 234 | 180 | 180 | 143 | 141 | 193 | 210 | 213 | 213 | 250 | 252 | 287 | 287 | 287 | 287 | 236 | 203 |  | 250 | 253 | 252 | 252 | 271 | 269 | 234 | 5630400
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 30 | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2191680
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4413 | 4205 | 4084 | 4006 | 3760 | 3864 | 4123 | 4329 | 4844 | 4982 | 4995 | 5067 | 5193 | 5185 | 5045 | 4923 | 5093 | 5750 |  | 6170 | 6055 | 6022 | 5812 | 5279 | 4943 | 4470 | 119187901
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 51 | 32 | 32 | 32 | 16 | 16 | 66 | 83 | 87 | 83 | 83 | 99 | 99 | 99 | 102 | 106 | 110 | 115 |  | 99 | 99 | 115 | 115 | 115 | 115 | 115 | 1932480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 70 | 70 | 70 | 35 | 35 | 35 |  | 90 | 90 | 90 | 90 | 35 |  |  | 1110240
130
131
132 | United Payra Power Ltd. | 17 | 17 | [24 empty] | 44400
133 | Bhola Nutan Biddut BD LTD (GAS) | 37 | 37 | 39 | 37 | 36 | 38 | 38 | 37 | 35 | 24 | 18 | 32 | 38 | 18 | 17 | 55 | 20 | 21 |  | 45 | 55 | 56 | 56 | 57 | 58 | 57 | 945927
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 32 | 32 | 48 | 32 |  |  | 138432
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 33 | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 61 | 60 | 60 | 61 | 62 | 62 | 62 | 31 | 31 | 64 |  | 80 | 82 | 84 | 84 | 84 | 76 | 58 | 1259296
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 24 | 23 | 21 | 17 | 18 | 19 | 20 | 20 | 20 | 21 | 19 | 21 | 21 | 20 | 20 | 18 | 20 | 25 |  | 26 | 27 | 28 | 28 | 28 | 25 | 24 | 515200
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 1 | [8 empty] | 22080
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 24 | 24 | 40 | 40 | 40 | 40 | 40 | 8 |  |  | 40 |  | 40 | [6 empty] | 308250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 47912
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 445 | 444 | 445 | 445 | 444 | 531 | 633 | 727 | 726 | 726 | 727 | 726 | 727 | 726 | 726 | 726 | 726 | 869 |  | 868 | 868 | 869 | 869 | 869 | 869 | 729 | 16661090
147 | Bheramara 410 MW CCPP | 310 | 310 | 310 | 310 | 310 | 360 | 315 | 305 | 305 | 305 | 325 | 360 | 375 | 375 | 350 | 300 | 250 | 300 |  | 370 | 370 | 370 | 355 | 360 | 360 | 360 | 8090496
148 | Payra 1320 MW | 370 | 370 | 370 | 370 | 350 | 350 | 380 | 420 | 520 | 480 | 450 | 450 | 450 | 400 | 370 | 370 | 350 | 320 |  | 440 | 500 | 500 | 500 | 480 | 460 | 460 | 10887600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 148 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3652200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 |  |  |  |  | 135472
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 333 | 331 | 327 | 296 | 341 | 410 | 377 | 416 | 385 | 420 | 359 | 369 | 315 | 292 | 334 | 399 | 341 | 386 |  | 285 | 338 | 296 | 314 | 316 | 334 | 343 | 8468200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 167878
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 24 |  | 25 | 25 | 25 |  |  |  |  | 75370
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 | [8 empty] | 23016
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 24 | [8 empty] | 30720
170 | Chapainawabganj 100 MW Peaking PP | 26 | [16 empty] | 105 |  | 105 | 105 | 105 | 105 | 105 | 33 |  | 592896
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 35 | 35 | 35 | 50 | 89 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 35 | 45 | 95 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2166528
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [5 empty] | 35 | 90 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 50 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1707744
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | [5 empty] | 34 | 64 | 106 | 107 | 113 | 113 | 113 | 72 | 70 | 35 | 70 | 106 |  | 107 | 113 | 113 | 113 | 113 | 70 | 0 | 1558080
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 1 | 1 | 1 | 3 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 19479
178
178