## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-19 | Tuesday
|  |  | Date (day): | 2021-01-19 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12322.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13459 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-18 | 2021-01-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 237 | 234 | 230 | 230
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 380 | 300 | 300 | 65 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 330 | 329 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 277 | 221 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 26 | 68 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 86 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 76 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 90 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 92 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 25 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 37 |  | 18 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 113 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 72 | 100 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 104 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2306 | 2810 | 3418 | 3670 | 1074 | 1360
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 17 | 0 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 15 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 47 | 45 | 43 | 43 | 187 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 70 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 22 | 10 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 90 | 90 |  | 18 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 303 | 271 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 35 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 596 | 688 | 1099 | 1214 | 922 | 123
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 150 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 250 | 360 | 360
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 250 | 360 | 360
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 3 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 75 | 75 | 75 |  | 75 | Engine Problem
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 40 | 50 | 50 |  | 113 | Engine problem
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 90 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 108 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 0 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 31 | 26 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1073 | 1078 | 1833 | 2097 | 680 | 188
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 96 | 104 | 105 | 105 | 97 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 83 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 8 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 386 | 441 | 610.6 | 559 | 97 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 20 | 20 |  | 50 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 20 | 8 | 8
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 10 | 5 | 5
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 40 | 40
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 72 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 162 | 160 | 160 |  | 71 | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 270 | 270 | 270 | 270 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1023 | 1063 | 1268 | 1268 | 0 | 884
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 726 | 868 | 741 | 886
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 345 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 77 | 77 | 90 | 90 |  | 15 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 918 | 1455 | 1651 | 2082 | 0 | 73
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 22 | 24 | 28 |  | 5 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 62 | 85 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 500 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 7 | 13 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 515 | 668 | 1029 | 1039 | 0 | 199
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 12 | 28 | 28 |  | 22 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 346 | 362 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 43 | 103 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 673 | 831 | 1143 | 1267 | 821 | 22
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 268 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7758 | 9297 | 12322.6 | 13459 | 3718 | 3059
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7449.2488 | 8927 | 11832.1878 | 12923.3616
| A. |  | 2021-01-18 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9297 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5746 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9297 | MW
| 3 | Day peak Generation : |  |  | 7758 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8927 | MW
| 4 | Evening peak Generation : |  |  | 9297 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 176.7315 | MKWHr | By Solar | 0.17798 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 97.2213 | MKWHr |  | By Oil: | 44.6756 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.0498 | MKWHr |  | By Hydro: | 1.1188 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3718 | MW | Dhaka | 3087 | 3087 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3059 | MW | Chittagong | 984 | 984 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6777 | MW | Khulna | 1092 | 1092 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 739.16 | MMCFD |  |  | Rajshahi | 966 | 966 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 101027931.774 | ii) Oil : | Taka | 326405937.77 | Comilla | 748 | 748 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69845529 | Total | Taka | 497279398.544 | Mymensingh | 806 | 806 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.197 | MKWHr. | Sylhet | 331 | 331 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 54 | MW (E to W) at | 19:00 | hrs | Barisal | 242 | 242 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -95 | MW at | 7:00 | hrs | Rangpur | 671 | 671 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 23.9° C |  |  | Total | 8927 | 8927 |  | 0
| B. |  | 2021-01-19 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13459 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
| 4 | Reserve(Generation end) |  |  |  | 4059 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 178.6895 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5711 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6313 | MKWHr. | ii) HVDC Flow at Peak Time |  | 868 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8566 | MKWHr. | iii) Maximum HVDC Flow : |  | 870 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.03 |  | (b) Today: | 96.95 |  | (c) Rule Curve: |  | 99.58
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 369 | 235 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 15 | 32 | 0 | 0 | 0 | 260 | 260 | 180 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 107 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 161 | 0 | 0 | 9 | 320 | 8 | 11 | 0 | 148 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 68 | 75 | 0 | 0 | 0 | 0 | 0 | 234 | 40 | 0 | 0 | 8 | 100 | 270 | 53 | 0 | 72 | 0 | 0 |  | 445 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 339 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 70 | 440 | 57 | 0 | 0 |  | 4384 | 2196 | 6580 | 2799 | 445 | 1379 | 1248 | 589 | 48 | 0 | 72 | 0 | 0 | 97.04
2:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 345 | 264 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 42 | 0 | 0 | 0 | 265 | 260 | 186 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 161 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 68 | 73 | 0 | 0 | 0 | 0 | 0 | 234 | 36 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 72 | 0 | 0 |  | 445 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 342 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 440 | 57 | 0 | 0 |  | 4078 | 2029 | 6107 | 2784 | 445 | 1376 | 793 | 589 | 48 | 0 | 72 | 0 | 0 | 97.04
3:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 354 | 277 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 42 | 0 | 0 | 0 | 260 | 260 | 185 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 160 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 200 | 36 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 72 | 0 | 0 |  | 445 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 57 | 0 | 0 |  | 4007 | 1930 | 5937 | 2776 | 445 | 1389 | 640 | 570 | 45 | 0 | 72 | 0 | 0 | 97.04
4:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 365 | 288 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 42 | 0 | 0 | 0 | 260 | 260 | 185 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 72 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 163 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 36 | 0 | 0 | 0 | 50 | 270 | 0 | 0 | 72 | 0 | 0 |  | 445 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 56 | 0 | 0 |  | 3868 | 1919 | 5787 | 2790 | 445 | 1396 | 469 | 570 | 45 | 0 | 72 | 0 | 0 | 97.03
5:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 351 | 288 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 42 | 0 | 0 | 0 | 265 | 260 | 182 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 70 | 107 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 70 | 0 | 162 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 36 | 0 | 0 | 0 | 50 | 270 | 0 | 0 | 72 | 0 | 0 |  | 444 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 57 | 0 | 0 |  | 3836 | 1910 | 5746 | 2750 | 444 | 1398 | 469 | 570 | 45 | 0 | 70 | 0 | 0 | 97.03
6:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 347 | 306 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 42 | 0 | 0 | 0 | 265 | 260 | 181 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 74 | 105 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 72 | 0 | 162 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 7 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 68 | 43 | 0 | 0 | 0 | 0 | 0 | 216 | 36 | 0 | 0 | 0 | 50 | 270 | 3 | 0 | 72 | 0 | 0 |  | 511 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 342 | 0 | 0 | 19 | 0 | 34 | 0 | 0 | 0 | 420 | 58 | 0 | 0 |  | 3970 | 1905 | 5875 | 2606 | 511 | 1418 | 651 | 570 | 45 | 0 | 74 | 0 | 0 | 97.03
7:00 | 0 | 0 | 200 | 0 | 300 | 12 | 0 | 332 | 302 |  | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 22 | 25 | 8 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 0 | 0 | 260 | 260 | 177 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 68 | 105 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 72 | 0 | 162 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 97 | 0 | 0 | 25 | 0 | 34 | 1 | 20 | 68 | 76 | 0 | 0 | 0 | 0 | 0 | 215 | 36 | 0 | 0 | 0 | 100 | 270 | 32 | 0 | 72 | 0 | 0 |  | 634 | 0 | 30 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 420 | 24 | 0 | 0 |  | 4236 | 1810 | 6046 | 2382 | 634 | 1353 | 996 | 570 | 42 | 0 | 68 | 1 | 0 | 97.02
8:00 | 0 | 0 | 235 | 0 | 280 | 12 | 0 | 350 | 273 |  | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 22 | 3 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 17 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 260 | 260 | 175 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 78 | 104 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 20 | 72 | 0 | 162 | 0 | 0 | 9 | 305 | 8 | 11 | 0 | 136 | 0 | 0 | 125 | 0 | 95 | 5 | 50 | 68 | 75 | 0 | 0 | 0 | 0 | 1 | 283 | 36 | 0 | 0 | 0 | 100 | 270 | 53 | 3 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 338 | 70 | 0 | 89 | 0 | 98 | 0 | 1 | 75 | 440 | 26 | 0 | 0 |  | 4625 | 2210 | 6835 | 2384 | 726 | 1323 | 1681 | 590 | 43 | 0 | 78 | 10 | 0 | 97.02
9:00 | 0 | 0 | 247 | 0 | 280 | 12 | 0 | 360 | 288 |  | 0 | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 0 | 50 | 24 | 30 | 62 | 0 | 0 | 0 | 0 | 17 | 8 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 13 | 7 | 0 | 0 | 0 | 265 | 260 | 172 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 68 | 105 | 14 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 32 | 70 | 0 | 163 | 0 | 0 | 9 | 340 | 8 | 8 | 0 | 204 | 0 | 0 | 172 | 0 | 105 | 10 | 50 | 68 | 75 | 0 | 0 | 12 | 0 | 2 | 306 | 36 | 0 | 0 | 0 | 100 | 270 | 72 | 7 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 430 | 70 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 450 | 41 | 0 | 0 |  | 5041 | 2416 | 7457 | 2447 | 726 | 1469 | 2052 | 600 | 44 | 30 | 68 | 21 | 0 | 97.02
10:00 | 0 | 0 | 238 | 0 | 260 | 12 | 0 | 340 | 278 |  | 0 | 0 | 0 | 24 | 68 | 0 | 0 | 0 | 0 | 70 | 64 | 48 | 62 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 12 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 0 | 0 | 0 | 260 | 260 | 177 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 18 | 70 | 103 | 48 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 70 | 0 | 163 | 0 | 0 | 9 | 310 | 8 | 8 | 0 | 275 | 0 | 0 | 200 | 0 | 139 | 14 | 50 | 68 | 73 | 0 | 0 | 70 | 0 | 3 | 297 | 36 | 0 | 0 | 0 | 100 | 265 | 72 | 0 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 386 | 70 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 430 | 0 | 0 | 0 |  | 5289 | 2368 | 7657 | 2386 | 726 | 1341 | 2396 | 580 | 46 | 91 | 70 | 21 | 0 | 97.01
11:00 | 0 | 0 | 237 | 0 | 250 | 12 | 0 | 326 | 285 |  | 0 | 0 | 0 | 24 | 80 | 0 | 0 | 0 | 0 | 70 | 64 | 48 | 66 | 0 | 0 | 0 | 10 | 17 | 17 | 22 | 25 | 12 | 25 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 0 | 0 | 0 | 260 | 260 | 180 | 8 | 0 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 62 | 98 | 48 | 22 | 1 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 70 | 0 | 162 | 0 | 0 | 9 | 280 | 8 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 16 | 50 | 68 | 75 | 0 | 0 | 72 | 0 | 4 | 303 | 36 | 0 | 0 | 9 | 100 | 270 | 72 | 0 | 72 | 0 | 0 |  | 727 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 376 | 76 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 430 | 0 | 0 | 0 |  | 5308 | 2396 | 7704 | 2367 | 727 | 1330 | 2476 | 580 | 46 | 91 | 62 | 25 | 0 | 97.01
12:00 | 0 | 0 | 237 | 0 | 250 | 12 | 0 | 330 | 277 |  | 0 | 0 | 0 | 26 | 86 | 0 | 0 | 0 | 0 | 70 | 64 | 48 | 76 | 0 | 0 | 0 | 25 | 17 | 17 | 22 | 25 | 17 | 25 | 17 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 15 | 17 | 8 | 0 | 0 | 0 | 265 | 260 | 180 | 8 | 0 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 62 | 96 | 48 | 22 | 2 | 0 | 43 | 8 | 5 | 130 | 0 | 31 | 70 | 0 | 163 | 0 | 0 | 7 | 280 | 8 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 16 | 50 | 68 | 75 | 0 | 0 | 72 | 0 | 4 | 303 | 36 | 0 | 0 | 31 | 100 | 270 | 72 | 0 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 346 | 77 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 430 | 7 | 0 | 0 |  | 5384 | 2374 | 7758 | 2378 | 726 | 1301 | 2546 | 580 | 47 | 91 | 62 | 27 | 0 | 97.01
13:00 | 0 | 0 | 237 | 0 | 250 | 12 | 0 | 329 | 277 |  | 0 | 0 | 0 | 64 | 98 | 0 | 0 | 0 | 0 | 80 | 64 | 48 | 86 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 31 | 25 | 17 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 48 | 17 | 12 | 0 | 0 | 0 | 260 | 260 | 178 | 8 | 0 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 18 | 62 | 96 | 25 | 20 | 2 | 0 | 43 | 17 | 10 | 130 | 0 | 31 | 69 | 0 | 163 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 145 | 16 | 20 | 68 | 75 | 0 | 0 | 102 | 0 | 4 | 255 | 36 | 0 | 0 | 55 | 100 | 270 | 73 | 0 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 19 | 0 | 0 | 0 | 40 | 0 | 0 | 43 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 355 | 77 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 430 | 31 | 0 | 0 |  | 5487 | 2460 | 7947 | 2411 | 726 | 1365 | 2638 | 580 | 47 | 91 | 62 | 27 | 7947 | 97
14:00 | 0 | 0 | 237 | 0 | 250 | 12 | 0 | 328 | 277 |  | 0 | 0 | 0 | 76 | 64 | 0 | 0 | 0 | 0 | 100 | 32 | 48 | 86 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 17 | 10 | 0 | 0 | 0 | 260 | 260 | 174 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 18 | 68 | 87 | 24 | 22 | 2 | 0 | 43 | 20 | 10 | 110 | 0 | 31 | 70 | 0 | 163 | 18 | 0 | 9 | 275 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 116 | 14 | 20 | 68 | 75 | 0 | 0 | 52 | 0 | 3 | 255 | 35 | 0 | 0 | 55 | 100 | 270 | 75 | 0 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 43 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 325 | 77 | 0 | 113 | 0 | 96 | 0 | 4 | 113 | 430 | 33 | 0 | 0 |  | 5372 | 2413 | 7785 | 2428 | 726 | 1311 | 2510 | 580 | 48 | 91 | 68 | 23 | 0 | 97
15:00 | 0 | 0 | 238 | 0 | 300 | 12 | 0 | 330 | 277 |  | 0 | 0 | 0 | 59 | 64 | 0 | 0 | 0 | 0 | 100 | 32 | 48 | 86 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 17 | 5 | 0 | 0 | 0 | 260 | 260 | 160 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 18 | 64 | 85 | 24 | 22 | 1 | 0 | 43 | 20 | 10 | 110 | 0 | 31 | 70 | 0 | 162 | 18 | 0 | 9 | 270 | 8 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 100 | 11 | 20 | 50 | 75 | 0 | 0 | 52 | 0 | 2 | 253 | 35 | 0 | 0 | 25 | 100 | 270 | 102 | 0 | 90 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 43 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 315 | 77 | 0 | 113 | 0 | 70 | 0 | 3 | 70 | 430 | 17 | 0 | 0 |  | 5295 | 2341 | 7636 | 2494 | 726 | 1269 | 2348 | 580 | 47 | 91 | 64 | 17 | 0 | 97
16:00 | 0 | 0 | 234 | 0 | 366 | 12 | 0 | 327 | 279 |  | 0 | 0 | 0 | 62 | 64 | 0 | 0 | 0 | 0 | 70 | 32 | 32 | 86 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 17 | 8 | 0 | 0 | 0 | 250 | 250 | 156 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 18 | 58 | 85 | 8 | 22 | 1 | 0 | 43 | 20 | 10 | 110 | 0 | 31 | 69 | 0 | 162 | 18 | 0 | 9 | 265 | 8 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 64 | 6 | 20 | 34 | 75 | 0 | 0 | 17 | 0 | 1 | 253 | 35 | 0 | 0 | 25 | 70 | 270 | 104 | 0 | 90 | 0 | 0 |  | 727 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 43 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 321 | 77 | 0 | 70 | 0 | 70 | 0 | 1 | 70 | 400 | 16 | 0 | 0 |  | 5125 | 2216 | 7341 | 2529 | 727 | 1253 | 2093 | 550 | 47 | 75 | 58 | 9 | 0 | 96.99
17:00 | 0 | 0 | 236 | 0 | 380 | 12 | 0 | 336 | 269 |  | 0 | 0 | 0 | 68 | 64 | 0 | 0 | 0 | 0 | 40 | 32 | 64 | 86 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 31 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 8 | 6 | 50 | 17 | 12 | 0 | 0 | 0 | 250 | 250 | 150 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 2 | 19 | 8 | 33 | 18 | 72 | 103 | 8 | 22 | 0 | 0 | 43 | 20 | 10 | 110 | 0 | 31 | 69 | 0 | 162 | 18 | 0 | 7 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 160 | 0 | 52 | 1 | 20 | 34 | 75 | 0 | 5 | 17 | 0 | 0 | 253 | 35 | 0 | 0 | 25 | 70 | 270 | 104 | 0 | 144 | 0 | 0 |  | 727 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 60 | 12 | 0 | 0 | 7 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 350 | 77 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 400 | 55 | 0 | 0 |  | 5204 | 2289 | 7493 | 2541 | 727 | 1338 | 2093 | 550 | 47 | 124 | 72 | 1 | 0 | 96.99
18:00 | 0 | 0 | 234 | 0 | 380 | 12 | 0 | 347 | 262 |  | 0 | 0 | 0 | 68 | 72 | 15 | 0 | 0 | 0 | 50 | 50 | 115 | 85 | 0 | 0 | 0 | 17 | 17 | 25 | 16 | 25 | 18 | 25 | 25 | 14 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 85 | 40 | 18 | 50 | 17 | 13 | 0 | 0 | 0 | 250 | 250 | 149 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 96 | 104 | 38 | 22 | 0 | 0 | 43 | 20 | 10 | 110 | 0 | 31 | 69 | 0 | 162 | 18 | 0 | 7 | 300 | 8 | 11 | 0 | 249 | 0 | 0 | 168 | 0 | 85 | 0 | 80 | 36 | 75 | 0 | 26 | 58 | 0 | 0 | 253 | 35 | 0 | 0 | 25 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 868 | 0 | 135 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 102 | 18 | 0 | 0 | 35 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1 | 0 | 0 | 414 | 77 | 0 | 82 | 0 | 103 | 0 | 0 | 100 | 410 | 55 | 0 | 0 |  | 5713 | 2826 | 8539 | 2632 | 868 | 1441 | 2594 | 560 | 46 | 302 | 96 | 0 | 0 | 96.99
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 234 | 0 | 380 | 12 | 0 | 329 | 221 |  | 0 | 0 | 0 | 68 | 100 | 30 | 0 | 0 | 0 | 90 | 92 | 150 | 85 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 32 | 25 | 25 | 8 | 0 | 45 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 10 | 50 | 17 | 22 | 0 | 0 | 0 | 250 | 250 | 150 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 108 | 104 | 83 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 72 | 0 | 162 | 18 | 0 | 7 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 113 | 0 | 70 | 90 | 75 | 0 | 8 | 100 | 0 | 0 | 271 | 35 | 0 | 0 | 26 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 868 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 48 | 0 | 0 | 0 | 43 | 0 | 103 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | 0 | 0 | 362 | 77 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 13 | 0 | 0 |  | 6080 | 3217 | 9297 | 2832 | 868 | 1337 | 3110 | 650 | 45 | 347 | 108 | 0 | 0 | 96.98
19:30 | 0 | 0 | 233 | 0 | 380 | 12 | 0 | 326 | 211 |  | 0 | 0 | 0 | 68 | 101 | 30 | 0 | 0 | 0 | 70 | 102 | 150 | 86 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 32 | 25 | 25 | 8 | 0 | 44 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 0 | 50 | 17 | 26 | 0 | 0 | 0 | 250 | 250 | 144 | 8 | 50 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 0 | 18 | 110 | 104 | 81 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 72 | 0 | 162 | 18 | 0 | 7 | 330 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 115 | 0 | 70 | 100 | 75 | 0 | 8 | 72 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 869 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 48 | 0 | 0 | 0 | 27 | 0 | 103 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 410 | 77 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 37 | 0 | 0 |  | 6054 | 3226 | 9280 | 2850 | 869 | 1454 | 2989 | 650 | 44 | 314 | 110 | 0 | 0 | 0
20:00 | 0 | 0 | 234 | 0 | 380 | 12 | 0 | 326 | 214 |  | 0 | 0 | 0 | 68 | 101 | 30 | 0 | 0 | 0 | 70 | 102 | 150 | 86 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 0 | 50 | 17 | 29 | 0 | 0 | 0 | 250 | 240 | 137 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 17 | 20 | 108 | 104 | 81 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 73 | 0 | 162 | 18 | 0 | 7 | 295 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 117 | 0 | 70 | 100 | 75 | 0 | 8 | 72 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 99 | 0 | 144 | 0 | 0 |  | 868 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 48 | 0 | 0 | 0 | 25 | 0 | 103 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 370 | 77 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 37 | 0 | 0 |  | 5987 | 3180 | 9167 | 2843 | 868 | 1388 | 2953 | 650 | 45 | 312 | 108 | 0 | 0 | 96.98
21:00 | 0 | 0 | 234 | 0 | 380 | 0 | 0 | 326 | 190 |  | 0 | 0 | 0 | 68 | 101 | 0 | 0 | 0 | 0 | 48 | 102 | 133 | 82 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 0 | 50 | 18 | 35 | 0 | 0 | 0 | 250 | 240 | 133 | 8 | 42 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 100 | 102 | 82 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 73 | 0 | 162 | 18 | 0 | 7 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 115 | 0 | 70 | 100 | 75 | 0 | 8 | 35 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 91 | 0 | 144 | 0 | 0 |  | 868 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 370 | 77 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 46 | 0 | 0 |  | 5785 | 3119 | 8904 | 2854 | 868 | 1351 | 2766 | 650 | 45 | 270 | 100 | 0 | 0 | 96.98
22:00 | 0 | 0 | 237 | 0 | 380 | 0 | 0 | 332 | 180 |  | 0 | 0 | 0 | 40 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 100 | 75 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 35 | 0 | 0 | 0 | 250 | 240 | 135 | 8 | 46 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 100 | 102 | 16 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 73 | 0 | 162 | 18 | 0 | 7 | 270 | 8 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 90 | 0 | 40 | 100 | 75 | 0 | 0 | 0 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 869 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 379 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 57 | 0 | 0 |  | 5311 | 3087 | 8398 | 2870 | 869 | 1353 | 2307 | 650 | 46 | 203 | 100 | 0 | 0 | 96.97
23:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 338 | 222 |  | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 24 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 33 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 34 | 0 | 0 | 0 | 250 | 240 | 152 | 8 | 46 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 0 | 33 | 21 | 92 | 109 | 8 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 73 | 0 | 162 | 18 | 0 | 7 | 280 | 8 | 11 | 0 | 200 | 0 | 0 | 150 | 0 | 40 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 64 | 0 | 144 | 0 | 0 |  | 870 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 383 | 17 | 0 | 113 | 0 | 59 | 0 | 0 | 50 | 480 | 56 | 0 | 0 |  | 4875 | 2782 | 7657 | 2886 | 870 | 1390 | 1693 | 630 | 46 | 50 | 92 | 0 | 0 | 96.97
24:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 346 | 264 |  | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 33 | 20 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 34 | 0 | 0 | 0 | 250 | 240 | 160 | 8 | 46 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 80 | 109 | 8 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 73 | 0 | 162 | 19 | 0 | 7 | 290 | 8 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 16 | 0 | 0 | 34 | 73 | 0 | 0 | 0 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 30 | 0 | 144 | 0 | 0 |  | 633 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 358 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 460 | 58 | 0 | 0 |  | 4726 | 2397 | 7123 | 2913 | 633 | 1403 | 1405 | 610 | 47 | 32 | 80 | 0 | 0 | 96.97
KWH | 0 | 0 | 5375000 | 0 | 7573791 | 253000 | 0 | 8312600 | 6252000 |  | 0 | 0 | 0 | 756480 | 1315512 | 92159 | 0 | 0 | 0 | 1026240 | 925776 | 1160160 | 1370900 | 0 | 0 | 0 | 379440 | 311055 | 445881 | 398412 | 600000 | 603540 | 621300 | 579100 | 32532 | 0 | 1118836 | 0 | 0 | 0 | 34295 | 0 | 0 | 0 | 0 |  | 387360 | 0 | 230774 | 36840 | 39360 | 643680 | 393408 | 608160 | 0 | 0 | 0 | 6499500 | 6261000 | 4049000 | 200727 | 219730 | 71928 | 0 | 0 | 1190902 | 0 | 0 | 17520 | 430128 | 182700 | 720100 | 457260 | 1856640 | 2398480 | 618240 | 512568 | 7550 | 0 | 1012200 | 313800 | 279072 | 3217909 | 0 | 670656 | 1696320 | 0 | 3905570 | 173000 | 0 | 193680 | 7269500 | 190136 | 249048 | 0 | 478734 | 0 | 0 | 3441600 | 0 | 1748300 | 108675 | 769920 | 1701120 | 1629236 | 0 | 80400 | 827688 | 0 | 24479 | 6051927 | 872641 | 0 | 0 | 375480 | 2254080 | 6462500 | 1558080 | 7970 | 2355840 | 0 | 0 |  | 16631272 | 0 | 4403808 | 0 | 2456640 | 0 | 0 | 0 | 0 | 0 | 185250 | 0 | 456400 | 192288 | 0 | 0 | 245000 | 66112 | 0 | 741056 | 194800 | 0 | 0 | 106560 | 0 | 519600 | 0 | 224442 | 0 | 0 | 3666900 | 0 | 0 | 0 | 0 | 0 | 0 | 1313325 | 16320 | 0 | 0 | 8717000 | 1128000 | 0 | 2119296 | 0 | 1660800 | 0 | 29303 | 1839264 | 11382900 | 944045 | 0 | 0 |  | 117491125 | 59240381 | 176731506 | 63795905 | 16631272 | 33425440 | 42477534 | 15049800 | 1118836 | 2198102 | 1856640 | 177977 | 0
Fuel Cost | 0 | 0 | 7847500 | 0 | 8406908.01 | 333960 | 0 | 8395726 | 6439560 |  | 0 | 0 | 0 | 5741683.2 | 9063877.68 | 779665.14 | 0 | 0 | 0 | 7727587.2 | 8443077.12 | 11415974.4 | 12639698 | 0 | 0 | 0 | 2769912 | 2404455.15 | 4396386.66 | 298809 | 450000 | 0 | 0 | 0 | 314584.44 | 0 | 302085.72 | 0 | 0 | 0 | 318600.55 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2238507.8 | 351822 | 342432 | 5097945.6 | 495694.08 | 1806235.2 | 0 | 0 | 0 | 4809630 | 6261000 | 3725080 | 258937.83 | 252689.5 | 81278.64 | 0 | 0 | 2036442.42 | 0 | 0 | 167316 | 546262.56 | 137025 | 1260175 | 342945 | 13924800 | 2542388.8 | 5613619.2 | 650961.36 | 120347 | 0 | 1619520 | 558564 | 435352.32 | 3668416.26 | 0 | 1321192.32 | 3239971.2 | 0 | 6756636.1 | 378870 | 0 | 395107.2 | 7342195 | 142602 | 189276.48 | 0 | 3619229.04 | 0 | 0 | 17896320 | 0 | 17203272 | 1270410.75 | 6274848 | 18457152 | 11486113.8 | 0 | 733248 | 7821651.6 | 0 | 0 | 45752568.12 | 7600703.11 | 0 | 0 | 3217863.6 | 15012172.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95796126.72 | 0 | 4623998.4 | 0 | 19309190.4 | 0 | 0 | 0 | 0 | 0 | 1930305 | 0 | 707420 | 1876730.88 | 0 | 0 | 502250 | 650542.08 | 0 | 6558345.6 | 1499960 | 0 | 0 | 1032566.4 | 0 | 997632 | 0 | 169902.594 | 0 | 0 | 19874598 | 0 | 0 | 0 | 0 | 0 | 0 | 1969987.5 | 277603.2 | 0 | 0 | 8629830 | 11776320 | 0 | 20112119.04 | 0 | 12887808 | 0 | 323798.15 | 13592160.96 | 49970931 | 0 | 0 | 0 |  | 333946840.96 | 275070125.924 | 609016966.884 | 62208320.844 | 95796126.72 | 38819610.93 | 305542567.89 | 69845529 | 302085.72 | 20863369.88 | 13924800 | 1714555.9 | 0
Yesterday Day Peak | 0 | 0 | 237 | 0 | 250 | 12 | 0 | 330 | 277 |  | 0 | 0 | 0 | 26 | 86 | 0 | 0 | 0 | 0 | 70 | 64 | 48 | 76 | 0 | 0 | 0 | 25 | 17 | 17 | 22 | 25 | 17 | 25 | 17 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 15 | 17 | 8 | 0 | 0 | 0 | 265 | 260 | 180 | 8 | 0 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 62 | 96 | 48 | 22 | 2 | 0 | 43 | 8 | 5 | 130 | 0 | 31 | 70 | 0 | 163 | 0 | 0 | 7 | 280 | 8 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 16 | 50 | 68 | 75 | 0 | 0 | 72 | 0 | 4 | 303 | 36 | 0 | 0 | 31 | 100 | 270 | 72 | 0 | 72 | 0 | 0 |  | 726 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 346 | 77 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 430 | 7 | 0 | 0 |  | 7758 | DayPeak
Yesterday Evening Peak | 0 | 0 | 234 | 0 | 380 | 12 | 0 | 329 | 221 | 0 | 0 | 0 | 0 | 68 | 100 | 30 | 0 | 0 | 0 | 90 | 92 | 150 | 85 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 32 | 25 | 25 | 8 | 0 | 45 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 0 | 10 | 50 | 17 | 22 | 0 | 0 | 0 | 250 | 250 | 150 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 108 | 104 | 83 | 22 | 0 | 0 | 43 | 20 | 10 | 130 | 0 | 32 | 72 | 0 | 162 | 18 | 0 | 7 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 113 | 0 | 70 | 90 | 75 | 0 | 8 | 100 | 0 | 0 | 271 | 35 | 0 | 0 | 26 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 868 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 48 | 0 | 0 | 0 | 43 | 0 | 103 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | 0 | 0 | 362 | 77 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 13 | 0 | 0 |  | 9297 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 300 | 50 | 0 | 412 | 300 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 37 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 25 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 50 | 5 | 0 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 22 | 147 | 105 | 95 | 22 | 0 | 20 | 43 | 8 | 5 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 75 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 90 | 0 | 144 | 0 | 100 |  | 886 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 28 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 28 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 150
Forecast for Day | 0 | 0 | 230 | 0 | 300 | 50 | 0 | 412 | 300 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 10 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 50 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 135 | 105 | 95 | 22 | 1.6 | 20 | 43 | 8 | 5 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 75 | 0 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 90 | 50 | 144 | 0 | 100 |  | 741 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 28 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 150
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 281 | 0 | 0 | 363 | 292 | 0 | 0 | 0 | 0 | 16 | 28 | 15 | 0 | 0 | 0 | 0 | 24 | 10 | 77 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 25 | 22 | 25 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 18 | 19 | 14 | 0 | 0 | 0 | 280 | 240 | 165 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 0 | 33 | 18 | 78 | 104 | 5 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 32 | 60 | 0 | 120 | 18 | 0 | 0 | 320 | 0 | 11 | 0 | 96 | 0 | 0 | 132 | 0 | 17 | 4 | 90 | 17 | 75 | 0 | 0 | 0 | 0 | 1 | 251 | 35 | 0 | 0 | 26 | 100 | 270 | 20 | 2 | 35 | 0 | 0 | 0 | 726 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 373 | 53 | 0 | 80 | 0 | 90 | 0 | 0 | 90 | 360 | 16 | 0 | 0 | 0
199
| Minimum Generation |  | 5746 | 5:00
| Highest Generation |  | 9297 | 19:00
| Day Peak Generation |  | 7758 | 12:00
| Evening Peak Generation |  | 9297 | 19:00
| HVDC Max Flow |  | 870 | 23:00
| HVDC EvPeak Flow |  | 868 | 19:00
| Load factor L.F |  | 79.21%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7758 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5711 | MW
Evening Peak Generation : |  | 9297 | MW Hour : | 19:00 | Available Max Generation : |  | 13459 | MW
E.P. Demand (at gen end) : |  | 9297 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 9297 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4059 | MW
Total Gen. (MKWH) : |  | 176.7315 | System Load Factor : | 79.21% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -95 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-19
Actual : | 96.95 | Ft.(MSL) , | Rule curve : | 99.58 | Ft.( MSL )
Gas Consumed : | Total = | 739.16 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 101027931.774
: |  | Coal : | 69845529 | Oil : | 326405937.77 | Total : | 497279398.544
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3367.9214 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1141.0745 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1021.6156 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 922.8498 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 834.1128 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 673.0889 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 381.7696 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 173.4455 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 519.0937 |  |  | 0 | 0%
Total | 0 |  | 9034.9717 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-3,4,5
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,3,5
4) Shahjibazar 330 MW
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,3 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Baroaulia-Kulshi 132 kV Ckt was under shut down from 08:38 to 15:31 for A/M.
b) Julda-Shahmirpur 132 kV Ckt-1 was under shut down from 08:24 to 15:48 for A/M.
c) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 08:27 to 16:55 for A/M.
d) Mirpur 132/33 kV T2 Transformer was under shut down from 08:27 to 20:34 for A/M
e) Kulaura-Fenchuganj 132 kV Ckt-2 was under shut down from 09:24 to 15:05 for A/M.
f) Haripur-Siddhirganj 132 kV Ckt-1 was under shut down from 08:37 to 12:22 for C/M.
g) Haripur-Siddhirganj 132 kV Ckt-2 was under shut down from 12:27 to 20:26 for C/M.
h) Ashuganj-Bhulta 400 kV Ckt-2 was under shut down from 10:16 to 16:12 for A/M.
i) Aminbazar-Manikganj 162 MW P/S 132 kV Ckt-2 was under shut down from 10:34 to 20:20 for A/M.
j) Savar-Manikganj 162 MW P/S 132 kV Ckt-1 was under shut down from 09:38 to 20:47 for D/W.
k) Mymensingh-Jamalpur 132 kV Ckt-2 was under shut down from 08:58 to 17:20 for D/W.
l) Mymensingh-Mymensingh Solar 50 MW 132 kV Ckt was under shut down from 09:14 to 20:45 for A/M.
m) Mymensingh 132 kV Bus-A was under shut down from 09:48 to 16:56 for D/W.
n) Tongi 132 kV Bus-1 was under shut down from 09:25 to 14:05 for A/M.
o) Tangail-RPCL 132 kV Ckt-2 was under shut down from 09:35 to 16:48 for A/M.
p) Kishoreganj 132/33 kV T3 Transformer is under shut down since 08:24 for A/M
q) Rajshahi(N)-Rajshahi 132 kV Ckt-1 was under shut down from 08:19 to 19:58 for A/M.
r) Bogura-Sherpur 132 kV Ckt-1 was under shut down from 11:16 to 15:39 for A/M.
s) Barisal(N)-Barisal(O) 132 kV Ckt-2 was under shut down from 08:37 to 17:03 for A/M.
t) Narail-Magura 132 kV Ckt-2 was under shut down from 07:14 to 20:12 for A/M.
u) Kustia-Jhenaidah 132 kV Ckt-2 was under shut down from 08:29 to 20:27 for A/M.
v) Bheramara S/S-Bheramara NWPGCL 132 kV Ckt was under shut down from 08:12 to 13:24 for A/M.
w) Rajshahi-HVDC 230 kV Ckt-1 is under shut down since 11:13 for D/W.
x) Rajshahi-HVDC 230 kV Ckt-2 was under shut down from 11:29 to 16:05 for D/W.
y) Rajshahi 230/132 kV ATR-2 transformer was under shut down from 10:53 to 16:28 for A/M.
z) Saidpur-Jaldhaka 132 kV Ckt-1 was under shut down from 11:05 to 13:43 for SCADA work.
aa) Baghabari 71 MW was synchronized at 12:19.
ab) Kustia 132/33 kV T2 transformer was under shut down from 11:12 to 13:42 for SPMC test.
ac) Kustia 132/33 kV T1 transformer was under shut down from 11:02 to 13:42 for C/M.
ad) New Tongi 132/33 kV T1 transformer was under shut down from 10:20 to 13:53 for C/M.
ae) Madaripur-Shariatpur 132 kV Ckt-2 was under shut down from 11:30 to 17:00 for A/M.
af) HVDC 400 kV reactor is under shut down since 15:04 for C/M.
ag) Ashuganj 132 kV reactor-1 was closed at 16:36.
ah) Netrokona 132/33 kV T4 transformer was closed at 17:05.
ai) Cumilla(N) 132/33 kV T3 transformer tripped at 18:55 showing O/C, E/F and was switched on at 19:10.
aj) Bottail 132/33 kV T1 transformer was closed at 16:40.
ak) Bheramara NWPGCL GT & ST MW were synchronized at 16:23 & 17:39 respectively.
al) Sylhet 132/33 kV T1 transformer tripped at 03:21(19/01/2021) from both side due to 33 kV U/G |  |  |  |  | About 20 MW power interruption has been occurring under Sylhet S/S
cable burst. |  |  |  |  | area since 03:21(19/01/2021).
am) APR-Shyampur 230 kV Ckt tripped at 07:33(19/01/2021) from APR end showing E/F and was
switched on at 07:34(19/01/2021).
an) Narail-Magura 132 kV Ckt-1 is under shut down since 07:38 for A/M.
ao) APR-Shyampur 230 kV Ckt tripped at 07:40(19/01/2021) from APR end showing E/F, O/C.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 234 | 5375000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7573791 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 253000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8312600 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 221 | 6252000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 68 | 756480 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1315512
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 92159 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1370900 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 398412
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1026240 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 925776 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 379440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1160160
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 311055
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 445881 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1203540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 621300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 579100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 32532 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 478734
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 113 | 1748300 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 100 | 827688
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1558080
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2355840
| Dhaka area Total |  |  |  | 6057 | 2810 | 45353520
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 34295
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 108675
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 643680
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1118836 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 230774 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 36840 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 769920 | High Voltage.
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 393408 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 608160
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 39360 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24479
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 271 | 6051927 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 872641 | Engine problem
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2254080
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 688 | 13187075
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 150 | 4049000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 6499500 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6261000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 3 | 71928 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1190902
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 75 | 1629236 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 219730 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 90 | 1701120 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 430128
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 182700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 1856640
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 720100 | Machine problem
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 17520 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 457260 | Machine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 375480 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1078 | 25862971
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2398480 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512568
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 83 | 618240 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7550
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3441600 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 80400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 7970
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 387360
| Mymensingh Area Total |  |  |  | 709 | 441 | 7454168
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1012200 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3217909 | Frequency Control
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 20 | 313800 | Gas shortage
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 10 | 279072 | Gas shortage
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 249048
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 670656 | Gas shortage
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1696320 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 3905570
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 173000 | Engine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 190136 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7269500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 193680
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 270 | 6462500 | On test
| Sylhet Area Total |  |  |  | 1988 | 1063 | 25633391
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 868 | 16631272
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2456640
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 4403808 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 185250
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 16320 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 77 | 1128000 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1455 | 24821290
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 192288 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 456400 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 85 | 1313325 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 11382900 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 13 | 944045 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1676 | 668 | 14288958
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 245000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 66112
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 194800 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 362 | 8717000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 519600
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224442
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 106560
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 103 | 741056
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2119296
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1839264
| Rajshahi Area Total |  |  |  | 2183 | 831 | 14773130
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3666900
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1660800
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29303
| Rangpur Area Total |  |  |  | 605 | 263 | 5357003
| Total |  |  |  | 20748 | 9297 | 176731506
| Eastern Grid Total |  |  |  | 14000 | 6080 | 117491125
| Western Grid Total |  |  |  | 6748 | 3217 | 59240381
| National Grid Total |  |  |  | 20748 | 9297 | 176731506
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-18
| (a) ENTIRE EASTERN GRID : |  | 5956 | MW | (b) ENTIRE WESTERN GRID : |  | 2971 | MW
| i) Dhaka area |  | 3087 | MW | i) Khulna area |  | 1092 | MW
| ii) Chittagong area |  | 984 | MW | ii) Rajshahi area |  | 966 | MW
| iii) Comilla area |  | 748 | MW | iii) Barisal area |  | 242 | MW
| iv) Mymensingh area |  | 806 | MW | iv) Rangpur area |  | 671 | MW
| v) Sylhet area |  | 331 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8927 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 12:00 | Jamalpur | 95 | 18:30 | Benapol | 46 | 19:00
| Munsiganj | 80 | 19:30 | Sherpur | 112 | 18:00 | Jhenida | 83 | 18:30
| Sonargaon | 54 | 0:00 | Srimongal | 31 | 18:30 | Bottail | 100 | 18:30
| Shyampur | 172 | 10:00 | Shahjibazar | 90 | 18:30 | G.K Project | 36 | 18:30
| Bhulta | 152 | 0:00 | Fenchuganj | 26 | 18:30 | Faridpur | 134 | 18:30
| Madanganj | 56 | 10:00 | Kulawara | 27 | 18:30 | Madaripur | 63 | 19:30
| Shitalakhya | 98 | 11:00 | Sylhet | 72 | 14:00 | Sariatpur | 46 | 20:00
| Rahim steel | 22 | 9:00 | Chatak | 19 | 18:00 | Gopalganj | 66 | 18:30
| Matuail | 42 | 10:00 | Sunamganj | 29 | 20:00 | Bagerhat | 79 | 20:00
| Ghorasal | 65 | 18:00 | Biani Bazar | 40 | 18:30 | Mongla | 38 | 10:00
| Narsingdi | 127 | 19:30 | Comilla (S) | 110 | 19:30 | Satkhira | 72 | 18:30
| Haripur (SBU) | 98 | 20:00 | Comilla(N) | 89 | 18:30 | Gallamari | 17 | 13:00
| Ullon | 40 | 18:00 | Chandpur | 56 | 19:30 | Magura | 40 | 18:30
| Hasnabad | 125 | 19:30 | Feni | 74 | 18:30 | Norail | 24 | 18:30
| Magbazar | 64 | 14:00 | Chowmuhani | 118 | 19:00 | Chuadanga | 65 | 18:30
| Maniknagar | 60 | 12:00 | Ashuganj | 39 | 19:00 | Barisal(N) | 27 | 19:30
| Bangabhaban | 14 | 12:00 | Daudkandi | 94 | 19:30 | Barisal (S) | 76 | 20:00
| Narinda | 70 | 13:00 | B.Baria | 100 | 20:00 | Patuakhali | 83 | 18:30
| Dhanmondi | 89 | 13:00 | Ramganj | 74 | 20:00 | Bhandaria | 40 | 19:00
| Lalbag | 67 | 18:30 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 21:00
| Madartek | 43 | 20:00 | PHP | 7 | 18:30 | Ishurdi | 46 | 19:30
| Dhaka University |  |  | Madunaghat | 46 | 18:30 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 65 | 0.77083 | Natore | 88 | 0.77083
| Fatullah | 45 | 9:00 | Khulshi | 167 | 11:00 | Bogra | 121 | 19:00
| Mirpur | 72 | 18:30 | Halishahar | 87 | 18:00 | Noagaon | 86 | 9:00
| Kalyanpur | 69 | 18:00 | Baraulia | 121 | 16:00 | Rajshahi | 98 | 20:00
| Gulshan | 74 | 13:00 | Sikalbaha | 20 | 18:00 | Rajshahi New | 12 | 20:00
| Uttara | 59 | 13:00 | Dohazari | 62 | 19:00 | C.Nawabganj | 59 | 19:00
| Uttara New | 28 | 18:00 | Cox'sbazar | 73 | 21:00 | Amnura | 44 | 19:00
| Kamrangirchar | 68 | 18:30 | Chandraghona | 22 | 18:00 | Pabna | 65 | 18:30
| Savar | 118 | 18:30 | Kaptai | 3.6 | 18:00 | Shahjadpur | 78 | 18:00
| Bhasantec | 98 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 69 | 19:30
| Agargaon | 46 | 13:00 | Bakulia | 72 | 18:30 | Niyamatpur | 75 | 19:00
| Satmosjid | 63 | 0.58333 | Julda | 19 | 0.5 | Joypurhat | 57 | 0.83333
| Tongi | 86 | 18:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 44 | 18:30
| Kabirpur | 182 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 19:30
| Basundhara | 89 | 18:00 | Shahmirpur | 18.2 | 18:00 | Bangura | 15 | 18:00
| Manikganj | 60 | 18:30 | Khagrachhari | 18 | 18:30 | Rangpur | 119 | 18:30
| Joydevpur | 124 | 18:30 | Matarbari | 26 | 18:30 | Lalmonirhat | 55 | 18:30
| New Tongi | 85 | 9:00 | Baroiar Hat | 26 | 18:00 | Saidpur | 97 | 18:30
| Kodda | 181 | 18:30 | Rangamati | 8 | 12:00 | Purbasadipur | 90 | 18:30
| Dhamrai | 58 | 18:30 | Abul Khair 230 | 152 | 12:00 | Thakurgaon | 60 | 18:30
| Rajendrapur | 68 | 18:30 | BSRM | 158 | 9:00 | Palashbari | 103 | 18:30
| Valuka | 88 | 18:00 | GPH Ispat | 91 | 10:00 | Barapukuria | 48 | 21:00
| Tangail | 150 | 18:30 | Goalpara | 16 | 18:30 | Panchagar | 44 | 18:30
| Mymensing | 163 | 19:00 | Central s/s | 78 | 18:30 | Joldhaka | 32 | 18:30
| Kishorganj | 98 | 19:00 | Noapara | 55 | 18:30 | Kurigram | 45 | 19:30
| Netrokona | 109 | 19:00 | Jessore | 84 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 20:00 | 409 | 12:00 | Kaliakoir | 401 | 0.16667 | 386 | 0.66667
| Bheramara | 410 | 18:30 | 393 | 19:30 | Bhulta | 394 | 0.83333 | 380 | 0.5
| Ashuganj(N) | 399 | 21:00 | 390 | 12:00 | Gopalganj | 410 | 0.125 | 399 | 0.77083
| Payra | 414 | 20:00 | 408 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 18:00 | Hathazari | 227 | 5:00 | 219 | 10:00
| Ishurdi | 245 | 1:00 | 228 | 12:00 | Megnaghat | 238 | 19:00 | 229 | 15:00
| Ashuganj | 244 | 1:00 | 238 | 8:00 | Fenchuganj | 246 | 6:00 | 239 | 5:00
| Serajganj | 235 | 1:00 | 226 | 12:00 | Siddhirganj | 236 | 18:30 | 231 | 15:00
| Baghabari | 242 | 19:00 | 236 | 23:00 | Maniknagar | 235 | 20:00 | 229 | 12:00
| Barapukuria | 232 | 22:00 | 227 | 18:00 | Agargaon | 236 | 5:00 | 228 | 12:00
| Bogra | 235 | 1:00 | 228 | 12:00 | Barisal | 251 | 20:00 | 246 | 10:00
| Rajshahi | 240 | 22:00 | 225 | 8:00 | Bhola 225 MW | 253 | 6:00 | 246 | 10:00
| Khulna South | 247 | 1:00 | 232 | 8:00 | AKSML | 230 | 20:00 | 218 | 12:00
| Rampura | 233 | 18:30 | 229 | 16:00 | BSRM | 231 | 18:30 | 219 | 17:00
| Haripur | 236 | 20:00 | 229 | 11:00 | Bibiyana | 424 | 14:00 | 238 | 5:00
| Hasnabad | 232 | 2:00 | 230 | 1:00 | Bhulta | 238 | 18:30 | 230 | 12:00
| Shyampur | 235 | 20:00 | 220 | 12:00 | Ashuganj (S) | 240 | 18:30 | 235 | 12:00
| Aminbazar | 237 | 19:00 | 232 | 3:00 | Kaliakoir | 236 | 21:00 | 226 | 16:00
| Tongi | 230 | 9:00 | 222 | 16:00 | GPH | 226 | 18:00 | 221 | 4:00
| Comilla (N) | 240 | 20:00 | 233 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 18:30 | 135 | 2:00 | Madanhat | 140 | 0.33333 | 134 | 0.95833
| Munsiganj | 141 | 18:00 | 133 | 23:00 | Hathazari | 139 | 0.77083 | 134 | 0.41667
| Sonargaon | 137 | 18:00 | 133 | 7:00 | Khulshi | 137 | 0.33333 | 132 | 0.5
| Shyampur | 135 | 19:00 | 130 | 12:00 | Halishahar | 139 | 0.77083 | 134 | 0.5
| Bhulta | 136 | 18:00 | 132 | 11:00 | Baraulia | 137 | 0.875 | 128 | 0.66667
| Madanganj | 139 | 19:30 | 132 | 23:00 | Sikalbaha | 139 | 0.33333 | 135 | 0.41667
| Shitalakhya | 139 | 18:30 | 130 | 16:00 | Dohazari | 137 | 0.77083 | 131 | 0.5
| Rahim steal | 138 | 18:30 | 135 | 11:00 | Cox'sbazar | 127 | 0.125 | 118 | 0.75
| Matuail | 139 | 18:30 | 135 | 2:00 | Chandraghona | 138 | 0.77083 | 132 | 0.70833
| Ghorasal | 140 | 1:00 | 138 | 9:00 | Kaptai | 140 | 0.75 | 132 | 0.66667
| Narsinghdi | 136 | 18:30 | 132 | 16:00 | A. Khaer Stl. | 136 | 0.041667 | 134 | 0.5
| Haripur (SBU) | 139 | 19:00 | 134 | 1:00 | Bakulia | 137 | 0.33333 | 133 | 0.20833
| Ullon | 134 | 4:00 | 129 | 12:00 | Julda | 140 | 0.29167 | 134 | 0.58333
| Hasnabad | 136 | 6:00 | 129 | 16:00 | TK Chemical | 138 | 0.375 | 133 | 0.25
| Magbazar | 134 | 3:00 | 130 | 11:00 | Modern Steel | 139 | 0.25 | 131 | 0.70833
| Maniknagar | 139 | 4:00 | 136 | 12:00 | Shahmirpur | 139 | 0.33333 | 134 | 0.625
| Bangabhaban | 139 | 4:00 | 136 | 12:00 | Khagrachhari | 138 | 0.77083 | 133 | 0.41667
| Narinda | 139 | 4:00 | 136 | 12:00 | Matarbari | 129 | 0.375 | 116 | 0.8125
| Dhanmondi | 134 | 4:00 | 129 | 12:00 | Baroiar Hat | 138 | 0.5 | 134 | 0.70833
| Lalbag | 137 | 7:00 | 131 | 12:00 | Rangamati | 140 | 6:00 | 132 | 13:00
| Madartek | 134 | 7:00 | 130 | 12:00 | Goalpara S/S | 140 | 1:00 | 131 | 12:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Khulna Central S/S | 140 | 1:00 | 130 | 0.5
| Aftabnagar | 134 | 19:30 | 130 | 11:00 | Noapara | 137 | 3:00 | 127 | 0.29167
| Fatuiiah | 135 | 19:00 | 130 | 10:00 | Jessore | 135 | 5:00 | 121 | 0.33333
| Mirpur | 138 | 22:00 | 131 | 16:00 | Benapol | 136 | 0.25 | 123 | 0.5
| Kalyanpur | 137 | 18:00 | 133 | 8:00 | Jhenida | 136 | 3:00 | 119 | 0.5
| Gulshan | 134 | 7:00 | 130 | 12:00 | Bottail | 138 | 0.25 | 127 | 0.5
| Uttara | 138 | 20:00 | 132 | 12:00 | G.K Project | 141 | 0.041667 | 132 | 0.5
| Uttara New | 139 | 18:30 | 133 | 15;00 | Faridpur | 137 | 0.125 | 132 | 0.5
| Kamrangirchar | 135 | 6:00 | 129 | 11:00 | Madaripur | 142 | 0.16667 | 138 | 0.5
| Savar | 139 | 18:30 | 133 | 10:00 | Shariyatpur S/S | 142 | 5:00 | 137 | 0.5
| Bhasantec | 138 | 18:30 | 132 | 12:00 | Gopalganj | 143 | 0.083333 | 137 | 0.77083
| Agargaon | 139 | 20:00 | 134 | 12:00 | Bagerhat | 138 | 1:00 | 130 | 0.5
| Satmosjid | 138 | 7:00 | 133 | 12:00 | Mongla | 135 | 2:00 | 127 | 0.5
| Tongi | 140 | 18:00 | 136 | 23:00 | Satkhira | 139 | 2:00 | 130 | 12:00
| Kabirpur | 135 | 1:00 | 126 | 16:00 | Gallamari | 140 | 0.041667 | 130 | 0.5
| Basundhara | 139 | 21:00 | 133 | 17:00 | Magura | 136 | 3:00 | 118 | 0.5
| Manikganj | 143 | 18:30 | 137 | 16:00 | Narail | 134 | 0.25 | 119 | 0.5
| Joydevpur | 140 | 20:00 | 134 | 4:00 | Chuadanga | 134 | 3:00 | 115 | 0.5
| New Tongi | 140 | 19:00 | 134 | 16:00 | Barisal(N) | 142 | 1:00 | 139 | 12:00
| Kodda | 140 | 18:00 | 132 | 23:00 | Barisal (S) | 141 | 0.16667 | 137 | 0.41667
| Dhamrai | 134 | 1:00 | 127 | 13:00 | Patuakhali(S) | 138 | 0.041667 | 136 | 0.5
| Rajendrapur | 140 | 19:30 | 134 | 17:00 | Bhandaria | 141 | 0.20833 | 135 | 0.75
| Valuka | 125 | 0:00 | 115 | 8:00 | Ishurdi | 140 | 1:00 | 131 | 12:00
| Tangail | 134 | 1:00 | 126 | 11:00 | Ruppur Paromanobik | 139 | 1:00 | 132 | 7:00
| Mymensing | 129 | 1:00 | 119 | 8:00 | Natore | 139 | 1:00 | 130 | 8:00
| Kishorganj | 128 | 3:00 | 122 | 8:00 | Bogra | 139 | 1:00 | 133 | 12:00
| Netrokona | 124 | 1:00 | 115 | 8:00 | Noagaon | 134 | 1:00 | 126 | 13:00
| Jamalpur | 138 | 11:00 | 121 | 6:00 | Rajshahi | 138 | 1:00 | 129 | 8:00
| Sherpur | 137 | 11:00 | 119 | 6:00 | Rajshahi New | 138 | 2:00 | 128 | 8:00
| Srimongal | 136 | 4:00 | 135 | 1:00 | C.Nawabganj | 135 | 2:00 | 126 | 8:00
| Shahjibazar | 134 | 4:00 | 132 | 17:00 | Amnura | 137 | 1:00 | 125 | 8:00
| Fenchuganj | 137 | 6:00 | 135 | 12:00 | Pabna | 140 | 1:00 | 130 | 12:00
| Khulawara | 138 | 5;00 | 135 | 12:00 | Shahjadpur | 142 | 1:00 | 136 | 8:00
| Sylhet | 135 | 1:00 | 134 | 10:00 | Serajganj | 137 | 1:00 | 132 | 12:00
| Chatak | 135 | 2:00 | 133 | 12:00 | Niyamatpur | 133 | 2:00 | 122 | 10:00
| Sunamganj | 135 | 1:00 | 133 | 12:00 | Joypurhat | 134 | 2:00 | 123 | 12:00
| Biani Bazar | 136 | 1:00 | 133 | 12:00 | Sherpur(Bogura) | 140 | 1:00 | 132 | 12:00
| Comilla(s) | 130 | 1:00 | 127 | 18:00 | Mohastangor | 137 | 4:00 | 132 | 8:00
| Comilla(n) | 142 | 8:00 | 139 | 16:00 | Bangura | 140 | 1:00 | 134 | 10:00
| Chandpur | 143 | 11:00 | 140 | 7:00 | Rangpur | 130 | 3:00 | 122 | 18:00
| Feni | 140 | 18:00 | 134 | 16:00 | Lalmonirhat | 131 | 5:00 | 120 | 18:30
| Chowmuhani | 137 | 18:30 | 132 | 18:00 | Saidpur | 132 | 3:00 | 120 | 18:30
| Ashuganj | 136 | 1:00 | 134 | 8:00 | Purbasadipur | 132 | 6:00 | 120 | 12:00
| Daudkandi | 140 | 18:30 | 136 | 12:00 | Thakurgaon | 130 | 24:00 | 120 | 8:00
| B.Baria | 132 | 10:00 | 130 | 21:00 | Palashbari | 134 | 5:00 | 126 | 18:00
| Ramganj | 136 | 18:30 | 133 | 17:00 | Barapukuria | 131 | 1:00 | 127 | 18:00
| Chaddagram | 140 | 7:00 | 136 | 16:00 | Panchagar | 31 | 6:00 | 118 | 12:00

## L-Curve
Date | 2021-01-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 205 | 4726 | 2397 | 7123 |  |  |  | QF-LDC-11
0:30 | 180 | 4555 | 2296.5 | 6851.5 | Date: | 2021-01-18
1:00 | 155 | 4384 | 2196 | 6580
1:30 | 145 | 4231 | 2112.5 | 6343.5
2:00 | 135 | 4078 | 2029 | 6107
2:30 | 132.5 | 4042.5 | 1979.5 | 6022 | [5 empty] | Gen. at Eve. Peak | 9297 | 9297 MW (19:00 )
3:00 | 130 | 4007 | 1930 | 5937 | [6 empty] | 19:00
3:30 | 137.5 | 3937.5 | 1924.5 | 5862 | [5 empty] | Gen. at Day Peak | 7758 | 7758 MW (12:00 )
4:00 | 145 | 3868 | 1919 | 5787 | [6 empty] | 12:00
4:30 | 155.5 | 3852 | 1914.5 | 5766.5 | [5 empty] | Highest Generation | 9297
5:00 | 166 | 3836 | 1910 | 5746 | [6 empty] | 19:00
5:30 | 147 | 3903 | 1907.5 | 5810.5
6:00 | 128 | 3970 | 1905 | 5875
6:30 | 111.5 | 4103 | 1857.5 | 5960.5
7:00 | 95 | 4236 | 1810 | 6046
7:30 | 90.5 | 4430.5 | 2010 | 6440.5
8:00 | 86 | 4625 | 2210 | 6835
8:30 | 83.5 | 4833 | 2313 | 7146
9:00 | 81 | 5041 | 2416 | 7457
9:30 | 57 | 5165 | 2392 | 7557
10:00 | 33 | 5289 | 2368 | 7657
10:30 | 50.5 | 5298.5 | 2382 | 7680.5
11:00 | 68 | 5308 | 2396 | 7704
11:30 | 47 | 5346 | 2385 | 7731
12:00 | 26 | 5384 | 2374 | 7758
12:30 | 24.5 | 5435.5 | 2417 | 7852.5
13:00 | 23 | 5487 | 2460 | 7947
13:30 | 54.5 | 5429.5 | 2436.5 | 7866
14:00 | 86 | 5372 | 2413 | 7785
14:30 | 151 | 5333.5 | 2377 | 7710.5
15:00 | 216 | 5295 | 2341 | 7636
15:30 | 238 | 5210 | 2278.5 | 7488.5
16:00 | 260 | 5125 | 2216 | 7341
16:30 | 244 | 5164.5 | 2252.5 | 7417
17:00 | 228 | 5204 | 2289 | 7493
17:30 | 135 | 5458.5 | 2557.5 | 8016
18:00 | 42 | 5713 | 2826 | 8539
18:30 | 48 | 5896.5 | 3021.5 | 8918
19:00 | 54 | 6080 | 3217 | 9297
19:30 | 57 | 6054 | 3226 | 9280
20:00 | 78 | 5987 | 3180 | 9167 |  |  |  | Executive Engineer
20:30 | 101 | 5886 | 3149.5 | 9035.5 |  |  |  | Network Operation Division
21:00 | 124 | 5785 | 3119 | 8904
21:30 | 248.5 | 5548 | 3103 | 8651
22:00 | 373 | 5311 | 3087 | 8398 |  |  |  |  | Page 6 of 7
22:30 | 376.5 | 5093 | 2934.5 | 8027.5
23:00 | 380 | 4875 | 2782 | 7657
23:30 | 292.5 | 4800.5 | 2589.5 | 7390
24:00 | 205 | 4726 | 2397 | 7123
9297 MW (19:00 )
7758 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-18 |  | Energy | 176731506
[11 empty] | 2021-01-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2913 | 633 | 1403 | 1693 | 610 | 47 | 32 | 0 | 80 | 0
0:30 | 2856 | 539 | 1391 | 1470.5 | 599.5 | 47.5 | 16 | 0 | 76 | 0 | Date: | 2021-01-18
1:00 | 2799 | 445 | 1379 | 1248 | 589 | 48 | 0 | 0 | 72 | 0
1:30 | 2791.5 | 445 | 1377.5 | 1020.5 | 589 | 48 | 0 | 0 | 72 | 0 | [7 empty] | Total Energy | 176.7315 | Total Energy Gen 176.732 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.732 MKWHr
2:00 | 2784 | 445 | 1376 | 793 | 589 | 48 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2780 | 445 | 1382.5 | 716.5 | 579.5 | 46.5 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 176.7315
3:00 | 2776 | 445 | 1389 | 640 | 570 | 45 | 0 | 0 | 72 | 0
3:30 | 2783 | 445 | 1392.5 | 554.5 | 570 | 45 | 0 | 0 | 72 | 0 | [6 empty] | Shortage
4:00 | 2790 | 445 | 1396 | 469 | 570 | 45 | 0 | 0 | 72 | 0
4:30 | 2770 | 444.5 | 1397 | 469 | 570 | 45 | 0 | 0 | 71 | 0
5:00 | 2750 | 444 | 1398 | 469 | 570 | 45 | 0 | 0 | 70 | 0
5:30 | 2678 | 477.5 | 1408 | 560 | 570 | 45 | 0 | 0 | 72 | 0
6:00 | 2606 | 511 | 1418 | 651 | 570 | 45 | 0 | 0 | 74 | 0
6:30 | 2494 | 572.5 | 1385.5 | 823.5 | 570 | 43.5 | 0 | 0 | 71 | 0.5 |  |  |  |  | Coal
7:00 | 2382 | 634 | 1353 | 996 | 570 | 42 | 0 | 0 | 68 | 1
7:30 | 2383 | 680 | 1338 | 1338.5 | 580 | 42.5 | 0 | 0 | 73 | 5.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2384 | 726 | 1323 | 1681 | 590 | 43 | 0 | 0 | 78 | 10
8:30 | 2415.5 | 726 | 1396 | 1866.5 | 595 | 43.5 | 15 | 0 | 73 | 15.5
9:00 | 2447 | 726 | 1469 | 2052 | 600 | 44 | 30 | 0 | 68 | 21
9:30 | 2416.5 | 726 | 1405 | 2224 | 590 | 45 | 60.5 | 0 | 69 | 21
10:00 | 2386 | 726 | 1341 | 2396 | 580 | 46 | 91 | 0 | 70 | 21
10:30 | 2376.5 | 726.5 | 1335.5 | 2436 | 580 | 46 | 91 | 0 | 66 | 23
11:00 | 2367 | 727 | 1330 | 2476 | 580 | 46 | 91 | 0 | 62 | 25
11:30 | 2372.5 | 726.5 | 1315.5 | 2511 | 580 | 46.5 | 91 | 0 | 62 | 26
12:00 | 2378 | 726 | 1301 | 2546 | 580 | 47 | 91 | 0 | 62 | 27
12:30 | 2394.5 | 726 | 1333 | 2592 | 580 | 47 | 91 | 0 | 62 | 27
13:00 | 2411 | 726 | 1365 | 2638 | 580 | 47 | 91 | 0 | 62 | 27
13:30 | 2411 | 726 | 1365 | 2638 | 580 | 47 | 91 | 0 | 62 | 27
14:00 | 2411 | 726 | 1365 | 2638 | 580 | 47 | 91 | 0 | 62 | 27
14:30 | 2452.5 | 726 | 1317 | 2493 | 580 | 47 | 91 | 0 | 63 | 22
15:00 | 2494 | 726 | 1269 | 2348 | 580 | 47 | 91 | 0 | 64 | 17
15:30 | 2511.5 | 726.5 | 1261 | 2220.5 | 565 | 47 | 83 | 0 | 61 | 13
16:00 | 2529 | 727 | 1253 | 2093 | 550 | 47 | 75 | 0 | 58 | 9
16:30 | 2535 | 727 | 1295.5 | 2093 | 550 | 47 | 99.5 | 0 | 65 | 5
17:00 | 2541 | 727 | 1338 | 2093 | 550 | 47 | 124 | 0 | 72 | 1
17:30 | 2586.5 | 797.5 | 1389.5 | 2343.5 | 555 | 46.5 | 213 | 0 | 84 | 0.5
18:00 | 2632 | 868 | 1441 | 2594 | 560 | 46 | 302 | 0 | 96 | 0
18:30 | 2732 | 868 | 1389 | 2852 | 605 | 45.5 | 324.5 | 0 | 102 | 0
19:00 | 2832 | 868 | 1337 | 3110 | 650 | 45 | 347 | 0 | 108 | 0
19:30 | 2850 | 869 | 1454 | 2989 | 650 | 44 | 314 | 0 | 110 | 0
20:00 | 2843 | 868 | 1388 | 2953 | 650 | 45 | 312 | 0 | 108 | 0
20:30 | 2848.5 | 868 | 1369.5 | 2859.5 | 650 | 45 | 291 | 0 | 104 | 0
21:00 | 2854 | 868 | 1351 | 2766 | 650 | 45 | 270 | 0 | 100 | 0
21:30 | 2862 | 868.5 | 1352 | 2536.5 | 650 | 45.5 | 236.5 | 0 | 100 | 0
22:00 | 2870 | 869 | 1353 | 2307 | 650 | 46 | 203 | 0 | 100 | 0
22:30 | 2878 | 869.5 | 1371.5 | 2000 | 640 | 46 | 126.5 | 0 | 96 | 0
23:00 | 2886 | 870 | 1390 | 1693 | 630 | 46 | 50 | 0 | 92 | 0
23:30 | 2899.5 | 751.5 | 1396.5 | 1693 | 620 | 46.5 | 41 | 0 | 86 | 0 | Max Temp. in Dhaka |  | 23.9° C
24:00 | 2913 | 633 | 1403 | 1693 | 610 | 47 | 32 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 176.732 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.732 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 48 | 48 | 45 | 45 | 45 | 45 | 42 | 43 | 44 | 46 | 46 | 47 | 47 | 48 | 47 | 47 | 47 | 46 |  | 45 | 44 | 45 | 45 | 46 | 46 | 47 | 1118836
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 17 | 25 |  |  |  |  | 0 | 34295
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 16 | 16 | 14 | 11 | 6 | 1 | [9 empty] | 108675
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 51 | 34 | 34 | 34 |  |  | 0 | 230774
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 148 |  |  |  |  | 7 | 97 | 136 | 204 | 275 | 300 | 300 | 300 | 300 | 245 | 245 | 245 | 249 |  | 300 | 300 | 300 | 300 | 300 | 200 | 145 | 478734
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 235 | 247 | 238 | 237 | 237 | 237 | 237 | 238 | 234 | 236 | 234 |  | 234 | 233 | 234 | 234 | 237 | 233 | 233 | 5375000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 260 | 250 | 250 | 250 | 250 | 300 | 366 | 380 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 7573791
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 71928
33 | Ashuganj 225 MW CCPP | 180 | 186 | 185 | 185 | 182 | 181 | 177 | 175 | 172 | 177 | 180 | 180 | 178 | 174 | 160 | 156 | 150 | 149 |  | 150 | 144 | 137 | 133 | 135 | 152 | 160 | 4049000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 250 |  | 250 | 250 | 240 | 240 | 240 | 240 | 240 | 6261000
| Ashuganj 450 MW CCPP(North) | 260 | 265 | 260 | 260 | 265 | 265 | 260 | 260 | 265 | 260 | 260 | 265 | 260 | 260 | 260 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6499500
35 | Ashuganj 55 MW PP (Precision) | [25 empty] | 0 | 0
36 | Chandpur 150 MW CCPP | [19 empty] | 40 | 50 | 45 | 42 | 46 | 46 | 46 | 219730
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 369 | 345 | 354 | 365 | 351 | 347 | 332 | 350 | 360 | 340 | 326 | 330 | 329 | 328 | 330 | 327 | 336 | 347 |  | 329 | 326 | 326 | 326 | 332 | 338 | 346 | 8312600
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 235 | 264 | 277 | 288 | 288 | 306 | 302 | 273 | 288 | 278 | 285 | 277 | 277 | 277 | 277 | 279 | 269 | 262 |  | 221 | 211 | 214 | 190 | 180 | 222 | 264 | 6252000
42 | RPCL 210MW CCPP | 107 | 108 | 108 | 108 | 107 | 105 | 105 | 104 | 105 | 103 | 98 | 96 | 96 | 87 | 85 | 85 | 103 | 104 |  | 104 | 104 | 104 | 102 | 102 | 109 | 109 | 2398480
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 7 | [17 empty] | 7970
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1012200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 32 | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 670656
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 70 | 70 | 70 | 70 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 69 | 70 | 70 | 69 | 69 | 69 |  | 72 | 72 | 73 | 73 | 73 | 73 | 73 | 1696320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 161 | 161 | 160 | 163 | 162 | 162 | 162 | 162 | 163 | 163 | 162 | 163 | 163 | 163 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3905570
51 | Sylhet 20 MW GTPP | [13 empty] | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 173000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 193680
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249048
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 8 | 8 | 313800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190136
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 300 | 300 | 290 | 300 | 300 | 280 | 305 | 340 | 310 | 280 | 280 | 290 | 275 | 270 | 265 | 290 | 300 |  | 280 | 330 | 295 | 280 | 270 | 280 | 290 | 7269500
| Bibiyana South 400 MW | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 265 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6462500
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 |  | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 445881
59 | Tangail Palli Power Gen 22 MW | 25 |  |  |  |  | 5 | 25 | 24 | 18 | 25 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 24 | 24 | 24 | 24 | 24 |  | 0 | 387360
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 19 | 19 | 19 | 393408
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 398412
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512568
63 | Impoprt (Tripura) | 72 | 72 | 72 | 72 | 70 | 74 | 68 | 78 | 68 | 70 | 62 | 62 | 62 | 68 | 64 | 58 | 72 | 96 |  | 108 | 110 | 108 | 100 | 100 | 92 | 80 | 1856640
64 | Malancha, Ctg. EPZ (United) | 32 | 42 | 42 | 42 | 42 | 42 | 40 | 15 | 7 | 5 | 4 | 8 | 12 | 10 | 5 | 8 | 12 | 13 |  | 22 | 26 | 29 | 35 | 35 | 34 | 34 | 608160
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 12 | 19 | 430128
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 8 | 182700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 |  |  |  | 17 | 33 | 33 | 33 | 33 | 720100
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  | 18 | 20 | 18 | 18 | 21 | 21 | 457260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 0 | 10 | 22 | 10 | 10 | 12 | 12 | 17 | 31 | 31 | 31 | 31 | 31 | 18 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 603540
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 621300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 17 | 25 | 25 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 579100
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 |  |  |  | 0 | 253000
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 8 | [9 empty] | 9 | 31 | 55 | 55 | 25 | 25 | 25 | 25 |  | 26 | [5 empty] | 0 | 375480
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 90 | 90 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2355840
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 2 | 22 | 50 | 70 | 70 | 70 | 80 | 100 | 100 | 70 | 40 | 50 |  | 90 | 70 | 70 | 48 |  |  | 0 | 1026240
78 | Gazipur 52 MW PP | [17 empty] | 14 |  | 8 | 8 |  |  |  |  | 0 | 32532
79 | Kodda 150MW PP | [8 empty] | 30 | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 64 | 115 |  | 150 | 150 | 150 | 133 | 100 | 50 | 32 | 1160160
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 14 | 48 | 48 | 48 | 25 | 24 | 24 | 8 | 8 | 38 |  | 83 | 81 | 81 | 82 | 16 | 8 | 8 | 618240
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 8 | [8 empty] | 17520
| Gazipur 100 MW PP | [8 empty] | 12 | 70 | 72 | 72 | 102 | 52 | 52 | 17 | 17 | 58 |  | 100 | 72 | 72 | 35 |  |  | 0 | 827688
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 24479
| Jodiac Power | 40 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 872641
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 |  |  |  | 12 | 41 | 41 | 68 | 80 | 86 | 98 | 64 | 64 | 64 | 64 | 72 |  | 100 | 101 | 101 | 101 | 64 | 18 | 16 | 1315512
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [5 empty] | 16 | 30 | 51 | 62 | 62 | 66 | 76 | 86 | 86 | 86 | 86 | 86 | 85 |  | 85 | 86 | 86 | 82 | 75 | 60 | 40 | 1370900
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 10 | 24 | 24 | 26 | 64 | 76 | 59 | 62 | 68 | 68 |  | 68 | 68 | 68 | 68 | 40 |  | 0 | 756480
| Meghnaghat 104 MW PP (OPCL) | 53 |  |  |  |  | 3 | 32 | 53 | 72 | 72 | 72 | 72 | 73 | 75 | 102 | 104 | 104 | 104 |  | 104 | 104 | 99 | 91 | 104 | 64 | 30 | 1558080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 8 | 40 | [7 empty] | 0 | 36840
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 279072
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1190902
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 3 | 24 | 64 | 64 | 64 | 64 | 32 | 32 | 32 | 32 | 50 |  | 92 | 102 | 102 | 102 | 24 | 24 | 24 | 925776
95 | Patenga 50MW PP (Baraka) | 25 | 10 | [9 empty] | 15 | 48 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 19 | 643680
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 6 | 18 |  | 10 | [5 empty] | 0 | 39360
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 15 |  | 30 | 30 | 30 |  |  |  | 0 | 92159
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 17 | 17 | 17 |  | 35 | 17 | 17 |  |  |  | 0 | 311055
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3217909
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 |  | 0 | 1 | 2 | 2 | 2 | 1 | 1 | [10 empty] | 7550
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 10 | 25 | 35 | 35 | 35 | 35 | 17 | 17 |  | 54 | 54 | 54 | 35 |  |  | 0 | 379440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 90 | 32 | 16 | 16 | 16 | 16 | 25 | 125 | 172 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 160 | 168 |  | 200 | 200 | 200 | 200 | 180 | 150 | 150 | 3441600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 34 | 95 | 105 | 139 | 149 | 149 | 145 | 116 | 100 | 64 | 52 | 85 |  | 113 | 115 | 117 | 115 | 90 | 40 | 16 | 1748300
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 20 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 80 |  | 70 | 70 | 70 | 70 | 40 |  | 0 | 769920
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 50 | 34 | 34 | 36 |  | 90 | 100 | 100 | 100 | 100 | 70 | 34 | 1701120
117 | Ashuganj 150MW PP (Midland) | 75 | 73 | 50 |  |  | 43 | 76 | 75 | 75 | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 70 | 73 | 1629236
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [16 empty] | 5 | 26 |  | 8 | 8 | 8 | 8 |  |  | 0 | 80400
| Anwara 300 MW PP (United) | 234 | 234 | 200 | 161 | 161 | 216 | 215 | 283 | 306 | 297 | 303 | 303 | 255 | 255 | 253 | 253 | 253 | 253 |  | 271 | 271 | 271 | 271 | 271 | 271 | 271 | 6051927
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2254080
| Anlima Energy Ltd. | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4384 | 4078 | 4007 | 3868 | 3836 | 3970 | 4236 | 4625 | 5041 | 5289 | 5308 | 5384 | 5487 | 5372 | 5295 | 5125 | 5204 | 5713 |  | 6080 | 6054 | 5987 | 5785 | 5311 | 4875 | 4726 | 117491125
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 83 | 83 | 66 | 66 | 66 | 66 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 103 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 83 | 2456640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 70 | 70 | 70 | 76 | 77 | 77 | 77 | 77 | 77 | 77 | 77 |  | 77 | 77 | 77 | 77 | 70 | 17 | 0 | 1128000
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 57 | 57 | 57 | 56 | 57 | 58 | 24 | 26 | 41 |  |  | 7 | 31 | 33 | 17 | 16 | 55 | 55 |  | 13 | 37 | 37 | 46 | 57 | 56 | 58 | 944045
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 48 | 48 | 48 | 48 | 16 |  | 0 | 192288
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 58 | 34 | 34 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 63 | 62 | 61 | 62 | 61 | 41 | 41 | 64 |  | 85 | 85 | 87 | 88 | 88 | 88 | 74 | 1313325
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 21 | 21 | 21 | 17 | 17 | 16 | 15 | 15 | 16 | 19 | 17 | 12 | 12 | 12 | 24 |  | 22 | 23 | 24 | 22 | 23 | 23 | 21 | 456400
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 1 |  | 10 | [5 empty] | 0 | 16320
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 24 | 24 | 24 |  |  | 24 |  | 40 | 40 | 40 | 16 |  |  | 0 | 185250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 445 | 445 | 445 | 445 | 444 | 511 | 634 | 726 | 726 | 726 | 727 | 726 | 726 | 726 | 726 | 727 | 727 | 868 |  | 868 | 869 | 868 | 868 | 869 | 870 | 633 | 16631272
147 | Bheramara 410 MW CCPP | 360 | 360 | 350 | 350 | 350 | 225 | 30 | [10 empty] | 135 |  | 345 | 345 | 340 | 345 | 345 | 345 | 345 | 4403808
148 | Payra 1320 MW | 440 | 440 | 420 | 420 | 420 | 420 | 420 | 440 | 450 | 430 | 430 | 430 | 430 | 430 | 430 | 400 | 400 | 410 |  | 500 | 500 | 500 | 500 | 500 | 480 | 460 | 11382900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3666900
153 | Baghabari 71 MW GTPP | [12 empty] | 40 | 40 | 70 | 70 | 40 | [8 empty] | 0 | 245000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 27 | 25 |  |  |  |  | 66112
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 339 | 342 | 342 | 351 | 342 | 342 | 341 | 338 | 430 | 386 | 376 | 346 | 355 | 325 | 315 | 321 | 350 | 414 |  | 362 | 410 | 370 | 370 | 379 | 383 | 358 | 8717000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 21 | 21 | 22 | 22 | 22 | 519600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224442
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 12 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 18 |  | 12 | [5 empty] | 0 | 194800
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 7 | 35 |  | 52 | 25 | 25 |  |  |  | 0 | 106560
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 60 | 102 |  | 103 | 103 | 103 | 103 | 103 |  |  | 741056
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 110 | 70 |  |  |  | 19 | 35 | 89 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 82 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2119296
172 | Confidence Power Bogura Unit-1 113 MW | 70 | [6 empty] | 75 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 100 |  | 113 | 113 | 113 | 113 | 113 | 50 | 35 | 1839264
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [5 empty] | 34 | 34 | 98 | 113 | 113 | 113 | 113 | 113 | 96 | 70 | 70 | 70 | 103 |  | 113 | 113 | 113 | 113 | 113 | 59 | 34 | 1660800
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 2 | 4 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 29303
178
178