## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:December 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | December 2020 |  | November 2020 |  | December 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9098 | 05-12-2020 | 11572 | 02-11-2020 | 8778 | 01/12/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 4945 | 19/12/20 | 5330 | 28/11/20 | 4418 | 27/12/19 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9098 | 05-12-2020 | 11572 | 02-11-2020 | 8778 | 01/12/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 7608 | 01-12-2020 | 9280 | 02-11-2020 | 7011.5 | 01/12/19 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9098 | 05/12/20 | 11572 | 02/11/20 | 8778 | 01/12/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8691.1613 |  | 9501.5333 |  | 8416.1613 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 6979.6774 |  | 7762.9 |  | 6544.6806 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 821 | 31/12/2020 | 915 | 01/11/2020 | 734 | 05/12/19 | 956 | 27/3/2019
|  |  | 19:00 |  | 19:00 |  | 21:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 120 | 03/12/2020 | 152 | 03/11/2020 | 134 | 23/12/19 | 194 | 12/06/19
|  |  | 19:00 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2669.4632 |  | 3010.001 |  | 3036.8815 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 69.6277 |  | 92.709 |  | 95.8747
22 | Net Generation of BPDB (MKWH) | 2599.8354 |  | 2917.292 |  | 2941.0068
23 | Net Generation of IPP & RPCL (MKWH) | 1680.4416 |  | 1607.0453 |  | 1215.9765
24 | Net Generation of REB (MKWH) | 124.3119 |  | 122.2164 |  | 120.3414
24 | Net Generation of Rental Power Plant (MKWH) | 305.4926 |  | 280.216 |  | 237.505
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4710.0814 |  | 4926.7697 |  | 4514.8296 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 3403.3482 |  | 3705.2202 |  | 4033.994 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 102.7579 |  | 139.7118 |  | 26.263 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 857.005 |  | 634.4156 |  | 350.3363 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 39.3592 |  | 103.6451 |  | 53.8332 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.6748 |  | 4.6869 |  | 4.8563 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 372.5639 |  | 431.7992 |  | 141.4215 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 430.7191 |  | 536.2305 |  | 270.3349 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 79.5417 |  | 66.6805 |  | 74.7384 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:December' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9098 | 05-12-2020 | 19:00
Generation Period
| Dhaka | MW | 3109
| Chattogram | MW | 1003
| Cumilla | MW | 723
| Mymensingh | MW | 674
| Sylhet | MW | 317
a) | Total supply in East zone | MW | 5826
| Khulna | MW | 1051
| Barisal | MW | 243
| Rajshahi | MW | 845
| Rangpur | MW | 587
b) | Total supply in West zone | MW | 2726
c) | Total supply in both zone ( a+b) | MW | 8552
Ref: | 27.21.0000.603.16.087.20.360 | Date: 17/01/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:December' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 480 | 08/12/20 | 8:00
| b) Ishurdi end | MW | 185 | 28/12/20 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 430 | 28/12/20 | 16:00
| b) Ishurdi end | MW | 194 | 08/12/20 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 2.211 | 30/12/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.7413 | 30/12/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 20.115
| b) Ishurdi end | MKWH | 9.3338
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 9.0538
| b) Ishurdi end | MKWH | 19.5291
23 | Transmission loss of EWI/ NO-1 | % | 2.91
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 30/12/20 | 19:00
| b)Serajganj end | MW | 400 | 21/12/20 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 290 | 21/12/20 | 15:00
| b)Sirajganj end | MW | 370 | 30/12/20 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.386 | 08/12/20
| b)Sirajganj end | MKWH |  | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH |  | -
| b)Sirajganj end | MKWH | 4.378 | 08/12/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 39.112
| b)Sirajganj end | MKWH | 30.822
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 30.238
| b)Sirajganj end | MKWH | 38.96
30 | Transmission loss of EWI /NO-2 | % | 0.619
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | 33 kV Bus | 2020-12-02 10:46 | 2020-12-02 11:25 | 1:28 | E/O | Due to SF6 gas filling at 33 kV side | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1 | 2020-12-28 10:36 | 2020-12-28 13:04 | 2:28 | T | Due to DC fail & metering problem | 110 | 271.3333 | Power interruption 10:36 to 13:04
| 132/33 kV Transformers-T2 | 2020-12-28 10:36 | 2020-12-30 01:18 | 38:42 | T
| 132/33 kV Transformers-T3 | 2020-12-28 10:36 | 2020-12-28 23:23 | 12:47 | T
|  |  | Total : | 55:25 |  | Unserved Energy: |  | 271.3333
Dhaka (South) Grid Circle :
Sonargaon | 132/33 kV Transformer-T-2 | 2020-12-04 23:28 | 2020-12-05 11:14 | 11:46 | T | Tripped showing buchholz relay at 33 kV side | 0 | 0 | No interruption
Ghorashal | 132/33 kV Transformers-T1 | 2020-12-07 13:25 | 2020-12-07 13:44 | 0:19 | T | Tripped showing O/C& E/F relay at 33 kV side | 0 | 0
| 132/33 kV Transformers-T2 | 2020-12-07 13:25 | 2020-12-07 13:45 | 0:20 | T |  | 44 | 14.6667 | Power interruption
Haripur | 230/132 kV Transformer-Tr-1 | 2020-12-10 12:14 | 2020-12-10 12:37 | 0:23 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Lalbagh | 132/33 kV Transformer-T-2 | 2020-12-16 08:00 | 2020-12-16 16:13 | 8:13 | T | Tripped showing diff.relay | 0 | 0 | No interruption
Haripur | 132 kV main Bus | 2020-12-22 12:50 | 2020-12-22 15:58 | 3:08 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-2 | 2020-12-22 21:10 | 2020-12-22 22:53 | 1:43 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 25:52 |  | Unserved Energy: |  | 14.6667
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T3 | 2020-12-08 07:44 | 2020-12-08 10:33 | 2:49 | T | Due to spark at 33 kV CB | 22 | 61.9667 | Power interruption
| 132/33 kV Transformer-T-3 | 2020-12-30 01:30 | 2020-12-30 01:58 | 0:28 | T | Tripped showing 33 kV feeder fault | 18 | 8.4 | Power interruption
|  |  | Total : | 3:17 |  | Unserved Energy: |  | 70.3667
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV Transformer-T3 | 2020-12-15 12:36 | 2020-12-15 13:56 | 1:20 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 & T4 | 2020-12-19 18:08 | 2020-12-19 18:40 | 0:32 | T | Tripped showing O/C relay at 33 kV side | 28 | 14.9333 | Power interruption
| 132/33 kV Transformer-T-3 | 2020-12-23 17:11 | 2020-12-23 19:17 | 2:06 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T-4 | 2020-12-24 22:32 | 2020-12-24 22:41 | 0:09 | T | Tripped showing O/C relay | 47 | 7.05 | Power interruption
|  |  | Total : | 4:07 |  |  |  | 21.9833
Khulna Grid Circle :
Patuakahli | 132/33 kV Transformers-T2 | 2020-12-12 15:26 | 2020-12-12 16:40 | 1:14 | E/O | Due to Oil filling | 300 | 370 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2020-12-16 23:32 | 2020-12-16 23:35 | 0:03 | T | Tripped 33 kV feeder fault | 50 | 2.5 | Power interruption
Goalpara | 132/33 kV Transformer-T6 | 2020-12-17 11:55 | 2020-12-17 12:28 | 0:33 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Mongla | 33 V bus | 2020-12-28 06:18 | 2020-12-28 06:37 | 0:19 | T | Due to bird fall | 36 | 11.4 | Power interruption
| 33 kV Bus | 2020-12-29 05:59 | 2020-12-29 06:24 | 0:28 | T | Tripped showing E/F relay | 30 | 14 | Power interruption
|  |  | Total : | 2:37 |  | Unserved Energy: |  | 397.9
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
HVDC Bheramara | HVDC Bheramara pole-2 | 2020-12-02 17:31 | 2020-12-02 18:25 | 0:54 | T | Due to tripping of all 400 kV filter | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformesr-T-01 | 2020-12-02 22:52 | 2020-12-02 23:50 | 0:58 | E/O | Due to Ishurdi-Natore 132 kV line-1 CB problem at Ishurdi S/S | 0 | 0 | No interruption
| 230/132 kV Transformers-T-03 | 2020-12-02 22:52 | 2020-12-03 00:03 | 1:11 | E/O |  | 0 | 0 | No interruption
| 230/132 kV Transformers-T-02 | 2020-12-02 22:52 | 2020-12-03 07:03 | 8:11 | E/O |  | 0 | 0 | No interruption
| 132/33 kV Transformesr-T-01 | 2020-12-02 22:52 | 2020-12-03 01:15 | 2:23 | E/O |  | 0 | 0 | No interruption
| 132/33 kV Transformesr-T-02 | 2020-12-02 22:52 | 2020-12-03 07:29 | 8:37 | E/O |  | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara pole-2 | 2020-12-07 09:58 | 2020-12-07 12:35 | 2:37 | T | Tripped showing protection relay | 0 | 0 | No interruption
| HVDC Bheramara 400 kV filter 10CF 24 | 2020-12-16 12:35 | 2020-12-16 12:35 | 0:00 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
| HVDC Bheramara 400 kV block-2 filter 10CF 24 | 2020-12-22 06:05 | 2020-12-22 06:05 | 0:00 | T | Tripped showing protection relay | 0 | 0 | No interruption
|  |  | Total : | 24:51 |  |  |  | 0
Bogura Grid Circle:
Rajshahi | 230/132 kV Transformers-T-02 | 2020-12-04 16:56 | 2020-12-04 19:13 | 2:17 | T | Tripped showing O/V relay at 33 kV side | 0 | 0 | No interruption
Niamatpur | 132/33 kV Transformer-T-3 | 2020-12-20 15:55 | 2020-12-20 17:25 | 1:30 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 3:47 |  |  |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 119:56 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kadda | Kadda-Summite 149 MW P/S 132 kV line | 2020-12-02 17:07 | 2020-12-02 20:28 | 3:21 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV line-1 | 2020-12-06 06:07 | 2020-12-06 15:45 | 9:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2020-12-06 07:07 | 2020-12-06 07:15 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kadda | Kadda-Joydevpur 132 kV line-1 | 2020-12-14 16:35 | 2020-12-14 16:50 | 0:15 | T | Tripped showing dist. relay | 50 | 12.5 | Power interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-12-25 11:38 | 2020-12-25 14:58 | 3:20 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
|  |  | Total : | 16:42 |  | Unserved Energy: |  | 12.5
Dhaka (South) Grid Circle :
Haripur | Haripur-Haripur 360 MW 132 kV line-2 | 2020-12-01 08:58 | 2020-12-01 10:45 | 1:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-12-02 22:52 | 2020-12-03 00:09 | 1:17 | T | Tripped showing dist. relay
| Ghorashal-Ishurdi 230 kV line-1 | 2020-12-10 12:49 | 2020-12-11 01:26 | 12:37 | T |  | 0 | 0 | No interruption
APR P/P | APR P/P-Shyampur S/S 230 kV line | 2020-12-15 06:42 | 2020-12-15 07:46 | 1:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-12-15 18:53 | 2020-12-15 20:47 | 1:54 | T | Tripped showing dist.C-phase relay | 68 | 19.2667 | Power interruption18:53 to 19:10
Rampura | Rampura-Ullon 132 kV line-1 | 2020-12-20 15:26 | 2020-12-20 15:46 | 0:20 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj P/S 132 kV line-1 | 2020-12-31 15:07 | 2020-12-31 16:20 | 1:13 | T | Tripped showing master protection. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-2 | 2020-12-31 15:08 | 2020-12-31 16:04 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 21:08 |  | Unserved Energy: |  | 19.2667
Chattogram Grid Circle :
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-12-27 15:48 | 2020-12-27 16:19 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:31 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV line-2 | 2020-12-03 10:04 | 2020-12-03 12:57 | 2:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2020-12-05 06:50 | 2020-12-05 07:16 | 0:26 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/P 132 kV line | 2020-12-06 00:14 | 2020-12-06 10:44 | 10:30 | T | Due tripping of MCB | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV line-1 | 2020-12-06 12:55 | 2020-12-06 13:23 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-12-25 18:50 | 2020-12-26 17:33 | 22:43 | E/O | Due to sparking wire at Tangail cantonment | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-12-29 21:18 | 2020-12-29 21:39 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 37:21 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna© | Khulna©-Noapara 132 kV line-1 | 2020-12-12 21:17 | 2020-12-12 21:27 | 0:10 | T | Tripped showing O/C.& E/F relay | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj(N) 132 kV line-1 | 2020-12-14 12:58 | 2020-12-14 15:21 | 2:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 2:33 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Baghabari | Baghabari-Ishurdi 230 kV line-1 | 2020-12-02 22:52 | 2020-12-02 23:42 | 0:50 | E/O | Due to Ishurdi-Natore 132 kV line-1 CB problem at Ishurdi S/S | 613 | 500.6167 | Power interruption:22:52 to 23:41
| Baghabari-Ishurdi 230 kV line-2 | 2020-12-02 22:52 | 2020-12-02 23:41 | 0:49 | E/O
Ishurdi | Ishurdi-HVDC 230 kV line-4 | 2020-12-02 22:52 | 2020-12-02 23:54 | 1:02 | E/O
| Ishurdi-HVDC 230 kV line-3 | 2020-12-02 22:52 | 2020-12-03 00:13 | 1:21 | E/O
HVDC | HVDC -Khulna(S) 230 kV line- 1 | 2020-12-02 22:52 | 2020-12-03 00:17 | 1:25 | E/O
| HVDC -Khulna(S) 230 kV line- 2 | 2020-12-02 22:52 | 2020-12-03 00:15 | 1:23 | E/O
| HVDC -Rajshahi 230 kV line-2 | 2020-12-02 22:52 | 2020-12-03 02:56 | 4:04 | E/O
| HVDC -Bheramara 230 kV line-1 | 2020-12-02 22:52 | 2020-12-03 00:24 | 1:32 | E/O
| HVDC -Bheramara 230 kV line-2 | 2020-12-02 22:52 | 2020-12-03 00:32 | 1:40 | E/O
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-12-02 22:52 | 2020-12-03 07:16 | 8:24 | E/O
| Ishurdi-Bheramara 132 kV line-2 | 2020-12-02 22:52 | 2020-12-03 07:17 | 8:25 | E/O
| Ishurdi-Pabna 132 kV line | 2020-12-02 22:52 | 2020-12-03 07:26 | 8:34 | E/O
| Ishurdi-Baghabari 132 kV line | 2020-12-02 22:52 | 2020-12-03 07:33 | 8:41 | E/O
Bheramara | Bheramara HVDC pole-2 | 2020-12-06 04:24 | 2020-12-06 10:54 | 6:30 | T | Tripped showing external protection trip | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2020-12-10 04:40 | 2020-12-10 14:36 | 9:56 | E/O | Due to sparking at -R-phase L/A | 0 | 0 | No interruption
Bottal | Bottail-Jhenidah 132 kV line-1 | 2020-12-18 06:59 | 2020-12-18 18:09 | 11:10 | E/O | Due to bursting of -Yphase L/A | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-12-27 11:22 | 2020-12-27 13:37 | 2:15 | E/O | Due to flashing at middle phase L/A | 0 | 0 | No interruption
|  |  | Total : | 78:01 |  | Unserved Energy: |  | 500.6167
Bogura Grid Circle:
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-12-08 06:44 | 2020-12-08 06:58 | 0:14 | T | Tripped showing A31 ful pump relay | 18 | 21 | Power interruption
Sirajganj | Sirajganj-Bogura 230 kV line-2 | 2020-12-27 19:29 | 2020-12-27 20:11 | 0:42 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
|  |  | Total : | 0:56 |  | Unserved Energy: |  | 21
Others :
Ullon | Ullon-Dhanmondi 132 kV line-3 | 2020-11-02 07:40 | 2020-11-02 16:05 | 8:25 | T | Tripped showing interconnection trip | 0 | 0 | No interruption
|  |  | Total : | 8:25 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 243:38 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | 132/33 kV Transformer-T3 | 2020-12-01 06:52 | 2020-12-01 07:50 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2020-12-01 09:15 | 2020-12-01 14:45 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-1 | 2020-12-01 08:36 | 2020-12-01 08:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-12-01 08:30 | 2020-12-01 16:29 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 200/132 kV Transformer-T2 | 2020-12-01 09:23 | 2020-12-01 14:29 | 5:06 | S/O | Due to painting work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-12-01 11:09 | 2020-12-01 14:06 | 2:57 | S/O | Due to relay test | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2020-12-02 07:30 | 2020-12-02 07:30 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-2 | 2020-12-02 08:37 | 2020-12-02 14:17 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2020-12-03 08:16 | 2020-12-03 17:11 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 | 2020-12-03 07:51 | 2020-12-03 18:08 | 10:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2020-12-04 08:54 | 2020-12-04 14:24 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-12-05 08:12 | 2020-12-05 13:56 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2020-12-06 08:05 | 2020-12-06 18:11 | 10:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-12-06 08:50 | 2020-12-06 16:50 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T02 | 2020-12-06 08:01 | 2020-12-06 19:52 | 11:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 132/33 kV Transformer-T1 | 2020-12-07 08:52 | 2020-12-07 17:38 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT4 | 2020-12-07 09:02 | 2020-12-07 16:37 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-GT1 | 2020-12-07 10:00 | 2020-12-07 14:11 | 4:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-12-07 11:48 | 2020-12-07 13:40 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-12-07 15:14 | 2020-12-07 16:18 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-12-07 16:24 | 2020-12-07 16:42 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-12-08 07:36 | 2020-12-08 17:18 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-12-08 07:36 | 2020-12-08 17:18 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-12-08 09:37 | 2020-12-08 15:19 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-12-08 12:43 | 2020-12-08 16:40 | 3:57 | S/O | Due to ten delta test | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2020-12-09 17:26 | 2020-12-09 17:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T1 | 2020-12-09 09:09 | 2020-12-09 16:15 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 132/33 kV Transformer-T1 | 2020-12-09 10:02 | 2020-12-09 16:23 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2020-12-09 10:06 | 2020-12-09 16:42 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-12-09 09:30 | 2020-12-09 15:16 | 5:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T1 | 2020-12-10 08:54 | 2020-12-10 16:04 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-12-10 09:32 | 2020-12-10 16:10 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2020-12-10 09:26 | 2020-12-10 16:53 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-11 09:09 | 2020-12-11 12:35 | 3:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T02 | 2020-12-12 09:40 | 2020-12-12 13:48 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 132/33 kV Transformer-T1 | 2020-12-12 10:22 | 2020-12-12 16:30 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-12-12 09:24 | 2020-12-12 16:26 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve Bus | 2020-12-13 07:48 | 2020-12-13 20:10 | 12:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-12-13 09:30 | 2020-12-13 16:54 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T3 | 2020-12-13 12:38 | 2020-12-13 14:03 | 1:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T-03 | 2020-12-14 09:05 | 2020-12-14 15:12 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-GT2 | 2020-12-14 10:23 | 2020-12-14 15:29 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-12-14 11:26 | 2020-12-14 16:06 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T-03 | 2020-12-15 09:28 | 2020-12-15 15:26 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T02 | 2020-12-15 08:38 | 2020-12-15 14:52 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2020-12-14 11:26 | 2020-12-14 16:06 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-15 09:15 | 2020-12-15 14:06 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT2 | 2020-12-15 09:07 | 2020-12-15 13:25 | 4:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T3 | 2020-12-17 09:22 | 2020-12-17 13:20 | 3:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T2 | 2020-12-17 08:54 | 2020-12-17 17:29 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-12-17 08:52 | 2020-12-17 20:07 | 11:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132 kV bus-2 | 2020-12-17 15:46 | 2020-12-17 17:40 | 1:54 | S/O | Due to removing kite | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T1 | 2020-12-18 07:13 | 2020-12-18 16:11 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | 132/33 kV Transformer-T1 | 2020-12-18 07:45 | 2020-12-18 20:46 | 13:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-12-19 07:52 | 2020-12-19 19:20 | 11:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T2 | 2020-12-20 08:41 | 2020-12-20 17:37 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-12-20 09:22 | 2020-12-20 17:01 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2020-12-20 08:45 | 2020-12-20 19:03 | 10:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-12-21 09:18 | 2020-12-21 16:55 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T2 | 2020-12-21 10:43 | 2020-12-21 14:22 | 3:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-21 08:51 | 2020-12-21 17:46 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-12-22 09:27 | 2020-12-22 16:45 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-12-22 09:25 | 2020-12-22 17:15 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-23 09:24 | 2020-12-23 19:22 | 9:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus-1 | 2020-12-23 09:05 | 2020-12-23 17:19 | 8:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T3 | 2020-12-23 09:13 | 2020-12-23 15:51 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-23 09:03 | 2020-12-23 16:43 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-12-23 10:31 | 2020-12-23 15:55 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 |  | 2020-12-23 19:17 |  | S/O | After maintenance work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2020-12-24 09:07 | 2020-12-24 17:33 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T3 | 2020-12-24 09:05 | 2020-12-24 17:11 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-24 09:15 | 2020-12-24 17:14 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230 kV Bus coupler | 2020-12-25 11:40 | 2020-12-25 12:04 | 0:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus coupler | 2020-12-25 12:08 | 2020-12-25 12:38 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 |  | 2020-12-25 15:48 |  | S/O | After maintenance work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2020-12-26 09:35 | 2020-12-26 16:33 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-12-26 10:04 | 2020-12-26 15:55 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-26 08:45 | 2020-12-26 16:53 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T2 | 2020-12-26 09:47 | 2020-12-26 13:54 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-12-26 18:51 | 2020-12-27 11:06 | 16:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-12-27 09:25 | 2020-12-27 20:01 | 10:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-12-27 09:39 | 2020-12-27 17:08 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-12-27 09:46 | 2020-12-27 16:09 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-12-27 16:09 | 2020-12-27 20:07 | 3:58 | S/O | Due to protection work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT3 | 2020-12-28 08:39 | 2020-12-28 20:28 | 11:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-12-28 09:38 | 2020-12-28 16:52 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-12-28 09:10 | 2020-12-28 16:32 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT3 | 2020-12-29 08:38 | 2020-12-29 09:28 | 0:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-12-29 09:02 | 2020-12-29 16:21 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T4 | 2020-12-31 08:50 | 2020-12-31 17:20 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-12-31 12:20 | 2020-12-31 13:56 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-12-31 08:38 | 2020-12-31 17:28 | 8:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-12-31 15:46 | 2020-12-31 17:17 | 1:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-12-31 14:10 | 2020-12-31 15:43 | 1:33 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 583:14 |  | Unserved Energy: |  | 0
Page: 3/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Rampura | Rampura 132 kV capacitor bank -1 | 2020-12-01 07:33 | 2020-12-01 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2020-12-01 15:51 | 2020-12-01 16:43 | 0:52 | S/O | Due to protecton test | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2020-12-05 12:11 | 2020-12-05 12:11 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Matuail | 132/33 kV Transformer-T1 | 2020-12-06 09:22 | 2020-12-06 17:01 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV capacitor bank | 2020-12-06 08:47 | 2020-12-06 14:14 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | 132/33 kV Transformer-T1 | 2020-12-07 10:03 | 2020-12-07 17:15 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-Tr-3 | 2020-12-10 09:42 | 2020-12-10 16:34 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV Transformer-Tr-02 | 2020-12-10 08:40 | 2020-12-10 17:12 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-Tr-3 | 2020-12-11 08:17 | 2020-12-11 17:09 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132 kV Bus-2 | 2020-12-11 12:17 | 2020-12-11 15:18 | 3:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T-3 | 2020-12-12 08:35 | 2020-12-12 17:02 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T-1 | 2020-12-12 11:12 | 2020-12-12 17:25 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV AutoTransformer-MTR-1 | 2020-12-13 09:11 | 2020-12-13 20:54 | 11:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV AutoTransformer-Tr-1 | 2020-12-13 09:04 | 2020-12-13 17:48 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV AutoTransformer-MTR-1 | 2020-12-14 09:25 | 2020-12-14 15:01 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV AutoTransformer-Tr-1 | 2020-12-14 09:28 | 2020-12-14 20:04 | 10:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV bay -2 | 2020-12-14 07:48 | 2020-12-14 20:10 | 12:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV AutoTransformer-T04 | 2020-12-15 08:03 | 2020-12-15 21:20 | 13:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400 kV Bus-1 | 2020-12-15 08:53 | 2020-12-15 14:44 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus-1 | 2020-12-15 08:49 | 2020-12-15 12:16 | 3:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV Bus-1 | 2020-12-15 17:20 | 2020-12-15 17:50 | 0:30 | S/O | Due to relay test | 0 | 0 | No interruption
Hasnabad | 230/132 kV AutoTransformer-Tr-02 | 2020-12-16 08:16 | 2020-12-16 20:18 | 12:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | 132/33 kV Transformer-T3 | 2020-12-17 09:40 | 2020-12-17 14:19 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230 kV Busbar-1 | 2020-12-17 08:36 | 2020-12-17 16:16 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T1 | 2020-12-17 09:10 | 2020-12-17 14:05 | 4:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2020-12-18 08:24 | 2020-12-18 13:07 | 4:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T01 | 2020-12-19 08:19 | 2020-12-19 17:29 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T2 | 2020-12-20 07:44 | 2020-12-20 16:38 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus-2 | 2020-12-20 09:03 | 2020-12-20 17:36 | 8:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T2 | 2020-12-20 09:56 | 2020-12-20 20:34 | 10:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T3 | 2020-12-20 08:17 | 2020-12-20 18:26 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV Bus-1 | 2020-12-21 08:36 | 2020-12-21 17:11 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T3 | 2020-12-22 08:06 | 2020-12-22 21:11 | 13:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 33 kV Bus-1 | 2020-12-22 08:37 | 2020-12-22 15:00 | 6:23 | S/O | Due to A/M work | 25 | 159.5833 | Power interruption
Siddhirganj | 230 kV Bus-2 | 2020-12-23 08:58 | 2020-12-23 16:10 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-Tr-03 | 2020-12-23 08:55 | 2020-12-23 15:02 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-T02 | 2020-12-26 09:47 | 2020-12-26 14:22 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2020-12-26 08:54 | 2020-12-26 16:37 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 | 2020-12-26 08:12 | 2020-12-26 09:24 | 1:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakhya | 132/33 kV Transformer-T3 | 2020-12-26 10:02 | 2020-12-26 17:15 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2020-12-26 09:33 | 2020-12-26 13:44 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-T02 | 2020-12-27 09:03 | 2020-12-27 17:12 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus-2 | 2020-12-28 09:20 | 2020-12-28 16:40 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-11 | 2020-12-29 09:42 | 2020-12-29 13:16 | 3:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakhya | 132/33 kV Transformer-GT-2 | 2020-12-28 10:02 | 2020-12-28 18:23 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV Transformer-T02 | 2020-12-28 10:41 | 2020-12-28 11:20 | 0:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2020-12-29 08:54 | 2020-12-29 20:20 | 11:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV Transformer-ATR1 | 2020-12-30 07:34 | 2020-12-30 07:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 322:21 |  | Unserved Energy: |  | 159.5833
Page: 4/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Juldah | 132/33 kV Transformer-T2 | 2020-12-01 08:25 | 2020-12-06 13:44 | 125:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2020-12-06 07:13 | 2020-12-06 09:14 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | 132 kV main Bus | 2020-12-06 06:23 | 2020-12-06 10:27 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T02 | 2020-12-08 09:30 | 2020-12-08 09:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132 kV Bus-A | 2020-12-09 09:32 | 2020-12-09 12:32 | 3:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | 132/33 kV Transformer-T1 | 2020-12-09 10:50 | 2020-12-09 13:40 | 2:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132 kV Bus-B | 2020-12-10 08:23 | 2020-12-10 16:15 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-12-10 09:33 | 2020-12-10 11:49 | 2:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-12-10 11:40 | 2020-12-10 12:27 | 0:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132 kV main Bus | 2020-12-11 06:50 | 2020-12-11 11:57 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | 230 kV Bus-1 | 2020-12-11 09:29 | 2020-12-11 09:29 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T02 |  | 2020-12-13 09:29 |  | S/O | After maintenance work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 & 33 kV Bus | 2020-12-17 07:28 | 2020-12-17 10:07 | 2:39 | S/O | Due to A/M work | 12 | 31.8 | Power interruption
Bakulia | 132/33 kV Transformer-T1 | 2020-12-18 14:26 | 2020-12-18 14:26 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV Transformer-T01 | 2020-12-18 10:54 | 2020-12-18 15:55 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2020-12-20 12:16 | 2020-12-20 22:28 | 10:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T01 |  | 2020-12-20 17:25 |  | S/O | After maintenance work | 0 | 0 | No interruption
BSRM | 230 kV Bus-1 | 2020-12-22 09:34 | 2020-12-22 20:05 | 10:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-12-22 20:42 | 2020-12-22 20:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Juldha | 132/33 kV Transformer-T1 | 2020-12-25 08:00 | 2020-12-25 15:14 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhkulia | 132/33 kV Transformer-T1 | 2020-12-28 11:50 | 2020-12-28 12:04 | 0:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-28 12:08 | 2020-12-28 12:35 | 0:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2020-12-29 11:15 | 2020-12-29 13:52 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T2 | 2020-12-31 08:44 | 2020-12-31 15:50 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-12-31 15:59 | 2020-12-31 16:45 | 0:46 | S/O | Due to tan-delta test | 0 | 0 | No interruption
|  |  | Total : | 200:03 |  | Unserved Energy : |  | 31.8
Cumilla Grid Circle :
B.Baria | 132/33 kV Transformer-T1 | 2020-12-01 08:48 | 2020-12-01 16:02 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-T01 | 2020-12-01 08:23 | 2020-12-01 15:42 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-12-02 08:16 | 2020-12-02 15:01 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2020-12-03 08:24 | 2020-12-03 16:54 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2020-12-05 08:48 | 2020-12-05 16:53 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T3 | 2020-12-05 08:10 | 2020-12-05 17:47 | 9:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2020-12-06 08:32 | 2020-12-06 19:56 | 11:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-12-07 08:25 | 2020-12-07 14:56 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2020-12-07 09:13 | 2020-12-07 10:40 | 1:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 & 132kV Bus | 2020-12-07 09:12 | 2020-12-07 10:40 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | 132/33 kV Transformer-T3 | 2020-12-08 09:03 | 2020-12-08 16:53 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2020-12-09 08:30 | 2020-12-09 16:15 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | 132/33 kV Transformer-T3 | 2020-12-09 09:38 | 2020-12-09 17:23 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2020-12-10 08:38 | 2020-12-10 15:07 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132 kV bus-1 & 2 | 2020-12-10 10:52 | 2020-12-10 16:23 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132 kV main Bus | 2020-12-11 08:17 | 2020-12-11 18:20 | 10:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T1 | 2020-12-12 08:20 | 2020-12-12 15:46 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-12-12 08:31 | 2020-12-12 08:31 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2020-12-12 10:29 | 2020-12-12 16:32 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T2 | 2020-12-13 08:26 | 2020-12-13 15:43 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 |  | 2020-12-13 20:37 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-12-13 09:00 | 2020-12-13 18:03 | 9:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132 kV Bus-1 | 2020-12-14 12:36 | 2020-12-14 15:07 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T3 | 2020-12-14 08:26 | 2020-12-14 14:31 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-12-15 09:28 | 2020-12-15 15:26 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T-04 | 2020-12-15 08:38 | 2020-12-15 14:52 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Kulaura | 132/33 kV Transformer-T2 | 2020-12-17 09:09 | 2020-12-17 16:19 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-12-17 08:17 | 2020-12-17 20:18 | 12:01 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | 132/33 kV Transformer-T2 | 2020-12-17 09:25 | 2020-12-17 12:18 | 2:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132 kV Bus | 2020-12-18 06:36 | 2020-12-18 06:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2020-12-18 10:20 | 2020-12-18 17:50 | 7:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 33 kV Bus-1 & 2 | 2020-12-19 07:36 | 2020-12-19 07:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2020-12-22 08:34 | 2020-12-22 16:17 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-12-22 14:00 | 2020-12-22 20:21 | 6:21 | S/O | Due to protection work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2020-12-23 08:28 | 2020-12-23 16:21 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2020-12-24 08:36 | 2020-12-24 17:43 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2020-12-24 08:50 | 2020-12-24 16:22 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-12-27 08:30 | 2020-12-31 20:08 | 107:38 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 340:08 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Khulna(S) | 132 kV capacitor bank | 2020-12-02 09:10 | 2020-12-02 14:25 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T1 | 2020-12-02 08:30 | 2020-12-02 15:52 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-03 08:21 | 2020-12-03 16:12 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV Transformer-T2 | 2020-12-07 10:06 | 2020-12-07 13:47 | 3:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-12-08 09:03 | 2020-12-08 12:29 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-12-09 10:18 | 2020-12-09 13:43 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2020-12-21 08:04 | 2020-12-21 17:02 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-23 08:12 | 2020-12-23 16:10 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-12-23 20:50 | 2020-12-24 14:40 | 17:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2020-12-24 08:18 | 2020-12-24 15:47 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(new) | Gopalganj(new)-Madaripur 132 kV line-1 | 2020-12-24 08:57 | 2020-12-24 16:43 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 | 2020-12-25 07:17 | 2020-12-26 17:54 | 34:37 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 115:38 |  | Unserved Energy : |  | 0:00
HVDC Grid Circle :
Ishurdi | 132 kV Bus-2 | 2020-12-02 08:24 | 2020-12-02 17:18 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC 400 kV filter 10CF26 |  | 2020-12-02 13:10 |  | S/O | After maintenace work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2020-12-05 15:13 | 2020-12-05 15:50 | 0:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T1 | 2020-12-06 08:14 | 2020-12-06 15:01 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-07 08:07 | 2020-12-07 14:44 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132 kV bus-2 | 2020-12-07 12:05 | 2020-12-07 15:38 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T3 | 2020-12-08 08:09 | 2020-12-08 15:06 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV capacitor bank | 2020-12-09 09:30 | 2020-12-09 14:36 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC pole-1 | 2020-12-11 06:17 | 2020-12-11 06:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2020-12-12 09:02 | 2020-12-12 14:37 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-13 09:03 | 2020-12-13 14:53 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230 kV bus-2 | 2020-12-15 09:30 | 2020-12-15 20:52 | 11:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-02 | 2020-12-15 09:31 | 2020-12-15 20:54 | 11:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC pole-2 | 2020-12-16 17:53 | 2020-12-16 17:53 | 0:00 | S/O | Due to filter problem | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2020-12-17 09:42 | 2020-12-17 20:05 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | 132 kV Bus-A& D | 2020-12-18 07:00 | 2020-12-18 07:00 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-A& B | 2020-12-19 07:01 | 2020-12-19 07:01 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-A& D | 2020-12-19 06:55 | 2020-12-19 16:23 | 9:28 | S/O | Due to D/W work | 96 | 908.8 | Power interruption
Ishurdi | 132 kV bus-1 | 2020-12-19 12:56 | 2020-12-19 22:12 | 9:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV bus-2 | 2020-12-19 07:06 | 2020-12-19 12:48 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC 400 kV bus-2 | 2020-12-20 07:45 | 2020-12-20 07:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132 kV bus-2 | 2020-12-20 07:06 | 2020-12-20 12:48 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T-02 | 2020-12-21 20:30 | 2020-12-21 20:42 | 0:12 | S/O | Due to CB problem | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-02 | 2020-12-23 08:11 | 2020-12-23 20:14 | 12:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2020-12-23 08:09 | 2020-12-23 16:13 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T2 | 2020-12-23 16:18 | 2020-12-23 17:11 | 0:53 | S/O | Due to protection work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-12-23 16:18 | 2020-12-23 17:11 | 0:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-02 | 2020-12-24 08:22 | 2020-12-24 20:16 | 11:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Bangura | 132 kV Grid S/S |  | 2020-12-24 22:34 |  |  | New connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 |  | 2020-12-24 22:39 |  |  |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 |  | 2020-12-24 22:42 |  |  |  | 0 | 0 | No interruption
Jhenidah | 132 kV Bus-A& B | 2020-12-26 07:12 | 2020-12-26 16:22 | 9:10 | S/O | Due to D/W work | 150 | 1375 | Power interruption
Ruppur | 132/33 kV Transformer-T-1 | 2020-12-27 08:26 | 2020-12-27 08:26 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC 400 kV 10CF25 | 2020-12-28 09:40 | 2020-12-28 14:46 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T-02 |  | 2020-12-28 15:50 |  | S/O | After maintenance work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-02 | 2020-12-28 08:21 | 2020-12-28 14:50 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T-01 | 2020-12-29 09:10 | 2020-12-29 20:23 | 11:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-03 | 2020-12-31 09:28 | 2020-12-31 18:18 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 187:59 |  | Unserved Energy : |  | 2283.8 |  | 2283.8
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformer-T-1 | 2020-12-01 08:25 | 2020-12-01 16:22 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-02 |  | 2020-12-01 09:51 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-01 | 2020-12-01 10:27 | 2020-12-01 10:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-12-02 08:02 | 2020-12-02 16:45 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-12-03 08:20 | 2020-12-03 16:35 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2020-12-05 07:56 | 2020-12-05 17:22 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-12-05 08:10 | 2020-12-05 17:10 | 9:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-3 | 2020-12-06 08:22 | 2020-12-06 16:15 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132 kV Bus-1 | 2020-12-07 10:17 | 2020-12-07 11:06 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132 kV Bus-2 | 2020-12-09 11:39 | 2020-12-09 11:39 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T4 | 2020-12-11 08:10 | 2020-12-11 15:06 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 33 kV Bus | 2020-12-11 08:30 | 2020-12-11 17:00 | 8:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T4 | 2020-12-12 08:05 | 2020-12-12 17:25 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(new) | 132/33 kV Transformer-T-1 | 2020-12-12 08:29 | 2020-12-12 17:19 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-12-13 08:28 | 2020-12-13 20:04 | 11:36 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-1 | 2020-12-13 16:38 | 2020-12-13 19:17 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(new) | 132/33 kV Transformer-T-2 | 2020-12-14 08:19 | 2020-12-14 16:34 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-12-15 08:38 | 2020-12-15 15:40 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC 230 kV line-2 | 2020-12-23 09:47 | 2020-12-23 20:51 | 11:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 & 33 kV bus | 2020-12-24 08:10 | 2020-12-24 10:30 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 230 kV Bus-1 | 2020-12-24 11:38 | 2020-12-24 13:11 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(new) | 230/132 kV Transformer-T-02 | 2020-12-26 10:27 | 2020-12-26 15:03 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-2 | 2020-12-26 09:05 | 2020-12-26 11:08 | 2:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-1 | 2020-12-26 10:15 | 2020-12-26 16:30 | 6:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-01 | 2020-12-28 08:30 | 2020-12-28 17:30 | 9:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-4 | 2020-12-28 09:13 | 2020-12-31 10:59 | 73:46 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 225:48 |  | Unserved Energy : |  | 0
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1975:11 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Mymensingh RPCL 132 kV line-2 | 2020-12-01 07:45 | 2020-12-01 17:20 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2020-12-01 07:42 | 2020-12-01 17:18 | 9:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-2 | 2020-12-01 10:38 | 2020-12-01 17:07 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2020-12-01 09:13 | 2020-12-01 16:44 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-1 | 2020-12-01 09:07 | 2020-12-01 16:56 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-12-01 11:19 | 2020-12-01 11:19 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-12-01 09:14 | 2020-12-01 16:30 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2020-12-02 07:36 | 2020-12-02 07:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2020-12-02 08:11 | 2020-12-02 16:42 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
RPCL | RPCL-Mymensigh 132 kV line-2 | 2020-12-02 08:40 | 2020-12-02 17:25 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2020-12-02 09:14 | 2020-12-02 17:07 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-1 | 2020-12-02 09:06 | 2020-12-02 16:36 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj Power 132 kV line-2 | 2020-12-02 09:27 | 2020-12-02 16:05 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda 300 MW 132 kV line | 2020-12-02 10:11 | 2020-12-02 16:37 | 6:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-2 | 2020-12-02 11:49 | 2020-12-02 17:18 | 5:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV line-2 | 2020-12-03 08:55 | 2020-12-03 15:53 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-12-03 08:11 | 2020-12-03 16:42 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL P/P 132 kV line-1 | 2020-12-03 09:01 | 2020-12-03 16:49 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
New Tongi | New Tongi-Tongi 132 kV line-2 | 2020-12-03 10:22 | 2020-12-03 14:09 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
RPCL | RPCL-Mymensigh 132 kV line-2 | 2020-12-03 08:32 | 2020-12-03 17:02 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Bhaluka 132 kv line-1 | 2020-12-05 07:45 | 2020-12-05 17:36 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV line-2 | 2020-12-05 09:05 | 2020-12-05 17:14 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2020-12-05 08:18 | 2020-12-05 16:19 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2020-12-05 09:22 | 2020-12-05 17:18 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2020-12-06 08:16 | 2020-12-06 16:23 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P132 kV line | 2020-12-06 09:22 | 2020-12-06 20:35 | 11:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-06 09:00 | 2020-12-06 17:04 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-12-06 10:33 | 2020-12-06 16:31 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-07 09:14 | 2020-12-07 17:34 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kalakoir 230 kV line-1 | 2020-12-07 10:22 | 2020-12-07 15:34 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Bhaluka 132 kv line-1 | 2020-12-08 08:25 | 2020-12-08 16:41 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Jamalpur 132 kV line-1 | 2020-12-08 09:47 | 2020-12-08 16:30 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 132 kV line-2 | 2020-12-08 10:29 | 2020-12-08 15:47 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2020-12-08 09:15 | 2020-12-08 18:04 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Kadda 132 kV line-1 | 2020-12-09 08:58 | 2020-12-09 16:13 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-1 | 2020-12-09 08:51 | 2020-12-09 15:44 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-09 09:19 | 2020-12-09 16:25 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi S/S | Tongi S/S-Kodda 300 MW P/P 230 kV line | 2020-12-09 12:57 | 2020-12-09 16:06 | 3:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2020-12-10 07:40 | 2020-12-10 07:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-1 | 2020-12-10 09:44 | 2020-12-10 12:45 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-2 | 2020-12-10 09:35 | 2020-12-10 15:06 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-10 09:13 | 2020-12-10 15:43 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2020-12-11 06:34 | 2020-12-11 17:20 | 10:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-CLC Bosila 132 kV line | 2020-12-11 06:34 | 2020-12-11 17:20 | 10:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-kodda 300 MW 230 kV line | 2020-12-11 08:36 | 2020-12-11 15:01 | 6:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2020-12-12 06:36 | 2020-12-12 16:12 | 9:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-CLC Bosila 132 kV line | 2020-12-12 06:36 | 2020-12-12 16:12 | 9:36 | S/O |  | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2020-12-12 07:55 | 2020-12-12 20:07 | 12:12 | S/O | Due to CT problem | 0 | 0 | No interruption
Page: 2/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensigh | Mymensigh-Baluka 132 kV line-2 | 2020-12-12 08:26 | 2020-12-12 16:24 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-2 | 2020-12-12 09:38 | 2020-12-12 15:59 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-12 09:17 | 2020-12-12 20:11 | 10:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-2 | 2020-12-13 08:25 | 2020-12-13 16:23 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh line-2 & aminbazar-CLC P/S 132 kV line | 2020-12-13 09:14 | 2020-12-13 16:21 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 V line-2 | 2020-12-13 09:28 | 2020-12-13 15:55 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2020-12-13 08:52 | 2020-12-13 17:07 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Jamalpur 132 kV line-1 | 2020-12-13 09:17 | 2020-12-13 20:11 | 10:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-2 | 2020-12-14 09:25 | 2020-12-14 16:38 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2020-12-14 09:02 | 2020-12-14 17:17 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-joydevpur 132 kV line-2 | 2020-12-14 10:13 | 2020-12-14 16:47 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kadda-MTR1 132 kV line-5 | 2020-12-14 09:53 | 2020-12-14 12:00 | 2:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2020-12-15 07:24 | 2020-12-15 19:10 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-2 | 2020-12-15 08:38 | 2020-12-16 14:52 | 30:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2020-12-15 09:20 | 2020-12-15 16:20 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-2 | 2020-12-15 10:53 | 2020-12-15 15:19 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2020-12-17 09:33 | 2020-12-17 17:07 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Baluka 132 kV line-2 | 2020-12-17 09:09 | 2020-12-17 17:51 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Netrakona 132 kV line-1 | 2020-12-17 09:46 | 2020-12-17 16:58 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-12-18 07:05 | 2020-12-18 12:59 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-2 | 2020-12-18 13:01 | 2020-12-18 17:09 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-12-20 09:28 | 2020-12-20 16:46 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-12-20 09:09 | 2020-12-20 16:45 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2020-12-21 08:54 | 2020-12-21 18:36 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-12-21 09:16 | 2020-12-21 17:03 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-12-21 09:10 | 2020-12-21 17:16 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2020-12-22 09:33 | 2020-12-22 15:01 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-12-22 09:27 | 2020-12-22 16:52 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-12-22 09:08 | 2020-12-22 16:44 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-2 | 2020-12-22 10:56 | 2020-12-22 16:41 | 5:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensigh-Kishoreganj 132 kV line-1 | 2020-12-22 08:34 | 2020-12-22 10:45 | 2:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2020-12-22 09:34 | 2020-12-22 17:53 | 8:19 | S/O | Due to protcetion work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2020-12-22 13:56 | 2020-12-22 17:01 | 3:05 | S/O | Due to loop refixing work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2020-12-23 09:46 | 2020-12-23 14:50 | 5:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-12-23 09:17 | 2020-12-23 16:59 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-12-23 09:26 | 2020-12-23 17:00 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-1 | 2020-12-23 10:41 | 2020-12-23 15:30 | 4:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kodda-Joydevpur 132 kV line-2 | 2020-12-23 15:33 | 2020-12-23 16:52 | 1:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Netrakona 132 kV line-1 & 2 | 2020-12-24 07:40 | 2020-12-24 13:50 | 6:10 | S/O | Due to C/M work | 55 | 339.1667 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-12-24 08:57 | 2020-12-24 16:44 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| UMPL-Sherpur 132 kV line-2 | 2020-12-24 09:26 | 2020-12-24 16:57 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2020-12-24 11:13 | 2020-12-24 15:32 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2020-12-26 09:43 | 2020-12-26 15:20 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2020-12-31 09:07 | 2020-12-31 16:36 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 666:23 |  | Unserved Energy: |  | 339.1667
Page: 3/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Haripur | Haripur-Sonargaon 132 kV line-2 | 2020-12-01 10:47 | 2020-12-01 15:28 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur (new) 132 kV line-1 | 2020-12-02 07:41 | 2020-12-04 19:21 | 59:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Ghorashal 132 kV line | 2020-12-05 09:02 | 2020-12-05 17:12 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur (new) 132 kV line-2 | 2020-12-06 07:40 | 2020-12-06 07:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2020-12-06 08:22 | 2020-12-06 17:27 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line-1 | 2020-12-07 09:47 | 2020-12-07 15:58 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2020-12-08 07:36 | 2020-12-08 16:38 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalkyha 132 kV line-1 | 2020-12-08 09:24 | 2020-12-08 12:12 | 2:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur (new) 132 kV line-1 | 2020-12-09 10:39 | 2020-12-09 17:58 | 7:19 | S/O | Due to OPGW work | 0 | 0 | No interruption
| Shyampur(O)-Shyampur (new) 132 kV line-2 |  | 2020-12-09 19:13 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2020-12-10 07:41 | 2020-12-10 16:43 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-1 | 2020-12-12 07:27 | 2020-12-12 15:57 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2020-12-12 07:07 | 2020-12-12 20:51 | 13:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Fatulla 132 kV line | 2020-12-12 07:58 | 2020-12-12 21:08 | 13:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-1 | 2020-12-12 08:34 | 2020-12-12 17:16 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2020-12-13 07:40 | 2020-12-13 16:59 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2020-12-13 09:52 | 2020-12-13 13:42 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Narsinghdi 132 kV line | 2020-12-14 09:53 | 2020-12-14 16:00 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2020-12-14 08:18 | 2020-12-14 16:09 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2020-12-15 08:34 | 2020-12-15 16:31 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | Sitalakyha-Hasnabad 132 kV line | 2020-12-15 08:39 | 2020-12-15 16:14 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Fatullah | Fatullah-Shyampur 132 kV line-1 & 2 | 2020-12-17 09:17 | 2020-12-17 15:16 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-12-18 07:42 | 2020-12-18 19:20 | 11:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2020-12-19 09:04 | 2020-12-19 17:11 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV line | 2020-12-19 09:04 | 2020-12-19 17:11 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2020-12-19 09:53 | 2020-12-19 16:52 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakyha -Bramongaon 132 kV line | 2020-12-20 07:04 | 2020-12-20 15:55 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-12-20 08:32 | 2020-12-20 20:31 | 11:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2020-12-21 07:17 | 2020-12-21 07:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-12-21 07:47 | 2020-12-21 07:47 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaganj | Madaganj-Munshiganj 132 kV line-1 | 2020-12-21 09:34 | 2020-12-21 12:26 | 2:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaganj-Munshiganj 132 kV line-2 | 2020-12-21 12:36 | 2020-12-21 16:39 | 4:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2020-12-21 08:37 | 2020-12-21 18:54 | 10:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 132 kV line-1 | 2020-12-22 07:52 | 2020-12-22 07:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-2 | 2020-12-22 10:05 | 2020-12-22 20:18 | 10:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2020-12-23 07:29 | 2020-12-23 07:29 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2020-12-24 10:09 | 2020-12-24 15:23 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2020-12-25 08:21 | 2020-12-25 12:44 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2020-12-26 09:21 | 2020-12-26 14:30 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-1 | 2020-12-26 08:18 | 2020-12-26 19:14 | 10:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Ullon 132 kV line-2 | 2020-12-26 14:38 | 2020-12-26 17:35 | 2:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-2 | 2020-12-26 08:31 | 2020-12-26 16:49 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 Kv line-2 | 2020-12-27 08:29 | 2020-12-27 12:49 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2020-12-27 12:44 | 2020-12-27 17:36 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Fatulla | Fatulla-Shyampur 132 kV line-1 | 2020-12-27 13:14 | 2020-12-27 13:40 | 0:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | SiddhirganjS/S-Siddhirganj 132 kV line-1 | 2020-12-27 11:50 | 2020-12-27 15:10 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhrara 132 kV line-1 | 2020-12-28 08:26 | 2020-12-28 16:56 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Meghnaghat 230 kV line-1 | 2020-12-28 08:19 | 2020-12-28 20:38 | 12:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bahudhara 132 kV line-1 | 2020-12-29 08:39 | 2020-12-29 20:18 | 11:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Meghnaghat 230 kV line-2 | 2020-12-29 09:31 | 2020-12-29 17:22 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-12-29 09:40 | 2020-12-29 14:38 | 4:58 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2020-12-31 08:34 | 2020-12-31 15:30 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 391:02 |  | Unserved Energy: |  | 0
Page: 4/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2020-12-01 08:45 | 2020-12-01 16:58 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Hathazari 132 kV line-2 | 2020-12-01 08:54 | 2020-12-01 17:11 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraoulia | Baraoulia-Hathazari 132 kV line-1 | 2020-12-03 08:26 | 2020-12-03 15:26 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-GPS Ispat 230 kV line | 2020-12-05 09:00 | 2020-12-05 15:31 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-12-06 10:22 | 2020-12-06 17:00 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-2 | 2020-12-06 08:46 | 2020-12-06 18:06 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2020-12-06 12:48 | 2020-12-06 16:50 | 4:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2020-12-07 09:13 | 2020-12-07 12:04 | 2:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2020-12-07 10:05 | 2020-12-07 16:41 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2020-12-07 10:00 | 2020-12-07 20:23 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line | 2020-12-08 10:09 | 2020-12-08 17:05 | 6:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Baraoulia | Baraoulia-Hathazari 132 kV line-1 | 2020-12-09 08:45 | 2020-12-09 16:48 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2020-12-09 08:28 | 2020-12-09 17:12 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
AKSML | AKSML-BSRM 230 kV line | 2020-12-10 08:56 | 2020-12-10 15:32 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line | 2020-12-10 12:36 | 2020-12-10 13:45 | 1:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2020-12-10 14:20 | 2020-12-10 15:34 | 1:14 | S/O | Due to A/M work | 0 | 0 | No interruption
AKSML | AKSML-BSRM 230 kV line | 2020-12-11 08:20 | 2020-12-11 15:38 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV line-2 |  | 2020-12-11 14:04 |  | S/O | After maintenance work | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line |  | 2020-12-11 15:54 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-12 07:42 | 2020-12-12 16:23 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
AKSML | AKSML-BSRM 230 kV line | 2020-12-12 08:33 | 2020-12-12 15:29 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-12 07:42 | 2020-12-12 16:23 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Skalbaha 132 kV line-2 | 2020-12-13 08:21 | 2020-12-13 16:44 | 8:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-13 07:42 | 2020-12-13 16:23 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Skalbaha 132 kV line-2 | 2020-12-15 08:43 | 2020-12-15 16:28 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-GPH 230 kV line | 2020-12-17 08:43 | 2020-12-17 16:50 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2020-12-17 08:34 | 2020-12-17 16:52 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Skalbaha 132 kV line-2 | 2020-12-18 08:19 | 2020-12-18 16:45 | 8:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-19 07:41 | 2020-12-19 16:53 | 9:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Skalbaha 132 kV line-2 | 2020-12-19 07:11 | 2020-12-19 17:07 | 9:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-20 07:31 | 2020-12-20 16:41 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | GPH-Hathazari 230 kV line-2 | 2020-12-20 08:51 | 2020-12-20 15:53 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2020-12-20 09:45 | 2020-12-20 16:17 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2020-12-20 08:38 | 2020-12-20 15:40 | 7:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Skalbaha 132 kV line-4 | 2020-12-21 07:30 | 2020-12-21 07:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-12-21 08:50 | 2020-12-21 17:06 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV line | 2020-12-21 08:31 | 2020-12-21 16:20 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-21 12:39 | 2020-12-21 16:43 | 4:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-1 | 2020-12-22 07:46 | 2020-12-25 17:58 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-12-22 09:05 | 2020-12-22 14:39 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-22 08:20 | 2020-12-22 16:56 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dohazari-100 MW PP 132 kV line | 2020-12-22 08:35 | 2020-12-22 16:04 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Matarbari | Matarbari-Cox'sbazar 132 kV line |  | 2020-12-22 10:36 |  | S/O | After maintenance work | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV line | 2020-12-22 08:46 | 2020-12-22 15:42 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| GPH-BSRM 230 kV line | 2020-12-23 08:46 | 2020-12-23 15:44 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-2 | 2020-12-23 09:02 | 2020-12-23 14:28 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-24 07:10 | 2020-12-24 16:50 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-24 07:14 | 2020-12-24 17:08 | 9:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur-Khulshi 132 kV line-2 | 2020-12-24 09:17 | 2020-12-24 15:13 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-1 | 2020-12-25 07:44 | 2020-12-25 07:44 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 5/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-25 07:37 | 2020-12-25 16:27 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-12-26 08:44 | 2020-12-26 16:58 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur-Khulshi 132 kV line | 2020-12-26 08:55 | 2020-12-26 14:14 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-12-27 07:03 | 2020-12-27 17:05 | 10:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line | 2020-12-27 07:33 | 2020-12-27 17:13 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-12-27 08:51 | 2020-12-27 16:57 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-3 | 2020-12-27 08:30 | 2020-12-27 17:35 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2020-12-28 07:22 | 2020-12-28 16:32 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2020-12-28 08:20 | 2020-12-28 16:28 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-12-28 08:39 | 2020-12-28 15:46 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cos'xbazar 132 kV line-2 | 2020-12-28 09:10 | 2021-01-01 15:31 | 102:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dohazari-Cos'xbazar 132 kV line-1 | 2020-12-29 07:37 | 2020-12-29 16:40 | 9:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-1 | 2020-12-29 08:45 | 2020-12-29 22:40 | 13:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line | 2020-12-29 09:33 | 2020-12-29 16:07 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2020-12-30 07:35 | 2020-12-30 16:42 | 9:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2020-12-30 07:30 | 2020-12-30 16:56 | 9:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-12-31 08:40 | 2020-12-31 15:18 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2020-12-31 08:31 | 2020-12-31 15:12 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 548:17 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2020-12-01 09:18 | 2020-12-01 13:13 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur Desh Energy-Ramganj 132 kV line-2 | 2020-12-01 09:10 | 2020-12-01 18:35 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2020-12-02 07:17 | 2020-12-02 19:56 | 12:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2020-12-02 10:12 | 2020-12-02 13:34 | 3:22 | S/O | Due to protection test | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV line-1 | 2020-12-02 13:35 | 2020-12-02 16:58 | 3:23 | S/O | Due to protection test | 0 | 0 | No interruption
| Sreemongal-Fenchuganj 132 kV line-2 | 2020-12-02 09:07 | 2020-12-02 13:22 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2020-12-06 08:19 | 2020-12-06 16:28 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2020-12-06 08:37 | 2020-12-06 14:45 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-2 | 2020-12-06 10:56 | 2020-12-06 11:55 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV line-1 | 2020-12-06 11:57 | 2020-12-06 12:53 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2020-12-07 09:08 | 2020-12-07 14:40 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ashuganj(N) 230 kV line-1 | 2020-12-07 12:54 | 2020-12-07 17:29 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-1 | 2020-12-12 09:06 | 2020-12-12 14:34 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2020-12-12 08:23 | 2020-12-12 16:22 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2020-12-12 09:17 | 2020-12-12 09:17 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2020-12-13 08:38 | 2020-12-13 16:30 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2020-12-14 10:33 | 2020-12-14 13:00 | 2:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.Baria-Shahjibazar 132 kV line-2 | 2020-12-14 13:04 | 2020-12-14 16:38 | 3:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-2 | 2020-12-14 08:22 | 2020-12-14 16:41 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-1 | 2020-12-15 07:19 | 2020-12-15 15:58 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2020-12-15 10:52 | 2020-12-15 12:21 | 1:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV line-2 | 2020-12-15 12:24 | 2020-12-15 16:28 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 |  | 2020-12-17 16:55 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV line-2 | 2020-12-19 08:54 | 2020-12-19 09:46 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV line-1 | 2020-12-20 07:37 | 2020-12-20 21:24 | 13:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV line-2 | 2020-12-20 07:37 | 2020-12-20 21:09 | 3:42
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2020-12-21 12:56 | 2020-12-21 16:38 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2020-12-22 10:15 | 2020-12-22 12:39 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV line-2 | 2020-12-22 12:40 | 2020-12-22 14:54 | 2:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-1 | 2020-12-23 11:14 | 2020-12-23 14:04 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-2 | 2020-12-23 11:02 | 2020-12-23 13:10 | 2:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Daudkandi-Cumilla(N) 132 kV line-2 | 2020-12-23 13:11 | 2020-12-23 16:55 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-12-23 09:47 | 2020-12-23 16:19 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2020-12-26 09:09 | 2020-12-26 13:22 | 4:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Baghabari 132 kV line-1 | 2020-12-26 08:14 | 2020-12-26 16:41 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj(N)-Bhulta 400 kV line-2 | 2020-12-27 07:25 | 2020-12-27 17:33 | 10:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj(N)-Sirajganj 230 kV line-2 | 2020-12-27 08:57 | 2020-12-27 17:10 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj(N)-Sirajganj 230 kV line-2 | 2020-12-28 07:05 | 2020-12-28 07:05 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 | 2020-12-28 08:05 | 2020-12-28 14:16 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2020-12-28 09:29 | 2020-12-28 13:43 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2020-12-28 09:15 | 2020-12-28 17:05 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line-1 | 2020-12-29 09:49 | 2020-12-29 17:14 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Sylhet 132 kV line | 2020-12-30 07:41 | 2020-12-30 07:41 | 0:00 | S/O | Due to A/M work | 20 | 0 | Power interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2020-12-31 08:38 | 2020-12-31 17:28 | 8:50 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 220:20 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-12-02 07:15 | 2020-12-02 15:37 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Khulna(S) 132 kV line-1 | 2020-12-02 08:27 | 2020-12-02 15:55 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2020-12-03 07:58 | 2020-12-03 16:41 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 | 2020-12-05 09:00 | 2020-12-05 15:31 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna(C) 132 kV line-2 | 2020-12-05 08:33 | 2020-12-05 16:31 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 | 2020-12-06 08:10 | 2020-12-06 16:47 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna(C) 132 kV line-2 | 2020-12-06 08:07 | 2020-12-06 16:09 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-1 | 2020-12-06 09:03 | 2020-12-06 13:27 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 | 2020-12-07 08:11 | 2020-12-07 16:39 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2020-12-07 09:11 | 2020-12-07 17:52 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 | 2020-12-08 08:04 | 2020-12-08 16:33 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-12-08 07:56 | 2020-12-08 15:30 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2020-12-08 09:19 | 2020-12-08 16:42 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV line-2 | 2020-12-08 07:34 | 2020-12-08 17:59 | 10:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-2 | 2020-12-09 08:45 | 2020-12-09 17:09 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-12-09 09:02 | 2020-12-09 15:21 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2020-12-09 09:09 | 2020-12-09 16:55 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj S/S | Gopalganj S/S-Gopalganj P/P 132 kV line | 2020-12-09 01:51 | 2020-12-10 16:26 | 38:35 | S/O | Due to Bay connection | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-2 | 2020-12-10 08:20 | 2020-12-10 16:48 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola Agg.PP.230 kV line-1 | 2020-12-11 08:48 | 2020-12-11 08:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-1 | 2020-12-12 07:18 | 2020-12-12 21:07 | 13:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-12-12 08:11 | 2020-12-12 15:42 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-12-12 09:07 | 2020-12-12 16:34 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-1 | 2020-12-13 07:31 | 2020-12-13 19:04 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-12-13 08:42 | 2020-12-13 14:39 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-12-13 08:40 | 2020-12-13 17:45 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2020-12-13 09:39 | 2020-12-13 14:30 | 4:51 | S/O | Due to TRTUD testing work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-12-14 07:58 | 2020-12-14 07:58 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barishal(N) 132 kV line-1 | 2020-12-14 11:17 | 2020-12-14 13:17 | 2:00 | S/O | Due to TRTUD testing work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-12-15 08:39 | 2020-12-15 17:02 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2020-12-15 09:10 | 2020-12-15 16:20 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line | 2020-12-15 09:24 | 2020-12-15 15:17 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gopalgaj P/S 132 kV line-2 | 2020-12-17 08:03 | 2020-12-17 16:33 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-1 | 2020-12-17 10:20 | 2020-12-17 11:26 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Patuakhali | Patuakhali-Payra 132 kV line-1 |  | 2020-12-17 14:43 |  | S/O | After maintenance work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj(New) 132 kV line-1 | 2020-12-19 08:17 | 2020-12-19 17:21 | 9:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-2 | 2020-12-20 07:26 | 2020-12-20 20:36 | 13:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj(New) 132 kV line-1 | 2020-12-20 08:39 | 2020-12-20 14:47 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-12-21 07:06 | 2020-12-21 07:06 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-2 | 2020-12-21 07:20 | 2020-12-21 17:08 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-2 | 2020-12-21 08:54 | 2020-12-21 16:40 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Faridpur-Gopalganj 132 kV line-2 | 2020-12-22 07:42 | 2020-12-22 07:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj 400 S/S | Gopalganj 400 S/S-Madaripur 132 kV line-1 | 2020-12-23 09:05 | 2020-12-23 17:09 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV line-1 | 2020-12-24 08:57 | 2020-12-24 14:37 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-12-26 08:13 | 2020-12-26 14:34 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Norail 132 kV line-1 | 2020-12-26 07:25 | 2020-12-26 16:27 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-12-27 08:26 | 2020-12-27 17:56 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV line-2 | 2020-12-27 08:37 | 2020-12-27 14:43 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV line-1 | 2020-12-27 11:51 | 2020-12-27 20:48 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-12-28 09:01 | 2020-12-28 16:49 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj 400 S/S | Gopalganj 400 S/S-Madaripur 132 kV line-2 | 2020-12-28 08:29 | 2020-12-28 17:00 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-12-29 08:04 | 2020-12-29 14:51 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV line-2 | 2020-12-29 09:17 | 2020-12-29 16:41 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-KPCL-2 132 kV line | 2020-12-29 08:23 | 2020-12-29 12:30 | 4:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2020-12-30 07:48 | 2020-12-30 16:24 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-12-31 08:05 | 2020-12-31 14:23 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj 400 S/S | Gopalganj 400 S/S-Madaripur 132 kV line-1 | 2020-12-31 08:55 | 2020-12-31 15:52 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Bagerhat 132 kV line-1 | 2020-12-31 07:45 | 2020-12-31 16:09 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 426:47 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC-Rajshahi (N) 230 kV line-1 | 2020-12-01 10:08 | 2020-12-01 19:00 | 8:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bhramara 132 kV line-1 | 2020-12-02 08:23 | 2020-12-02 17:21 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 |  | 2020-12-05 19:36 |  | S/O | After maintenance work | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV line-1 | 2020-12-06 09:17 | 2020-12-06 13:31 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara -Faridpur 132 kV line-1 | 2020-12-07 08:07 | 2020-12-07 16:05 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2020-12-10 10:32 | 2020-12-10 14:36 | 4:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2020-12-12 08:55 | 2020-12-12 17:54 | 8:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line-1 | 2020-12-12 09:52 | 2020-12-12 12:56 | 3:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2020-12-13 08:44 | 2020-12-13 17:21 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-12-18 07:09 | 2020-12-18 07:09 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bhramara 132 kV line-1 & 2 | 2020-12-19 06:52 | 2020-12-19 23:12 | 16:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 | 2020-12-19 12:51 | 2020-12-19 22:18 | 9:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line-2 | 2020-12-20 08:28 | 2020-12-20 17:17 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 230 kV line-1 | 2020-12-21 08:16 | 2020-12-21 20:19 | 12:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2020-12-22 08:53 | 2020-12-22 20:40 | 11:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2020-12-24 07:42 | 2020-12-24 16:35 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Jashore | Jashore-Jhenidah 132 kV line-2 |  | 2020-12-24 16:48 |  | S/O | After maintenance work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2020-12-27 08:10 | 2020-12-27 16:52 | 8:42 | S/O | Due to A/M work | 0 | 0
Jhenidah | Jhenidah-Bootail 132 kV line | 2020-12-28 09:59 | 2020-12-28 14:12 | 4:13 | S/O | Due to protection work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bheramara 230 kV line-2 | 2020-12-28 12:01 | 2020-12-28 15:12 | 3:11 | S/O | Due to protection test | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-2 | 2020-12-29 08:28 | 2020-12-29 17:50 | 9:22 | S/O | Due to A/M work | 0 | 0
Ishurdi | Ishurdi-Rppur 132 kV line-1 | 2020-12-29 08:32 | 2020-12-29 20:04 | 11:32 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 159:05 |  | Unserved Energy: |  | 0
Page: 8/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2020-12-01 08:34 | 2020-12-01 16:54 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 kV line-1 | 2020-12-01 08:20 | 2020-12-01 17:54 | 9:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2020-12-02 08:42 | 2020-12-02 16:45 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 kV line-1 | 2020-12-02 09:18 | 2020-12-02 16:40 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Naogaon-Bogura 132 kV line-1 | 2020-12-03 09:12 | 2020-12-03 16:22 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-2 | 2020-12-03 08:40 | 2020-12-03 16:56 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line-1 |  | 2020-12-04 10:36 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rajshahi(New) | Rajshahi(New)-Bheramara HVDC 230 kV line-2 | 2020-12-04 11:02 | 2020-12-04 20:39 | 9:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Rajshahi(New)-Bheramara HVDC 230 kV line-1 | 2020-12-04 09:45 | 2020-12-04 10:37 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jaldhaka | Jaldhaka-Magura 132 kV line-1 | 2020-12-04 08:23 | 2020-12-04 11:51 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-2 | 2020-12-05 08:36 | 2020-12-05 15:27 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 kV line-2 | 2020-12-05 08:24 | 2020-12-05 17:50 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(New) | Rajshahi(New)-Bheramara HVDC 230 kV line-2 |  | 2020-12-05 20:25 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-HVDC Bheramara 230 kV line-2 | 2020-12-06 09:33 | 2020-12-06 20:21 | 10:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-2 | 2020-12-06 08:37 | 2020-12-06 16:34 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-2 | 2020-12-06 09:26 | 2020-12-06 16:16 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2020-12-07 09:07 | 2020-12-07 16:27 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 kV line-2 | 2020-12-07 09:35 | 2020-12-07 14:16 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line-2 | 2020-12-07 12:01 | 2020-12-07 20:39 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rajshahi-HVDC Bheramara 230 kV line-1 | 2020-12-08 10:59 | 2020-12-08 20:24 | 9:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Confidence P/P 132 kV line-1 | 2020-12-08 08:19 | 2020-12-08 16:33 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2020-12-08 09:10 | 2020-12-08 16:29 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura S/S | Amnura S/S-Amnura P/P (100MW) 132 kV line-2 | 2020-12-08 09:06 | 2020-12-08 14:59 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-12-08 08:45 | 2020-12-08 16:59 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura S/S | Amnura S/S-Amnura 50 MW RPP P/P 132 kV line | 2020-12-08 11:01 | 2020-12-08 15:45 | 4:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Confidence P/P 132 kV line-1 | 2020-12-09 08:28 | 2020-12-09 17:12 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2020-12-09 08:38 | 2020-12-09 15:56 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura S/S | Amnura S/S-Amnura 100 MW RPP P/P 132 kV line | 2020-12-09 09:02 | 2020-12-09 15:41 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-1 | 2020-12-09 08:55 | 2020-12-09 16:00 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line-1 | 2020-12-09 11:23 | 2020-12-09 21:01 | 9:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2020-12-10 09:02 | 2020-12-10 15:26 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-2 | 2020-12-10 08:53 | 2020-12-10 19:33 | 10:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-12-11 08:40 | 2020-12-11 17:15 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur -Rangpur confidence 132 kV line-1 | 2020-12-11 10:32 | 2020-12-11 14:19 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur -Rangpur confidence 132 kV line-2 | 2020-12-12 09:32 | 2020-12-12 16:04 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2020-12-12 08:41 | 2020-12-12 16:39 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line-1 | 2020-12-12 11:24 | 2020-12-12 16:59 | 5:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajshahi-Bheramara HVDC 230 kV line-1 | 2020-12-13 11:24 | 2020-12-13 16:39 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2020-12-13 08:46 | 2020-12-13 16:02 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2020-12-13 09:01 | 2020-12-13 17:28 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence 132 kV line-2 | 2020-12-13 09:11 | 2020-12-13 16:52 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line | 2020-12-13 11:28 | 2020-12-13 20:23 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2020-12-14 08:36 | 2020-12-14 15:47 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2020-12-14 08:41 | 2020-12-14 18:10 | 9:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Rajshahi RPP 132 kV line | 2020-12-14 08:10 | 2020-12-14 16:49 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2020-12-15 08:46 | 2020-12-15 17:12 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV line | 2020-12-15 09:14 | 2020-12-15 15:35 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura (new) | Bogura (new)-Bogura (Old) 132 kV line-1 | 2020-12-15 08:54 | 2020-12-15 11:59 | 3:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura (new)-Bogura (Old) 132 kV line-2 | 2020-12-15 12:06 | 2020-12-15 15:21 | 3:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2020-12-15 10:37 | 2020-12-15 15:17 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-1 | 2020-12-19 08:20 | 2020-12-19 17:50 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Barapukuria 230 kV line-1 | 2020-12-19 08:39 | 2020-12-19 16:30 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2020-12-19 09:30 | 2020-12-19 16:54 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 9/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:December 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Rajshahi S/S | Rajshahi S/S-Rajshahi RPP 132 kV line | 2020-12-19 08:17 | 2020-12-19 16:50 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-1 | 2020-12-20 08:32 | 2020-12-20 16:35 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV line-1 | 2020-12-20 08:38 | 2020-12-20 15:45 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2020-12-20 09:40 | 2020-12-20 16:26 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2020-12-20 08:24 | 2020-12-20 17:05 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-1 | 2020-12-21 08:49 | 2020-12-21 16:36 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV line-1 | 2020-12-21 08:32 | 2020-12-21 16:50 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2020-12-21 10:14 | 2020-12-21 17:04 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2020-12-21 08:19 | 2020-12-21 16:46 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-2 | 2020-12-22 08:41 | 2020-12-22 16:29 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV line-2 | 2020-12-22 08:22 | 2020-12-22 16:12 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-2 | 2020-12-22 08:01 | 2020-12-22 16:53 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-2 | 2020-12-23 08:36 | 2020-12-23 16:32 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Barapukuria 230 kV line-2 | 2020-12-23 08:37 | 2020-12-23 16:22 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-2 | 2020-12-23 08:10 | 2020-12-23 17:11 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV line-1 | 2020-12-23 08:39 | 2020-12-23 14:27 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-2 | 2020-12-24 09:55 | 2020-12-24 14:15 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Barapukuria 230 kV line-2 | 2020-12-24 09:04 | 2020-12-24 17:28 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC Bheramara 230 kV line-2 | 2020-12-24 09:26 | 2020-12-24 15:51 | 6:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-12-24 08:35 | 2020-12-24 17:29 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-12-25 08:28 | 2020-12-25 17:30 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangarth 132 kV line-1 | 2020-12-26 09:14 | 2020-12-26 16:13 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV line-2 | 2020-12-26 08:27 | 2020-12-26 15:34 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC Bheramara 230 kV line-2 |  | 2020-12-26 11:08 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Rajshahi-HVDC Bheramara 230 kV line-1 | 2020-12-26 11:40 | 2020-12-26 11:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangarth 132 kV line-2 | 2020-12-27 08:37 | 2020-12-27 17:42 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line-2 | 2020-12-27 08:37 | 2020-12-27 17:42 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria S/S | Barapukuria S/S-Barapukuria P/S 132 kV line-1 | 2020-12-27 09:50 | 2020-12-27 15:52 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(New) | Rajshahi(New)-Amnura 132 kV line | 2020-12-28 08:23 | 2020-12-28 16:56 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria S/S | Barapukuria S/S-Barapukuria S/S 230 kV line-2 | 2020-12-28 09:14 | 2020-12-28 16:12 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangarth 132 kV line-1 | 2020-12-28 09:45 | 2020-12-28 15:20 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Confidence P/P 132 kV line-1 | 2020-12-29 07:41 | 2020-12-29 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangarth 132 kV line-2 | 2020-12-29 09:20 | 2020-12-29 15:45 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi (New) 132 kV line | 2020-12-29 08:15 | 2020-12-29 16:20 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-2 | 2020-12-30 07:09 | 2020-12-30 07:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangarth 132 kV line-2 | 2020-12-31 08:29 | 2020-12-31 16:44 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi (New) 132 kV line | 2020-12-31 08:48 | 2020-12-31 15:44 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 623:04 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2020-12-04 09:22 | 2020-12-04 17:21 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Narindah 132 kV line-2 | 2020-12-05 09:14 | 2020-12-05 17:32 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Matuail | Matuail-Maniknagar 132 kV line-1 | 2020-12-13 08:43 | 2020-12-13 16:48 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Matuail-Maniknagar 132 kV line | 2020-12-14 08:38 | 2020-12-14 16:17 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Dhanmondi 132 kV line-3 | 2020-12-22 09:57 | 2020-12-22 15:15 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV line-2 | 2020-12-22 15:50 | 2020-12-22 17:12 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line | 2020-12-24 15:31 | 2020-12-24 17:52 | 2:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2020-12-26 10:15 | 2020-12-26 17:12 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Bangabhaban 132 kV line-2 | 2020-12-29 10:43 | 2020-12-29 20:43 | 10:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Maniknagar-Bangabhaban 132 kV line-1 | 2020-12-31 10:40 | 2020-12-31 15:14 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 62:33 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3097:31 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:December' 2020
| Area | Previous Month (November) 2020) |  |  |  | Current Month (December 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 9 | 5 | 233 | 247 | 7 | 2 | 185 | 194
2 | Dhaka (South) Grid Circle. | 9 | 1 | 53 | 63 | 11 | 4 | 100 | 115
3 | Chattogram Grid Circle. | 6 | 2 | 68 | 75 | 3 |  | 93 | 96
4 | Cumilla Grid Circle. | 14 | 11 | 77 | 103 | 9 | 1 | 82 | 92
5 | Khulna Grid Circle. | 6 | 8 | 105 | 119 | 5 | 2 | 70 | 77
6 | HVDC Grid Circle | 1 | 3 | 46 | 50 | 5 | 21 | 59 | 85
7 | Bogura Grid Circle. | 6 | 8 | 109 | 123 | 3 | 1 | 116 | 120
8 | Others | 1 |  | 3 | 4 | 1 |  | 10 | 11
9 | Total | 52 | 38 | 694 | 784 | 44 | 31 | 715 | 790
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:December' 2020
| Area | Previous Month (November 2020) |  |  |  | Current Month (December 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 98.66 | 58.67 | 1248.2 | 1405.53 | 283.83 |  | 339.17 | 623
2 | Dhaka (South) Grid Circle. | 41.39 |  | 157.67 | 199.06 | 33.94 |  | 159.58 | 193.52
3 | Chattogram Grid Circle. | 35.45 | 148 | 61 | 244.45 | 70.37 |  | 31.8 | 102.17
4 | Cumilla Grid Circle. | 39 | 426.67 | 681.32 | 1146.99 | 21.98 |  |  | 21.98
5 | Khulna Grid Circle. | 36.92 | 211.2 | 510.08 | 758.2 | 27.9 | 370 |  | 397.9
6 | HVDC Grid Circle |  |  | 119.9 | 119.9 |  | 500.62 | 2283.8 | 2784.42
7 | Bogura Grid Circle. | 30.5 | 189.33 | 670.33 | 890.16 | 21 |  |  | 21
8 | Others
9 | Total | 281.92 | 1033.87 | 3448.5 | 4764.29 | 459.02 | 870.62 | 2814.35 | 4143.99
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:December2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 1 |  |  | - |  | 1 | 271.33
2 | Dhaka (South) | 5031.6 | 1 | 1 | 2 | 1 |  | 1 | 174.25
3 | Chattogram | 2042 | 2 | 1 | 3 | 1 | - | 2 | 102.17
4 | Khulna | 2434 | 4 |  | 4 | 3 | - | 1 | 397.9
5 | HVDC | 5954.3 |  | 2 | 2 | - | - | 2 | 2283.8
6 | Bogura | 3145.6 | - | - | - | - | - | - | -
7 | Cumilla | 2981 | 2 |  | 2 | 1 | 1 |  | 21.98
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 3251.43
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.9%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.98%
4 | Khulna | 99.99%
5 | HVDC | 99.91% | [6 empty] | Executive Engineer
6 | Bogura | 99.99% | [6 empty] | Information Management Division
7 | Cumilla | 99.98% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:December' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | 1 | 2 | 1 | - | 1 | 351.67
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | - |  | 1 | 19.27
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | 501 | 1 | - | 1 | - | - | 1 | 500.62
6 | Bogura | 1803.3 | - | 1 |  | 1 | 1 |  |  | 21
7 | Cumilla | 1648.16 | - | - | - | - | - | - | - | -
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 892.56
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.67%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.96% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.85% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:December' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-12-18 | 24 | - | 1 | 0hr49 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:December' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 1 | 2:28 | 110 | 271.3333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Kadda | 1 | 0:15 | 50 | 12.5 | Due to tripping of Kodda-Joydevpur 132 kV line
Mymensigh |  | 6:10 | 55 | 339.1667 | Due to S/D of Mymensingh-Netrakona 132 kV line
Ghorashal | 1 | 0:20 | 44 | 14.6667 | Due to tripping O/C relay at 33 kV side
Hasnabad | 1 | 0:17 | 68 | 19.2667 | Due to tripping of hasnabad-Lalbagh 132 kV line
Munshiganj |  | 6:23 | 25 | 159.5833 | Due to S/D of 33 kV bus-1
Cox'sbazar | 3 | 2:49 | 22 | 61.9667 | Due to tripping of 132/33 kV Transformer-T3
|  | 0:28 | 18 | 8.4
|  | 2:39 | 12 | 31.8 | Due to S/D of132/33 kV Transformer-T3
Cumilla(N) | 1 | 0:32 | 28 | 14.9333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Shahjibazar |  | 0:09 | 47 | 7.05 | Due to tripping of 132/33 kV Transformer-T4
Patuakahli | 1 | 1:14 | 300 | 370 | Due to oil filling of 132/33 kV Transformer T2
Bagerhat |  | 0:03 | 50 | 2.5 | Due to 33 kV feeder fault
Mongla | 2 | 0:19 | 36 | 11.4 | Due to tripping of 33 kV Bus
|  | 0:28 | 30 | 14
Baghabari | 1 | 0:49 | 613 | 500.6167 | Due to tripping of ishurdi-Natre 132 KV line-1 CB problem
Jhenidah | 2 | 9:28 | 96 | 908.8 | Due to S/D of 132 kV Bus-A& B
|  | 9:10 | 150 | 1375
Naogaon | 1 | 0:14 | 18 | 21 | Due to tripping ofNaogaon- Niyamatpur 132 kV line
| Total Unserved energy : |  |  | 4143.9833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:Decemder'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 110 | 1 | 2020-12-01 | 15:00
2 | Munsiganj | 88 | 8 | 2020-12-01 | 18:30
3 | Sonargaon | 64 | 3 | 2020-12-01 | 19:00
4 | Shyampur | 184 | 10 | 2020-12-01 | 10:00
5 | Bhulta | 165 | 20 | 2020-12-01 | 12:00
6 | Madanganj | 61 | 27 | 2020-12-01 | 17:00
7 | Shitalakhya | 106 | 12 | 2020-12-01 | 11:00
8 | Rahim steel | 19 | 8 | 2020-12-01 | 15:00
9 | Matuail | 72 | 3 | 2020-12-01 | 10:00
10 | Ghorasal | 69 | 19 | 2020-12-01 | 20:00
11 | Narsingdi | 132 | 7 | 2020-12-01 | 19:00
12 | Haripur (SBU) | 111 | 7 | 2020-12-01 | 12:00
13 | Ullon | 46 | 1 | 2020-12-01 | 18:00
14 | Hasnabad | 151 | 6 | 2020-12-01 | 18:00
15 | Magbazar | 76 | 3 | 2020-12-01 | 15:00
16 | Maniknagar | 72 | 27 | 2020-12-01 | 18:00
17 | Bangabhaban | 24 | 1 | 2020-12-01 | 10:00
18 | Narinda | 80 | 7 | 2020-12-01 | 18:00
19 | Dhanmondi | 112 | 2 | 2020-12-01 | 13:00
20 | Lalbag | 75 | 8 | 2020-12-01 | 13:00
21 | Madartek | 49 | 1 | 2020-12-01 | 18:00
22 | Dhaka University | - | - | - | -
23 | Aftabnagar | 7 | 1 | 2020-12-01 | 18:00
24 | Fatullah | 46 | 31 | 2020-12-01 | 11:00
25 | Mirpur | 78 | 2 | 2020-12-01 | 18:00
26 | Kalyanpur | 66 | 1 | 2020-12-01 | 18:00
27 | Gulshan | 88 | 1 | 2020-12-01 | 13:00
28 | Uttara | 85 | 21 | 2020-12-01 | 12:00
29 | Uttara(new) | 24 | 6 | 2020-12-01 | 18:00
30 | Kamrangirchar | 77 | 1 | 2020-12-01 | 18:00
31 | Savar | 131 | 21 | 2020-12-01 | 18:00
32 | Bhasantec | 116 | 3 | 2020-12-01 | 13:00
33 | Agargaon | 51 | 2 | 2020-12-01 | 13:00
34 | Satmosjid | 75 | 7 | 2020-12-01 | 18:00
35 | Tongi | 93 | 5 | 2020-12-01 | 11:00
36 | Kabirpur | 192 | 5 | 2020-12-01 | 18:30
37 | Basundhara | 112 | 1 | 2020-12-01 | 18:00
38 | Manikganj | 54 | 2 | 2020-12-01 | 18:00
39 | Joydevpur | 128 | 7 | 2020-12-01 | 18:30
40 | New Tongi | 100 | 21 | 2020-12-01 | 11:00
41 | Kodda | 215 | 14 | 2020-12-01 | 18:00
42 | Dhamrai | 93 | 6 | 2020-12-01 | 13:00
43 | Rajendrapur | 86 | 20 | 2020-12-01 | 19:00
44 | Valuka | 92 | 27 | 2020-12-01 | 18:30
45 | Tangail | 149 | 23 | 2020-12-01 | 18:00
46 | Mymensing | 159 | 21 | 2020-12-01 | 18:30
47 | Kishorganj | 92 | 24 | 2020-12-01 | 20:00
48 | Netrokona | 92 | 19 | 2020-12-01 | 18:00
49 | Jamalpur | 100 | 2 | 2020-12-01 | 18:00
50 | Sherpur | 96 | 26 | 2020-12-01 | 18:30
51 | Srimongal | 39 | 5 | 2020-12-01 | 18:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:Decemder'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
52 | Shahjibazar | 89 | 2 | 2020-12-01 | 18:00
53 | Fenchuganj | 35 | 19 | 2020-12-01 | 18:00
54 | Kulawara | 31 | 15 | 2020-12-01 | 18:00
55 | Sylhet | 107 | 19 | 2020-12-01 | 21:00
56 | Chatak | 23 | 20 | 2020-12-01 | 18:00
57 | Sunamganj | 32 | 10 | 2020-12-01 | 18:00
58 | Bianibazar | 41 | 19 | 2020-12-01 | 18:00
59 | Cumilla (S) | 120 | 3 | 2020-12-01 | 19:00
60 | Cumilla(N) | 83 | 5 | 2020-12-01 | 19:30
61 | Chandpur | 74 | 12 | 2020-12-01 | 20:00
62 | Feni | 85 | 1 | 2020-12-01 | 18:00
63 | Chowmuhani | 132 | 14 | 2020-12-01 | 18:00
64 | Ashuganj | 46 | 12 | 2020-12-01 | 19:00
65 | Daudkandi | 108 | 23 | 2020-12-01 | 19:30
66 | B.Baria | 98 | 2 | 2020-12-01 | 19:30
67 | Ramganj | 72 | 21 | 2020-12-01 | 19:00
68 | Chaddagram | 34 | 3 | 2020-12-01 | 17:00
69 | PHP | 11 | 12 | 2020-12-01 | 14:00
70 | Madanhat | 54 | 26 | 2020-12-01 | 18:30
71 | Hathazari | 78 | 1 | 2020-12-01 | 18:00
72 | Khulshi | 182 | 3 | 2020-12-01 | 12:00
73 | Halishahar | 131 | 5 | 2020-12-01 | 12:00
74 | Baraulia | 161 | 26 | 2020-12-01 | 23:00
75 | Sikalbaha | 24 | 7 | 2020-12-01 | 11:00
76 | Dohazari | 66 | 23 | 2020-12-01 | 19:30
77 | Cox'sbazar | 81 | 6 | 2020-12-01 | 18:00
78 | Chandraghona | 22 | 15 | 2020-12-01 | 18:30
79 | Kaptai | 16 | 21 | 2020-12-01 | 13:00
80 | A. Khaer Stl. | 9 | 1 | 2020-12-01 | 16:00
81 | Bakulia | 84 | 4 | 2020-12-01 | 1:00
82 | Julda | 22 | 3 | 2020-12-01 | 8:00
83 | TK chemical | 23 | 19 | 2020-12-01 | 17:00
84 | Modern Steel | 18 | 1 | 2020-12-01 | 20:00
85 | Shahmirpur | 22 | 22 | 2020-12-01 | 18:00
86 | Khagrachhari | 20 | 1 | 2020-12-01 | 18:30
87 | Matarbari | 50 | 1 | 2020-12-01 | 0:00
88 | Baroiar Hat | 34 | 3 | 2020-12-01 | 18:00
89 | Rangamati | 10 | 1 | 2020-12-01 | 18:00
90 | Abul Khair 230 | 200 | 27 | 2020-12-01 | 14:00
91 | BSRM | 161 | 23 | 2020-12-01 | 7:00
92 | GPH Ispat | 88 | 19 | 2020-12-01 | 21:00
93 | Goalpara | 18 | 30 | 2020-12-01 | 13:00
94 | Central s/s | 81 | 9 | 2020-12-01 | 18:00
95 | Noapara | 52 | 15 | 2020-12-01 | 18:30
96 | Jashore | 84 | 1 | 2020-12-01 | 18:00
97 | Benapol | 38 | 23 | 2020-12-01 | 18:00
98 | Jhenidah | 98 | 18 | 2020-12-01 | 18:30
99 | Bottail | 114 | 21 | 2020-12-01 | 18:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:Decemder'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
100 | G.K Project | 46 | 26 | 2020-12-01 | 18:00
101 | Faridpur | 135 | 23 | 2020-12-01 | 18:00
102 | Madaripur | 68 | 11 | 2020-12-01 | 19:00
103 | Sariatpur | 42 | 9 | 2020-12-01 | 20:00
104 | Gopalganj | 65 | 26 | 2020-12-01 | 18:00
105 | Bagerhat | 88 | 20 | 2020-12-01 | 18:00
106 | Mongla | 40 | 19 | 2020-12-01 | 18:00
107 | Satkhira | 79 | 26 | 2020-12-01 | 18:30
108 | Gallamari | 35 | 13 | 2020-12-01 | 13:00
109 | Magura | 46 | 18 | 2020-12-01 | 18:30
110 | Norail | 28 | 1 | 2020-12-01 | 18:30
111 | Chuadanga | 78 | 26 | 2020-12-01 | 18:00
112 | Barsal(N) | 30 | 5 | 2020-12-01 | 20:00
113 | Barsal(S) | 74 | 27 | 2020-12-01 | 21:00
114 | Patuakhali | 83 | 1 | 2020-12-01 | 20:00
115 | Bhandaria | 42 | 19 | 2020-12-01 | 20:00
116 | Borhan Uddin | 27 | 6 | 2020-12-01 | 21:00
117 | Ishurdi | 50 | 19 | 2020-12-01 | 18:00
118 | Ruppur Paromanobik | 2 | 1 | 2020-12-01 | 18:00
119 | Natore | 83 | 3 | 2020-12-01 | 18:00
120 | Bogura | 126 | 1 | 2020-12-01 | 18:30
121 | Naogaon | 84 | 23 | 2020-12-01 | 18:30
122 | Rajshahi | 101 | 21 | 2020-12-01 | 19:30
123 | Rajshahi New | 9 | 5 | 2020-12-01 | 18:00
124 | C.Nawabganj | 54 | 9 | 2020-12-01 | 20:00
125 | Amnura | 32 | 23 | 2020-12-01 | 18:30
126 | Pabna | 85 | 26 | 2020-12-01 | 18:00
127 | Shahjadpur | 79 | 22 | 2020-12-01 | 19:00
128 | Serajganj | 80 | 23 | 2020-12-01 | 19:00
129 | Niyamatpur | 46 | 20 | 2020-12-01 | 18:00
130 | Joypurhat | 46 | 21 | 2020-12-01 | 18:00
131 | Sherpur(Bogura) | 44 | 15 | 2020-12-01 | 18:00
132 | Mohastangar | 34 | 21 | 2020-12-01 | 18:30
133 | Rangpur | 122 | 5 | 2020-12-01 | 18:30
134 | Lalmonirhat | 49 | 21 | 2020-12-01 | 18:30
135 | Saidpur | 93 | 5 | 2020-12-01 | 18:00
136 | Purbasadipur | 90 | 15 | 2020-12-01 | 18:00
137 | Thakurgaon | 64 | 3 | 2020-12-01 | 18:00
138 | Palshbari | 98 | 26 | 2020-12-01 | 18:00
139 | Barapukuria | 41 | 15 | 2020-12-01 | 19:00
140 | Panchugar | 45 | 12 | 2020-12-01 | 18:00
141 | Joldhaka | 26 | 18 | 2020-12-01 | 9:00
142 | Kurigram | 45 | 8 | 2020-12-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:December' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 3264 | 03.12.2020 | 18:00
Chattogram | 1104 | 03.12.2020 | 12:00
Khulna | 1106 | 19.12.2020 | 18:30
Rajshahi | 900 | 21.12.2020 | 18:30
Cumilla | 765 | 14.12.2020 | 19:00
Mymensingh | 715 | 23.12.2020 | 18:00
Sylhet | 346 | 19.12.2020 | 20:00
Barisal | 250 | 29.12.2020 | 20:00
Rangpur | 624 | 22.12.2020 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 430 | 21 | 2020-12-01 | 20:00 | 397 | 26 | 2020-12-01 | 15:00
2 | Bheramara | 400 | 417 | 8 | 2020-12-01 | 17:00 | 392 | 22 | 2020-12-01 | 10:00
3 | Ashuganj(N) | 400 | 396 | 1 | 2020-12-01 | 3:00 | 366 | 26 | 2020-12-01 | 11:00
4 | Payra | 400 | 440 | 30 | 2020-12-01 | 24:00 | 388 | 31 | 2020-12-01 | 13:00
5 | Kaliakoir | 400 | 407 | 6 | 2020-12-01 | 1:00 | 362 | 27 | 2020-12-01 | 10:00
6 | Bhulta | 400 | 391 | 31 | 2020-12-01 | 22:00 | 363 | 26 | 2020-12-01 | 11:00
7 | Gopalganj | 400 | 436 | 30 | 2020-12-01 | 4:00 | 382 | 6 | 2020-12-01 | 18:30
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 2 | 2020-12-01 | 1:00 | 228 | 26 | 2020-12-01 | 11:00
2 | Ishurdi | 230 | 243 | 19 | 2020-12-01 | 5:00 | 224 | 7 | 2020-12-01 | 12:00
3 | Ashuganj | 230 | 240 | 1 | 2020-12-01 | 18:00 | 228 | 26 | 2020-12-01 | 12:00
4 | Serajganj | 230 | 235 | 21 | 2020-12-01 | 24:00 | 225 | 17 | 2020-12-01 | 18:00
5 | Baghabari | 230 | 245 | 12 | 2020-12-01 | 6:00 | 234 | 8 | 2020-12-01 | 12:00
6 | Barapukuria | 230 | 234 | 19 | 2020-12-01 | 4:00 | 220 | 17 | 2020-12-01 | 18:00
7 | Bogura | 230 | 237 | 22 | 2020-12-01 | 1:00 | 220 | 17 | 2020-12-01 | 18:00
8 | Rajshahi | 230 | 234 | 22 | 2020-12-01 | 23:00 | 208 | 2 | 2020-12-01 | 24:00
9 | Khulna South | 230 | 238 | 22 | 2020-12-01 | 6:00 | 213 | 5 | 2020-12-01 | 18:00
10 | Rampura | 230 | 232 | 4 | 2020-12-01 | 7:00 | 220 | 26 | 2020-12-01 | 10:00
11 | Haripur | 230 | 234 | 31 | 2020-12-01 | 22:00 | 220 | 26 | 2020-12-01 | 11:00
12 | Hasnabad | 230 | 236 | 22 | 2020-12-01 | 1:00 | 218 | 26 | 2020-12-01 | 11:00
13 | Shyampur | 230 | 239 | 19 | 2020-12-01 | 6:00 | 220 | 1 | 2020-12-01 | 12:00
14 | Aminbazar | 230 | 235 | 21 | 2020-12-01 | 24:00 | 217 | 28 | 2020-12-01 | 16:00
15 | Tongi | 230 | 236 | 31 | 2020-12-01 | 23:00 | 214 | 27 | 2020-12-01 | 9:00
16 | Comilla (N) | 230 | 240 | 2 | 2020-12-01 | 13:00 | 226 | 26 | 2020-12-01 | 12:00
17 | Hathazari | 230 | 230 | 12 | 2020-12-01 | 6:00 | 206 | 17 | 2020-12-01 | 12:00
18 | Megnaghat | 230 | 238 | 2 | 2020-12-01 | 24:00 | 222 | 21 | 2020-12-01 | 12:00
19 | Fenchuganj | 230 | 250 | 20 | 2020-12-01 | 7:00 | 234 | 15 | 2020-12-01 | 13:00
20 | Siddhirganj | 230 | 235 | 22 | 2020-12-01 | 1:00 | 221 | 26 | 2020-12-01 | 11:00
21 | Maniknagar | 230 | 234 | 31 | 2020-12-01 | 22:00 | 219 | 26 | 2020-12-01 | 11:00
22 | Old Airport | 230 | 235 | 30 | 2020-12-01 | 15:00 | 216 | 26 | 2020-12-01 | 12:00
23 | Barisal | 230 | 255 | 30 | 2020-12-01 | 19:00 | 229 | 13 | 2020-12-01 | 14:00
24 | AKSML | 230 | 231 | 22 | 2020-12-01 | 1:00 | 206 | 18 | 2020-12-01 | 10:00
25 | BSRM | 230 | 232 | 20 | 2020-12-01 | 24:00 | 209 | 6 | 2020-12-01 | 17:00
26 | Bibiyana | 230 | 251 | 21 | 2020-12-01 | 24:00 | 235 | 26 | 2020-12-01 | 15:00
27 | Bhulta | 230 | 237 | 30 | 2020-12-01 | 19:00 | 221 | 26 | 2020-12-01 | 17:00
28 | Ashuganj (S) | 230 | 238 | 1 | 2020-12-01 | 20:00 | 226 | 26 | 2020-12-01 | 11:00
29 | Kaliakoir | 230 | 236 | 3 | 2020-12-01 | 4:00 | 213 | 28 | 2020-12-01 | 16:00
30 | GPH | 230 | 230 | 20 | 2020-12-01 | 22:00 | 205 | 18 | 2020-12-01 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 31 | 2020-12-01 | 0.875 | 128 | 5 | 2020-12-01 | 1899-12-31
2 | Munsiganj | 132 | 142 | 12 | 2020-12-01 | 0.54167 | 131 | 26 | 2020-12-01 | 0.45833
3 | Sonargaon | 132 | 140 | 2 | 2020-12-01 | 0 | 130 | 26 | 2020-12-01 | 0.45833
4 | Shyampur | 132 | 136 | 2 | 2020-12-01 | 0 | 122 | 24 | 2020-12-01 | 0.083333
5 | Bhulta | 132 | 135 | 11 | 2020-12-01 | 0.75 | 124 | 7 | 2020-12-01 | 0.5
6 | Madanganj | 132 | 142 | 12 | 2020-12-01 | 0.58333 | 128 | 28 | 2020-12-01 | 0.5
7 | Shitalakhya | 132 | 143 | 14 | 2020-12-01 | 0.77083 | 128 | 26 | 2020-12-01 | 0.5
8 | Rahim Steal | 132 | 140 | 1 | 2020-12-01 | 0.83333 | 132 | 26 | 2020-12-01 | 0.45833
9 | Matuail | 132 | 141 | 31 | 2020-12-01 | 0.875 | 128 | 5 | 2020-12-01 | 1899-12-31
10 | Ghorasal | 132 | 144 | 9 | 2020-12-01 | 0.375 | 130 | 29 | 2020-12-01 | 0.375
11 | Narsinghdi | 132 | 139 | 15 | 2020-12-01 | 0.79167 | 125 | 14 | 2020-12-01 | 0.45833
12 | Haripur (SBU) | 132 | 140 | 12 | 2020-12-01 | 0.58333 | 131 | 2 | 2020-12-01 | 0.20833
13 | Ullon | 132 | 134 | 13 | 2020-12-01 | 0.25 | 124 | 26 | 2020-12-01 | 0.45833
14 | Hasnabad | 132 | 141 | 30 | 2020-12-01 | 1899-12-31 | 129 | 26 | 2020-12-01 | 0.5
15 | Magbazar | 132 | 138 | 13 | 2020-12-01 | 0.16667 | 123 | 26 | 2020-12-01 | 0.45833
16 | Maniknagar | 132 | 139 | 2 | 2020-12-01 | 1899-12-31 | 127 | 12 | 2020-12-01 | 0.625
17 | Bangabhaban | 132 | 139 | 2 | 2020-12-01 | 1899-12-31 | 127 | 12 | 2020-12-01 | 0.625
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
18 | Narinda | 132 | 139 | 2 | 2020-12-01 | 1899-12-31 | 127 | 12 | 2020-12-01 | 0.625
19 | Dhanmondi | 132 | 134 | 30 | 2020-12-01 | 1899-12-31 | 124 | 26 | 2020-12-01 | 0.45833
20 | Lalbag | 132 | 142 | 4 | 2020-12-01 | 0.75 | 117 | 1 | 2020-12-01 | 0.5
21 | Madartek | 132 | 134 | 31 | 2020-12-01 | 0.875 | 123 | 26 | 2020-12-01 | 0.45833
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Aftabnagar | 132 | 134 | 31 | 2020-12-01 | 0.041667 | 123 | 27 | 2020-12-01 | 0.5
24 | Fatullah | 132 | 137 | 2 | 2020-12-01 | 1899-12-31 | 127 | 26 | 2020-12-01 | 0.5
25 | Mirpur | 132 | 138 | 31 | 2020-12-01 | 0.125 | 119 | 1 | 2020-12-01 | 0.5
26 | Kalyanpur | 132 | 137 | 31 | 2020-12-01 | 0.91667 | 121 | 1 | 2020-12-01 | 0.5
27 | Gulshan | 132 | 134 | 13 | 2020-12-01 | 0.25 | 123 | 26 | 2020-12-01 | 0.45833
28 | Uttara | 132 | 139 | 15 | 2020-12-01 | 0.79167 | 119 | 1 | 2020-12-01 | 0.5
29 | Uttara(New) | 132 | 140 | 31 | 2020-12-01 | 0.875 | 118 | 1 | 2020-12-01 | 0.5
30 | Kamrangirchar | 132 | 141 | 21 | 2020-12-01 | 1899-12-31 | 128 | 0 | 2020-12-01 | 0.25
31 | Savar | 132 | 139 | 25 | 2020-12-01 | 0.25 | 118 | 1 | 2020-12-01 | 0.5
32 | Bhasantec | 132 | 138 | 30 | 2020-12-01 | 1899-12-31 | 123 | 26 | 2020-12-01 | 0.45833
33 | Agargaon | 132 | 138 | 21 | 2020-12-01 | 1899-12-31 | 125 | 26 | 2020-12-01 | 0.5
34 | Satmosjid | 132 | 138 | 22 | 2020-12-01 | 0.041667 | 125 | 26 | 2020-12-01 | 0.5
35 | Tongi | 132 | 142 | 3 | 2020-12-01 | 0.75 | 129 | 28 | 2020-12-01 | 0.625
36 | Kabirpur | 132 | 138 | 30 | 2020-12-01 | 1899-12-31 | 123 | 1 | 2020-12-01 | 0.5
37 | Basundhara | 132 | 141 | 22 | 2020-12-01 | 0.33333 | 124 | 26 | 2020-12-01 | 0.625
38 | Manikganj | 132 | 146 | 21 | 2020-12-01 | 0.875 | 128 | 1 | 2020-12-01 | 0.33333
39 | Joydevpur | 132 | 143 | 9 | 2020-12-01 | 0.75 | 130 | 27 | 2020-12-01 | 0.5
40 | New Tongi | 132 | 141 | 16 | 2020-12-01 | 0.66667 | 128 | 15 | 2020-12-01 | 0.625
41 | Kodda | 132 | 143 | 21 | 2020-12-01 | 0.875 | 120 | 28 | 2020-12-01 | 0.5
42 | Dhamrai | 132 | 137 | 4 | 2020-12-01 | 0.875 | 122 | 27 | 2020-12-01 | 0.41667
43 | Rajendrapur | 132 | 141 | 11 | 2020-12-01 | 0.75 | 124 | 17 | 2020-12-01 | 0.70833
44 | Valuka | 132 | 135 | 11 | 2020-12-01 | 0.70833 | 119 | 5 | 2020-12-01 | 0.375
45 | Tangail | 132 | 136 | 12 | 2020-12-01 | 0.16667 | 120 | 1 | 2020-12-01 | 0.20833
46 | Mymensing | 132 | 135 | 11 | 2020-12-01 | 0.70833 | 120 | 26 | 2020-12-01 | 0.75
47 | Kishorganj | 132 | 135 | 22 | 2020-12-01 | 0.20833 | 120 | 28 | 2020-12-01 | 0.29167
48 | Netrokona | 132 | 135 | 22 | 2020-12-01 | 0.29167 | 117 | 24 | 2020-12-01 | 0.75
49 | Jamalpur | 132 | 141 | 21 | 2020-12-01 | 0.79167 | 119 | 2 | 2020-12-01 | 0.29167
50 | Sherpur | 132 | 140 | 5 | 2020-12-01 | 0.79167 | 117 | 7 | 2020-12-01 | 0.33333
51 | Srimongal | 132 | 140 | 2 | 2020-12-01 | 1899-12-31 | 134 | 26 | 2020-12-01 | 0.45833
52 | Shahjibazar | 132 | 138 | 3 | 2020-12-01 | 0.16667 | 129 | 27 | 2020-12-01 | 0.5
53 | Fenchuganj | 132 | 139 | 12 | 2020-12-01 | 0.95833 | 134 | 26 | 2020-12-01 | 0.77083
54 | Khulawara | 132 | 139 | 23 | 2020-12-01 | 0.29167 | 133 | 26 | 2020-12-01 | 0.8125
55 | Sylhet | 132 | 137 | 9 | 2020-12-01 | 0.375 | 131 | 3 | 2020-12-01 | 0.5
56 | Chattak | 132 | 136 | 9 | 2020-12-01 | 0.083333 | 130 | 3 | 2020-12-01 | 0.5
57 | Sunamganj | 132 | 136 | 8 | 2020-12-01 | 1899-12-31 | 130 | 3 | 2020-12-01 | 0.5
58 | Biani Bazar | 132 | 138 | 19 | 2020-12-01 | 0.33333 | 130 | 5 | 2020-12-01 | 0.75
59 | Comilla(South) | 132 | 133 | 20 | 2020-12-01 | 1900-01-01 12:00 | 122 | 29 | 2020-12-01 | 0.375
60 | Comilla (North) | 132 | 144 | 21 | 2020-12-01 | 0.77083 | 136 | 1 | 2020-12-01 | 11::00
61 | Chandpur | 132 | 145 | 2 | 2020-12-01 | 0.95833 | 136 | 4 | 2020-12-01 | 0.66667
62 | Feni | 132 | 140 | 1 | 2020-12-01 | 0.79167 | 132 | 4 | 2020-12-01 | 0.66667
63 | Chowmuhani | 132 | 140 | 24 | 2020-12-01 | 0.41667 | 128 | 4 | 2020-12-01 | 0.625
64 | Ashuganj | 132 | 140 | 22 | 2020-12-01 | 0.25 | 130 | 26 | 2020-12-01 | 0.66667
65 | Daudkandi | 132 | 141 | 21 | 2020-12-01 | 0.875 | 133 | 1 | 2020-12-01 | 0.41667
66 | Brahminbaria | 132 | 135 | 4 | 2020-12-01 | 0.375 | 125 | 24 | 2020-12-01 | 0.75
67 | Ramganj | 132 | 140 | 31 | 2020-12-01 | 0.95833 | 128 | 5 | 2020-12-01 | 0.83333
68 | Chaddagram | 132 | 142 | 13 | 2020-12-01 | 0.70833 | 133 | 4 | 2020-12-01 | 0.70833
69 | PHP | 132 | 140 | 22 | 2020-12-01 | 0.25 | 125 | 18 | 2020-12-01 | 0.45833
70 | Madanhat | 132 | 141 | 22 | 2020-12-01 | 0 | 127 | 18 | 2020-12-01 | 0.45833
71 | Hathazari | 132 | 139 | 21 | 2020-12-01 | 0.875 | 127 | 6 | 2020-12-01 | 0.66667
72 | Khulshi | 132 | 138 | 31 | 2020-12-01 | 0.77083 | 124 | 4 | 2020-12-01 | 0.66667
73 | Halishahar | 132 | 140 | 31 | 2020-12-01 | 0.77083 | 125 | 2 | 2020-12-01 | 0.125
74 | Baraulia | 132 | 140 | 21 | 2020-12-01 | 0.95833 | 125 | 2 | 2020-12-01 | 0.16667
75 | Sikalbaha | 132 | 140 | 21 | 2020-12-01 | 0.79167 | 125 | 2 | 2020-12-01 | 0.25
76 | Dohazari | 132 | 138 | 30 | 2020-12-01 | 0.77083 | 121 | 24 | 2020-12-01 | 0.41667
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
77 | Cox'sbazar | 132 | 130 | 8 | 2020-12-01 | 0.33333 | 115 | 10 | 2020-12-01 | 0.125
78 | Chandraghona | 132 | 139 | 21 | 2020-12-01 | 0.77083 | 126 | 18 | 2020-12-01 | 0.125
79 | Kaptai | 132 | 139 | 30 | 2020-12-01 | 0.77083 | 127 | 21 | 2020-12-01 | 0.5
80 | A. Khaer Stl. | 132 | 137 | 21 | 2020-12-01 | 0.83333 | 125 | 2 | 2020-12-01 | 0.45833
81 | Bakulia | 132 | 138 | 21 | 2020-12-01 | 0.77083 | 124 | 10 | 2020-12-01 | 0.125
82 | Julda | 132 | 141 | 31 | 2020-12-01 | 0.77083 | 124 | 2 | 2020-12-01 | 0.125
83 | TK Chemical | 132 | 140 | 21 | 2020-12-01 | 0.79167 | 126 | 2 | 2020-12-01 | 0.66667
84 | Modern Steel | 132 | 138 | 22 | 2020-12-01 | 0.041667 | 125 | 10 | 2020-12-01 | 0.125
85 | Shahmirpur | 132 | 140 | 31 | 2020-12-01 | 0.77083 | 124 | 9 | 2020-12-01 | 0.54167
86 | Khagrachhari | 132 | 138 | 24 | 2020-12-01 | 0.29167 | 126 | 2 | 2020-12-01 | 0.45833
87 | Matarbari | 132 | 135 | 10 | 2020-12-01 | 0.77083 | 117 | 22 | 2020-12-01 | 0.75
88 | Baroiar Hat | 132 | 139 | 22 | 2020-12-01 | 0.33333 | 126 | 18 | 2020-12-01 | 0.41667
89 | Rangamati | 132 | 138 | 21 | 2020-12-01 | 0.95833 | 125 | 18 | 2020-12-01 | 0.41667
90 | Goalpara | 132 | 142 | 19 | 2020-12-01 | 0.20833 | 125 | 26 | 2020-12-01 | 0.54167
91 | Khulna Central | 132 | 141 | 31 | 2020-12-01 | 0.91667 | 124 | 15 | 2020-12-01 | 0.75
92 | Noapara | 132 | 140 | 19 | 2020-12-01 | 0.20833 | 123 | 5 | 2020-12-01 | 0.75
93 | Jessore | 132 | 140 | 19 | 2020-12-01 | 0.20833 | 120 | 26 | 2020-12-01 | 0.54167
94 | Benapol | 132 | 137 | 11 | 2020-12-01 | 0.20833 | 119 | 15 | 2020-12-01 | 0.75
95 | Jhenida | 132 | 136 | 12 | 2020-12-01 | 0.083333 | 118 | 5 | 2020-12-01 | 0.75
96 | Bottail | 132 | 139 | 12 | 2020-12-01 | 0.16667 | 124 | 5 | 2020-12-01 | 0.75
97 | G.K Project | 132 | 142 | 20 | 2020-12-01 | 0.16667 | 130 | 3 | 2020-12-01 | 0.83333
98 | Faridpur | 132 | 140 | 19 | 2020-12-01 | 0.125 | 114 | 18 | 2020-12-01 | 0.75
99 | Madaripur | 132 | 142 | 2 | 2020-12-01 | 0.16667 | 129 | 31 | 2020-12-01 | 0.33333
100 | Sariatpur | 132 | 142 | 1 | 2020-12-01 | 0.16667 | 128 | 6 | 2020-12-01 | 0.77083
101 | Gopalganj | 132 | 145 | 30 | 2020-12-01 | 0.70833 | 130 | 2 | 2020-12-01 | 0.8125
102 | Bagerhat | 132 | 140 | 3 | 2020-12-01 | 0.91667 | 122 | 30 | 2020-12-01 | 0.33333
103 | Mongla | 132 | 138 | 11 | 2020-12-01 | 0.41667 | 118 | 30 | 2020-12-01 | 0.33333
104 | Satkhira | 132 | 140 | 21 | 2020-12-01 | 0.625 | 123 | 15 | 2020-12-01 | 0.75
105 | Gallamari | 132 | 141 | 18 | 2020-12-01 | 0.70833 | 123 | 15 | 2020-12-01 | 0.75
106 | Magura | 132 | 136 | 12 | 2020-12-01 | 0.20833 | 116 | 26 | 2020-12-01 | 0.77083
107 | Norail | 132 | 137 | 12 | 2020-12-01 | 0.16667 | 116 | 18 | 2020-12-01 | 0.75
108 | Chuadanga | 132 | 136 | 19 | 2020-12-01 | 0.20833 | 112 | 26 | 2020-12-01 | 0.77083
109 | Barisal(N) | 132 | 144 | 30 | 2020-12-01 | 0.625 | 130 | 13 | 2020-12-01 | 0.58333
110 | Barisal(S) | 132 | 143 | 30 | 2020-12-01 | 0.66667 | 127 | 11 | 2020-12-01 | 0.54167
111 | Patuakhali | 132 | 142 | 31 | 2020-12-01 | 0.625 | 126 | 11 | 2020-12-01 | 0.54167
112 | Bhandaria | 132 | 141 | 20 | 2020-12-01 | 0.16667 | 126 | 11 | 2020-12-01 | 0.54167
113 | Ishurdi | 132 | 140 | 2 | 2020-12-01 | 0.125 | 130 | 3 | 2020-12-01 | 0.83333
114 | Ruppur paromanobik | 132 | 140 | 12 | 2020-12-01 | 0.16667 | 130 | 3 | 2020-12-01 | 0.83333
115 | Natore | 132 | 140 | 12 | 2020-12-01 | 0.125 | 128 | 4 | 2020-12-01 | 0.33333
116 | Bogra | 132 | 140 | 29 | 2020-12-01 | 1899-12-31 | 126 | 17 | 2020-12-01 | 0.75
117 | Noagaon | 132 | 136 | 29 | 2020-12-01 | 1899-12-31 | 120 | 1 | 2020-12-01 | 0.5
118 | Rajshahi | 132 | 142 | 19 | 2020-12-01 | 0.20833 | 130 | 3 | 2020-12-01 | 0.29167
119 | Rajshahi New | 132 | 144 | 23 | 2020-12-01 | 0.70833 | 130 | 3 | 2020-12-01 | 0.041667
120 | C.Nawabganj | 132 | 142 | 23 | 2020-12-01 | 0.70833 | 128 | 3 | 2020-12-01 | 0.5
121 | Amnura | 132 | 143 | 28 | 2020-12-01 | 0.79167 | 128 | 3 | 2020-12-01 | 0.33333
122 | Pabna | 132 | 140 | 19 | 2020-12-01 | 0.16667 | 130 | 3 | 2020-12-01 | 0.83333
123 | Shahjadpur | 132 | 142 | 29 | 2020-12-01 | 0.25 | 133 | 7 | 2020-12-01 | 0.375
124 | Serajganj | 132 | 137 | 31 | 2020-12-01 | 0.041667 | 128 | 4 | 2020-12-01 | 0.33333
125 | Niyamatpur | 132 | 135 | 22 | 2020-12-01 | 0.125 | 118 | 1 | 2020-12-01 | 0.5
126 | Joypurhat | 132 | 137 | 29 | 2020-12-01 | 0.95833 | 119 | 1 | 2020-12-01 | 0.5
127 | Sherpur(Bogura) | 132 | 140 | 31 | 2020-12-01 | 0.041667 | 128 | 4 | 2020-12-01 | 0.33333
128 | Mohastangor | 132 | 138 | 12 | 2020-12-01 | 0.41667 | 119 | 7 | 2020-12-01 | 0.77083
129 | Rangpur | 132 | 132 | 21 | 2020-12-01 | 0.70833 | 114 | 17 | 2020-12-01 | 0.75
130 | Lalmonirhat | 132 | 132 | 12 | 2020-12-01 | 0.25 | 115 | 6 | 2020-12-01 | 0.75
131 | Saidpur | 132 | 132 | 12 | 2020-12-01 | 0.25 | 115 | 18 | 2020-12-01 | 0.75
132 | Purbasadipur | 132 | 132 | 19 | 2020-12-01 | 0.20833 | 112 | 17 | 2020-12-01 | 0.75
133 | Thakurgaon | 132 | 133 | 27 | 2020-12-01 | 0.25 | 112 | 6 | 2020-12-01 | 0.75
134 | Palashbari | 132 | 135 | 19 | 2020-12-01 | 0.25 | 121 | 17 | 2020-12-01 | 0.75
135 | Barapukuria | 132 | 134 | 19 | 2020-12-01 | 0.16667 | 120 | 17 | 2020-12-01 | 0.75
136 | Panchagar | 132 | 132 | 19 | 2020-12-01 | 0.20833 | 108 | 6 | 2020-12-01 | 0.75
137 | Joldhaka | 132 | 133 | 27 | 2020-12-01 | 0.20833 | 112 | 17 | 2020-12-01 | 0.75
138 | Kurigram | 132 | 131 | 23 | 2020-12-01 | 0.70833 | 111 | 17 | 2020-12-01 | 0.75
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:December' 2020
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 120 | 300
Hasnabad | TR2 | 225 | 110 | 300 | 12.12.2020 | 10:00
| TR3 | 225 | 110 | 295
| TR1 | 225 | 130 | 360
Tongi | TR2 | 225 | 130 | 360 | 17.12.2020 | 18:00
| TR3 | 225 | 130 | 360
Haripur | TR1 | 225 | 66 | 175 | 11.12.2020 | 06:00
| TR2 | 225 | 66 | 175
| TR3 | 225 | 66 | 175
| TR1 | 225 | 125 | 323
Rampura | TR2 | 225 | 125 | 323
| TR3 | 225 | 125 | 323 | 07.12.2020 | 12:00
| TR1 | 225 | 190 | 544
Aminbazar | TR2 | 225 |  |  |  |  | S/D
| TR3 | 225 | 199 | 566 | 01.12.2020 | 12:00
Maniknagar | TR1 | 300 | 105 | 330
| TR2 | 300 | 105 | 330 | 03.12.2020 | 11:00
Cumilla (N) | TR1 | 225 | 145 | 371
| TR2 | 225 | 142 | 366 | 25.12.2020 | 6:00
Fenchuganj | AT2 | 300 | 217 | 526 | 19.12.2020 | 20:00
| MT1 | 150 | 59 | 130 | 31.12.2020
Hathazari | MT2 | 150 | 59 | 130
| MT3 | 150 | 59 | 130 |  | 09:00
| MT4 | 150 | 59 | 130
| TR1 | 225 | 117 | 294
Ishurdi | TR2 | 225 | 117 | 294
| TR3 | 225 | 117 | 294 | 30.12.2020 | 19:00
Khulna(S) | TR1 | 225 | 101 | 276
| TR2 | 225 | 101 | 276
| TR3 | 300 | 128 | 358 | 18.12.2020 | 08:00
Bogura | TR1 | 225 | 110 | 293
| TR2 | 225 | 110 | 293 | 21.12.2020 | 24:00
| TR3 | 225 | 159 | 386
Baghabari | TR1 | 300 | 136 | 380
| TR2 | 225 | 100 | 280 | 27.12.2020 | 18:30
Barapukuria | TR1 | 225 | 141 | 650 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 130 | 620 | 29.12.2020 | 19:00 | 132 kV current is being provided
| TR6 | 300 | 170 | 788
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:December' 2020
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 160 | 245 | 08.12.2020 | 5:30
| TR2(400/230 kV) | 520 | 162 | 245
| TR1(400/132 kV) | 325 | 192.5 | 293 | 08.12.2020 | 18:30
| TR2(400/132 kV) | 325 | 192.5 | 293
Bibiyana | ICT1(400/230 kV) | 520 | 371 | 534 | 31.12.2020 | 7:00
| ICT2(400/230kV) | 520 | 364 | 533
Bhulta | ATR1(400/230 kV) | 520 | 154 | 290 | 30.12.2020 | 21:45
| ATR2(400/230kV) | 520 | 154 | 290
Ashuganj(N) | GSUT1 | 567 | 347 | 420 | 02.12.2020 | 17:20
Gopalganj | ATR1(400/138 kV) | 325 | 313 | 473 | 02.12.2020 | 19:30
| ATR2(400/138kV) | 325 | 313 | 473
Payra | GSUT1 | 810 | 624 | 988 | 02.12.2020 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:December' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:December' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-12-20 | 8968 | 8968 | - | - | - | - | - | - | - | - | - | - | - | - | 01-12-20 | 7608 | 7608 | - | - | - | - | - | - | - | - | - | - | - | -
02-12-20 | 8991 | 8991 | - | - | - | - | - | - | - | - | - | - | - | - | 02-12-20 | 7396 | 7396 | - | - | - | - | - | - | - | - | - | - | - | -
03-12-20 | 8928 | 8928 | - | - | - | - | - | - | - | - | - | - | - | - | 03-12-20 | 7491 | 7491 | - | - | - | - | - | - | - | - | - | - | - | -
04-12-20 | 7922 | 7922 | - | - | - | - | - | - | - | - | - | - | - | - | 04-12-20 | 6202 | 6202 | - | - | - | - | - | - | - | - | - | - | - | -
05-12-20 | 9098 | 9098 | - | - | - | - | - | - | - | - | - | - | - | - | 05-12-20 | 6764 | 6764 | - | - | - | - | - | - | - | - | - | - | - | -
06-12-20 | 8996 | 8996 | - | - | - | - | - | - | - | - | - | - | - | - | 06-12-20 | 7331 | 7331 | - | - | - | - | - | - | - | - | - | - | - | -
07-12-20 | 8940 | 8940 | - | - | - | - | - | - | - | - | - | - | - | - | 07-12-20 | 7331 | 7331 | - | - | - | - | - | - | - | - | - | - | - | -
08-12-20 | 8940 | 8940 | - | - | - | - | - | - | - | - | - | - | - | - | 08-12-20 | 7331 | 7331 | - | - | - | - | - | - | - | - | - | - | - | -
09-12-20 | 8815 | 8815 | - | - | - | - | - | - | - | - | - | - | - | - | 09-12-20 | 7249 | 7249 | - | - | - | - | - | - | - | - | - | - | - | -
10-12-20 | 8884 | 8884 | - | - | - | - | - | - | - | - | - | - | - | - | 10-12-20 | 7454 | 7454 | - | - | - | - | - | - | - | - | - | - | - | -
11-12-20 | 7871 | 7871 | - | - | - | - | - | - | - | - | - | - | - | - | 11-12-20 | 6316 | 6316 | - | - | - | - | - | - | - | - | - | - | - | -
12-12-20 | 8743 | 8743 | - | - | - | - | - | - | - | - | - | - | - | - | 12-12-20 | 6644 | 6644 | - | - | - | - | - | - | - | - | - | - | - | -
13-12-20 | 8699 | 8699 | - | - | - | - | - | - | - | - | - | - | - | - | 13-12-20 | 7111 | 7111 | - | - | - | - | - | - | - | - | - | - | - | -
14-12-20 | 8877 | 8877 | - | - | - | - | - | - | - | - | - | - | - | - | 14-12-20 | 7260 | 7260 | - | - | - | - | - | - | - | - | - | - | - | -
15-12-20 | 8816 | 8816 | - | - | - | - | - | - | - | - | - | - | - | - | 15-12-20 | 7160 | 7160 | - | - | - | - | - | - | - | - | - | - | - | -
16-12-20 | 7679 | 7679 | - | - | - | - | - | - | - | - | - | - | - | - | 16-12-20 | 6211 | 6211 | - | - | - | - | - | - | - | - | - | - | - | -
17-12-20 | 8546 | 8546 | - | - | - | - | - | - | - | - | - | - | - | - | 17-12-20 | 6877 | 6877 | - | - | - | - | - | - | - | - | - | - | - | -
18-12-20 | 7888 | 7888 | - | - | - | - | - | - | - | - | - | - | - | - | 18-12-20 | 5988 | 5988 | - | - | - | - | - | - | - | - | - | - | - | -
19-12-20 | 8602 | 8602 | - | - | - | - | - | - | - | - | - | - | - | - | 19-12-20 | 6253 | 6253 | - | - | - | - | - | - | - | - | - | - | - | -
20-12-20 | 8763 | 8763 | - | - | - | - | - | - | - | - | - | - | - | - | 20-12-20 | 7251 | 7251 | - | - | - | - | - | - | - | - | - | - | - | -
21-12-20 | 8862 | 8862 | - | - | - | - | - | - | - | - | - | - | - | - | 21-12-20 | 7108 | 7108 | - | - | - | - | - | - | - | - | - | - | - | -
22-12-20 | 8860 | 8860 | - | - | - | - | - | - | - | - | - | - | - | - | 22-12-20 | 7089 | 7089 | - | - | - | - | - | - | - | - | - | - | - | -
23-12-20 | 8950 | 8950 | - | - | - | - | - | - | - | - | - | - | - | - | 23-12-20 | 6930 | 6930 | - | - | - | - | - | - | - | - | - | - | - | -
24-12-20 | 8838 | 8838 | - | - | - | - | - | - | - | - | - | - | - | - | 24-12-20 | 7129 | 7129 | - | - | - | - | - | - | - | - | - | - | - | -
25-12-20 | 7815 | 7815 | - | - | - | - | - | - | - | - | - | - | - | - | 25-12-20 | 6248 | 6248 | - | - | - | - | - | - | - | - | - | - | - | -
26-12-20 | 8775 | 8775 | - | - | - | - | - | - | - | - | - | - | - | - | 26-12-20 | 6305 | 6305 | - | - | - | - | - | - | - | - | - | - | - | -
27-12-20 | 8843 | 8843 | - | - | - | - | - | - | - | - | - | - | - | - | 27-12-20 | 7231 | 7231 | - | - | - | - | - | - | - | - | - | - | - | -
28-12-20 | 8808 | 8808 | - | - | - | - | - | - | - | - | - | - | - | - | 28-12-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-12-20 | 8945 | 8945 | - | - | - | - | - | - | - | - | - | - | - | - | 29-12-20 | 7434 | 7434 | - | - | - | - | - | - | - | - | - | - | - | -
30-12-20 | 8911 | 8911 | - | - | - | - | - | - | - | - | - | - | - | - | 30-12-20 | 7367 | 7367 | - | - | - | - | - | - | - | - | - | - | - | -
31-12-20 | 8853 | 8853 | - | - | - | - | - | - | - | - | - | - | - | - | 31-12-20 | 7275 | 7275 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:December' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9098 | 05-12-2020 | 19:00
2 | Maximum Day Peak Genaration | MW | 7608 | 01-12-2020 | 12:00
3 | Maximum Evening Peak Demand | MW | 9098 | 05/12/20 | 19:00
4 | Minimum Generation | MW | 4945 | 19/12/20 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8691.1613
6 | Average of the daily day peak Genaration | MW | 6979.6774
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5210.4282
12 | Total Generation by BPDB | MKWH | 2669.4632 | % of total Gen. | 51.23%
13 | Total Generation by IPP | MKWH | 1594.4422 | '' | 30.6%
14 | A) Total Generation by RPCL | MKWH | 85.9993 | '' | 1.651%
| B) Total Generation by REB | MKWH | 124.3119 | " | 2.386%
| C) Total Generation by RENTAL | MKWH | 305.4926 | " | 5.863%
| D) Total Imported from India (BIPTC) | MKWH | 370.5357 | " | 7.111%
| E) Total Imported from Tripura, India (A.C) | MKWH | 60.1834 | " | 1.155%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3403.3482 | % of total Gen. | 65.32%
| B) Oil | MKWH | 959.763 | '' | 18.42%
| C) Hydro | MKWH | 39.3592 | '' | 0.7554%
| D) Solar | MKWH | 4.6748 | '' | 0.08972%
| E) Coal | MKWH | 372.5639 | '' | 7.15%
| F) BIPTC (Import from India) | MKWH | 370.5357 | '' | 7.111%
| G) A.C (Import from Tripura, India) | MKWH | 60.1834 | '' | 1.155%
16 | Maximun of the daily total Generation . | MKWH | 194.5302 | 08-12-2020
17 | Monthly Load factor | % | 79.5417
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 14729.2262
| A) Gas | M.Taka | 3678.5884
| B) Liquid fuel | M.Taka | 6994.7221
| C) Coal | M.Taka | 1714.8083
| D) BIPTC (Import from India) | M.Taka | 1889.7322
| E) Tripura(Import from India) | M.Taka | 451.3752
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 587.362 | 10/12/2020
| A) Gas | M.Taka | 161.717 | 08/12/2020
| B) Liquid fuel | M.Taka | 395.3061 | 10/12/2020
| C) Coal | M.Taka | 69.1176 | 02/12/2020
| D) BIPTC (Import from India) | M.Taka | 69.8014 | 30-12-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.8451
| B) Excluding Hydro & Solar | Taka/KWHR | 2.8689
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 103.2 | 31/12/2020 | 06:00
b) | Actual | FT (MSL) | 98.21 | 31/12/2020 | 06:00
22 | Peak Genaration of December 2019 | MW | 8778 | 01/12/19 | 19:00
23 | Peak Demand of December 2019 | MW | 8778 | 01/12/19 | 19:00
24 | Maximum peak Generation recorded upto 31/12/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/12/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/12/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.