## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-20 | Wednesday
|  |  | Date (day): | 2021-01-20 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11811.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12946 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-19 | 2021-01-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 234 | 233 | 230 | 230
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 380 | 365 | 365 | 0
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 324 | 335 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 242 | 218 | 280 | 280 | 80 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 55 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 88 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 86 | 85 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 70 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 6 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 19 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 285 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 139 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 99 | 104 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2169 | 2873 | 3433 | 3697 | 1001 | 1328
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 0 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 44 | 44 | 44 | 186 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 50 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 13 | 10 | 15
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 16 | 90 | 90 |  | 18 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 270 | 306 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 572 | 745 | 1100 | 1205 | 921 | 123
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 151 | 159 | 180 | 180 |  |  | Gas shortage
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 260 | 280 | 280 |  |  | Gas shortage
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 250 | 250 |  |  | Gas shortage
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 3 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 73 | 75 | 75 |  | 75 | Engine Problem
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 36 | 50 | 50 |  | 113 | Engine problem
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 23 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 19 | 21 | 21
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 86 | 108 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 55 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1037 | 1097 | 1598 | 1862 | 680 | 188
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 103 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 67 | 82 | 95 | 95
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 17 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 7 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 25 | 25 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 399 | 449 | 615.6 | 564 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 20 | 20 |  | 50 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 31 | 32 | 43 | 43
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 140 | 163 | 163
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 19 | 8 | 8 |  |  | Gas shortage
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 15 | 20 | 20
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 32 | 32 | 40 | 40
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 68 | 70 | 70 | 70 |  | 16 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 162 | 160 | 160 |  | 71 | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 300 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 270 | 270 | 270 | 270 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 988 | 1086 | 1183 | 1183 | 0 | 884
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 726 | 871 | 741 | 886
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 35 | 35 |  | 19 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 7 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 345 | 350 | 350
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 24 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 72 | 90 | 90 |  | 15 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1275 | 1438 | 1591 | 2022 | 0 | 73
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 22 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 84 | 91 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 430 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 15 | 57 | 50 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 553 | 616 | 877 | 883 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 28 | 28 |  | 22 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 378 | 351 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 21 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 631 | 813 | 1143 | 1267 | 821 | 22
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 264 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7888 | 9380 | 11811.6 | 12946 | 3639 | 3033
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7529.7603 | 8954 | 11275.167 | 12358.0473
| A. |  | 2021-01-19 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9380 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5711 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9380 | MW
| 3 | Day peak Generation : |  |  | 7888 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8954 | MW
| 4 | Evening peak Generation : |  |  | 9380 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 182.7549 | MKWHr | By Solar | 0.21785 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 101.5274 | MKWHr |  | By Oil: | 46.5584 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.5923 | MKWHr |  | By Hydro: | 1.1216 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3639 | MW | Dhaka | 3078 | 3078 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3033 | MW | Chittagong | 1032 | 1032 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6672 | MW | Khulna | 1102 | 1102 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 758.53 | MMCFD |  |  | Rajshahi | 960 | 960 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 104684141.664 | ii) Oil : | Taka | 342111476.08 | Comilla | 746 | 746 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 67837722 | Total | Taka | 514633339.744 | Mymensingh | 810 | 810 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.15 | MKWHr. | Sylhet | 329 | 329 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 2 | MW (E to W) at | 19:00 | hrs | Barisal | 233 | 233 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -46 | MW at | 19:30 | hrs | Rangpur | 664 | 664 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 24.0° C |  |  | Total | 8954 | 8954 |  | 0
| B. |  | 2021-01-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 26.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12946 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 3446 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 185.0929 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5941 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6589 | MKWHr. | ii) HVDC Flow at Peak Time |  | 871 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0784 | MKWHr. | iii) Maximum HVDC Flow : |  | 872 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.95 |  | (b) Today: | 96.87 |  | (c) Rule Curve: |  | 99.39
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 234 | 0 | 380 | 0 | 0 | 350 | 281 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 33 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 33 | 0 | 0 | 0 | 250 | 240 | 160 | 8 | 44 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 21 | 76 | 109 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 73 | 0 | 156 | 19 | 0 | 7 | 290 | 8 | 11 | 0 | 145 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 17 | 75 | 0 | 0 | 0 | 0 | 0 | 271 | 24 | 0 | 0 | 0 | 100 | 271 | 17 | 0 | 35 | 0 | 0 |  | 445 | 0 | 345 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 293 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 440 | 57 | 0 | 0 |  | 4447 | 2089 | 6536 | 2889 | 445 | 1353 | 1137 | 590 | 46 | 0 | 76 | 0 | 0 | 96.96
2:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 343 | 281 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 33 | 0 | 0 | 0 | 250 | 240 | 158 | 8 | 47 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 74 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 130 | 0 | 33 | 73 | 0 | 149 | 19 | 0 | 7 | 280 | 8 | 11 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 35 | 0 | 0 |  | 445 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 334 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 440 | 57 | 0 | 0 |  | 4215 | 1983 | 6198 | 2887 | 445 | 1342 | 814 | 590 | 46 | 0 | 74 | 0 | 0 | 96.96
3:00 | 0 | 0 | 234 | 0 | 380 | 0 | 0 | 335 | 283 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 250 | 240 | 157 | 8 | 42 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 72 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 33 | 73 | 0 | 149 | 19 | 0 | 7 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 271 | 35 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 35 | 0 | 0 |  | 445 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 310 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 57 | 0 | 0 |  | 4084 | 1850 | 5934 | 2869 | 445 | 1327 | 616 | 560 | 45 | 0 | 72 | 0 | 0 | 96.96
4:00 | 0 | 0 | 232 | 0 | 380 | 0 | 0 | 335 | 292 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 250 | 240 | 164 | 8 | 43 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 70 | 108 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 33 | 73 | 0 | 150 | 19 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 234 | 35 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 35 | 0 | 0 |  | 445 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 57 | 0 | 0 |  | 4036 | 1803 | 5839 | 2863 | 445 | 1327 | 529 | 560 | 45 | 0 | 70 | 0 | 0 | 96.95
5:00 | 0 | 0 | 233 | 0 | 340 | 0 | 0 | 337 | 303 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 250 | 240 | 170 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 72 | 109 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 20 | 40 | 0 | 120 | 19 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 216 | 35 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 35 | 0 | 0 |  | 445 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 59 | 0 | 0 |  | 3935 | 1776 | 5711 | 2806 | 445 | 1333 | 509 | 500 | 46 | 0 | 72 | 0 | 0 | 96.95
6:00 | 0 | 0 | 231 | 0 | 340 | 0 | 0 | 359 | 303 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 20 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 250 | 240 | 172 | 8 | 46 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 74 | 109 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 140 | 0 | 21 | 40 | 0 | 120 | 19 | 0 | 0 | 310 | 0 | 11 | 0 | 5 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 216 | 35 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 35 | 0 | 0 |  | 588 | 0 | 395 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 58 | 0 | 0 |  | 4000 | 1980 | 5980 | 2852 | 588 | 1378 | 543 | 500 | 45 | 0 | 74 | 0 | 0 | 96.95
7:00 | 0 | 0 | 234 | 0 | 300 | 0 | 0 | 358 | 294 |  | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 18 | 20 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 9 | 19 | 38 | 0 | 0 | 0 | 250 | 240 | 178 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 0 | 33 | 18 | 74 | 109 | 0 | 22 | 0 | 0 | 43 | 8 | 5 | 140 | 0 | 32 | 40 | 0 | 120 | 18 | 0 | 0 | 310 | 0 | 11 | 0 | 36 | 0 | 0 | 65 | 0 | 2 | 1 | 24 | 12 | 75 | 0 | 0 | 0 | 0 | 0 | 215 | 35 | 0 | 0 | 2 | 100 | 270 | 6 | 0 | 35 | 0 | 0 |  | 633 | 0 | 375 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 340 | 17 | 0 | 30 | 0 | 50 | 0 | 0 | 35 | 350 | 57 | 0 | 0 |  | 4149 | 2167 | 6316 | 2809 | 633 | 1364 | 887 | 500 | 48 | 0 | 74 | 1 | 0 | 96.94
8:00 | 0 | 0 | 235 | 0 | 281 | 0 | 0 | 363 | 292 |  | 0 | 0 | 0 | 16 | 28 | 15 | 0 | 0 | 0 | 0 | 24 | 10 | 77 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 25 | 22 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 18 | 19 | 14 | 0 | 0 | 0 | 280 | 240 | 165 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 0 | 33 | 18 | 78 | 104 | 5 | 22 | 0 | 0 | 43 | 8 | 5 | 110 | 0 | 32 | 60 | 0 | 120 | 18 | 0 | 0 | 320 | 0 | 11 | 0 | 96 | 0 | 0 | 132 | 0 | 17 | 4 | 90 | 17 | 75 | 0 | 0 | 0 | 0 | 1 | 251 | 35 | 0 | 0 | 26 | 100 | 270 | 20 | 2 | 35 | 0 | 0 |  | 726 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 373 | 53 | 0 | 80 | 0 | 90 | 0 | 0 | 90 | 360 | 16 | 0 | 0 |  | 4569 | 2498 | 7067 | 2855 | 726 | 1330 | 1506 | 510 | 45 | 10 | 78 | 7 | 0 | 96.94
9:00 | 0 | 0 | 230 | 0 | 250 | 0 | 0 | 340 | 245 |  | 0 | 0 | 0 | 16 | 55 | 33 | 0 | 0 | 0 | 20 | 60 | 48 | 84 | 0 | 0 | 0 | 17 | 17 | 15 | 19 | 25 | 22 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 30 | 19 | 12 | 0 | 0 | 0 | 270 | 240 | 140 | 8 | 46 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 30 | 18 | 78 | 106 | 52 | 22 | 0 | 0 | 31 | 8 | 5 | 140 | 0 | 32 | 67 | 0 | 120 | 18 | 0 | 7 | 300 | 0 | 11 | 0 | 204 | 0 | 0 | 200 | 0 | 65 | 9 | 100 | 17 | 75 | 0 | 16 | 10 | 0 | 2 | 270 | 35 | 0 | 0 | 26 | 100 | 270 | 72 | 4 | 35 | 0 | 0 |  | 726 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 393 | 70 | 0 | 113 | 0 | 108 | 0 | 1 | 109 | 440 | 17 | 0 | 0 |  | 5014 | 2739 | 7753 | 2692 | 726 | 1370 | 2188 | 590 | 45 | 48 | 78 | 16 | 0 | 96.94
10:00 | 0 | 0 | 234 | 0 | 250 | 0 | 0 | 324 | 242 |  | 0 | 0 | 0 | 16 | 88 | 41 | 0 | 0 | 0 | 40 | 102 | 48 | 86 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 20 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 32 | 19 | 5 | 0 | 0 | 0 | 270 | 240 | 151 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 14 | 8 | 25 | 18 | 86 | 102 | 67 | 20 | 0 | 0 | 31 | 8 | 5 | 140 | 0 | 32 | 68 | 0 | 120 | 18 | 0 | 5 | 280 | 0 | 11 | 0 | 285 | 0 | 0 | 170 | 0 | 100 | 13 | 50 | 17 | 75 | 0 | 8 | 17 | 0 | 3 | 270 | 35 | 0 | 0 | 26 | 100 | 270 | 99 | 7 | 35 | 0 | 0 |  | 726 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 378 | 70 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 440 | 15 | 0 | 0 |  | 5165 | 2723 | 7888 | 2661 | 726 | 1325 | 2383 | 590 | 45 | 48 | 86 | 24 | 0 | 96.93
11:00 | 0 | 0 | 231 | 0 | 250 | 0 | 0 | 353 | 231 |  | 0 | 0 | 0 | 16 | 80 | 30 | 0 | 0 | 0 | 15 | 74 | 32 | 85 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 26 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 32 | 19 | 2 | 0 | 0 | 0 | 270 | 240 | 165 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 14 | 8 | 25 | 18 | 88 | 102 | 48 | 20 | 0 | 0 | 31 | 8 | 5 | 140 | 0 | 31 | 67 | 0 | 120 | 18 | 0 | 7 | 300 | 0 | 11 | 0 | 285 | 0 | 0 | 151 | 0 | 78 | 15 | 95 | 17 | 75 | 0 | 8 | 17 | 0 | 4 | 270 | 35 | 0 | 0 | 26 | 90 | 270 | 104 | 8 | 35 | 0 | 0 |  | 727 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 2 | 0 | 24 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 426 | 70 | 0 | 113 | 0 | 113 | 0 | 1 | 57 | 380 | 54 | 0 | 0 |  | 5132 | 2642 | 7774 | 2666 | 727 | 1420 | 2236 | 530 | 45 | 34 | 88 | 28 | 0 | 96.93
12:00 | 0 | 0 | 236 | 0 | 280 | 0 | 0 | 326 | 246 |  | 0 | 0 | 0 | 20 | 80 | 31 | 0 | 0 | 0 | 15 | 93 | 48 | 86 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 30 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 33 | 19 | 2 | 0 | 0 | 0 | 275 | 240 | 156 | 8 | 42 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 25 | 18 | 92 | 102 | 48 | 20 | 2 | 0 | 31 | 8 | 5 | 140 | 0 | 31 | 70 | 0 | 120 | 18 | 0 | 9 | 300 | 5 | 11 | 0 | 287 | 0 | 0 | 160 | 0 | 71 | 16 | 100 | 17 | 75 | 0 | 8 | 17 | 0 | 4 | 270 | 49 | 0 | 0 | 31 | 100 | 270 | 104 | 24 | 35 | 0 | 0 |  | 726 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 24 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 401 | 77 | 0 | 113 | 0 | 107 | 0 | 2 | 57 | 380 | 33 | 0 | 0 |  | 5286 | 2598 | 7884 | 2678 | 726 | 1394 | 2320 | 530 | 45 | 51 | 92 | 48 | 0 | 96.93
13:00 | 0 | 0 | 232 | 0 | 350 | 0 | 0 | 327 | 244 |  | 0 | 0 | 0 | 34 | 92 | 41 | 0 | 0 | 0 | 50 | 102 | 82 | 86 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 25 | 30 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 48 | 19 | 2 | 0 | 0 | 0 | 275 | 240 | 156 | 8 | 37 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 25 | 18 | 92 | 97 | 56 | 20 | 2 | 0 | 31 | 8 | 5 | 110 | 0 | 31 | 70 | 0 | 120 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 170 | 0 | 127 | 16 | 60 | 17 | 75 | 0 | 0 | 17 | 0 | 4 | 285 | 54 | 0 | 0 | 55 | 90 | 240 | 104 | 29 | 35 | 0 | 0 |  | 727 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 30 | 0 | 0 | 322 | 77 | 0 | 113 | 0 | 107 | 0 | 3 | 57 | 400 | 46 | 0 | 0 |  | 5404 | 2634 | 8038 | 2728 | 727 | 1292 | 2464 | 550 | 46 | 85 | 92 | 54 | 8038 | 96.92
14:00 | 0 | 0 | 235 | 0 | 370 | 0 | 0 | 327 | 244 |  | 0 | 0 | 0 | 11 | 64 | 30 | 0 | 0 | 0 | 40 | 16 | 48 | 86 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 25 | 30 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 2 | 0 | 0 | 0 | 270 | 240 | 148 | 8 | 41 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 25 | 15 | 92 | 85 | 48 | 20 | 1 | 0 | 32 | 8 | 5 | 110 | 0 | 30 | 70 | 0 | 120 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 210 | 0 | 0 | 140 | 0 | 104 | 13 | 20 | 17 | 75 | 0 | 0 | 0 | 0 | 3 | 285 | 54 | 0 | 0 | 55 | 90 | 270 | 104 | 0 | 35 | 0 | 0 |  | 727 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 350 | 77 | 0 | 113 | 0 | 113 | 0 | 3 | 35 | 410 | 56 | 0 | 0 |  | 5062 | 2590 | 7652 | 2757 | 727 | 1332 | 2065 | 560 | 48 | 51 | 92 | 20 | 0 | 96.92
15:00 | 0 | 0 | 232 | 0 | 375 | 0 | 0 | 335 | 234 |  | 0 | 0 | 0 | 7 | 64 | 30 | 0 | 0 | 0 | 20 | 0 | 32 | 86 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 31 | 25 | 25 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 2 | 0 | 0 | 0 | 270 | 240 | 139 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 25 | 19 | 88 | 87 | 48 | 20 | 1 | 0 | 32 | 8 | 5 | 110 | 0 | 30 | 70 | 0 | 121 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 210 | 0 | 0 | 140 | 0 | 88 | 10 | 20 | 17 | 72 | 0 | 0 | 0 | 0 | 2 | 285 | 54 | 0 | 0 | 55 | 90 | 270 | 104 | 0 | 35 | 0 | 0 |  | 726 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 364 | 58 | 0 | 113 | 0 | 64 | 0 | 3 | 35 | 380 | 56 | 0 | 0 |  | 4998 | 2492 | 7490 | 2790 | 726 | 1297 | 1958 | 530 | 49 | 36 | 88 | 16 | 0 | 96.92
16:00 | 0 | 0 | 229 | 0 | 370 | 0 | 0 | 335 | 229 |  | 0 | 0 | 0 | 7 | 64 | 30 | 0 | 0 | 0 | 7 | 0 | 32 | 85 | 0 | 0 | 0 | 17 | 0 | 55 | 16 | 25 | 32 | 25 | 25 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 5 | 0 | 0 | 0 | 260 | 240 | 134 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 5 | 32 | 19 | 88 | 85 | 48 | 20 | 0 | 0 | 32 | 8 | 5 | 110 | 0 | 31 | 70 | 0 | 121 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 210 | 0 | 0 | 140 | 0 | 50 | 5 | 20 | 17 | 75 | 0 | 0 | 0 | 0 | 1 | 291 | 54 | 0 | 0 | 55 | 93 | 270 | 53 | 0 | 0 | 0 | 0 |  | 727 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 350 | 35 | 0 | 75 | 0 | 49 | 0 | 2 | 35 | 380 | 55 | 0 | 0 |  | 4847 | 2417 | 7264 | 2771 | 727 | 1300 | 1755 | 530 | 49 | 36 | 88 | 8 | 0 | 96.91
17:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 347 | 221 |  | 0 | 0 | 0 | 7 | 65 | 30 | 0 | 0 | 0 | 8 | 0 | 48 | 85 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 32 | 25 | 25 | 2 | 0 | 47 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 6 | 50 | 19 | 6 | 0 | 0 | 0 | 260 | 240 | 139 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 3 | 19 | 8 | 32 | 18 | 90 | 103 | 48 | 22 | 0 | 0 | 32 | 8 | 10 | 110 | 0 | 31 | 70 | 0 | 120 | 18 | 0 | 9 | 315 | 8 | 11 | 0 | 213 | 0 | 0 | 170 | 0 | 50 | 1 | 20 | 17 | 75 | 0 | 0 | 7 | 0 | 0 | 290 | 54 | 0 | 0 | 55 | 100 | 270 | 53 | 0 | 72 | 0 | 0 |  | 730 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 14 | 16 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 368 | 35 | 0 | 77 | 0 | 49 | 0 | 0 | 35 | 380 | 57 | 0 | 0 |  | 5062 | 2501 | 7563 | 2837 | 730 | 1323 | 1939 | 530 | 47 | 66 | 90 | 1 | 0 | 96.91
18:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 326 | 222 |  | 0 | 0 | 0 | 43 | 98 | 35 | 0 | 0 | 0 | 50 | 5 | 115 | 85 | 0 | 0 | 1 | 54 | 35 | 55 | 19 | 25 | 18 | 25 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 18 | 50 | 19 | 8 | 0 | 0 | 0 | 260 | 240 | 142 | 8 | 42 | 3 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 28 | 21 | 110 | 104 | 60 | 22 | 0 | 0 | 32 | 19 | 15 | 110 | 0 | 31 | 70 | 0 | 162 | 18 | 0 | 9 | 280 | 8 | 11 | 0 | 269 | 0 | 0 | 192 | 0 | 70 | 0 | 20 | 17 | 75 | 0 | 5 | 50 | 0 | 0 | 290 | 54 | 0 | 0 | 55 | 100 | 270 | 74 | 0 | 144 | 0 | 0 |  | 864 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 4 | 6 | 8 | 0 | 21 | 16 | 0 | 0 | 0 | 43 | 0 | 102 | 25 | 0 | 6 | 25 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 353 | 72 | 0 | 111 | 0 | 113 | 0 | 0 | 100 | 390 | 56 | 0 | 0 |  | 5692 | 3006 | 8698 | 2841 | 864 | 1298 | 2638 | 540 | 46 | 361 | 110 | 0 | 0 | 96.91
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 335 | 218 |  | 0 | 0 | 0 | 55 | 100 | 40 | 0 | 0 | 0 | 100 | 70 | 150 | 85 | 0 | 0 | 6 | 54 | 55 | 55 | 19 | 25 | 32 | 25 | 25 | 19 | 0 | 44 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 16 | 50 | 19 | 13 | 0 | 0 | 0 | 260 | 240 | 159 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 25 | 21 | 108 | 103 | 82 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 70 | 0 | 162 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 139 | 0 | 50 | 23 | 73 | 0 | 17 | 105 | 0 | 0 | 306 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 871 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 4 | 7 | 24 | 0 | 22 | 16 | 0 | 0 | 0 | 43 | 0 | 102 | 25 | 0 | 12 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 351 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 57 | 0 | 0 |  | 6250 | 3130 | 9380 | 2875 | 871 | 1385 | 3114 | 580 | 44 | 403 | 108 | 0 | 0 | 96.9
19:30 | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 325 | 219 |  | 0 | 0 | 0 | 55 | 100 | 40 | 0 | 0 | 0 | 100 | 70 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 32 | 25 | 25 | 8 | 0 | 43 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 54 | 0 | 0 | 50 | 19 | 14 | 0 | 0 | 0 | 260 | 240 | 161 | 8 | 42 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 108 | 101 | 82 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 70 | 0 | 162 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 148 | 0 | 50 | 34 | 75 | 0 | 25 | 103 | 0 | 0 | 307 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 872 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 5 | 7 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 369 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 57 | 0 | 0 |  | 6194 | 3047 | 9241 | 2871 | 872 | 1395 | 3024 | 610 | 43 | 318 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 231 | 0 | 380 | 0 | 0 | 326 | 219 |  | 0 | 0 | 0 | 55 | 100 | 40 | 0 | 0 | 0 | 80 | 70 | 150 | 86 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 32 | 25 | 25 | 8 | 0 | 45 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 59 | 0 | 0 | 50 | 19 | 12 | 0 | 0 | 0 | 260 | 240 | 164 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 108 | 103 | 82 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 69 | 0 | 162 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 148 | 0 | 50 | 34 | 76 | 0 | 25 | 53 | 0 | 0 | 307 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 871 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 5 | 7 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 399 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 57 | 0 | 0 |  | 6090 | 3063 | 9153 | 2869 | 871 | 1409 | 2918 | 610 | 45 | 323 | 108 | 0 | 0 | 96.9
21:00 | 0 | 0 | 235 | 0 | 380 | 0 | 0 | 340 | 204 |  | 0 | 0 | 0 | 55 | 100 | 40 | 0 | 0 | 0 | 35 | 70 | 115 | 86 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 44 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 17 | 0 | 0 | 50 | 19 | 14 | 0 | 0 | 0 | 260 | 240 | 169 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 19 | 106 | 98 | 82 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 69 | 0 | 162 | 18 | 0 | 9 | 305 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 108 | 0 | 50 | 34 | 73 | 0 | 8 | 53 | 0 | 0 | 307 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 872 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 388 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 470 | 57 | 0 | 0 |  | 5896 | 3093 | 8989 | 2897 | 872 | 1399 | 2812 | 620 | 44 | 239 | 106 | 0 | 0 | 96.9
22:00 | 0 | 0 | 232 | 0 | 380 | 0 | 0 | 334 | 207 |  | 0 | 0 | 0 | 25 | 64 | 15 | 0 | 0 | 0 | 0 | 48 | 64 | 86 | 0 | 0 | 0 | 17 | 0 | 55 | 16 | 25 | 32 | 25 | 17 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 23 | 0 | 0 | 0 | 260 | 240 | 175 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 94 | 101 | 64 | 22 | 0 | 0 | 31 | 19 | 15 | 140 | 0 | 32 | 69 | 0 | 161 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 32 | 0 | 20 | 34 | 75 | 0 | 0 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 872 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 365 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 21 | 0 | 0 |  | 5462 | 3080 | 8542 | 2900 | 872 | 1373 | 2418 | 670 | 44 | 171 | 94 | 0 | 0 | 96.89
23:00 | 0 | 0 | 234 | 0 | 380 | 0 | 0 | 324 | 212 |  | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 77 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 25 | 33 | 25 | 17 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 25 | 0 | 0 | 0 | 260 | 240 | 164 | 8 | 37 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 90 | 104 | 0 | 22 | 0 | 0 | 31 | 19 | 15 | 140 | 0 | 32 | 70 | 0 | 162 | 18 | 0 | 9 | 270 | 8 | 11 | 0 | 245 | 0 | 0 | 130 | 0 | 13 | 0 | 0 | 17 | 73 | 0 | 0 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 26 | 100 | 265 | 104 | 0 | 144 | 0 | 40 |  | 872 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 369 | 35 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 480 | 19 | 0 | 0 |  | 5017 | 2768 | 7785 | 2910 | 872 | 1342 | 1843 | 630 | 45 | 53 | 90 | 0 | 0 | 96.89
24:00 | 0 | 0 | 230 | 0 | 380 | 0 | 0 | 337 | 215 |  | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 33 | 20 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 20 | 0 | 0 | 0 | 260 | 240 | 160 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 80 | 104 | 0 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 70 | 0 | 162 | 19 | 0 | 9 | 310 | 8 | 11 | 0 | 180 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 17 | 76 | 0 | 0 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 26 | 100 | 265 | 58 | 0 | 144 | 0 | 50 |  | 653 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 405 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 70 | 470 | 56 | 0 | 0 |  | 4731 | 2486 | 7217 | 2933 | 653 | 1448 | 1417 | 619 | 46 | 21 | 80 | 0 | 0 | 96.89
KWH | 0 | 0 | 5588000 | 0 | 8177764 | 0 | 0 | 8246510 | 5912000 |  | 0 | 0 | 0 | 422400 | 1374480 | 512958 | 0 | 0 | 0 | 542400 | 780768 | 1100160 | 1636485 | 0 | 0 | 10368 | 380160 | 314613 | 719834 | 409824 | 600000 | 669780 | 613600 | 584900 | 51360 | 0 | 1121629 | 0 | 0 | 0 | 39049 | 0 | 0 | 0 | 0 |  | 407280 | 0 | 251493 | 0 | 47040 | 797280 | 454560 | 471360 | 0 | 0 | 0 | 6634000 | 5894000 | 3820000 | 200727 | 978610 | 71280 | 0 | 0 | 1249561 | 0 | 0 | 22690 | 385776 | 173700 | 714300 | 473700 | 2078400 | 2404560 | 901440 | 499356 | 5750 | 0 | 842280 | 273000 | 283752 | 3253664 | 0 | 735264 | 1585920 | 0 | 3287790 | 441000 | 0 | 150660 | 7442000 | 107760 | 264000 | 0 | 4606689 | 0 | 0 | 3324000 | 0 | 1283620 | 99900 | 817920 | 421440 | 1798182 | 0 | 117600 | 414888 | 0 | 22080 | 6646581 | 1086230 | 0 | 0 | 839160 | 2365440 | 6434400 | 1561920 | 69540 | 1654560 | 0 | 80770 |  | 16658909 | 0 | 8548416 | 0 | 1825920 | 0 | 0 | 0 | 46560 | 16640 | 228000 | 0 | 426300 | 44064 | 0 | 0 | 0 | 82272 | 0 | 510232 | 73510 | 0 | 11976 | 51360 | 0 | 520080 | 0 | 171252 | 0 | 0 | 3667500 | 0 | 0 | 0 | 0 | 0 | 0 | 1588422 | 66240 | 0 | 0 | 8689818 | 1084320 | 0 | 2165760 | 0 | 1635840 | 0 | 20579 | 1465248 | 10924800 | 1173000 | 0 | 0 |  | 121057915 | 61697018 | 182754933 | 68307152 | 16658909 | 33220264 | 44539097 | 14592300 | 1121629 | 2019333 | 2078400 | 217849 | 0
Fuel Cost | 0 | 0 | 8158480 | 0 | 9077318.04 | 0 | 0 | 8328975.1 | 6089360 |  | 0 | 0 | 0 | 3206016 | 9470167.2 | 4339624.68 | 0 | 0 | 0 | 4084272 | 7120604.16 | 10825574.4 | 15088391.7 | 0 | 0 | 94245.12 | 2775168 | 2431958.49 | 7097563.24 | 307368 | 450000 | 0 | 0 | 0 | 496651.2 | 0 | 302839.83 | 0 | 0 | 0 | 362765.21 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2439482.1 | 0 | 409248 | 6314457.6 | 572745.6 | 1399939.2 | 0 | 0 | 0 | 4909160 | 5894000 | 3514400 | 258937.83 | 1125401.5 | 80546.4 | 0 | 0 | 2136749.31 | 0 | 0 | 216689.5 | 489935.52 | 130275 | 1250025 | 355275 | 15588000 | 2548833.6 | 8185075.2 | 634182.12 | 91655 | 0 | 1347648 | 485940 | 442653.12 | 3709176.96 | 0 | 1448470.08 | 3029107.2 | 0 | 5687876.7 | 965790 | 0 | 307346.4 | 7516420 | 80820 | 200640 | 0 | 34826568.84 | 0 | 0 | 17284800 | 0 | 12630820.8 | 1167831 | 6666048 | 4572624 | 12677183.1 | 0 | 1072512 | 3920691.6 | 0 | 0 | 50248152.36 | 9461063.3 | 0 | 0 | 7191601.2 | 15753830.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95955315.84 | 0 | 8975836.8 | 0 | 14351731.2 | 0 | 0 | 0 | 488414.4 | 174387.2 | 2375760 | 0 | 660765 | 430064.64 | 0 | 0 | 0 | 809556.48 | 0 | 4515553.2 | 566027 | 0 | 116047.44 | 497678.4 | 0 | 998553.6 | 0 | 129637.764 | 0 | 0 | 19877850 | 0 | 0 | 0 | 0 | 0 | 0 | 2382633 | 1126742.4 | 0 | 0 | 8602919.82 | 11320300.8 | 0 | 20553062.4 | 0 | 12694118.4 | 0 | 227397.95 | 10828182.72 | 47959872 | 0 | 0 | 0 |  | 361347970.91 | 266618408.454 | 627966379.364 | 66663640.224 | 95955315.84 | 38020501.44 | 322742460.86 | 67837722 | 302839.83 | 19369015.22 | 15588000 | 1486883.95 | 0
Yesterday Day Peak | 0 | 0 | 234 | 0 | 250 | 0 | 0 | 324 | 242 |  | 0 | 0 | 0 | 16 | 88 | 41 | 0 | 0 | 0 | 40 | 102 | 48 | 86 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 20 | 25 | 25 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 32 | 19 | 5 | 0 | 0 | 0 | 270 | 240 | 151 | 8 | 45 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 14 | 8 | 25 | 18 | 86 | 102 | 67 | 20 | 0 | 0 | 31 | 8 | 5 | 140 | 0 | 32 | 68 | 0 | 120 | 18 | 0 | 5 | 280 | 0 | 11 | 0 | 285 | 0 | 0 | 170 | 0 | 100 | 13 | 50 | 17 | 75 | 0 | 8 | 17 | 0 | 3 | 270 | 35 | 0 | 0 | 26 | 100 | 270 | 99 | 7 | 35 | 0 | 0 |  | 726 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 378 | 70 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 440 | 15 | 0 | 0 |  | 7888 | DayPeak
Yesterday Evening Peak | 0 | 0 | 233 | 0 | 380 | 0 | 0 | 335 | 218 | 0 | 0 | 0 | 0 | 55 | 100 | 40 | 0 | 0 | 0 | 100 | 70 | 150 | 85 | 0 | 0 | 6 | 54 | 55 | 55 | 19 | 25 | 32 | 25 | 25 | 19 | 0 | 44 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 85 | 0 | 16 | 50 | 19 | 13 | 0 | 0 | 0 | 260 | 240 | 159 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 25 | 21 | 108 | 103 | 82 | 22 | 0 | 0 | 32 | 19 | 15 | 140 | 0 | 32 | 70 | 0 | 162 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 139 | 0 | 50 | 23 | 73 | 0 | 17 | 105 | 0 | 0 | 306 | 54 | 0 | 0 | 55 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 871 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 4 | 7 | 24 | 0 | 22 | 16 | 0 | 0 | 0 | 43 | 0 | 102 | 25 | 0 | 12 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 351 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 57 | 0 | 0 |  | 9380 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 365 | 0 | 0 | 412 | 280 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 44 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 15 | 0 | 0 | 0 | 280 | 250 | 180 | 8 | 50 | 5 | 0 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 22 | 147 | 110 | 95 | 22 | 0 | 20 | 43 | 8 | 20 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 75 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 104 | 0 | 144 | 0 | 0 |  | 886 | 16 | 350 | 0 | 115 | 220 | 0 | 0 | 35 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 28 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 56 |  | 0
Forecast for Day | 0 | 0 | 230 | 0 | 365 | 0 | 0 | 412 | 280 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 15 | 10 | 0 | 0 | 0 | 280 | 250 | 180 | 8 | 50 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 135 | 110 | 95 | 22 | 1.6 | 20 | 43 | 8 | 20 | 163 | 0 | 40 | 70 | 0 | 160 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 75 | 0 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 270 | 90 | 50 | 144 | 0 | 0 |  | 741 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 28 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 50 |  | 0
Generation at 08:00(Today) | 0 | 0 | 219 | 0 | 380 | 0 | 0 | 324 | 247 | 0 | 0 | 0 | 0 | 43 | 49 | 0 | 0 | 0 | 0 | 27 | 40 | 32 | 73 | 0 | 0 | 0 | 54 | 0 | 35 | 13 | 25 | 22 | 25 |  | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 6 | 0 | 21 | 19 | 8 | 0 | 0 | 0 | 260 | 240 | 162 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 80 | 107 | 60 | 22 | 0 | 0 | 31 | 8 | 20 | 100 | 0 | 20 | 72 | 0 | 131 | 0 | 0 | 0 | 280 | 8 | 11 | 0 | 119 | 0 | 0 | 122 | 0 | 62 | 3 | 60 | 17 | 72 | 0 | 8 | 52 | 0 | 1 | 307 | 54 | 0 | 0 | 35 | 90 | 236 | 66 | 4 | 144 | 0 | 0 | 0 | 725 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 53 | 0 | 50 | 0 | 111 | 0 | 0 | 50 | 380 | 26 | 0 | 0 | 0
199
| Minimum Generation |  | 5711 | 5:00
| Highest Generation |  | 9380 | 19:00
| Day Peak Generation |  | 7888 | 10:00
| Evening Peak Generation |  | 9380 | 19:00
| HVDC Max Flow |  | 872 | 19:30
| HVDC EvPeak Flow |  | 871 | 19:00
| Load factor L.F |  | 81.18%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7888 | MW Hour : | 10:00 | Min. Gen. at | 5:00 | 5941 | MW
Evening Peak Generation : |  | 9380 | MW Hour : | 19:00 | Available Max Generation : |  | 12946 | MW
E.P. Demand (at gen end) : |  | 9380 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9380 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3446 | MW
Total Gen. (MKWH) : |  | 182.7549 | System Load Factor : | 81.18% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -46 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-20
Actual : | 96.87 | Ft.(MSL) , | Rule curve : | 99.39 | Ft.( MSL )
Gas Consumed : | Total = | 758.53 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104684141.664
: |  | Coal : | 67837722 | Oil : | 342111476.08 | Total : | 514633339.744
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3384.1067 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1146.6958 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1026.673 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 927.427 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 838.245 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 676.4237 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 383.4833 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.3001 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 521.6664 |  |  | 0 | 0%
Total | 0 |  | 9079.0211 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-3,4,5
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,3,5
4) Shahjibazar 330 MW
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,3 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) B.Baria-Norsingdi 132 kV Ckt was under shut down from 09:04 to 17:00 for A/M.
b) Julda-Shahmirpur 132 kV Ckt-2 was under shut down from 08:36 to 15:47 for A/M.
c) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 08:54 to 17:36 for A/M.
d) Mirpur 132/33 kV T2 Transformer was under shut down from 08:35 to 16:02 for A/M
e) Kulaura-Fenchuganj 132 kV Ckt-2 was under shut down from 09:13 to 17:41 for A/M.
f) Haripur-Sonargaon 132 kV Ckt-1 was under shut down from 08:17 to 13:43 for A/M.
g) Tangail-RPCL 132 kV Ckt-2 was under shut down from 09:56 to 16:08 for A/M.
h) Ashuganj-Bhulta 400 kV Ckt-1 was under shut down from 08:46 to 20:13 for A/M.
i) Aminbazar-Manikganj 132 kV Ckt-1 was under shut down from 09:44 to 17:11 for D/W.
j) Mymensingh-Jamalpur 132 kV Ckt-2 was under shut down from 09:21 to 15:34 for A/M.
k) Rajshahi(N)-Rajshahi 132 kV Ckt-1 was under shut down from 08:08 to 17:22 for A/M.
l) Bogura-Sherpur 132 kV Ckt-1 was under shut down from 10:29 to 15:25 for A/M.
m) Barisal(N)-Barisal(O) 132 kV Ckt-2 was under shut down from 08:34 to 15:11 for A/M.
n) Kustia-Jhenaidah 132 kV Ckt-2 was under shut down from 08:42 to 20:27 for D/W.
o) Saver 132 kV Bus-A was under shut down from 10:15 to 17:55 for C/M.
p) Sirajganj 132/33 kV T3 Transformer was under shut down from 10:21 to 15:17 for C/M
q) Kamrangichar 132/33 kV T1 Transformer was under shut down from 10:21 to 15:17 for C/M
r) Saver 132/33 kV T1 Transformer was under shut down from 08:54 to 17:54 for C/M
s) Chandraghona 132/33 kV T2 Transformer was under shut down from 09:03 to 14:44 for C/M
t) Biyanibazar 132/33 kV T1 Transformer was under shut down from 10:07 to 16:28 for C/M
u) Mymensing 132 kV Bus-B was under shut down from 09:51 to 17:47 for D/W.
v) Shahjadpur 132/33 kV T3 Transformer was under shut down from 09:57 to 15:45 for A/M
w) Bheramara HVDC 20DF44 no shunt rector was under shut down from 09:23 to 14:46 for C/M.
x) Bottail-Bheramara 230 kV Ckt-2 was under shut down from 11:03 to 12:12 for protection test.
y) Bottail-Bheramara 230 kV Ckt-1 was under shut down from 12:33 to 13:35 for protection test.
z) Dohazari-Cox'sbazar 132 kV Ckt-1 was under shut down from 11:05 to 15:05 for D/W.
aa) Shyampur-APR 230 kV Ckt tripped at 12:31 showing E/F, Y-phase relay at APR end and was
switched on at 12:43.
ab) Natore 132/33 kV T2 transformer was under shut down from 11:44 to 14:36 for C/M.
ac) Keraniganj 230/132 kV T1 transformer was under shut down from 11:25 to 16:05 for A/M.
ad) Tangail-Kaliakoir 132 kV Ckt-2 was switched on at 11:38.
ae) Keraniganj 230/132 kV T2 transformer was under shut down from 11:45 to 15:01 for A/M.
af) Gopalganj(O)-Gollamari 132 kV Ckt-1 was shut down at 11:14 for A/M.
ag) Haripur-Sonargaon 132 kV Ckt-2 was under shut down from 13:44 to 16:39 for A/M.
ah) Kishoreganj-Mymensing 132 kV Ckt-1 was under shut down from 16:34 to 17:03 for relay test.
ai) Kishoreganj-Mymensing 132 kV Ckt-2 was under shut down from 17:05 to 17:38 for relay test.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 233 | 5588000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 8177764
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8246510 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 218 | 5912000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 55 | 422400 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1374480
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 512958 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1636485 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 409824
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 542400
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 70 | 780768 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 6 | 10368 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 380160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1100160
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 314613
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 719834
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1269780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 613600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 584900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 19 | 51360 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4606689
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 139 | 1283620
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 414888
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1561920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1654560 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2873 | 48170041
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 39049 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 99900
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 797280
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 1121629 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 251493
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 817920 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 454560 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 471360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 16 | 47040 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22080
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 6646581
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1086230
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | High Voltage.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2365440
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 745 | 14220562
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 159 | 3820000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6634000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5894000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 3 | 71280 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1249561
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 73 | 1798182 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 36 | 978610 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 23 | 421440 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 385776
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2078400
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 714300 | Machine problem
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 22690 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 473700 | Machine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 839160 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1097 | 25755526
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2404560 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499356
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 82 | 901440 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5750
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3324000 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 17 | 117600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 69540
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 407280
| Mymensingh Area Total |  |  |  | 709 | 449 | 7729526
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 842280 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3253664 | Frequency Control
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 19 | 273000 | Gas shortage
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 15 | 283752 | Gas shortage
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 735264 | Gas shortage
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 70 | 1585920 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 80770 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 3287790
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 441000 | Engine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 107760 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7442000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 150660
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 270 | 6434400 | On test
| Sylhet Area Total |  |  |  | 1988 | 1086 | 25182260
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 871 | 16658909
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1825920
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 46560
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 7 | 16640
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8548416 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 228000 | Low demand
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 66240 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 72 | 1084320 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1438 | 28475005
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 44064 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 426300 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 91 | 1588422
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 10924800 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 57 | 1173000 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1676 | 616 | 14156586
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 82272
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 73510 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 11976
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 351 | 8689818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 520080
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 171252
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 51360
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 510232
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2165760
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1465248
| Rajshahi Area Total |  |  |  | 2183 | 813 | 13741508
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3667500
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1635840
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20579
| Rangpur Area Total |  |  |  | 605 | 263 | 5323919
| Total |  |  |  | 20748 | 9380 | 182754933
| Eastern Grid Total |  |  |  | 14000 | 6250 | 121057915
| Western Grid Total |  |  |  | 6748 | 3130 | 61697018
| National Grid Total |  |  |  | 20748 | 9380 | 182754933
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-19
| (a) ENTIRE EASTERN GRID : |  | 5995 | MW | (b) ENTIRE WESTERN GRID : |  | 2959 | MW
| i) Dhaka area |  | 3078 | MW | i) Khulna area |  | 1102 | MW
| ii) Chittagong area |  | 1032 | MW | ii) Rajshahi area |  | 960 | MW
| iii) Comilla area |  | 746 | MW | iii) Barisal area |  | 233 | MW
| iv) Mymensingh area |  | 810 | MW | iv) Rangpur area |  | 664 | MW
| v) Sylhet area |  | 329 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8954 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 102 | 18:00 | Jamalpur | 98 | 20:00 | Benapol | 44 | 18:30
| Munsiganj | 84 | 19:30 | Sherpur | 116 | 19:00 | Jhenida | 82 | 18:30
| Sonargaon | 64 | 22:00 | Srimongal | 28 | 19:30 | Bottail | 104 | 18:30
| Shyampur | 168 | 0:00 | Shahjibazar | 90 | 19:30 | G.K Project | 27 | 19:00
| Bhulta | 147 | 12:00 | Fenchuganj | 25 | 18:00 | Faridpur | 134 | 19:00
| Madanganj | 52 | 11:00 | Kulawara | 27 | 18:00 | Madaripur | 63 | 19:00
| Shitalakhya | 94 | 12:00 | Sylhet | 81 | 18:00 | Sariatpur | 42 | 19:30
| Rahim steel | 22 | 14:00 | Chatak | 21 | 19:30 | Gopalganj | 60 | 18:30
| Matuail | 45 | 9:00 | Sunamganj | 30 | 19:00 | Bagerhat | 87 | 18:30
| Ghorasal | 66 | 18:00 | Biani Bazar | 35 | 20:00 | Mongla | 39 | 18:30
| Narsingdi | 128 | 19:30 | Comilla (S) | 110 | 18:00 | Satkhira | 71 | 18:30
| Haripur (SBU) | 99 | 18:30 | Comilla(N) | 77 | 19:00 | Gallamari | 21 | 13:00
| Ullon | 40 | 18:00 | Chandpur | 57 | 20:00 | Magura | 38 | 18:30
| Hasnabad | 124 | 19:30 | Feni | 75 | 18:00 | Norail | 24 | 18:30
| Magbazar | 56 | 12:00 | Chowmuhani | 116 | 19:00 | Chuadanga | 63 | 18:30
| Maniknagar | 60 | 13:00 | Ashuganj | 39 | 18:30 | Barisal(N) | 27 | 19:00
| Bangabhaban | 15 | 12:00 | Daudkandi | 92 | 20:00 | Barisal (S) | 70 | 20:00
| Narinda | 60 | 13:00 | B.Baria | 101 | 19:00 | Patuakhali | 77 | 18:30
| Dhanmondi | 82 | 13:00 | Ramganj | 76 | 19:30 | Bhandaria | 40 | 19:30
| Lalbag | 68 | 12:00 | Chaddagram | 23 | 19:00 | Borhan Uddin | 28 | 20:00
| Madartek | 42 | 21:00 | PHP | 10 | 14:00 | Ishurdi | 46 | 19:00
| Dhaka University |  |  | Madunaghat | 43 | 18:00 | Ruppur Paromanobik | 2 | 18:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 64 | 0.79167 | Natore | 87 | 0.77083
| Fatullah | 44 | 9:00 | Khulshi | 161 | 16:00 | Bogra | 118 | 18:30
| Mirpur | 72 | 18:00 | Halishahar | 93 | 12:00 | Noagaon | 85 | 19:30
| Kalyanpur | 69 | 18:00 | Baraulia | 136 | 7:00 | Rajshahi | 99 | 20:00
| Gulshan | 74 | 18:00 | Sikalbaha | 21 | 18:00 | Rajshahi New | 12 | 18:30
| Uttara | 58 | 18:00 | Dohazari | 58 | 18:00 | C.Nawabganj | 62 | 19:30
| Uttara New | 28 | 18:00 | Cox'sbazar | 79 | 18:00 | Amnura | 42 | 18:30
| Kamrangirchar | 72 | 18:30 | Chandraghona | 20 | 18:00 | Pabna | 59 | 18:30
| Savar | 121 | 18:30 | Kaptai | 3.6 | 18:00 | Shahjadpur | 68 | 19:00
| Bhasantec | 106 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 80 | 19:30
| Agargaon | 46 | 13:00 | Bakulia | 73 | 12:00 | Niyamatpur | 76 | 19:00
| Satmosjid | 56 | 0.54167 | Julda | 21 | 0.77083 | Joypurhat | 54 | 0.77083
| Tongi | 92 | 18:00 | TK chemical | 91 | 18:00 | Sherpur(Bogura) | 40 | 19:30
| Kabirpur | 189 | 14:00 | Modern Steel | 0 | 1:00 | Mohastangor | 32 | 18:30
| Basundhara | 89 | 18:30 | Shahmirpur | 21 | 18:30 | Bangura | 16 | 18:00
| Manikganj | 66 | 20:00 | Khagrachhari | 20 | 3:00 | Rangpur | 123 | 18:30
| Joydevpur | 125 | 19:00 | Matarbari | 29 | 18:30 | Lalmonirhat | 54 | 18:30
| New Tongi | 76 | 12:00 | Baroiar Hat | 26 | 18:00 | Saidpur | 103 | 18:30
| Kodda | 162 | 9:00 | Rangamati | 8 | 12:00 | Purbasadipur | 88 | 20:00
| Dhamrai | 54 | 18:30 | Abul Khair 230 | 146 | 2:00 | Thakurgaon | 62 | 18:30
| Rajendrapur | 66 | 18:30 | BSRM | 145 | 4:00 | Palashbari | 91 | 19:00
| Valuka | 90 | 18:30 | GPH Ispat | 82 | 0:00 | Barapukuria | 56 | 10:00
| Tangail | 149 | 18:30 | Goalpara | 15 | 18:30 | Panchagar | 43 | 19:00
| Mymensing | 162 | 19:00 | Central s/s | 78 | 18:30 | Joldhaka | 33 | 18:30
| Kishorganj | 100 | 19:00 | Noapara | 57 | 18:30 | Kurigram | 45 | 18:00
| Netrokona | 111 | 18:30 | Jessore | 82 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 21:00 | 409 | 12:00 | Kaliakoir | 400 | 0.20833 | 339 | 0.79167
| Bheramara | 409 | 10:00 | 391 | 19:00 | Bhulta | 392 | 0.041667 | 376 | 0.66667
| Ashuganj(N) | 398 | 21:00 | 388 | 15:00 | Gopalganj | 412 | 0.20833 | 397 | 0.875
| Payra | 416 | 19:00 | 407 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 18:00 | 238 | 1:00 | Hathazari | 226 | 18:30 | 219 | 23:00
| Ishurdi | 244 | 1:00 | 236 | 8:00 | Megnaghat | 238 | 6:00 | 230 | 7:00
| Ashuganj | 242 | 19:00 | 238 | 11:00 | Fenchuganj | 244 | 5:00 | 239 | 15:00
| Serajganj | 235 | 1:00 | 230 | 8:00 | Siddhirganj | 235 | 18:00 | 228 | 15:00
| Baghabari | 241 | 4:00 | 233 | 19:30 | Maniknagar | 234 | 19:00 | 227 | 15:00
| Barapukuria | 232 | 1:00 | 227 | 18:30 | Agargaon | 235 | 15:00 | 225 | 15:00
| Bogra | 235 | 1:00 | 229 | 16:00 | Barisal | 251 | 3:00 | 244 | 20:00
| Rajshahi | 240 | 22:00 | 229 | 8:00 | Bhola 225 MW | 253 | 2:00 | 222 | 18:00
| Khulna South | 244 | 1:00 | 234 | 18:30 | AKSML | 229 | 3:00 | 218 | 24:00
| Rampura | 232 | 18:00 | 228 | 15:00 | BSRM | 232 | 1:00 | 219 | 24:00
| Haripur | 234 | 18:00 | 228 | 16:00 | Bibiyana | 245 | 10:00 | 239 | 23:00
| Hasnabad | 234 | 7:00 | 226 | 15:00 | Bhulta | 237 | 21:00 | 229 | 15:00
| Shyampur | 234 | 19:00 | 220 | 15:00 | Ashuganj (S) | 239 | 1:00 | 234 | 15:00
| Aminbazar | 235 | 19:00 | 226 | 13:00 | Kaliakoir | 233 | 19:00 | 222 | 15:00
| Tongi | 230 | 18:00 | 223 | 7:00 | GPH | 227 | 4:00 | 213 | 24:00
| Comilla (N) | 240 | 19:00 | 233 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 18:00 | 133 | 15:00 | Madanhat | 141 | 0.33333 | 135 | 0.125
| Munsiganj | 142 | 18:00 | 134 | 1:00 | Hathazari | 137 | 0.20833 | 135 | 0.041667
| Sonargaon | 137 | 18:00 | 133 | 2:00 | Khulshi | 137 | 0.77083 | 133 | 0.45833
| Shyampur | 134 | 19:00 | 129 | 15:00 | Halishahar | 138 | 0.041667 | 134 | 0.41667
| Bhulta | 135 | 19:00 | 130 | 15:00 | Baraulia | 138 | 0.66667 | 132 | 0.75
| Madanganj | 138 | 18:00 | 132 | 5:00 | Sikalbaha | 139 | 0.125 | 134 | 0.625
| Shitalakhya | 139 | 20:00 | 129 | 15:00 | Dohazari | 136 | 0.375 | 131 | 0.041667
| Rahim steal | 138 | 18:00 | 134 | 15:00 | Cox'sbazar | 129 | 0.79167 | 122 | 0.5
| Matuail | 139 | 18:00 | 133 | 15:00 | Chandraghona | 138 | 0.75 | 134 | 0.5
| Ghorasal | 140 | 18:00 | 138 | 1:00 | Kaptai | 139 | 0.70833 | 135 | 0.041667
| Narsinghdi | 135 | 18:00 | 131 | 10:00 | A. Khaer Stl. | 136 | 0.75 | 134 | 0.41667
| Haripur (SBU) | 138 | 16:00 | 134 | 7:00 | Bakulia | 137 | 0.20833 | 132 | 0.95833
| Ullon | 134 | 1:00 | 129 | 15:00 | Julda | 139 | 0.29167 | 135 | 0.41667
| Hasnabad | 136 | 21:00 | 128 | 16:00 | TK Chemical | 139 | 0.79167 | 132 | 0.54167
| Magbazar | 135 | 4:00 | 128 | 15:00 | Modern Steel | 138 | 0.33333 | 134 | 0.5
| Maniknagar | 139 | 1:00 | 136 | 11:00 | Shahmirpur | 138 | 0.41667 | 132 | 0
| Bangabhaban | 139 | 1:00 | 136 | 11:00 | Khagrachhari | 139 | 0.125 | 134 | 0.45833
| Narinda | 139 | 1:00 | 136 | 11:00 | Matarbari | 133 | 0.66667 | 124 | 0.041667
| Dhanmondi | 134 | 1:00 | 129 | 15:00 | Baroiar Hat | 138 | 0.75 | 135 | 0.041667
| Lalbag | 136 | 21:00 | 130 | 3:00 | Rangamati | 139 | 10:00 | 134 | 11:00
| Madartek | 133 | 1:00 | 128 | 15:00 | Goalpara S/S | 138 | 3:00 | 133 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 138 | 1:00 | 134 | 0.77083
| Aftabnagar | 133 | 1:00 | 129 | 16:00 | Noapara | 136 | 1:00 | 130 | 0.33333
| Fatuiiah | 135 | 19:00 | 129 | 15:00 | Jessore | 133 | 4:00 | 126 | 0.77083
| Mirpur | 136 | 19:00 | 130 | 16:00 | Benapol | 135 | 0.16667 | 126 | 0.77083
| Kalyanpur | 136 | 19:00 | 130 | 14:00 | Jhenida | 135 | 1:00 | 124 | 0.77083
| Gulshan | 137 | 6:00 | 128 | 12:00 | Bottail | 136 | 0.16667 | 131 | 0.5
| Uttara | 135 | 6:00 | 129 | 15:00 | G.K Project | 141 | 0.041667 | 138 | 0.375
| Uttara New | 139 | 19:00 | 133 | 12:00 | Faridpur | 138 | 0.25 | 134 | 0.8125
| Kamrangirchar | 134 | 19:30 | 130 | 15:00 | Madaripur | 142 | 0.16667 | 139 | 0.54167
| Savar | 137 | 19:30 | 129 | 12:00 | Shariyatpur S/S | 142 | 6:00 | 136 | 0.8125
| Bhasantec | 138 | 1:00 | 131 | 15:00 | Gopalganj | 144 | 0.20833 | 138 | 0.8125
| Agargaon | 138 | 1:00 | 134 | 12:00 | Bagerhat | 137 | 9:00 | 131 | 0.77083
| Satmosjid | 138 | 21;00 | 132 | 15:00 | Mongla | 136 | 10:00 | 129 | 0.29167
| Tongi | 139 | 18:00 | 134 | 17:00 | Satkhira | 138 | 1:00 | 131 | 18:30
| Kabirpur | 135 | 17:00 | 126 | 12:00 | Gallamari | 139 | 0.041667 | 133 | 0.77083
| Basundhara | 139 | 21:00 | 132 | 15:00 | Magura | 135 | 1:00 | 124 | 0.77083
| Manikganj | 145 | 13:00 | 135 | 23:00 | Narail | 134 | 0.125 | 124 | 0.45833
| Joydevpur | 138 | 19:00 | 133 | 15:00 | Chuadanga | 131 | 2:00 | 119 | 0.77083
| New Tongi | 139 | 19:00 | 133 | 15:00 | Barisal(N) | 142 | 1:00 | 137 | 20:00
| Kodda | 140 | 18:30 | 127 | 23:00 | Barisal (S) | 141 | 0.20833 | 136 | 0.8125
| Dhamrai | 133 | 1:00 | 124 | 15:00 | Patuakhali(S) | 141 | 0.41667 | 137 | 0.70833
| Rajendrapur | 139 | 19:00 | 133 | 16:00 | Bhandaria | 140 | 0.125 | 134 | 0.8125
| Valuka | 125 | 1:00 | 115 | 15:00 | Ishurdi | 140 | 4:00 | 136 | 11:00
| Tangail | 134 | 22:00 | 126 | 8:00 | Ruppur Paromanobik | 138 | 3:00 | 136 | 12:00
| Mymensing | 127 | 1:00 | 120 | 12:00 | Natore | 137 | 18:00 | 133 | 8:00
| Kishorganj | 130 | 4:00 | 124 | 12:00 | Bogra | 139 | 1:00 | 134 | 11:00
| Netrokona | 126 | 3:00 | 117 | 14:00 | Noagaon | 133 | 3:00 | 126 | 9:00
| Jamalpur | 137 | 19:00 | 121 | 2:00 | Rajshahi | 136 | 5:00 | 131 | 8:00
| Sherpur | 135 | 19:00 | 119 | 7:00 | Rajshahi New | 137 | 5:00 | 131 | 13:00
| Srimongal | 136 | 1:00 | 135 | 7:00 | C.Nawabganj | 136 | 18:00 | 128 | 12:00
| Shahjibazar | 134 | 5:00 | 131 | 12:00 | Amnura | 135 | 18:00 | 128 | 11:00
| Fenchuganj | 137 | 6:00 | 134 | 12:00 | Pabna | 141 | 1:00 | 134 | 18:30
| Khulawara | 137 | 5:00 | 135 | 11:00 | Shahjadpur | 141 | 5:00 | 138 | 7:00
| Sylhet | 135 | 4:00 | 134 | 1:00 | Serajganj | 137 | 5:00 | 133 | 12:00
| Chatak | 135 | 4:00 | 132 | 18:00 | Niyamatpur | 131 | 1:00 | 123 | 11:00
| Sunamganj | 135 | 4:00 | 132 | 13:00 | Joypurhat | 134 | 5:00 | 124 | 9:00
| Biani Bazar | 136 | 6:00 | 133 | 15:00 | Sherpur(Bogura) | 138 | 4:00 | 133 | 10:00
| Comilla(s) | 131 | 2:00 | 127 | 11:00 | Mohastangor | 135 | 4:00 | 132 | 8:00
| Comilla(n) | 143 | 19:00 | 140 | 11:00 | Bangura | 139 | 3:00 | 136 | 16:00
| Chandpur | 142 | 1:00 | 140 | 18:30 | Rangpur | 129 | 6:00 | 122 | 18:30
| Feni | 139 | 14:00 | 136 | 17:00 | Lalmonirhat | 130 | 5:00 | 121 | 18:30
| Chowmuhani | 136 | 18:00 | 135 | 7:00 | Saidpur | 130 | 4:00 | 120 | 18:30
| Ashuganj | 136 | 1:00 | 135 | 7:00 | Purbasadipur | 129 | 6:00 | 120 | 18:30
| Daudkandi | 139 | 9:00 | 135 | 17:00 | Thakurgaon | 130 | 1:00 | 120 | 18:30
| B.Baria | 132 | 8:00 | 130 | 11:00 | Palashbari | 134 | 3:00 | 125 | 8:00
| Ramganj | 138 | 16:00 | 134 | 20:00 | Barapukuria | 132 | 3:00 | 127 | 18:30
| Chaddagram | 140 | 19:00 | 137 | 10:00 | Panchagar | 128 | 5:00 | 119 | 18:30

## L-Curve
Date | 2021-01-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 269 | 4731 | 2486 | 7217 |  |  |  | QF-LDC-11
0:30 | 145.5 | 4589 | 2287.5 | 6876.5 | Date: | 2021-01-19
1:00 | 22 | 4447 | 2089 | 6536
1:30 | 30 | 4331 | 2036 | 6367
2:00 | 38 | 4215 | 1983 | 6198
2:30 | 26 | 4149.5 | 1916.5 | 6066 | [5 empty] | Gen. at Eve. Peak | 9380 | 9380 MW (19:00 )
3:00 | 14 | 4084 | 1850 | 5934 | [6 empty] | 19:00
3:30 | 19.5 | 4060 | 1826.5 | 5886.5 | [5 empty] | Gen. at Day Peak | 7888 | 7888 MW (10:00 )
4:00 | 25 | 4036 | 1803 | 5839 | [6 empty] | 10:00
4:30 | 26 | 3985.5 | 1789.5 | 5775 | [5 empty] | Highest Generation | 9380
5:00 | 27 | 3935 | 1776 | 5711 | [6 empty] | 19:00
5:30 | 55.5 | 3967.5 | 1878 | 5845.5
6:00 | 84 | 4000 | 1980 | 5980
6:30 | 69.5 | 4074.5 | 2073.5 | 6148
7:00 | 55 | 4149 | 2167 | 6316
7:30 | 69 | 4359 | 2332.5 | 6691.5
8:00 | 83 | 4569 | 2498 | 7067
8:30 | 110 | 4791.5 | 2618.5 | 7410
9:00 | 137 | 5014 | 2739 | 7753
9:30 | 217 | 5089.5 | 2731 | 7820.5
10:00 | 297 | 5165 | 2723 | 7888
10:30 | 294 | 5148.5 | 2682.5 | 7831
11:00 | 291 | 5132 | 2642 | 7774
11:30 | 234.5 | 5209 | 2620 | 7829
12:00 | 178 | 5286 | 2598 | 7884
12:30 | 149.5 | 5345 | 2616 | 7961
13:00 | 121 | 5404 | 2634 | 8038
13:30 | 204.5 | 5233 | 2612 | 7845
14:00 | 288 | 5062 | 2590 | 7652
14:30 | 335 | 5030 | 2541 | 7571
15:00 | 382 | 4998 | 2492 | 7490
15:30 | 349.5 | 4922.5 | 2454.5 | 7377
16:00 | 317 | 4847 | 2417 | 7264
16:30 | 337 | 4954.5 | 2459 | 7413.5
17:00 | 357 | 5062 | 2501 | 7563
17:30 | 205.5 | 5377 | 2753.5 | 8130.5
18:00 | 54 | 5692 | 3006 | 8698
18:30 | 28 | 5971 | 3068 | 9039
19:00 | 2 | 6250 | 3130 | 9380
19:30 | 46 | 6194 | 3047 | 9241
20:00 | 8 | 6090 | 3063 | 9153 |  |  |  | Executive Engineer
20:30 | 87.5 | 5993 | 3078 | 9071 |  |  |  | Network Operation Division
21:00 | 167 | 5896 | 3093 | 8989
21:30 | 264.5 | 5679 | 3086.5 | 8765.5
22:00 | 362 | 5462 | 3080 | 8542 |  |  |  |  | Page 6 of 7
22:30 | 351 | 5239.5 | 2924 | 8163.5
23:00 | 340 | 5017 | 2768 | 7785
23:30 | 304.5 | 4874 | 2627 | 7501
24:00 | 269 | 4731 | 2486 | 7217
9380 MW (19:00 )
7888 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-19 |  | Energy | 182754933
[11 empty] | 2021-01-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2933 | 653 | 1448 | 1843 | 619 | 46 | 21 | 0 | 80 | 0
0:30 | 2911 | 549 | 1400.5 | 1490 | 604.5 | 46 | 10.5 | 0 | 78 | 0 | Date: | 2021-01-19
1:00 | 2889 | 445 | 1353 | 1137 | 590 | 46 | 0 | 0 | 76 | 0
1:30 | 2888 | 445 | 1347.5 | 975.5 | 590 | 46 | 0 | 0 | 75 | 0 | [7 empty] | Total Energy | 182.7549 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2887 | 445 | 1342 | 814 | 590 | 46 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2878 | 445 | 1334.5 | 715 | 575 | 45.5 | 0 | 0 | 73 | 0 | [7 empty] | Energy Requirement | 182.7549
3:00 | 2869 | 445 | 1327 | 616 | 560 | 45 | 0 | 0 | 72 | 0
3:30 | 2866 | 445 | 1327 | 572.5 | 560 | 45 | 0 | 0 | 71 | 0 | [6 empty] | Shortage
4:00 | 2863 | 445 | 1327 | 529 | 560 | 45 | 0 | 0 | 70 | 0
4:30 | 2834.5 | 445 | 1330 | 519 | 530 | 45.5 | 0 | 0 | 71 | 0
5:00 | 2806 | 445 | 1333 | 509 | 500 | 46 | 0 | 0 | 72 | 0
5:30 | 2829 | 516.5 | 1355.5 | 526 | 500 | 45.5 | 0 | 0 | 73 | 0
6:00 | 2852 | 588 | 1378 | 543 | 500 | 45 | 0 | 0 | 74 | 0
6:30 | 2830.5 | 610.5 | 1371 | 715 | 500 | 46.5 | 0 | 0 | 74 | 0.5 |  |  |  |  | Coal
7:00 | 2809 | 633 | 1364 | 887 | 500 | 48 | 0 | 0 | 74 | 1
7:30 | 2832 | 679.5 | 1347 | 1196.5 | 505 | 46.5 | 5 | 0 | 76 | 4 |  |  |  | Oil |  |  |  | ,
8:00 | 2855 | 726 | 1330 | 1506 | 510 | 45 | 10 | 0 | 78 | 7
8:30 | 2773.5 | 726 | 1350 | 1847 | 550 | 45 | 29 | 0 | 78 | 11.5
9:00 | 2692 | 726 | 1370 | 2188 | 590 | 45 | 48 | 0 | 78 | 16
9:30 | 2676.5 | 726 | 1347.5 | 2285.5 | 590 | 45 | 48 | 0 | 82 | 20
10:00 | 2661 | 726 | 1325 | 2383 | 590 | 45 | 48 | 0 | 86 | 24
10:30 | 2663.5 | 726.5 | 1372.5 | 2309.5 | 560 | 45 | 41 | 0 | 87 | 26
11:00 | 2666 | 727 | 1420 | 2236 | 530 | 45 | 34 | 0 | 88 | 28
11:30 | 2672 | 726.5 | 1407 | 2278 | 530 | 45 | 42.5 | 0 | 90 | 38
12:00 | 2678 | 726 | 1394 | 2320 | 530 | 45 | 51 | 0 | 92 | 48
12:30 | 2703 | 726.5 | 1343 | 2392 | 540 | 45.5 | 68 | 0 | 92 | 51
13:00 | 2728 | 727 | 1292 | 2464 | 550 | 46 | 85 | 0 | 92 | 54
13:30 | 2728 | 727 | 1292 | 2464 | 550 | 46 | 85 | 0 | 92 | 54
14:00 | 2728 | 727 | 1292 | 2464 | 550 | 46 | 85 | 0 | 92 | 54
14:30 | 2759 | 726.5 | 1294.5 | 2211 | 540 | 47.5 | 60.5 | 0 | 90 | 35
15:00 | 2790 | 726 | 1297 | 1958 | 530 | 49 | 36 | 0 | 88 | 16
15:30 | 2780.5 | 726.5 | 1298.5 | 1856.5 | 530 | 49 | 36 | 0 | 88 | 12
16:00 | 2771 | 727 | 1300 | 1755 | 530 | 49 | 36 | 0 | 88 | 8
16:30 | 2804 | 728.5 | 1311.5 | 1847 | 530 | 48 | 51 | 0 | 89 | 4.5
17:00 | 2837 | 730 | 1323 | 1939 | 530 | 47 | 66 | 0 | 90 | 1
17:30 | 2839 | 797 | 1310.5 | 2288.5 | 535 | 46.5 | 213.5 | 0 | 100 | 0.5
18:00 | 2841 | 864 | 1298 | 2638 | 540 | 46 | 361 | 0 | 110 | 0
18:30 | 2858 | 867.5 | 1341.5 | 2876 | 560 | 45 | 382 | 0 | 109 | 0
19:00 | 2875 | 871 | 1385 | 3114 | 580 | 44 | 403 | 0 | 108 | 0
19:30 | 2871 | 872 | 1395 | 3024 | 610 | 43 | 318 | 0 | 108 | 0
20:00 | 2869 | 871 | 1409 | 2918 | 610 | 45 | 323 | 0 | 108 | 0
20:30 | 2883 | 871.5 | 1404 | 2865 | 615 | 44.5 | 281 | 0 | 107 | 0
21:00 | 2897 | 872 | 1399 | 2812 | 620 | 44 | 239 | 0 | 106 | 0
21:30 | 2898.5 | 872 | 1386 | 2615 | 645 | 44 | 205 | 0 | 100 | 0
22:00 | 2900 | 872 | 1373 | 2418 | 670 | 44 | 171 | 0 | 94 | 0
22:30 | 2905 | 872 | 1357.5 | 2130.5 | 650 | 44.5 | 112 | 0 | 92 | 0
23:00 | 2910 | 872 | 1342 | 1843 | 630 | 45 | 53 | 0 | 90 | 0
23:30 | 2921.5 | 762.5 | 1395 | 1843 | 624.5 | 45.5 | 37 | 0 | 85 | 0 | Max Temp. in Dhaka |  | 24.0° C
24:00 | 2933 | 653 | 1448 | 1843 | 619 | 46 | 21 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 45 | 45 | 46 | 46 | 48 | 45 | 45 | 45 | 45 | 45 | 46 | 48 | 49 | 49 | 47 | 46 |  | 44 | 43 | 45 | 44 | 44 | 45 | 46 | 1121629
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 2 | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 39049
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 9 | 13 | 15 | 16 | 16 | 13 | 10 | 5 | 1 | [9 empty] | 99900
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 54 | 59 | 17 |  |  |  | 251493
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 60 | 0 |  | 0 | 5 | 36 | 96 | 204 | 285 | 285 | 287 | 245 | 210 | 210 | 210 | 213 | 269 |  | 300 | 300 | 300 | 300 | 300 | 245 | 180 | 4606689
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 234 | 233 | 234 | 232 | 233 | 231 | 234 | 235 | 230 | 234 | 231 | 236 | 232 | 235 | 232 | 229 | 233 | 233 |  | 233 | 233 | 231 | 235 | 232 | 234 | 230 | 5588000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 380 | 380 | 380 | 340 | 340 | 300 | 281 | 250 | 250 | 250 | 280 | 350 | 370 | 375 | 370 | 380 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8177764
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 71280
33 | Ashuganj 225 MW CCPP | 160 | 158 | 157 | 164 | 170 | 172 | 178 | 165 | 140 | 151 | 165 | 156 | 156 | 148 | 139 | 134 | 139 | 142 |  | 159 | 161 | 164 | 169 | 175 | 164 | 160 | 3820000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5894000
| Ashuganj 450 MW CCPP(North) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 270 | 270 | 270 | 275 | 275 | 270 | 270 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6634000
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP | 44 | 47 | 42 | 43 | 45 | 46 | 45 | 45 | 46 | 45 | 45 | 42 | 37 | 41 | 40 | 40 | 36 | 42 |  | 36 | 42 | 36 | 36 | 36 | 37 | 39 | 978610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 343 | 335 | 335 | 337 | 359 | 358 | 363 | 340 | 324 | 353 | 326 | 327 | 327 | 335 | 335 | 347 | 326 |  | 335 | 325 | 326 | 340 | 334 | 324 | 337 | 8246510
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 281 | 281 | 283 | 292 | 303 | 303 | 294 | 292 | 245 | 242 | 231 | 246 | 244 | 244 | 234 | 229 | 221 | 222 |  | 218 | 219 | 219 | 204 | 207 | 212 | 215 | 5912000
42 | RPCL 210MW CCPP | 109 | 108 | 108 | 108 | 109 | 109 | 109 | 104 | 106 | 102 | 102 | 102 | 97 | 85 | 87 | 85 | 103 | 104 |  | 103 | 101 | 103 | 98 | 101 | 104 | 104 | 2404560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 4 | 7 | 8 | 24 | 29 | [13 empty] | 69540
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 31 | 31 | 32 | 842280
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 33 | 20 | 21 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 30 | 30 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 735264
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 73 | 73 | 40 | 40 | 40 | 60 | 67 | 68 | 67 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 69 | 69 | 69 | 70 | 70 | 1585920
| Shahjibazar 100 MW GTPP | [24 empty] | 40 | 50 | 80770
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 156 | 149 | 149 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 121 | 120 | 162 |  | 162 | 162 | 162 | 162 | 161 | 162 | 162 | 3287790
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 441000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 0 |  |  |  |  | 7 | 5 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 150660
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 273000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 0 | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 16 | 8 | 8 | 107760
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 300 | 290 | 300 | 310 | 310 | 320 | 300 | 280 | 300 | 300 | 290 | 290 | 290 | 310 | 315 | 280 |  | 300 | 290 | 290 | 305 | 310 | 270 | 310 | 7442000
| Bibiyana South 400 MW | 271 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 240 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 265 | 265 | 6434400
58 | Nababganj 55 MW PP (Southern power ) | 35 | 0 |  |  |  |  | 17 | 25 | 15 | 17 | 35 | 55 | 17 | 17 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 |  | 719834
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 11 | 25 | 25 | 25 | 25 | 24 | 21 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 407280
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 454560
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 |  | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 409824
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499356
63 | Impoprt (Tripura) | 76 | 74 | 72 | 70 | 72 | 74 | 74 | 78 | 78 | 86 | 88 | 92 | 92 | 92 | 88 | 88 | 90 | 110 |  | 108 | 108 | 108 | 106 | 94 | 90 | 80 | 2078400
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 40 | 40 | 40 | 40 | 38 | 14 | 12 | 5 | 2 | 2 | 2 | 2 | 2 | 5 | 6 | 8 |  | 13 | 14 | 12 | 14 | 23 | 25 | 20 | 471360
65 | Feni 22MW PP (Doreen) | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 385776
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 173700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 32 | 28 |  | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 714300
68 | Cumilla 25 MW PP (Summit) | 21 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 19 | 19 | 18 | 21 |  | 21 | 21 | 21 | 19 | 19 | 20 | 21 | 473700
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 28 | 28 | 28 | 10 | 18 | 22 | 22 | 20 | 26 | 30 | 30 | 30 | 31 | 32 | 32 | 18 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 669780
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 613600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 17 | 17 | 17 | 25 | 584900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [6 empty] | 2 | 26 | 26 | 26 | 26 | 31 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 26 | 26 | 839160
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 72 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 1654560
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 0 | 20 | 40 | 15 | 15 | 50 | 40 | 20 | 7 | 8 | 50 |  | 100 | 100 | 80 | 35 |  |  |  | 542400
78 | Gazipur 52 MW PP | [16 empty] | 2 | 8 |  | 19 | 8 | 8 | 8 |  |  |  | 51360
79 | Kodda 150MW PP | [7 empty] | 10 | 48 | 48 | 32 | 48 | 82 | 48 | 32 | 32 | 48 | 115 |  | 150 | 150 | 150 | 115 | 64 | 48 | 16 | 1100160
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 5 | 52 | 67 | 48 | 48 | 56 | 48 | 48 | 48 | 48 | 60 |  | 82 | 82 | 82 | 82 | 64 |  |  | 901440
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 3 | 8 |  | 8 | [6 empty] | 22690
| Gazipur 100 MW PP | [8 empty] | 10 | 17 | 17 | 17 | 17 |  |  |  | 7 | 50 |  | 105 | 103 | 53 | 53 |  |  |  | 414888
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 22080
| Jodiac Power | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 49 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1086230
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 | 55 | 88 | 80 | 80 | 92 | 64 | 64 | 64 | 65 | 98 |  | 100 | 100 | 100 | 100 | 64 | 45 | 16 | 1374480
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | 40 | 0 |  | 0 | 8 | 43 | 77 | 84 | 86 | 85 | 86 | 86 | 86 | 86 | 85 | 85 | 85 |  | 85 | 85 | 86 | 86 | 86 | 77 | 86 | 1636485
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 1 | 16 | 16 | 16 | 16 | 20 | 34 | 11 | 7 | 7 | 7 | 43 |  | 55 | 55 | 55 | 55 | 25 |  |  | 422400
| Meghnaghat 104 MW PP (OPCL) | 17 | 0 |  |  |  |  | 6 | 20 | 72 | 99 | 104 | 104 | 104 | 104 | 104 | 53 | 53 | 74 |  | 104 | 104 | 104 | 104 | 104 | 104 | 58 | 1561920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 283752
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1249561
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 3 | 24 | 60 | 102 | 74 | 93 | 102 | 16 |  |  |  | 5 |  | 70 | 70 | 70 | 70 | 48 |  |  | 780768
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 0 |  |  |  | 9 | 18 | 30 | 32 | 32 | 33 | 48 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 797280
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [5 empty] | 6 | 18 |  | 16 | [6 empty] | 47040
97 | katpotti 52 MW | [17 empty] | 1 |  | 6 | [6 empty] | 10368
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 15 | 33 | 41 | 30 | 31 | 41 | 30 | 30 | 30 | 30 | 35 |  | 40 | 40 | 40 | 40 | 15 |  |  | 512958
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 17 |  | 17 | 35 |  | 55 | 55 | 17 | 17 |  |  |  | 314613
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 110 | 110 | 110 | 140 | 140 | 110 | 140 | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 110 | 110 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3253664
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 |  | 2 | 2 | 1 | 1 | 0 | [10 empty] | 5750
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 35 | 17 |  |  | 380160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 110 | 35 | 35 | 35 | 35 | 38 | 65 | 132 | 200 | 170 | 151 | 160 | 170 | 140 | 140 | 140 | 170 | 192 |  | 200 | 200 | 200 | 200 | 200 | 130 | 70 | 3324000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 2 | 17 | 65 | 100 | 78 | 71 | 127 | 104 | 88 | 50 | 50 | 70 |  | 139 | 148 | 148 | 108 | 32 | 13 |  | 1283620
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 24 | 90 | 100 | 50 | 95 | 100 | 60 | 20 | 20 | 20 | 20 | 20 |  | 50 | 50 | 50 | 50 | 20 |  |  | 817920
116 | Chandpur 200MW (Desh energy) | 17 | 0 |  |  |  |  | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 23 | 34 | 34 | 34 | 34 | 17 | 17 | 421440
117 | Ashuganj 150MW PP (Midland) | 75 | 75 | 75 | 75 | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 72 | 75 | 75 | 75 |  | 73 | 75 | 76 | 73 | 75 | 73 | 76 | 1798182
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [8 empty] | 16 | 8 | 8 | 8 | [5 empty] | 5 |  | 17 | 25 | 25 | 8 |  |  |  | 117600
| Anwara 300 MW PP (United) | 271 | 271 | 271 | 234 | 216 | 216 | 215 | 251 | 270 | 270 | 270 | 270 | 285 | 285 | 285 | 291 | 290 | 290 |  | 306 | 307 | 307 | 307 | 307 | 307 | 307 | 6646581
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 90 | 90 | 90 | 93 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2365440
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4447 | 4215 | 4084 | 4036 | 3935 | 4001 | 4149 | 4569 | 5014 | 5165 | 5132 | 5286 | 5404 | 5062 | 4998 | 4847 | 5062 | 5692 |  | 6250 | 6194 | 6090 | 5896 | 5462 | 5017 | 4731 | 121057915
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 52 | 16 | 0 |  | 0 | 16 | 49 | 66 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 83 | 83 | 1825920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [10 empty] | 2 | 3 | 3 | 3 | 4 | 4 | 4 | 4 |  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 46560
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 17 | 53 | 70 | 70 | 70 | 77 | 77 | 77 | 58 | 35 | 35 | 72 |  | 72 | 72 | 72 | 90 | 90 | 35 | 35 | 1084320
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 57 | 57 | 57 | 57 | 59 | 58 | 57 | 16 | 17 | 15 | 54 | 33 | 46 | 56 | 56 | 55 | 57 | 56 |  | 57 | 57 | 57 | 57 | 21 | 19 | 56 | 1173000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 16 | [6 empty] | 44064
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 73 | 33 | 33 | 33 | 34 | 35 | 34 | 33 | 81 | 84 | 88 | 86 | 89 | 91 | 54 | 54 | 54 | 54 |  | 91 | 90 | 76 | 75 | 90 | 90 | 87 | 1588422
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 20 | 20 | 18 | 18 | 18 | 17 | 18 | 14 | 14 | 11 | 13 | 16 | 16 | 15 | 14 | 14 | 21 |  | 22 | 23 | 23 | 23 | 24 | 23 | 21 | 426300
141 | Noapara 100 MW PP (Bangla Trac) | [12 empty] | 30 | [13 empty] | 66240
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 40 | 40 | 24 | 24 | 40 |  |  |  | 8 | 8 |  | 24 | [6 empty] | 228000
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 6 |  | 7 | 7 | 7 |  |  |  |  | 16640
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 445 | 445 | 445 | 445 | 445 | 588 | 633 | 726 | 726 | 726 | 727 | 726 | 727 | 727 | 726 | 727 | 730 | 864 |  | 871 | 872 | 871 | 872 | 872 | 872 | 653 | 16658909
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 340 | 355 | 395 | 375 | 410 | 345 | 340 | 300 | 300 | 320 | 320 | 345 | 345 | 360 | 345 |  | 345 | 345 | 345 | 365 | 360 | 355 | 355 | 8548416
148 | Payra 1320 MW | 440 | 440 | 410 | 410 | 350 | 350 | 350 | 360 | 440 | 440 | 380 | 380 | 400 | 410 | 380 | 380 | 380 | 390 |  | 430 | 460 | 460 | 470 | 520 | 480 | 470 | 10924800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3667500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 14 | 43 |  | 43 | [6 empty] | 82272
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 293 | 334 | 310 | 320 | 335 | 340 | 340 | 373 | 393 | 378 | 426 | 401 | 322 | 350 | 364 | 350 | 368 | 353 |  | 351 | 369 | 399 | 388 | 365 | 369 | 405 | 8689818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 520080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 171252
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 25 |  | 25 | 12 | 12 | 12 |  |  |  | 73510
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 6 |  | 12 | [6 empty] | 11976
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 8 |  |  |  | 8 | 25 |  | 25 | [6 empty] | 51360
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 |  |  | 510232
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 50 | 0 |  | 0 | 30 | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 75 | 77 | 111 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2165760
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 0 |  |  |  |  | 35 | 90 | 109 | 113 | 57 | 57 | 57 | 35 | 35 | 35 | 35 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 1465248
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 |  |  |  |  | 50 | 90 | 108 | 113 | 113 | 107 | 107 | 113 | 64 | 49 | 49 | 113 |  | 113 | 113 | 113 | 113 | 113 | 34 |  | 1635840
177 | Sympa Solar Power 8MW | [8 empty] | 1 | 1 | 1 | 2 | 3 | 3 | 3 | 2 | 0 | [9 empty] | 20579
178
178