## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-23 | Saturday
|  |  | Date (day): | 2021-01-23 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10818.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11956 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-22 | 2021-01-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 170 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 55 | 107 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 349 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 254 | 304 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 50 | 99 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 73 | 74 | 85 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 15 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 58 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 52 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 55 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 98 | 101 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 90 | 90 | 90
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1760 | 2109 | 3011 | 3276 | 623 | 2063
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 0 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 47 | 47 | 48 | 48 | 182 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 50 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 40 | 20 | 30
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 97 | 97 |  | 11 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 216 | 250 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 524 | 695 | 1128 | 1238 | 917 | 109
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 151 | 177 | 180 | 180 | 41 |  | Gas shortage
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 170 | 150 | 200 | 200 | 160 |  | Gas shortage
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 230 | 350 | 350
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 3 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 53 | 50 | 54 | 54 |  | 96 | Engine Problem
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 39 | 50 | 40 | 40 |  | 123 | Engine problem
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 34 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 64 | 96 | 134 | 146
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 75 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 877 | 1006 | 1585 | 1849 | 881 | 219
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 98 | 105 | 140 | 140 | 62 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 82 | 90 | 90 |  | 5 | Engine problem
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 161 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 8 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 16 | 25 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 352 | 442 | 640.6 | 589 | 62 | 5
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 14 | 48 | 50 | 50
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 29 | 30 | 40 | 40
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 71 | 73 | 73 |  | 13 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 100 | 100 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 188 | 215 | 185 | 185 |  | 46 | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 315 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 250 | 0 | 200 | 200 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1066 | 906 | 1117 | 1117 | 163 | 846
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 466 | 713 | 743 | 888
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 105 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 320 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 90 | 90 | 90 |  | 15 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 878 | 1278 | 1643 | 2074 | 0 | 83
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 25 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 43 | 72 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 560 | 0 | 0 |  |  | 400 kV line maintenance
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 60 | 21 | 56 | 56
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 535 | 678 | 283 | 283 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 25 | 28 |  | 22 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 415 | 400 | 400 |  |  | FGMO
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 34 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 105 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 501 | 820 | 1140 | 1267 | 821 | 22
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 106 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 188 | 255 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 6681 | 8189 | 10818.6 | 11956 | 3591 | 3762
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6368.5292 | 7806 | 10312.6135 | 11396.8172
| A. |  | 2021-01-22 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 8189 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 5661 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8189 | MW
| 3 | Day peak Generation : |  |  | 6681 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7806 | MW
| 4 | Evening peak Generation : |  |  | 8189 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 162.428 | MKWHr | By Solar | 0.34635 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 87.8119 | MKWHr |  | By Oil: | 44.2747 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.2716 | MKWHr |  | By Hydro: | 1.1231 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3591 | MW | Dhaka | 2451 | 2451 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3762 | MW | Chittagong | 828 | 828 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7353 | MW | Khulna | 1016 | 1016 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 667.84 | MMCFD |  |  | Rajshahi | 874 | 874 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 90756868.142 | ii) Oil : | Taka | 310650220.18 | Comilla | 716 | 716 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 70816965 | Total | Taka | 472224053.322 | Mymensingh | 747 | 747 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.1715 | MKWHr. | Sylhet | 313 | 313 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 101 | MW (E to W) at | 20:00 | hrs | Barisal | 230 | 230 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -129 | MW at | 13:00 | hrs | Rangpur | 631 | 631 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 23.6° C |  |  | Total | 7806 | 7806 |  | 0
| B. |  | 2021-01-23 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 25.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 11956 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2456 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 188.4315 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5304 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8233 | MKWHr. | ii) HVDC Flow at Peak Time |  | 713 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.777 | MKWHr. | iii) Maximum HVDC Flow : |  | 713 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.71 |  | (b) Today: | 96.63 |  | (c) Rule Curve: |  | 98.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 324 | 240 |  | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 29 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 180 | 230 | 161 | 8 | 35 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 78 | 108 | 0 | 22 | 0 | 0 | 30 | 14 | 10 | 110 | 0 | 32 | 74 | 0 | 169 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 245 | 0 | 0 | 170 | 0 | 40 | 0 | 80 | 17 | 53 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 75 | 90 | 200 | 75 | 0 | 108 | 0 | 80 |  | 441 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 50 | 0 | 0 | 35 | 440 | 58 | 0 | 0 |  | 4473 | 2175 | 6648 | 2329 | 441 | 1438 | 1678 | 590 | 46 | 48 | 78 | 0 | 0 | 96.72
2:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 337 | 246 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 29 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 165 | 230 | 174 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 74 | 133 | 0 | 22 | 0 | 0 | 30 | 14 | 10 | 110 | 0 | 29 | 75 | 0 | 150 | 19 | 0 | 9 | 295 | 8 | 11 | 0 | 195 | 0 | 0 | 85 | 0 | 0 | 0 | 30 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 200 | 40 | 0 | 108 | 0 | 80 |  | 442 | 0 | 305 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 411 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 430 | 57 | 0 | 0 |  | 4020 | 2149 | 6169 | 2345 | 442 | 1433 | 1248 | 580 | 47 | 0 | 74 | 0 | 0 | 96.72
3:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 349 | 260 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 25 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 170 | 230 | 167 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 70 | 147 | 0 | 22 | 0 | 0 | 30 | 14 | 10 | 110 | 0 | 30 | 56 | 0 | 150 | 19 | 0 | 9 | 310 | 8 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 200 | 17 | 0 | 108 | 0 | 80 |  | 347 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 416 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 420 | 58 | 0 | 0 |  | 3847 | 1989 | 5836 | 2371 | 347 | 1449 | 981 | 570 | 48 | 0 | 70 | 0 | 0 | 96.72
4:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 340 | 280 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 25 | 25 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 170 | 230 | 164 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 68 | 151 | 0 | 22 | 0 | 0 | 30 | 14 | 10 | 110 | 0 | 30 | 56 | 0 | 150 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 200 | 17 | 0 | 108 | 0 | 80 |  | 347 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 411 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 410 | 56 | 0 | 0 |  | 3848 | 1972 | 5820 | 2363 | 347 | 1452 | 981 | 560 | 49 | 0 | 68 | 0 | 0 | 96.71
5:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 326 | 288 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 25 | 25 | 17 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 170 | 230 | 164 | 8 | 35 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 70 | 142 | 0 | 0 | 0 | 0 | 30 | 14 | 10 | 0 | 0 | 31 | 57 | 0 | 150 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 200 | 17 | 0 | 108 | 0 | 80 |  | 347 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 413 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 410 | 57 | 0 | 0 |  | 3688 | 1973 | 5661 | 2302 | 347 | 1352 | 981 | 560 | 49 | 0 | 70 | 0 | 0 | 96.71
6:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 338 | 290 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 25 | 25 | 25 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 0 | 170 | 230 | 166 | 8 | 34 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 72 | 139 | 0 | 0 | 0 | 0 | 30 | 14 | 10 | 0 | 0 | 30 | 57 | 0 | 150 | 19 | 0 | 9 | 305 | 8 | 11 | 0 | 145 | 0 | 0 | 79 | 0 | 2 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 200 | 22 | 0 | 108 | 0 | 80 |  | 347 | 0 | 315 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 426 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 420 | 23 | 0 | 0 |  | 3766 | 1967 | 5733 | 2316 | 347 | 1340 | 1040 | 570 | 48 | 0 | 72 | 0 | 0 | 96.71
7:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 318 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 25 | 25 | 17 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 0 | 170 | 230 | 174 | 8 | 32 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 66 | 142 | 13 | 22 | 0 | 0 | 0 | 14 | 10 | 0 | 0 | 30 | 57 | 0 | 150 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 158 | 0 | 0 | 80 | 0 | 22 | 0 | 0 | 17 | 36 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 26 | 100 | 250 | 35 | 0 | 108 | 0 | 80 |  | 347 | 0 | 300 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 430 | 19 | 0 | 0 |  | 3958 | 1896 | 5854 | 2332 | 347 | 1266 | 1215 | 580 | 48 | 0 | 66 | 0 | 0 | 96.7
8:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 346 | 300 |  | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 75 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 25 | 25 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 0 | 170 | 230 | 172 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 66 | 139 | 16 | 22 | 0 | 30 | 0 | 14 | 15 | 0 | 0 | 29 | 57 | 0 | 150 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 145 | 0 | 0 | 94 | 0 | 33 | 5 | 10 | 17 | 53 | 0 | 0 | 0 | 0 | 1 | 270 | 17 | 0 | 0 | 26 | 100 | 250 | 35 | 2 | 108 | 0 | 100 |  | 489 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 382 | 0 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 430 | 56 | 0 | 0 |  | 4097 | 2062 | 6159 | 2393 | 489 | 1348 | 1226 | 580 | 48 | 0 | 66 | 9 | 0 | 96.7
9:00 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 341 | 294 |  | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 64 | 0 | 74 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 21 | 25 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 32 | 19 | 42 | 0 | 0 | 0 | 170 | 230 | 171 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 60 | 140 | 16 | 22 | 0 | 30 | 0 | 14 | 47 | 0 | 0 | 31 | 59 | 0 | 150 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 182 | 0 | 0 | 150 | 0 | 38 | 10 | 20 | 17 | 55 | 0 | 0 | 0 | 0 | 2 | 270 | 17 | 0 | 0 | 26 | 100 | 250 | 61 | 3 | 108 | 0 | 100 |  | 489 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 401 | 10 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 420 | 47 | 0 | 0 |  | 4338 | 2122 | 6460 | 2382 | 489 | 1377 | 1520 | 570 | 46 | 0 | 60 | 16 | 0 | 96.7
10:00 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 345 | 283 |  | 0 | 0 | 0 | 0 | 15 | 30 | 0 | 0 | 0 | 0 | 64 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 21 | 25 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 46 | 19 | 33 | 0 | 0 | 0 | 170 | 230 | 163 | 8 | 41 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 30 | 18 | 62 | 123 | 16 | 22 | 0 | 30 | 0 | 14 | 47 | 0 | 0 | 30 | 70 | 0 | 176 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 195 | 0 | 0 | 150 | 0 | 49 | 14 | 20 | 17 | 53 | 0 | 0 | 0 | 0 | 3 | 214 | 17 | 0 | 0 | 26 | 90 | 250 | 70 | 7 | 126 | 0 | 100 |  | 488 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 418 | 17 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 420 | 56 | 0 | 0 |  | 4368 | 2151 | 6519 | 2391 | 488 | 1390 | 1546 | 570 | 46 | 0 | 62 | 26 | 0 | 96.69
11:00 | 0 | 0 | 0 | 0 | 170 | 40 | 0 | 327 | 255 |  | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 0 | 0 | 1 | 64 | 0 | 75 | 0 | 0 | 0 | 17 | 0 | 55 | 16 | 25 | 18 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 0 | 170 | 230 | 158 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 28 | 18 | 60 | 106 | 16 | 22 | 0 | 30 | 0 | 14 | 47 | 0 | 0 | 30 | 70 | 0 | 188 | 18 | 0 | 9 | 280 | 8 | 11 | 0 | 245 | 0 | 0 | 150 | 0 | 52 | 17 | 20 | 17 | 53 | 0 | 0 | 4 | 0 | 4 | 216 | 17 | 0 | 0 | 26 | 90 | 250 | 70 | 15 | 126 | 0 | 100 |  | 469 | 0 | 295 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 392 | 17 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 420 | 57 | 0 | 0 |  | 4445 | 2080 | 6525 | 2364 | 469 | 1334 | 1642 | 570 | 47 | 0 | 60 | 39 | 0 | 96.69
12:00 | 0 | 0 | 0 | 0 | 170 | 55 | 0 | 338 | 254 |  | 0 | 0 | 0 | 0 | 50 | 30 | 0 | 0 | 0 | 7 | 64 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 55 | 16 | 25 | 0 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 0 | 170 | 230 | 151 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 28 | 18 | 64 | 98 | 16 | 20 | 0 | 30 | 0 | 14 | 47 | 0 | 0 | 29 | 72 | 0 | 188 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 161 | 0 | 98 | 18 | 30 | 17 | 53 | 0 | 0 | 17 | 0 | 4 | 216 | 17 | 0 | 0 | 26 | 90 | 250 | 70 | 41 | 126 | 0 | 100 |  | 466 | 0 | 290 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 398 | 17 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 420 | 60 | 0 | 0 |  | 4579 | 2102 | 6681 | 2329 | 466 | 1368 | 1771 | 570 | 47 | 0 | 64 | 66 | 0 | 96.69
13:00 | 0 | 0 | 0 | 0 | 165 | 82 | 0 | 371 | 274 |  | 0 | 0 | 0 | 8 | 64 | 30 | 0 | 0 | 0 | 7 | 102 | 32 | 60 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 8 | 25 | 25 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 170 | 230 | 152 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 25 | 18 | 66 | 105 | 27 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 30 | 71 | 0 | 190 | 18 | 0 | 9 | 340 | 8 | 11 | 0 | 275 | 0 | 0 | 178 | 0 | 111 | 18 | 100 | 17 | 53 | 0 | 4 | 17 | 0 | 4 | 252 | 17 | 0 | 0 | 39 | 100 | 250 | 83 | 38 | 126 | 0 | 100 |  | 471 | 0 | 295 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 395 | 53 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 440 | 54 | 0 | 0 |  | 5063 | 2202 | 7265 | 2380 | 471 | 1503 | 2110 | 590 | 48 | 32 | 66 | 65 | 7265 | 96.68
14:00 | 0 | 0 | 0 | 0 | 14 | 101 | 0 | 325 | 275 |  | 0 | 0 | 0 | 24 | 40 | 15 | 0 | 0 | 0 | 7 | 64 | 16 | 60 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 9 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 38 | 19 | 35 | 0 | 0 | 0 | 150 | 230 | 140 | 8 | 34 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 62 | 105 | 40 | 22 | 2 | 30 | 0 | 45 | 20 | 0 | 0 | 29 | 40 | 0 | 164 | 18 | 0 | 9 | 260 | 8 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 107 | 16 | 60 | 17 | 53 | 0 | 8 | 17 | 0 | 3 | 216 | 17 | 0 | 0 | 55 | 90 | 100 | 85 | 33 | 126 | 0 | 100 |  | 471 | 0 | 285 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 307 | 35 | 0 | 35 | 0 | 35 | 0 | 4 | 35 | 440 | 56 | 0 | 0 |  | 4368 | 2096 | 6464 | 1968 | 471 | 1284 | 1969 | 589 | 47 | 16 | 62 | 58 | 0 | 96.68
15:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 332 | 286 |  | 0 | 0 | 0 | 15 | 30 | 15 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 0 | 17 | 55 | 16 | 25 | 8 | 0 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 25 | 19 | 25 | 0 | 0 | 0 | 150 | 230 | 156 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 60 | 103 | 40 | 22 | 1 | 30 | 0 | 45 | 20 | 0 | 0 | 28 | 40 | 0 | 164 | 18 | 0 | 9 | 270 | 8 | 11 | 0 | 195 | 0 | 0 | 180 | 0 | 81 | 12 | 50 | 17 | 55 | 0 | 0 | 0 | 0 | 2 | 198 | 17 | 0 | 0 | 35 | 70 | 100 | 65 | 23 | 144 | 0 | 100 |  | 470 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 325 | 35 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 420 | 57 | 0 | 0 |  | 4041 | 2035 | 6076 | 1959 | 470 | 1309 | 1622 | 569 | 47 | 0 | 60 | 40 | 0 | 96.68
16:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 333 | 282 |  | 0 | 0 | 0 | 7 | 30 | 15 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 0 | 25 | 35 | 0 | 25 | 11 | 25 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 25 | 19 | 34 | 0 | 0 | 0 | 150 | 230 | 163 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 25 | 18 | 52 | 102 | 40 | 22 | 0 | 30 | 0 | 14 | 20 | 0 | 0 | 29 | 20 | 0 | 164 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 195 | 0 | 0 | 150 | 0 | 72 | 7 | 50 | 17 | 56 | 0 | 0 | 0 | 0 | 1 | 162 | 17 | 0 | 0 | 35 | 50 | 100 | 35 | 11 | 144 | 0 | 100 |  | 469 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 331 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 400 | 41 | 0 | 0 |  | 3853 | 1966 | 5819 | 1956 | 469 | 1265 | 1461 | 549 | 47 | 0 | 52 | 20 | 0 | 96.67
17:00 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 359 | 285 |  | 0 | 0 | 0 | 7 | 30 | 15 | 0 | 0 | 0 | 3 | 48 | 32 | 40 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 25 | 11 | 25 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 19 | 34 | 0 | 0 | 0 | 150 | 230 | 168 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 8 | 18 | 72 | 103 | 40 | 22 | 0 | 30 | 0 | 14 | 20 | 0 | 0 | 29 | 20 | 0 | 215 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 195 | 0 | 0 | 150 | 0 | 65 | 1 | 30 | 17 | 50 | 0 | 0 | 3 | 0 | 0 | 162 | 25 | 0 | 0 | 35 | 50 | 150 | 35 | 2 | 144 | 0 | 100 |  | 473 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 337 | 17 | 0 | 37 | 0 | 35 | 0 | 0 | 35 | 400 | 41 | 0 | 0 |  | 4015 | 1998 | 6013 | 2092 | 473 | 1297 | 1447 | 549 | 48 | 32 | 72 | 3 | 0 | 96.67
18:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 343 | 303 |  | 0 | 0 | 0 | 14 | 60 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 70 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 11 | 25 | 24 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 0 | 26 | 19 | 38 | 0 | 0 | 0 | 150 | 230 | 177 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 31 | 18 | 88 | 106 | 40 | 22 | 0 | 30 | 0 | 22 | 27 | 0 | 0 | 30 | 69 | 0 | 215 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 250 | 0 | 0 | 168 | 0 | 65 | 0 | 30 | 17 | 53 | 0 | 2 | 17 | 0 | 0 | 196 | 52 | 0 | 0 | 46 | 90 | 250 | 56 | 0 | 144 | 0 | 100 |  | 713 | 0 | 325 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 395 | 35 | 0 | 79 | 0 | 104 | 0 | 0 | 90 | 370 | 56 | 0 | 0 |  | 4749 | 2673 | 7422 | 2257 | 713 | 1513 | 2047 | 519 | 47 | 238 | 88 | 0 | 0 | 96.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 354 | 305 |  | 0 | 0 | 0 | 74 | 99 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 23 | 25 | 24 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 0 | 48 | 19 | 38 | 0 | 0 | 0 | 150 | 230 | 177 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 98 | 106 | 68 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 30 | 71 | 0 | 215 | 19 | 0 | 9 | 310 | 8 | 11 | 0 | 300 | 44 | 0 | 200 | 0 | 96 | 0 | 50 | 31 | 55 | 0 | 10 | 17 | 0 | 0 | 250 | 54 | 0 | 0 | 68 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 713 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 5 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 401 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 93 | 490 | 34 | 0 | 0 |  | 5069 | 2932 | 8001 | 2038 | 713 | 1549 | 2679 | 639 | 47 | 238 | 98 | 0 | 0 | 96.66
19:30 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 339 | 305 |  | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 27 | 25 | 24 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 0 | 50 | 19 | 40 | 0 | 0 | 0 | 150 | 230 | 177 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 98 | 107 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 30 | 71 | 0 | 215 | 19 | 0 | 9 | 320 | 8 | 11 | 0 | 300 | 53 | 0 | 200 | 0 | 101 | 0 | 50 | 34 | 53 | 0 | 16 | 17 | 0 | 0 | 250 | 54 | 0 | 0 | 75 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 713 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 18 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 413 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 94 | 550 | 21 | 0 | 0 |  | 5143 | 3009 | 8152 | 2030 | 713 | 1564 | 2763 | 699 | 47 | 238 | 98 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 349 | 304 |  | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 27 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 0 | 50 | 19 | 40 | 0 | 0 | 0 | 150 | 230 | 177 | 8 | 50 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 96 | 105 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 30 | 71 | 0 | 215 | 19 | 0 | 9 | 315 | 8 | 11 | 0 | 300 | 55 | 0 | 200 | 0 | 101 | 0 | 50 | 34 | 50 | 0 | 8 | 17 | 0 | 0 | 250 | 54 | 0 | 0 | 75 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 713 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 415 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 95 | 560 | 21 | 0 | 0 |  | 5158 | 3031 | 8189 | 2057 | 713 | 1558 | 2771 | 709 | 47 | 238 | 96 | 0 | 0 | 96.66
21:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 338 | 298 |  | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 22 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 85 | 0 | 0 | 50 | 19 | 40 | 0 | 0 | 0 | 150 | 230 | 180 | 8 | 36 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 94 | 107 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 30 | 71 | 0 | 215 | 19 | 0 | 9 | 320 | 8 | 11 | 0 | 300 | 30 | 0 | 192 | 0 | 100 | 0 | 50 | 34 | 55 | 0 | 0 | 17 | 0 | 0 | 252 | 54 | 0 | 0 | 75 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 713 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 409 | 90 | 0 | 113 | 0 | 107 | 0 | 0 | 95 | 570 | 25 | 0 | 0 |  | 5094 | 3040 | 8134 | 2032 | 713 | 1554 | 2737 | 720 | 46 | 238 | 94 | 0 | 0 | 96.66
22:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 324 | 300 |  | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 13 | 58 | 32 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 55 | 0 | 0 | 50 | 19 | 30 | 0 | 0 | 0 | 150 | 230 | 173 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 94 | 108 | 64 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 31 | 71 | 0 | 176 | 19 | 0 | 9 | 280 | 8 | 11 | 0 | 289 | 0 | 0 | 200 | 0 | 100 | 0 | 50 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 252 | 54 | 0 | 0 | 75 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 489 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 416 | 90 | 0 | 113 | 0 | 107 | 0 | 0 | 95 | 560 | 56 | 0 | 0 |  | 4881 | 2843 | 7724 | 1987 | 489 | 1543 | 2663 | 710 | 46 | 192 | 94 | 0 | 0 | 96.65
23:00 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 324 | 310 |  | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 0 | 58 | 16 | 74 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 29 | 19 | 30 | 0 | 0 | 0 | 150 | 230 | 170 | 8 | 40 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 86 | 109 | 0 | 22 | 0 | 30 | 0 | 31 | 20 | 0 | 0 | 31 | 72 | 0 | 176 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 76 | 0 | 20 | 34 | 53 | 0 | 0 | 0 | 0 | 0 | 234 | 54 | 0 | 0 | 75 | 100 | 50 | 90 | 0 | 144 | 0 | 100 |  | 430 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 396 | 90 | 0 | 50 | 0 | 50 | 0 | 0 | 57 | 500 | 57 | 0 | 0 |  | 4645 | 2457 | 7102 | 2042 | 430 | 1498 | 2231 | 650 | 44 | 121 | 86 | 0 | 0 | 96.65
24:00 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 327 | 343 |  | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 28 | 17 | 33 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 37 | 19 | 32 | 0 | 0 | 0 | 150 | 230 | 180 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 74 | 108 | 0 | 22 | 0 | 30 | 0 | 31 | 20 | 0 | 0 | 30 | 72 | 0 | 176 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 34 | 55 | 0 | 0 | 0 | 0 | 0 | 236 | 17 | 0 | 0 | 46 | 100 | 200 | 90 | 0 | 144 | 0 | 100 |  | 447 | 0 | 335 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 349 | 90 | 0 | 50 | 0 | 35 | 0 | 0 | 57 | 440 | 57 | 0 | 0 |  | 4160 | 2322 | 6482 | 2199 | 447 | 1486 | 1572 | 590 | 44 | 70 | 74 | 0 | 0 | 96.65
KWH | 0 | 0 | 0 | 0 | 2422018 | 1244090 | 0 | 8239100 | 6742000 |  | 0 | 0 | 0 | 672960 | 1096728 | 299644 | 0 | 0 | 0 | 114240 | 1069920 | 395040 | 1400530 | 0 | 0 | 0 | 250200 | 285547 | 849962 | 345744 | 600000 | 478620 | 582600 | 571400 | 0 | 0 | 1123113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 351360 | 0 | 391518 | 0 | 0 | 856320 | 463488 | 931680 | 0 | 0 | 0 | 4174500 | 5751000 | 4040000 | 200727 | 889880 | 70560 | 0 | 0 | 1248090 | 0 | 0 | 0 | 451620 | 110520 | 740000 | 470130 | 1776960 | 2794840 | 663360 | 487980 | 3950 | 498000 | 0 | 652800 | 771624 | 0 | 0 | 722880 | 1473600 | 0 | 4233750 | 439000 | 0 | 210600 | 7485000 | 196176 | 264000 | 0 | 5462289 | 110114 | 0 | 3583200 | 0 | 1363680 | 117045 | 838080 | 524640 | 1117381 | 0 | 52800 | 150492 | 0 | 25801 | 5748327 | 665636 | 0 | 0 | 1162560 | 2213760 | 3864900 | 1486080 | 170630 | 3134880 | 0 | 2280000 |  | 11823273 | 0 | 7547328 | 0 | 2188800 | 0 | 0 | 0 | 0 | 0 | 199500 | 0 | 430500 | 0 | 0 | 0 | 0 | 0 | 0 | 645186 | 191450 | 0 | 0 | 124320 | 0 | 521520 | 0 | 246996 | 0 | 0 | 3664700 | 0 | 0 | 0 | 0 | 0 | 0 | 1442401 | 0 | 0 | 0 | 9265236 | 836160 | 0 | 1309920 | 0 | 1248960 | 0 | 28921 | 1219200 | 11606900 | 1215027 | 0 | 0 |  | 106671664 | 55756298 | 162427962 | 53977030 | 11823273 | 33834895 | 42843000 | 15271600 | 1123113 | 1431744 | 1776960 | 346347 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 2688439.98 | 1642198.8 | 0 | 8321491 | 6944260 |  | 0 | 0 | 0 | 5107766.4 | 7556455.92 | 2534988.24 | 0 | 0 | 0 | 860227.2 | 9757670.4 | 3887193.6 | 12912886.6 | 0 | 0 | 0 | 1826460 | 2207278.31 | 8380625.32 | 259308 | 450000 | 0 | 0 | 0 | 0 | 0 | 303240.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3797724.6 | 0 | 0 | 6782054.4 | 583994.88 | 2767089.6 | 0 | 0 | 0 | 3089130 | 5751000 | 3716800 | 258937.83 | 1023362 | 79732.8 | 0 | 0 | 2134233.9 | 0 | 0 | 0 | 573557.4 | 82890 | 1295000 | 352597.5 | 13327200 | 2962530.4 | 6023308.8 | 619734.6 | 62963 | 816720 | 0 | 1161984 | 1203733.44 | 0 | 0 | 1424073.6 | 2814576 | 0 | 7324387.5 | 961410 | 0 | 429624 | 7559850 | 147132 | 200640 | 0 | 41294904.84 | 1869735.72 | 0 | 18632640 | 0 | 13418611.2 | 1368256.05 | 6830352 | 5692344 | 7877536.05 | 0 | 481536 | 1422149.4 | 0 | 0 | 43457352.12 | 5797689.56 | 0 | 0 | 9963139.2 | 14743641.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 68102052.48 | 0 | 7924694.4 | 0 | 17203968 | 0 | 0 | 0 | 0 | 0 | 2078790 | 0 | 667275 | 0 | 0 | 0 | 0 | 0 | 0 | 5709896.1 | 1474165 | 0 | 0 | 1204660.8 | 0 | 1001318.4 | 0 | 186975.972 | 0 | 0 | 19862674 | 0 | 0 | 0 | 0 | 0 | 0 | 2163601.5 | 0 | 0 | 0 | 9172583.64 | 8729510.4 | 0 | 12431140.8 | 0 | 9691929.6 | 0 | 319577.05 | 9009888 | 50954291 | 0 | 0 | 0 |  | 327818350.27 | 227888992.142 | 555707342.412 | 50835602.032 | 68102052.48 | 39921266.11 | 297255405.88 | 70816965 | 303240.51 | 13394814.3 | 13327200 | 1750796.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 170 | 55 | 0 | 338 | 254 |  | 0 | 0 | 0 | 0 | 50 | 30 | 0 | 0 | 0 | 7 | 64 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 55 | 16 | 25 | 0 | 25 | 25 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 0 | 170 | 230 | 151 | 8 | 39 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 28 | 18 | 64 | 98 | 16 | 20 | 0 | 30 | 0 | 14 | 47 | 0 | 0 | 29 | 72 | 0 | 188 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 161 | 0 | 98 | 18 | 30 | 17 | 53 | 0 | 0 | 17 | 0 | 4 | 216 | 17 | 0 | 0 | 26 | 90 | 250 | 70 | 41 | 126 | 0 | 100 |  | 466 | 0 | 290 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 398 | 17 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 420 | 60 | 0 | 0 |  | 6681 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 349 | 304 | 0 | 0 | 0 | 0 | 100 | 99 | 15 | 0 | 0 | 0 | 15 | 58 | 48 | 74 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 27 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 85 | 0 | 0 | 50 | 19 | 40 | 0 | 0 | 0 | 150 | 230 | 177 | 8 | 50 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 96 | 105 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 30 | 71 | 0 | 215 | 19 | 0 | 9 | 315 | 8 | 11 | 0 | 300 | 55 | 0 | 200 | 0 | 101 | 0 | 50 | 34 | 50 | 0 | 8 | 17 | 0 | 0 | 250 | 54 | 0 | 0 | 75 | 100 | 0 | 90 | 0 | 144 | 0 | 100 |  | 713 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 25 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 415 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 95 | 560 | 21 | 0 | 0 |  | 8189 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 50 | 22 | 30 | 0 | 0 | 0 | 200 | 350 | 180 | 8 | 40 | 5 | 0 | 0 | 51 | 0 | 50 | 52 | 20 | 11 | 33 | 22 | 146 | 140 | 90 | 22 | 0 | 30 | 0 | 50 | 50 | 0 | 0 | 40 | 73 | 0 | 185 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 54 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 200 | 90 | 0 | 144 | 0 | 100 |  | 888 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 28 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 0 | 56 |  | 0
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 50 | 22 | 20 | 0 | 0 | 0 | 200 | 350 | 180 | 8 | 40 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 20 | 11 | 33 | 20 | 134 | 140 | 90 | 22 | 1.6 | 30 | 0 | 50 | 50 | 0 | 0 | 40 | 73 | 0 | 185 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 54 | 0 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 200 | 90 | 50 | 144 | 0 | 100 |  | 743 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 0 | 56 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 350 | 336 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 56 | 58 | 24 | 85 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 25 | 28 | 17 |  | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 19 | 21 | 0 | 0 | 0 | 150 | 285 | 172 | 8 | 50 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 74 | 102 | 24 | 22 | 0 | 30 | 0 | 31 | 50 | 0 | 0 | 31 | 69 | 0 | 156 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 115 | 0 | 0 | 170 | 0 | 33 | 4 | 100 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 251 | 17 | 0 | 0 | 113 | 90 | 200 | 62 | 2 | 144 | 0 | 100 | 0 | 729 | 0 | 390 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 432 | 70 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 0 | 57 | 0 | 0 | 0
199
| Minimum Generation |  | 5661 | 5:00
| Highest Generation |  | 8189 | 20:00
| Day Peak Generation |  | 6681 | 12:00
| Evening Peak Generation |  | 8189 | 20:00
| HVDC Max Flow |  | 713 | 18:00
| HVDC EvPeak Flow |  | 713 | 20:00
| Load factor L.F |  | 82.65%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6681 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5304 | MW
Evening Peak Generation : |  | 8189 | MW Hour : | 20:00 | Available Max Generation : |  | 11956 | MW
E.P. Demand (at gen end) : |  | 8189 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 8189 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2456 | MW
Total Gen. (MKWH) : |  | 162.428 | System Load Factor : | 82.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -129 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-23
Actual : | 96.63 | Ft.(MSL) , | Rule curve : | 98.8 | Ft.( MSL )
Gas Consumed : | Total = | 667.84 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 90756868.142
: |  | Coal : | 70816965 | Oil : | 310650220.18 | Total : | 472224053.322
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3379.5043 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1145.0973 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1025.2349 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 926.1255 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 837.07 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 675.4754 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 382.996 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.0571 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 520.9348 |  |  | 0 | 0%
Total | 0 |  | 9066.4952 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-3,4,5
2) Baghabari-71 &100 MW
3) Ghorasal Unit-1,2,3,4,5
4) Shahjibazar 330 MW
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,3 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ramganj-Desh Energy 132 kV Ckt-2 was under shut down from 09:48 to 17:27 for D/W.
b) Rampura 230/132 kV T0-1 transformer was under shut down from 09:23 to 20:01 for
c) Shahjibazar-Bibiyana 230 kV kV Ckt-2 was under shut down from 10:52 to 14:03 for C/W.
d) Hathazari 230 kV Bus-1 was under shut down from 11:28 to 15:37 for D/W.
e) After maintenance Comilla(S) 132/33 kV T-2 transformer was switched on at 11:12.
f) Mymensingh-RPCL 132 kV Ckt was under shut down from 12:55 to 17:17 for C/M.
g) Ghorashal unit-7 was shut down at 14:04 for DP high.
h) After maintenance Rampura-Bhulta 230 kV Ckt-3 was switched on at 17:56.
i) Bibiyana(South) CCPP tripped at 18:35 due to GBC problem and GT was synchronized at 22:42.
j) Siddhirganj 132/33 kV T-2 transformer was under shut down from 08:45 to 16:00 for A/M.
k) Kishoreganj 132/33 kV T-2 & T-3 transformer were under shut down from 07:15 to 18:24 for A/M.
l) Mohasthangarh 33 kV Bus under 132/33 kV T-2 transformer was shut down at 18:59 for R/H maintenance
at 33 kV isolator.
m) After maintenance Benapole-Jessore 132 kV both Ckts were switched on at 19:33.
n) After maintenance Bhulta-Rampura 230 kV Ckt-4 was switched on at 21:40.
o) After maintenance work Meghnaghat-Shympur 230 kV Ckt-1 was switched on at 21:31.
p) Benapole-Jessore 132 kV Ckt-1 tripped at 21:46 showing SF6 gas pressure low and was switched on
at 23:04 and was shut down at 23:32.
q) Meghnaghat-Shympur 230 kV Ckt-1 tripped at 00:57(23/01/2021) from Meghnaghat end showing
Cn,Z1 and was switched on at 01:17.
r) APR 230 kV Ckt tripped at 00:55(23/01/2021) from APR end showing O/C,E/F relay and was switched on at 01:07
s) Meghnaghat-Shympur 230 kV Ckt-1 tripped at 02:32(23/1/2021) from both ends showing Dist. 3-phase at
Meghnaghat ends showing Bn,Z1 at Meghnaghat end and Dist. B,SOTF at Shyampur end.
t) Meghnaghat-Shympur 230 kV Ckt-1 tripped at 02:19(23/1/2021) from both ends showing Dist. 3-phase at
Meghnaghat end and Dist. 3-phase at Shyampur end.
u) Payra uni-2 was shut down at 06:01(23/01/2021) for 400 kV line maintenance work.
v) Rampura 230/132 kV T-1 transformer was shut down at 07:47(23/01/2021) for A/M.
w) Daudkandi 132/33 kV T-3 transformer was shut down at 07:44(23/01/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 2422018 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1244090
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8239100 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 304 | 6742000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 672960
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 99 | 1096728
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 299644 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 74 | 1400530 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 345744 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 15 | 114240 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 1069920 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 250200 | High Voltage.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 395040 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 285547 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 849962
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1078620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 582600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 571400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5462289
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 55 | 110114
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 101 | 1363680 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 150492 | High Voltage.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1486080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3134880 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2109 | 39367878
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 117045
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 856320
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 47 | 1123113 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 391518
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 838080 | High Voltage.
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 463488 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 931680
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25801
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 250 | 5748327 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 665636
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2213760
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 695 | 13374768
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4040000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 150 | 4174500 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 230 | 5751000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 3 | 70560 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1248090
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1117381 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 889880 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 524640 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451620
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 110520 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 96 | 1776960
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 740000
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 470130
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 1162560 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1006 | 22728568
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2794840 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 487980
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 82 | 663360 | High Voltage.
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3950
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3583200 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 52800 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 170630
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 351360
| Mymensingh Area Total |  |  |  | 709 | 442 | 8108120
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 498000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | GT-4 under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | High Voltage.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 652800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 771624
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 722880 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1473600 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 2280000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 215 | 4233750
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 439000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 196176 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7485000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 210600
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 3864900 | On test
| Sylhet Area Total |  |  |  | 1988 | 906 | 23092330
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 713 | 11823273
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2188800
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7547328 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 199500
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 836160 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1278 | 22595061
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 430500 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 72 | 1442401 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 560 | 11606900 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 21 | 1215027 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1676 | 678 | 14694828
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 191450 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9265236 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 521520
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246996
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 124320 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 105 | 645186
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1309920
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1219200 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 820 | 13523828
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3664700
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 106 | 1248960
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28921
| Rangpur Area Total |  |  |  | 605 | 255 | 4942581
| Total |  |  |  | 20748 | 8189 | 162427962
| Eastern Grid Total |  |  |  | 14000 | 5158 | 106671664
| Western Grid Total |  |  |  | 6748 | 3031 | 55756298
| National Grid Total |  |  |  | 20748 | 8189 | 162427962
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-22
| (a) ENTIRE EASTERN GRID : |  | 5055 | MW | (b) ENTIRE WESTERN GRID : |  | 2751 | MW
| i) Dhaka area |  | 2451 | MW | i) Khulna area |  | 1016 | MW
| ii) Chittagong area |  | 828 | MW | ii) Rajshahi area |  | 874 | MW
| iii) Comilla area |  | 716 | MW | iii) Barisal area |  | 230 | MW
| iv) Mymensingh area |  | 747 | MW | iv) Rangpur area |  | 631 | MW
| v) Sylhet area |  | 313 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7806 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 80 | 23:00 | Jamalpur | 95 | 19:00 | Benapol | 40 | 20:00
| Munsiganj | 86 | 20:00 | Sherpur | 112 | 19:00 | Jhenida | 82 | 18:30
| Sonargaon | 61 | 20:00 | Srimongal | 27 | 18:30 | Bottail | 80 | 18:30
| Shyampur | 150 | 1:00 | Shahjibazar | 83 | 19:30 | G.K Project | 36 | 18:30
| Bhulta | 141 | 24:00 | Fenchuganj | 25 | 19:30 | Faridpur | 118 | 19:00
| Madanganj | 40 | 19:00 | Kulawara | 26 | 18:00 | Madaripur | 61 | 20:00
| Shitalakhya | 70 | 13:00 | Sylhet | 74 | 19:00 | Sariatpur | 40 | 19:30
| Rahim steel | 15 | 1:00 | Chatak | 19 | 18:00 | Gopalganj | 59 | 18:30
| Matuail | 30 | 1:00 | Sunamganj | 29 | 19:00 | Bagerhat | 79 | 18:30
| Ghorasal | 51 | 19:30 | Biani Bazar | 37 | 19:00 | Mongla | 36 | 22:00
| Narsingdi | 120 | 20:00 | Comilla (S) | 98 | 19:00 | Satkhira | 73 | 19:00
| Haripur (SBU) | 85 | 19:00 | Comilla(N) | 77 | 19:30 | Gallamari | 23 | 13:00
| Ullon | 45 | 13:00 | Chandpur | 54 | 19:30 | Magura | 38 | 18:30
| Hasnabad | 109 | 13:00 | Feni | 65 | 19:30 | Norail | 24 | 9:00
| Magbazar | 53 | 13:00 | Chowmuhani | 116 | 21:00 | Chuadanga | 63 | 18:30
| Maniknagar | 44 | 19:30 | Ashuganj | 38 | 13:00 | Barisal(N) | 26 | 18:30
| Bangabhaban | 7 | 13:00 | Daudkandi | 88 | 20:00 | Barisal (S) | 68 | 21:00
| Narinda | 48 | 12:00 | B.Baria | 100 | 19:00 | Patuakhali | 76 | 20:00
| Dhanmondi | 70 | 13:00 | Ramganj | 70 | 18:30 | Bhandaria | 38 | 19:00
| Lalbag | 51 | 1:00 | Chaddagram | 23 | 18:30 | Borhan Uddin | 25 | 22:00
| Madartek | 45 | 13:00 | PHP | 9 | 11:00 | Ishurdi | 41 | 19:30
| Dhaka University |  |  | Madunaghat | 38 | 19:00 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 58 | 0.79167 | Natore | 84 | 0.75
| Fatullah | 32 | 1:00 | Khulshi | 150 | 19:00 | Bogra | 107 | 20:00
| Mirpur | 60 | 12:00 | Halishahar | 80 | 18:30 | Noagaon | 85 | 18:30
| Kalyanpur | 60 | 13:00 | Baraulia | 144 | 1:00 | Rajshahi | 93 | 19:30
| Gulshan | 60 | 13:00 | Sikalbaha | 19 | 18:00 | Rajshahi New | 11 | 18:30
| Uttara | 62 | 13:00 | Dohazari | 58 | 19:30 | C.Nawabganj | 60 | 18:30
| Uttara New | 18 | 13:00 | Cox'sbazar | 81 | 19:00 | Amnura | 42 | 18:00
| Kamrangirchar | 51 | 12:00 | Chandraghona | 20 | 18:30 | Pabna | 54 | 18:30
| Savar | 88 | 18:30 | Kaptai | 3.6 | 18:00 | Shahjadpur | 66 | 19:00
| Bhasantec | 92 | 13:00 | A. Khaer Stl. | 8 | 3:00 | Serajganj | 50 | 18:30
| Agargaon | 45 | 13:00 | Bakulia | 60 | 13:00 | Niyamatpur | 73 | 9:00
| Satmosjid | 58 | 0.54167 | Julda | 20 | 0.29167 | Joypurhat | 58 | 0.79167
| Tongi | 67 | 13:00 | TK chemical | 18.5 | 19:00 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 121 | 21:00 | Modern Steel | 0 | 1:00 | Mohastangor | 36 | 18:30
| Basundhara | 78 | 18:30 | Shahmirpur | 14.8 | 1:00 | Bangura | 14 | 19:00
| Manikganj | 48 | 1:00 | Khagrachhari | 20 | 7:00 | Rangpur | 101 | 13:00
| Joydevpur | 82 | 21:00 | Matarbari | 27 | 18:30 | Lalmonirhat | 55 | 18:30
| New Tongi | 53 | 12:00 | Baroiar Hat | 44 | 18:00 | Saidpur | 90 | 10:00
| Kodda | 135 | 9:00 | Rangamati | 8 | 12:00 | Purbasadipur | 90 | 19:00
| Dhamrai | 56 | 19:30 | Abul Khair 230 | 212 | 10:00 | Thakurgaon | 65 | 18:30
| Rajendrapur | 58 | 21:00 | BSRM | 106 | 1:00 | Palashbari | 97 | 18:30
| Valuka | 82 | 11:00 | GPH Ispat | 70 | 13:00 | Barapukuria | 49 | 19:30
| Tangail | 134 | 22:00 | Goalpara | 7 | 18:30 | Panchagar | 43 | 18:30
| Mymensing | 171 | 18:30 | Central s/s | 75 | 19:30 | Joldhaka | 24 | 18:30
| Kishorganj | 114 | 18:30 | Noapara | 46 | 18:30 | Kurigram | 48 | 19:00
| Netrokona | 106 | 19:30 | Jessore | 84 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 423 | 22:00 | 416 | 24:00 | Kaliakoir | 418 | 0.70833 | 408 | 0.33333
| Bheramara | 408 | 1:00 | 395 | 18:00 | Bhulta | 398 | 0.041667 | 390 | 0.083333
| Ashuganj(N) | 402 | 1:00 | 393 | 24:00 | Gopalganj | 411 | 0.375 | 391 | 0.875
| Payra | 414 | 14:00 | 404 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 230 | 9:00 | 224 | 16:00
| Ishurdi | 244 | 22:00 | 235 | 8:00 | Megnaghat | 243 | 4:00 | 238 | 7:00
| Ashuganj | 246 | 7:00 | 242 | 3:00 | Fenchuganj | 250 | 21:00 | 242 | 24:00
| Serajganj | 235 | 22:00 | 230 | 8:00 | Siddhirganj | 241 | 7:00 | 236 | 15:00
| Baghabari | 242 | 21:00 | 234 | 11:00 | Maniknagar | 239 | 7:00 | 234 | 2:00
| Barapukuria | 233 | 2:00 | 226 | 12:00 | Agargaon | 241 | 5:00 | 235 | 3:00
| Bogra | 236 | 22:00 | 226 | 9:00 | Barisal | 252 | 9:00 | 242 | 19:30
| Rajshahi | 243 | 22:00 | 228 | 8:00 | Bhola 225 MW | 253 | 7:00 | 245 | 18:30
| Khulna South | 247 | 2:00 | 232 | 8:00 | AKSML | 237 | 9:00 | 223 | 10:00
| Rampura | 236 | 1:00 | 232 | 10:00 | BSRM | 237 | 19:30 | 225 | 3:00
| Haripur | 239 | 9:00 | 235 | 12:00 | Bibiyana | 251 | 13:00 | 245 | 24:00
| Hasnabad | 241 | 14:00 | 236 | 1:00 | Bhulta | 241 | 7:00 | 236 | 2:00
| Shyampur | 239 | 14:00 | 220 | 3:00 | Ashuganj (S) | 243 | 7:00 | 238 | 3:00
| Aminbazar | 242 | 21:00 | 236 | 11:00 | Kaliakoir | 241 | 1:00 | 236 | 2:00
| Tongi | 238 | 14:00 | 234 | 3:00 | GPH | 234 | 19:00 | 223 | 3:00
| Comilla (N) | 245 | 9:00 | 240 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 13:00 | 137 | 7:00 | Madanhat | 144 | 0.375 | 138 | 0.5
| Munsiganj | 141 | 11:00 | 136 | 5:00 | Hathazari | 140 | 0.33333 | 137 | 0.66667
| Sonargaon | 140 | 13:00 | 135 | 4:00 | Khulshi | 138 | 0.58333 | 133 | 0.66667
| Shyampur | 135 | 18:30 | 130 | 3:00 | Halishahar | 142 | 0.375 | 136 | 0.41667
| Bhulta | 137 | 14:00 | 133 | 24:00 | Baraulia | 141 | 0.45833 | 136 | 0.625
| Madanganj | 142 | 13:00 | 138 | 2:00 | Sikalbaha | 141 | 0.29167 | 135 | 0.66667
| Shitalakhya | 141 | 9:00 | 132 | 2:00 | Dohazari | 138 | 0.29167 | 132 | 0.5
| Rahim steal | 140 | 9:00 | 138 | 7:00 | Cox'sbazar | 131 | 0.16667 | 121 | 0.54167
| Matuail | 141 | 13:00 | 137 | 7:00 | Chandraghona | 143 | 0.58333 | 137 | 0.125
| Ghorasal | 142 | 1:00 | 140 | 8:00 | Kaptai | 140 | 0.75 | 135 | 0.45833
| Narsinghdi | 140 | 14:00 | 135 | 4:00 | A. Khaer Stl. | 139 | 0.041667 | 135 | 0.45833
| Haripur (SBU) | 140 | 7:00 | 137 | 2:00 | Bakulia | 141 | 0.375 | 134 | 0.66667
| Ullon | 135 | 1:00 | 130 | 13:00 | Julda | 140 | 0.20833 | 137 | 0.41667
| Hasnabad | 138 | 18:30 | 135 | 2:00 | TK Chemical | 141 | 0.875 | 135 | 0.16667
| Magbazar | 135 | 1:00 | 131 | 12:00 | Modern Steel | 140 | 0.54167 | 136 | 0.41667
| Maniknagar | 138 | 1:00 | 136 | 12:00 | Shahmirpur | 140 | 0.54167 | 136 | 0.66667
| Bangabhaban | 138 | 1:00 | 136 | 12:00 | Khagrachhari | 140 | 0.29167 | 136 | 0.54167
| Narinda | 138 | 1:00 | 136 | 12:00 | Matarbari | 136 | 0.77083 | 130 | 0.41667
| Dhanmondi | 135 | 1:00 | 130 | 13:00 | Baroiar Hat | 141 | 0.375 | 136 | 0.66667
| Lalbag | 140 | 21:00 | 131 | 3:00 | Rangamati | 141 | 19:30 | 136 | 3:00
| Madartek | 135 | 1:00 | 130 | 12:00 | Goalpara S/S | 140 | 7:00 | 133 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 141 | 9:00 | 133 | 0.33333
| Aftabnagar | 136 | 1:00 | 131 | 12:00 | Noapara | 139 | 9:00 | 132 | 0.33333
| Fatuiiah | 136 | 22:00 | 132 | 2:00 | Jessore | 135 | 3:00 | 128 | 0.75
| Mirpur | 140 | 1:00 | 137 | 8:00 | Benapol | 135 | 0.041667 | 126 | 0.83333
| Kalyanpur | 140 | 7:00 | 137 | 12:00 | Jhenida | 134 | 1:00 | 127 | 0.33333
| Gulshan | 134 | 6:00 | 130 | 12:00 | Bottail | 137 | 0.041667 | 133 | 0.29167
| Uttara | 140 | 7:00 | 134 | 12:00 | G.K Project | 142 | 0.083333 | 138 | 0.33333
| Uttara New | 142 | 7:00 | 137 | 12:00 | Faridpur | 137 | 0.125 | 131 | 0.83333
| Kamrangirchar | 137 | 11:00 | 135 | 12:00 | Madaripur | 141 | 0.45833 | 136 | 0.83333
| Savar | 140 | 7:00 | 137 | 12:00 | Shariyatpur S/S | 142 | 15:00 | 135 | 0.8125
| Bhasantec | 138 | 7:00 | 135 | 12:00 | Gopalganj | 143 | 0.25 | 135 | 0.8125
| Agargaon | 139 | 7:00 | 136 | 11:00 | Bagerhat | 139 | 13:00 | 131 | 0.77083
| Satmosjid | 137 | 6:00 | 135 | 12:00 | Mongla | 138 | 9:00 | 129 | 0.33333
| Tongi | 144 | 14:00 | 140 | 5:00 | Satkhira | 139 | 1:00 | 131 | 8:00
| Kabirpur | 138 | 14:00 | 135 | 15:00 | Gallamari | 140 | 0.29167 | 135 | 0.5
| Basundhara | 141 | 19:30 | 132 | 0:00 | Magura | 135 | 2:00 | 126 | 0.83333
| Manikganj | 146 | 22:00 | 140 | 4:00 | Narail | 134 | 0.20833 | 126 | 0.83333
| Joydevpur | 142 | 17:00 | 137 | 0:00 | Chuadanga | 133 | 1:00 | 124 | 0.77083
| New Tongi | 142 | 21:00 | 139 | 15:00 | Barisal(N) | 142 | 1:00 | 136 | 19:00
| Kodda | 138 | 11:00 | 135 | 1:00 | Barisal (S) | 141 | 0.375 | 135 | 0.79167
| Dhamrai | 138 | 1:00 | 134 | 12:00 | Patuakhali(S) | 140 | 0.25 | 131 | 0.79167
| Rajendrapur | 141 | 18:00 | 138 | 13:00 | Bhandaria | 142 | 0.16667 | 131 | 0.875
| Valuka | 127 | 13:00 | 132 | 7:00 | Ishurdi | 140 | 2:00 | 137 | 8:00
| Tangail | 137 | 11:00 | 133 | 8:00 | Ruppur Paromanobik | 140 | 2:00 | 135 | 12:00
| Mymensing | 134 | 5:00 | 128 | 18:30 | Natore | 139 | 4:00 | 133 | 7:00
| Kishorganj | 136 | 6:00 | 128 | 18:30 | Bogra | 139 | 2:00 | 132 | 8:00
| Netrokona | 130 | 3:00 | 126 | 18:30 | Noagaon | 132 | 1:00 | 125 | 8:00
| Jamalpur | 140 | 14:00 | 131 | 4:00 | Rajshahi | 137 | 7:00 | 132 | 8:00
| Sherpur | 139 | 15:00 | 130 | 3:00 | Rajshahi New | 138 | 20:00 | 130 | 8:00
| Srimongal | 140 | 4:00 | 137 | 1:00 | C.Nawabganj | 136 | 19:00 | 129 | 10:00
| Shahjibazar | 138 | 1:00 | 135 | 18:30 | Amnura | 139 | 19:00 | 127 | 8:00
| Fenchuganj | 141 | 23:00 | 137 | 15:00 | Pabna | 140 | 14:00 | 136 | 9:00
| Khulawara | 139 | 13:00 | 137 | 5:00 | Shahjadpur | 143 | 1:00 | 138 | 10:00
| Sylhet | 137 | 14:00 | 135 | 16:00 | Serajganj | 137 | 1:00 | 134 | 8:00
| Chatak | 136 | 2:00 | 134 | 17:00 | Niyamatpur | 131 | 2:00 | 121 | 9:00
| Sunamganj | 136 | 1:00 | 134 | 18:00 | Joypurhat | 133 | 2:00 | 124 | 8:00
| Biani Bazar | 137 | 8:00 | 135 | 17:00 | Sherpur(Bogura) | 136 | 3:00 | 132 | 10:00
| Comilla(s) | 131 | 14:00 | 128 | 18:00 | Mohastangor | 137 | 3:00 | 130 | 8:00
| Comilla(n) | 147 | 9:00 | 143 |  | Bangura | 140 | 1:00 | 138 | 7:00
| Chandpur | 145 | 22:00 | 142 | 15:00 | Rangpur | 131 | 5:00 | 120 | 10:00
| Feni | 141 | 20:00 | 138 | 15:00 | Lalmonirhat | 131 | 4:00 | 120 | 10:00
| Chowmuhani | 138 | 22:00 | 135 | 12:00 | Saidpur | 130 | 3:00 | 120 | 9:00
| Ashuganj | 141 | 5:00 | 138 | 0:00 | Purbasadipur | 130 | 1:00 | 118 | 9:00
| Daudkandi | 143 | 9:00 | 138 | 16:00 | Thakurgaon | 128 | 1:00 | 118 | 12:00
| B.Baria | 137 | 9:00 | 133 | 20:00 | Palashbari | 133 | 4:00 | 124 | 9:00
| Ramganj | 138 | 15:00 | 135 | 18:00 | Barapukuria | 133 | 2:00 | 126 | 12:00
| Chaddagram | 142 | 14:00 | 139 | 11:00 | Panchagar | 130 | 5:00 | 117 | 9:00

## L-Curve
Date | 2021-01-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 216 | 4160 | 2322 | 6482 |  |  |  | QF-LDC-11
0:30 | 151.5 | 4316.5 | 2248.5 | 6565 | Date: | 2021-01-22
1:00 | 87 | 4473 | 2175 | 6648
1:30 | 127 | 4246.5 | 2162 | 6408.5
2:00 | 167 | 4020 | 2149 | 6169
2:30 | 211.5 | 3933.5 | 2069 | 6002.5 | [5 empty] | Gen. at Eve. Peak | 8189 | 9500 MW (19:30 )
3:00 | 256 | 3847 | 1989 | 5836 | [6 empty] | 20:00
3:30 | 235 | 3847.5 | 1980.5 | 5828 | [5 empty] | Gen. at Day Peak | 6681 | 7952.5 MW (12:00 )
4:00 | 214 | 3848 | 1972 | 5820 | [6 empty] | 12:00
4:30 | 222.5 | 3768 | 1972.5 | 5740.5 | [5 empty] | Highest Generation | 8189
5:00 | 231 | 3688 | 1973 | 5661 | [6 empty] | 20:00
5:30 | 181 | 3727 | 1970 | 5697
6:00 | 131 | 3766 | 1967 | 5733
6:30 | 95.5 | 3862 | 1931.5 | 5793.5
7:00 | 60 | 3958 | 1896 | 5854
7:30 | 39 | 4027.5 | 1979 | 6006.5
8:00 | 18 | 4097 | 2062 | 6159
8:30 | 33 | 4217.5 | 2092 | 6309.5
9:00 | 48 | 4338 | 2122 | 6460
9:30 | 71 | 4353 | 2136.5 | 6489.5
10:00 | 94 | 4368 | 2151 | 6519
10:30 | 78 | 4406.5 | 2115.5 | 6522
11:00 | 62 | 4445 | 2080 | 6525
11:30 | 34 | 4512 | 2091 | 6603
12:00 | 6 | 4579 | 2102 | 6681
12:30 | 67.5 | 4821 | 2152 | 6973
13:00 | 129 | 5063 | 2202 | 7265
13:30 | 104 | 4715.5 | 2149 | 6864.5
14:00 | 79 | 4368 | 2096 | 6464
14:30 | 149.5 | 4204.5 | 2065.5 | 6270
15:00 | 220 | 4041 | 2035 | 6076
15:30 | 218.5 | 3947 | 2000.5 | 5947.5
16:00 | 217 | 3853 | 1966 | 5819
16:30 | 199 | 3934 | 1982 | 5916
17:00 | 181 | 4015 | 1998 | 6013
17:30 | 120.5 | 4382 | 2335.5 | 6717.5
18:00 | 60 | 4749 | 2673 | 7422
18:30 | 110 | 4909 | 2802.5 | 7711.5
19:00 | 160 | 5069 | 2932 | 8001
19:30 | 114 | 5143 | 3009 | 8152
20:00 | 101 | 5158 | 3031 | 8189 |  |  |  | Executive Engineer
20:30 | 157.5 | 5126 | 3035.5 | 8161.5 |  |  |  | Network Operation Division
21:00 | 214 | 5094 | 3040 | 8134
21:30 | 182.5 | 4987.5 | 2941.5 | 7929
22:00 | 151 | 4881 | 2843 | 7724 |  |  |  |  | Page 6 of 7
22:30 | 151.5 | 4763 | 2650 | 7413
23:00 | 152 | 4645 | 2457 | 7102
23:30 | 184 | 4402.5 | 2389.5 | 6792
24:00 | 216 | 4160 | 2322 | 6482
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-22 |  | Energy | 162427962
[11 empty] | 2021-01-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2199 | 447 | 1486 | 2231 | 590 | 44 | 70 | 0 | 74 | 0
0:30 | 2264 | 444 | 1462 | 1954.5 | 590 | 45 | 59 | 0 | 76 | 0 | Date: | 2021-01-22
1:00 | 2329 | 441 | 1438 | 1678 | 590 | 46 | 48 | 0 | 78 | 0
1:30 | 2337 | 441.5 | 1435.5 | 1463 | 585 | 46.5 | 24 | 0 | 76 | 0 | [7 empty] | Total Energy | 162.428 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2345 | 442 | 1433 | 1248 | 580 | 47 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2358 | 394.5 | 1441 | 1114.5 | 575 | 47.5 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 162.428
3:00 | 2371 | 347 | 1449 | 981 | 570 | 48 | 0 | 0 | 70 | 0
3:30 | 2367 | 347 | 1450.5 | 981 | 565 | 48.5 | 0 | 0 | 69 | 0 | [6 empty] | Shortage
4:00 | 2363 | 347 | 1452 | 981 | 560 | 49 | 0 | 0 | 68 | 0
4:30 | 2332.5 | 347 | 1402 | 981 | 560 | 49 | 0 | 0 | 69 | 0
5:00 | 2302 | 347 | 1352 | 981 | 560 | 49 | 0 | 0 | 70 | 0
5:30 | 2309 | 347 | 1346 | 1010.5 | 565 | 48.5 | 0 | 0 | 71 | 0
6:00 | 2316 | 347 | 1340 | 1040 | 570 | 48 | 0 | 0 | 72 | 0
6:30 | 2324 | 347 | 1303 | 1127.5 | 575 | 48 | 0 | 0 | 69 | 0 |  |  |  |  | Coal
7:00 | 2332 | 347 | 1266 | 1215 | 580 | 48 | 0 | 0 | 66 | 0
7:30 | 2362.5 | 418 | 1307 | 1220.5 | 580 | 48 | 0 | 0 | 66 | 4.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2393 | 489 | 1348 | 1226 | 580 | 48 | 0 | 0 | 66 | 9
8:30 | 2387.5 | 489 | 1362.5 | 1373 | 575 | 47 | 0 | 0 | 63 | 12.5
9:00 | 2382 | 489 | 1377 | 1520 | 570 | 46 | 0 | 0 | 60 | 16
9:30 | 2386.5 | 488.5 | 1383.5 | 1533 | 570 | 46 | 0 | 0 | 61 | 21
10:00 | 2391 | 488 | 1390 | 1546 | 570 | 46 | 0 | 0 | 62 | 26
10:30 | 2377.5 | 478.5 | 1362 | 1594 | 570 | 46.5 | 0 | 0 | 61 | 32.5
11:00 | 2364 | 469 | 1334 | 1642 | 570 | 47 | 0 | 0 | 60 | 39
11:30 | 2346.5 | 467.5 | 1351 | 1706.5 | 570 | 47 | 0 | 0 | 62 | 52.5
12:00 | 2329 | 466 | 1368 | 1771 | 570 | 47 | 0 | 0 | 64 | 66
12:30 | 2354.5 | 468.5 | 1435.5 | 1940.5 | 580 | 47.5 | 16 | 0 | 65 | 65.5
13:00 | 2380 | 471 | 1503 | 2110 | 590 | 48 | 32 | 0 | 66 | 65
13:30 | 2380 | 471 | 1503 | 2110 | 590 | 48 | 32 | 0 | 66 | 65
14:00 | 2380 | 471 | 1503 | 2110 | 590 | 48 | 32 | 0 | 66 | 65
14:30 | 2169.5 | 470.5 | 1406 | 1866 | 579.5 | 47.5 | 16 | 0 | 63 | 52.5
15:00 | 1959 | 470 | 1309 | 1622 | 569 | 47 | 0 | 0 | 60 | 40
15:30 | 1957.5 | 469.5 | 1287 | 1541.5 | 559 | 47 | 0 | 0 | 56 | 30
16:00 | 1956 | 469 | 1265 | 1461 | 549 | 47 | 0 | 0 | 52 | 20
16:30 | 2024 | 471 | 1281 | 1454 | 549 | 47.5 | 16 | 0 | 62 | 11.5
17:00 | 2092 | 473 | 1297 | 1447 | 549 | 48 | 32 | 0 | 72 | 3
17:30 | 2174.5 | 593 | 1405 | 1747 | 534 | 47.5 | 135 | 0 | 80 | 1.5
18:00 | 2257 | 713 | 1513 | 2047 | 519 | 47 | 238 | 0 | 88 | 0
18:30 | 2147.5 | 713 | 1531 | 2363 | 579 | 47 | 238 | 0 | 93 | 0
19:00 | 2038 | 713 | 1549 | 2679 | 639 | 47 | 238 | 0 | 98 | 0
19:30 | 2030 | 713 | 1564 | 2763 | 699 | 47 | 238 | 0 | 98 | 0
20:00 | 2057 | 713 | 1558 | 2771 | 709 | 47 | 238 | 0 | 96 | 0
20:30 | 2044.5 | 713 | 1556 | 2754 | 714.5 | 46.5 | 238 | 0 | 95 | 0
21:00 | 2032 | 713 | 1554 | 2737 | 720 | 46 | 238 | 0 | 94 | 0
21:30 | 2009.5 | 601 | 1548.5 | 2700 | 715 | 46 | 215 | 0 | 94 | 0
22:00 | 1987 | 489 | 1543 | 2663 | 710 | 46 | 192 | 0 | 94 | 0
22:30 | 2014.5 | 459.5 | 1520.5 | 2447 | 680 | 45 | 156.5 | 0 | 90 | 0
23:00 | 2042 | 430 | 1498 | 2231 | 650 | 44 | 121 | 0 | 86 | 0
23:30 | 2120.5 | 438.5 | 1492 | 2231 | 620 | 44 | 95.5 | 0 | 80 | 0 | Max Temp. in Dhaka |  | 23.6° C
24:00 | 2199 | 447 | 1486 | 2231 | 590 | 44 | 70 | 0 | 74 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 47 | 48 | 49 | 49 | 48 | 48 | 48 | 46 | 46 | 47 | 47 | 48 | 47 | 47 | 47 | 48 | 47 |  | 47 | 47 | 47 | 46 | 46 | 44 | 44 | 1123113
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 5 | 10 | 14 | 17 | 18 | 18 | 16 | 12 | 7 | 1 | [9 empty] | 117045
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 85 | 85 | 85 | 55 |  |  | 391518
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 195 | 145 | 145 | 145 | 145 | 158 | 145 | 182 | 195 | 245 | 245 | 275 | 245 | 195 | 195 | 195 | 250 |  | 300 | 300 | 300 | 300 | 289 | 300 | 95 | 5462289
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 170 | 170 | 165 | 14 | [12 empty] | 2422018
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 70560
33 | Ashuganj 225 MW CCPP | 161 | 174 | 167 | 164 | 164 | 166 | 174 | 172 | 171 | 163 | 158 | 151 | 152 | 140 | 156 | 163 | 168 | 177 |  | 177 | 177 | 177 | 180 | 173 | 170 | 180 | 4040000
34 | Ashuganj 450 MW CCPP(South) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5751000
| Ashuganj 450 MW CCPP(North) | 180 | 165 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4174500
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 35 | 36 | 36 | 36 | 35 | 34 | 32 | 36 | 40 | 41 | 36 | 39 | 39 | 34 | 40 | 40 | 40 | 40 |  | 40 | 39 | 50 | 36 | 39 | 40 | 39 | 889880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 324 | 337 | 349 | 340 | 326 | 338 | 318 | 346 | 341 | 345 | 327 | 338 | 371 | 325 | 332 | 333 | 359 | 343 |  | 354 | 339 | 349 | 338 | 324 | 324 | 327 | 8239100
40 | Meghnaghat 450 MW CCPP(MPL) | [26 empty] | 0
41 | Haripur 360MW CCPP(HPL) | 240 | 246 | 260 | 280 | 288 | 290 | 300 | 300 | 294 | 283 | 255 | 254 | 274 | 275 | 286 | 282 | 285 | 303 |  | 305 | 305 | 304 | 298 | 300 | 310 | 343 | 6742000
42 | RPCL 210MW CCPP | 108 | 133 | 147 | 151 | 142 | 139 | 142 | 139 | 140 | 123 | 106 | 98 | 105 | 105 | 103 | 102 | 103 | 106 |  | 106 | 107 | 105 | 107 | 108 | 109 | 108 | 2794840
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 3 | 7 | 15 | 41 | 38 | 33 | 23 | 11 | 2 | [9 empty] | 170630
44 | Fenchugonj CCPP Phase-1 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 498000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 0
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 29 | 30 | 30 | 31 | 30 | 30 | 29 | 31 | 30 | 30 | 29 | 30 | 29 | 28 | 29 | 29 | 30 |  | 30 | 30 | 30 | 30 | 31 | 31 | 30 | 722880
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 75 | 56 | 56 | 57 | 57 | 57 | 57 | 59 | 70 | 70 | 72 | 71 | 40 | 40 | 20 | 20 | 69 |  | 71 | 71 | 71 | 71 | 71 | 72 | 72 | 1473600
| Shahjibazar 100 MW GTPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2280000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 169 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 176 | 188 | 188 | 190 | 164 | 164 | 164 | 215 | 215 |  | 215 | 215 | 215 | 215 | 176 | 176 | 176 | 4233750
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 210600
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 47 | 45 | 45 | 14 | 14 | 22 |  | 48 | 48 | 48 | 48 | 48 | 31 | 31 | 652800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196176
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 295 | 310 | 300 | 300 | 305 | 290 | 310 | 300 | 300 | 280 | 290 | 340 | 260 | 270 | 290 | 310 | 310 |  | 310 | 320 | 315 | 320 | 280 | 290 | 290 | 7485000
| Bibiyana South 400 MW | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 100 | 100 | 100 | 150 | 250 | [6 empty] | 50 | 200 | 3864900
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  |  | 5 | 17 | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 849962
59 | Tangail Palli Power Gen 22 MW | 25 | 25 | [6 empty] | 15 | 18 | 18 | 16 |  |  | 3 | 21 | 24 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 351360
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 463488
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 345744
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 487980
63 | Impoprt (Tripura) | 78 | 74 | 70 | 68 | 70 | 72 | 66 | 66 | 60 | 62 | 60 | 64 | 66 | 62 | 60 | 52 | 72 | 88 |  | 98 | 98 | 96 | 94 | 94 | 86 | 74 | 1776960
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 40 | 40 | 40 | 42 | 33 | 33 | 33 | 42 | 35 | 25 | 34 | 34 | 38 |  | 38 | 40 | 40 | 40 | 30 | 30 | 32 | 931680
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 451620
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [11 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 110520
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 28 | 28 | 25 | 33 | 33 | 25 | 8 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 740000
68 | Cumilla 25 MW PP (Summit) | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 470130
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 18 |  | 8 | 9 | 8 | 11 | 11 | 11 |  | 23 | 27 | 27 | 22 | 32 | 28 | 28 | 478620
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 582600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 0 | 0 | 17 | 33 | 25 | 25 | 25 | 25 |  |  | 24 |  | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 571400
73 | Ghorashal 108MW PP (Regent) | [10 empty] | 40 | 55 | 82 | 101 | 97 | 101 | 103 | 107 |  | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 1244090
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 75 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 39 | 55 | 35 | 35 | 35 | 46 |  | 68 | 75 | 75 | 75 | 75 | 75 | 46 | 1162560
| Manikgonj 162MW PP(MPGL) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 126 | 126 | 126 | 126 | 126 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3134880
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 1 | 7 | 7 | 7 |  |  | 3 | 15 |  | 15 | 15 | 15 | 15 | 13 |  |  | 114240
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | 48 | [11 empty] | 32 | 16 |  |  | 32 | 48 |  | 48 | 48 | 48 | 48 | 32 | 16 |  | 395040
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 13 | 16 | 16 | 16 | 16 | 16 | 27 | 40 | 40 | 40 | 40 | 40 |  | 68 | 82 | 82 | 82 | 64 |  |  | 663360
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [10 empty] | 4 | 17 | 17 | 17 |  |  | 3 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 150492
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 25801
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 52 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 665636
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 25 | 50 | 64 | 40 | 30 | 30 | 30 | 60 |  | 99 | 99 | 99 | 99 | 99 | 99 | 30 | 1096728
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | 10 | 10 | 10 | 10 | 28 | 69 | 75 | 74 | 73 | 75 | 73 | 60 | 60 | 40 | 40 | 40 | 70 |  | 74 | 74 | 74 | 74 | 74 | 74 | 76 | 1400530
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 16 | [11 empty] | 8 | 24 | 15 | 7 | 7 | 14 |  | 74 | 100 | 100 | 100 | 100 | 100 | 65 | 672960
| Meghnaghat 104 MW PP (OPCL) | 75 | 40 | 17 | 17 | 17 | 22 | 35 | 35 | 61 | 70 | 70 | 70 | 83 | 85 | 65 | 35 | 35 | 56 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1486080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 47 | 47 | 47 | 47 | 50 | 20 | 20 | 20 | 20 | 27 |  | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 771624
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1248090
94 | Gagnagar 102 MW PP (Digital Power) | 48 | [5 empty] | 16 | 16 | 64 | 64 | 64 | 64 | 102 | 64 | 40 | 40 | 48 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1069920
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 46 | 50 | 50 | 50 | 38 | 25 | 25 | 25 | 26 |  | 48 | 50 | 50 | 50 | 50 | 29 | 37 | 856320
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 10 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 299644
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 17 | 25 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 |  | 285547
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | [10 empty] | 3950
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 250200
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 44 | 53 | 55 | 30 |  |  |  | 110114
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 85 | 50 | 50 | 50 | 79 | 80 | 94 | 150 | 150 | 150 | 161 | 178 | 200 | 180 | 150 | 150 | 168 |  | 200 | 200 | 200 | 192 | 200 | 200 | 100 | 3583200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 40 |  |  |  |  | 2 | 22 | 33 | 38 | 49 | 52 | 98 | 111 | 107 | 81 | 72 | 65 | 65 |  | 96 | 101 | 101 | 100 | 100 | 76 |  | 1363680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 80 | 30 | [5 empty] | 10 | 20 | 20 | 20 | 30 | 100 | 60 | 50 | 50 | 30 | 30 |  | 50 | 50 | 50 | 50 | 50 | 20 |  | 838080
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 31 | 34 | 34 | 34 | 34 | 34 | 34 | 524640
117 | Ashuganj 150MW PP (Midland) | 53 | 48 | 10 | 10 | 10 | 10 | 36 | 53 | 55 | 53 | 53 | 53 | 53 | 53 | 55 | 56 | 50 | 53 |  | 55 | 53 | 50 | 55 | 51 | 53 | 55 | 1117381
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [12 empty] | 4 | 8 |  |  |  | 2 |  | 10 | 16 | 8 |  |  |  |  | 52800
| Anwara 300 MW PP (United) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 214 | 216 | 216 | 252 | 216 | 198 | 162 | 162 | 196 |  | 250 | 250 | 250 | 252 | 252 | 234 | 236 | 5748327
| Juldah unit-2 (Acorn) | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 90 | 70 | 50 | 50 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2213760
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4473 | 4020 | 3847 | 3848 | 3688 | 3766 | 3958 | 4097 | 4338 | 4368 | 4445 | 4579 | 5063 | 4368 | 4041 | 3853 | 4015 | 4749 |  | 5069 | 5143 | 5158 | 5094 | 4881 | 4645 | 4160 | 106671664
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 66 | 66 | 66 | 66 | 69 | 32 | 83 | 83 | 83 | 105 | 115 | 115 | 83 | 66 | 66 | 103 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2188800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | [6 empty] | 10 | 17 | 17 | 17 | 53 | 35 | 35 | 17 | 17 | 35 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 836160
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 58 | 57 | 58 | 56 | 57 | 23 | 19 | 56 | 47 | 56 | 57 | 60 | 54 | 56 | 57 | 41 | 41 | 56 |  | 34 | 21 | 21 | 25 | 56 | 57 | 57 | 1215027
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 68 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 44 | 43 | 43 | 43 | 43 | 32 | 32 | 71 |  | 71 | 74 | 72 | 71 | 71 | 71 | 73 | 1442401
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 20 | 20 | 20 | 19 | 19 | 17 | 18 | 17 | 13 | 12 | 12 | 15 | 12 | 11 | 10 | 11 | 25 |  | 24 | 25 | 25 | 25 | 24 | 23 | 22 | 430500
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 24 | 8 |  |  |  | 8 |  | 40 | 40 | 40 | 40 | 40 |  |  | 199500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 441 | 442 | 347 | 347 | 347 | 347 | 347 | 489 | 489 | 488 | 469 | 466 | 471 | 471 | 470 | 469 | 473 | 713 |  | 713 | 713 | 713 | 713 | 489 | 430 | 447 | 11823273
147 | Bheramara 410 MW CCPP | 300 | 305 | 310 | 310 | 310 | 315 | 300 | 300 | 300 | 300 | 295 | 290 | 295 | 285 | 290 | 300 | 320 | 325 |  | 325 | 325 | 320 | 320 | 320 | 330 | 335 | 7547328
148 | Payra 1320 MW | 440 | 430 | 420 | 410 | 410 | 420 | 430 | 430 | 420 | 420 | 420 | 420 | 440 | 440 | 420 | 400 | 400 | 370 |  | 490 | 550 | 560 | 570 | 560 | 500 | 440 | 11606900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 3664700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 411 | 416 | 411 | 413 | 426 | 363 | 382 | 401 | 418 | 392 | 398 | 395 | 307 | 325 | 331 | 337 | 395 |  | 401 | 413 | 415 | 409 | 416 | 396 | 349 | 9265236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 521520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246996
165 | Amnura 50 MW PP(Sinha) | [13 empty] | 25 | 12 | 12 | 12 | 12 |  | 25 | 25 | 25 | 25 | 25 |  |  | 191450
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 4 | 8 | [5 empty] | 5 | 18 | 34 | 34 | 34 |  |  | 124320
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 645186
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 79 |  | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 1309920
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 |  | 93 | 94 | 95 | 95 | 95 | 57 | 57 | 1219200
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 104 |  | 106 | 106 | 106 | 107 | 107 | 50 | 35 | 1248960
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 1 | 2 | 3 | 3 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 28921
178
178