## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-26 | Tuesday
|  |  | Date (day): | 2021-01-26 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11050.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12269 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-25 | 2021-01-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 170 | 170 | 170
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 107 | 110 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2021-07-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 364 | 366 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 240 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 100 | 101 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 50 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 62 | 75 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 180 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 16 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 12 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 115 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 263 | 250 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 31 | 158 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 114 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 48 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 91 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 126 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2462 | 2744 | 3287 | 3537 | 108 | 2281
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 0 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 69 | 68 | 68 | 162 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 34 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 68 | 102 | 102 | 102
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 25 | 15 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 24 | 11 | 97 | 97 |  | 11 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 270 | 286 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 768 | 886 | 1143 | 1253 | 897 | 109
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 161 | 216 | 180 | 180 | 41 |  | Gas shortage
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 150 | 175 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 350 | 350
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 6 | 5 | 5 | 40 |  | Gas shortage
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 21 | 16 | 20 | 20 |  | 130 | Engine Problem
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 16 | 33 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 92 | 100 | 100 |  | 63 | ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 17 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 20 | 20
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 102 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 103 | 85 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1019 | 1147 | 1547 | 1811 | 586 | 553
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 106 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 49 | 52 | 92 | 92
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 16 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 411 | 420 | 612.6 | 561 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 140 | 163 | 163
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 13 | 51 | 50 | 50
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 20 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under maint
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 69 | 73 | 73 | 73 |  | 13 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 100 | 100 | 100 | 100 |  | 0 | Under maint
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 162 | 0 | 100 |  | 131 | under maint.
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 295 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Gas shortage
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 50 | 130 | 400 | 400 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 880 | 1077 | 1255 | 1355 | 0 | 931
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 720 | 907 | 741 | 885
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 13 | 18 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 7 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 405 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 60 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 72 | 95 | 90 | 90 |  | 15 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 50 | 67 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1355 | 1714 | 1641 | 2071 | 0 | 83
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 96 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 22 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 86 | 88 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 |  |  | 400 kV line maintenance
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 35 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 168 | 241 | 227 | 227 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 |  | Gas shortage
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 5 | 220 | 220 | 220 |  | Gas shortage
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 372 | 0 | 0 |  | 414 | Under maint.
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 13 | 22 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 104 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 94 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 677 | 796 | 1067 | 1191 | 821 | 439
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 103 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 153 | 253 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7893 | 9278 | 11050.6 | 12269 | 2628 | 4811
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7499.1156 | 8815 | 10499.1419 | 11656.7401
| A. |  | 2021-01-25 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9278 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5675 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9278 | MW
| 3 | Day peak Generation : |  |  | 7893 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8815 | MW
| 4 | Evening peak Generation : |  |  | 9278 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 180.7542 | MKWHr | By Solar | 0.19666 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 89.8538 | MKWHr |  | By Oil: | 67.141 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 3.6675 | MKWHr |  | By Hydro: | 1.2534 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2628 | MW | Dhaka | 3017 | 3017 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4811 | MW | Chittagong | 907 | 907 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7439 | MW | Khulna | 1100 | 1100 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 799.27 | MMCFD |  |  | Rajshahi | 982 | 982 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 99231980.716 | ii) Oil : | Taka | 469617575.49 | Comilla | 753 | 753 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 19877850 | Total | Taka | 588727406.206 | Mymensingh | 780 | 780 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.9785 | MKWHr. | Sylhet | 336 | 336 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -129 | MW (E to W) at | 19:00 | hrs | Barisal | 238 | 238 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -330 | MW at | 24:00 | hrs | Rangpur | 702 | 702 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 26.0° C |  |  | Total | 8815 | 8815 |  | 0
| B. |  | 2021-01-26 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12269 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2769 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 185.0792 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5815 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0294 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.47 |  | (b) Today: | 96.39 |  | (c) Rule Curve: |  | 98.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 355 |  | 0 | 0 | 285 | 70 | 48 | 0 | 0 | 0 | 90 | 0 | 48 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 40 | 0 | 0 | 0 | 150 | 250 | 161 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 22 | 74 | 108 | 0 | 22 | 0 | 30 | 0 | 51 | 47 | 110 | 0 | 0 | 74 | 0 | 222 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 268 | 0 | 0 | 150 | 0 | 0 | 0 | 60 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 16 | 100 | 50 | 91 | 0 | 144 | 0 | 100 |  | 437 | 0 | 400 | 0 | 97 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 370 | 35 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 57 | 0 | 0 |  | 4553 | 1815 | 6368 | 2032 | 437 | 1580 | 1979 | 148 | 46 | 72 | 74 | 0 | 0 | 96.48
2:00 | 0 | 0 | 0 | 110 | 0 | 109 | 0 | 0 | 363 |  | 0 | 0 | 260 | 25 | 48 | 0 | 0 | 0 | 90 | 0 | 48 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 41 | 0 | 0 | 0 | 150 | 250 | 154 | 8 | 101 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 72 | 110 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 74 | 0 | 222 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 195 | 0 | 0 | 100 | 0 | 0 | 0 | 60 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 16 | 100 | 50 | 91 | 0 | 126 | 0 | 100 |  | 437 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 395 | 35 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 57 | 0 | 0 |  | 4509 | 1744 | 6253 | 1998 | 437 | 1761 | 1738 | 149 | 46 | 52 | 72 | 0 | 0 | 96.48
3:00 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 363 |  | 0 | 0 | 260 | 7 | 48 | 0 | 0 | 0 | 88 | 0 | 48 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 42 | 0 | 0 | 0 | 150 | 250 | 152 | 8 | 93 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 72 | 110 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 74 | 0 | 222 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 70 | 0 | 0 | 0 | 60 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 8 | 60 | 50 | 60 | 0 | 108 | 0 | 100 |  | 437 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 380 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 0 | 57 | 0 | 0 |  | 4256 | 1685 | 5941 | 2000 | 437 | 1748 | 1479 | 149 | 47 | 9 | 72 | 0 | 0 | 96.48
4:00 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 363 |  | 0 | 0 | 260 | 7 | 30 | 0 | 0 | 0 | 89 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 25 | 26 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 42 | 0 | 0 | 0 | 150 | 250 | 149 | 8 | 101 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 20 | 18 | 72 | 103 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 74 | 0 | 222 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 0 | 30 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 8 | 60 | 50 | 54 | 0 | 108 | 0 | 100 |  | 437 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 365 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 0 | 57 | 0 | 0 |  | 4145 | 1618 | 5763 | 1980 | 437 | 1733 | 1336 | 149 | 47 | 9 | 72 | 0 | 0 | 96.47
5:00 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 365 |  | 0 | 0 | 285 | 7 | 30 | 0 | 0 | 0 | 40 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 25 | 26 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 42 | 0 | 0 | 0 | 150 | 250 | 133 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 72 | 103 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 110 | 0 | 0 | 74 | 0 | 222 | 19 | 0 | 9 | 305 | 8 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 0 | 0 | 30 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 8 | 60 | 50 | 54 | 0 | 108 | 0 | 100 |  | 436 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 395 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 0 | 22 | 0 | 0 |  | 4038 | 1637 | 5675 | 1952 | 436 | 1705 | 1305 | 149 | 47 | 9 | 72 | 0 | 0 | 96.47
6:00 | 0 | 0 | 0 | 115 | 0 | 109 | 0 | 0 | 314 |  | 0 | 0 | 260 | 20 | 35 | 0 | 0 | 0 | 65 | 0 | 32 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 46 | 22 | 25 | 26 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 27 | 17 | 42 | 0 | 0 | 0 | 150 | 250 | 136 | 8 | 92 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 72 | 103 | 2 | 22 | 0 | 30 | 0 | 31 | 30 | 140 | 0 | 0 | 74 | 0 | 208 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 167 | 0 | 0 | 67 | 0 | 10 | 0 | 60 | 0 | 40 | 0 | 0 | 3 | 0 | 0 | 288 | 0 | 0 | 0 | 20 | 100 | 50 | 54 | 0 | 0 | 0 | 100 |  | 500 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 362 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 0 | 17 | 0 | 0 |  | 4129 | 1709 | 5838 | 1933 | 500 | 1602 | 1525 | 150 | 47 | 9 | 72 | 0 | 0 | 96.47
7:00 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 340 |  | 0 | 0 | 260 | 40 | 64 | 13 | 0 | 0 | 40 | 0 | 40 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 26 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 17 | 39 | 0 | 0 | 0 | 150 | 250 | 131 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 68 | 102 | 24 | 22 | 0 | 30 | 0 | 31 | 30 | 110 | 0 | 0 | 68 | 0 | 215 | 18 | 0 | 9 | 315 | 8 | 11 | 0 | 230 | 0 | 0 | 85 | 0 | 30 | 1 | 76 | 0 | 41 | 0 | 0 | 17 | 0 | 0 | 301 | 0 | 0 | 0 | 24 | 100 | 50 | 53 | 0 | 40 | 0 | 100 |  | 604 | 0 | 415 | 0 | 99 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 442 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 0 | 20 | 0 | 0 |  | 4394 | 1981 | 6375 | 1988 | 604 | 1680 | 1828 | 150 | 47 | 9 | 68 | 1 | 0 | 96.46
8:00 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 364 |  | 0 | 0 | 260 | 40 | 64 | 15 | 0 | 0 | 90 | 7 | 40 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 55 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 25 | 17 | 12 | 0 | 0 | 0 | 150 | 250 | 120 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 20 | 74 | 102 | 24 | 22 | 0 | 30 | 0 | 48 | 44 | 140 | 0 | 0 | 69 | 0 | 215 | 18 | 0 | 9 | 330 | 8 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 58 | 5 | 100 | 0 | 40 | 0 | 16 | 17 | 0 | 1 | 306 | 0 | 0 | 0 | 24 | 100 | 50 | 53 | 4 | 126 | 0 | 100 |  | 720 | 0 | 430 | 0 | 115 | 0 | 0 | 0 | 4 | 0 | 16 | 0 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 19 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 430 | 90 | 0 | 0 | 0 | 35 | 0 | 1 | 35 | 0 | 40 | 0 | 0 |  | 4834 | 2259 | 7093 | 2045 | 720 | 1767 | 2259 | 150 | 47 | 20 | 74 | 11 | 0 | 96.46
9:00 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 364 |  | 0 | 0 | 260 | 72 | 64 | 15 | 0 | 0 | 90 | 36 | 74 | 100 | 50 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 10 | 1 | 36 | 17 | 5 | 0 | 0 | 0 | 150 | 250 | 120 | 8 | 93 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 20 | 78 | 99 | 54 | 22 | 0 | 30 | 0 | 48 | 50 | 110 | 0 | 0 | 68 | 0 | 180 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 245 | 162 | 0 | 200 | 0 | 102 | 10 | 100 | 0 | 40 | 0 | 16 | 17 | 5 | 2 | 290 | 0 | 0 | 0 | 72 | 100 | 50 | 84 | 9 | 126 | 0 | 100 |  | 720 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 13 | 0 | 33 | 0 | 18 | 64 | 0 | 0 | 0 | 45 | 0 | 0 | 25 | 42 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 62 | 0 | 0 | 308 | 90 | 0 | 0 | 50 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 |  | 5372 | 2271 | 7643 | 1910 | 720 | 1543 | 2947 | 150 | 47 | 226 | 78 | 22 | 0 | 96.46
10:00 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 363 |  | 0 | 0 | 275 | 100 | 80 | 15 | 0 | 0 | 90 | 60 | 102 | 100 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 10 | 7 | 45 | 18 | 2 | 0 | 0 | 0 | 150 | 250 | 120 | 8 | 100 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 20 | 82 | 99 | 53 | 22 | 1 | 30 | 0 | 14 | 20 | 110 | 0 | 0 | 68 | 0 | 162 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 253 | 54 | 0 | 200 | 0 | 149 | 14 | 100 | 0 | 41 | 0 | 16 | 17 | 34 | 3 | 287 | 0 | 0 | 0 | 109 | 100 | 50 | 91 | 5 | 108 | 0 | 100 |  | 719 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 33 | 0 | 17 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 42 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 45 | 0 | 0 | 311 | 90 | 0 | 0 | 50 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 |  | 5442 | 2254 | 7696 | 1902 | 719 | 1463 | 3078 | 150 | 47 | 231 | 82 | 24 | 0 | 96.45
11:00 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 363 |  | 0 | 0 | 270 | 100 | 100 | 15 | 0 | 0 | 90 | 60 | 102 | 100 | 60 | 0 | 0 | 0 | 45 | 35 | 55 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 10 | 13 | 45 | 18 | 5 | 0 | 0 | 0 | 150 | 250 | 128 | 8 | 100 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 16 | 8 | 33 | 20 | 86 | 99 | 49 | 22 | 2 | 30 | 0 | 11 | 20 | 110 | 0 | 0 | 69 | 0 | 163 | 18 | 0 | 9 | 300 | 8 | 0 | 0 | 253 | 30 | 0 | 200 | 0 | 149 | 16 | 100 | 0 | 40 | 0 | 16 | 17 | 34 | 4 | 305 | 0 | 0 | 0 | 107 | 92 | 50 | 91 | 0 | 108 | 0 | 100 |  | 719 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 40 | 0 | 18 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 331 | 90 | 0 | 0 | 50 | 0 | 0 | 2 | 35 | 0 | 0 | 0 | 0 |  | 5453 | 2318 | 7771 | 1921 | 719 | 1498 | 3079 | 150 | 47 | 247 | 86 | 24 | 0 | 96.45
12:00 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 364 |  | 0 | 0 | 280 | 100 | 100 | 15 | 0 | 0 | 90 | 70 | 102 | 100 | 62 | 0 | 0 | 0 | 54 | 35 | 55 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 10 | 24 | 46 | 18 | 5 | 0 | 0 | 0 | 150 | 250 | 161 | 8 | 100 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 18 | 8 | 33 | 20 | 88 | 104 | 49 | 22 | 2 | 30 | 0 | 13 | 20 | 110 | 0 | 0 | 69 | 0 | 163 | 18 | 0 | 9 | 290 | 8 | 0 | 0 | 263 | 31 | 0 | 200 | 0 | 149 | 18 | 100 | 0 | 21 | 0 | 16 | 48 | 34 | 4 | 270 | 0 | 0 | 0 | 103 | 100 | 50 | 91 | 0 | 108 | 0 | 100 |  | 720 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 13 | 0 | 40 | 0 | 18 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 52 | 13 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 419 | 72 | 0 | 0 | 50 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 0 |  | 5540 | 2353 | 7893 | 1937 | 720 | 1583 | 3082 | 150 | 46 | 260 | 88 | 27 | 0 | 96.45
13:00 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 364 |  | 0 | 0 | 260 | 100 | 100 | 15 | 0 | 0 | 150 | 100 | 16 | 100 | 65 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 31 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 30 | 26 | 46 | 18 | 14 | 0 | 0 | 0 | 150 | 250 | 181 | 8 | 100 | 0 | 0 | 0 | 35 | 0 | 16 | 0 | 21 | 8 | 33 | 20 | 90 | 102 | 64 | 22 | 2 | 30 | 0 | 16 | 20 | 140 | 0 | 0 | 68 | 0 | 163 | 18 | 0 | 9 | 320 | 8 | 5 | 0 | 268 | 174 | 0 | 200 | 0 | 149 | 17 | 100 | 0 | 20 | 0 | 16 | 71 | 34 | 4 | 271 | 0 | 0 | 0 | 100 | 90 | 56 | 91 | 0 | 90 | 0 | 100 |  | 719 | 0 | 435 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 40 | 0 | 18 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 52 | 22 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 330 | 95 | 0 | 0 | 50 | 0 | 0 | 4 | 35 | 0 | 0 | 0 | 0 |  | 5784 | 2370 | 8154 | 2121 | 719 | 1556 | 3193 | 150 | 46 | 252 | 90 | 27 | 8154 | 96.44
14:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 305 |  | 0 | 0 | 265 | 100 | 100 | 55 | 0 | 0 | 155 | 100 | 16 | 100 | 74 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 10 | 30 | 46 | 19 | 6 | 0 | 0 | 0 | 150 | 250 | 187 | 8 | 100 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 21 | 8 | 33 | 20 | 94 | 102 | 65 | 20 | 2 | 30 | 0 | 14 | 20 | 110 | 0 | 0 | 70 | 0 | 163 | 18 | 0 | 9 | 280 | 8 | 11 | 0 | 270 | 53 | 0 | 200 | 0 | 149 | 16 | 100 | 0 | 20 | 0 | 16 | 90 | 17 | 4 | 215 | 0 | 0 | 0 | 85 | 100 | 46 | 91 | 0 | 90 | 0 | 100 |  | 720 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 8 | 0 | 18 | 48 | 0 | 0 | 0 | 28 | 0 | 0 | 25 | 50 | 0 | 25 | 25 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 305 | 95 | 0 | 0 | 50 | 0 | 0 | 4 | 35 | 0 | 0 | 0 | 0 |  | 5581 | 2217 | 7798 | 2144 | 720 | 1406 | 2979 | 150 | 46 | 233 | 94 | 26 | 0 | 96.44
15:00 | 0 | 0 | 0 | 170 | 0 | 106 | 0 | 0 | 304 |  | 0 | 0 | 265 | 100 | 100 | 55 | 0 | 0 | 155 | 100 | 16 | 100 | 75 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 10 | 31 | 46 | 20 | 4 | 0 | 0 | 0 | 165 | 250 | 200 | 8 | 92 | 3 | 0 | 0 | 51 | 0 | 16 | 0 | 21 | 8 | 33 | 20 | 86 | 101 | 57 | 20 | 1 | 30 | 0 | 14 | 20 | 110 | 0 | 0 | 70 | 0 | 163 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 147 | 11 | 100 | 0 | 20 | 0 | 16 | 90 | 17 | 2 | 215 | 0 | 0 | 0 | 85 | 100 | 55 | 91 | 0 | 72 | 0 | 100 |  | 720 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 8 | 0 | 15 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 25 | 0 | 25 | 25 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 285 | 95 | 0 | 0 | 32 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 0 |  | 5531 | 2147 | 7678 | 2179 | 720 | 1394 | 2857 | 150 | 45 | 230 | 86 | 17 | 0 | 96.44
16:00 | 0 | 0 | 0 | 170 | 0 | 107 | 0 | 0 | 304 |  | 0 | 0 | 255 | 100 | 100 | 55 | 0 | 0 | 145 | 50 | 16 | 64 | 75 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 23 | 17 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 36 | 0 | 15 | 50 | 20 | 7 | 0 | 0 | 0 | 175 | 250 | 190 | 8 | 99 | 3 | 0 | 0 | 51 | 0 | 16 | 0 | 18 | 8 | 33 | 20 | 86 | 101 | 52 | 20 | 1 | 30 | 0 | 14 | 20 | 110 | 0 | 0 | 70 | 0 | 162 | 18 | 0 | 9 | 285 | 8 | 11 | 0 | 267 | 0 | 0 | 200 | 0 | 147 | 7 | 100 | 0 | 20 | 0 | 0 | 50 | 17 | 1 | 215 | 0 | 0 | 0 | 85 | 100 | 83 | 91 | 0 | 72 | 0 | 100 |  | 719 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 8 | 0 | 8 | 24 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 292 | 95 | 0 | 0 | 15 | 65 | 0 | 1 | 70 | 0 | 0 | 0 | 0 |  | 5346 | 2110 | 7456 | 2165 | 719 | 1349 | 2752 | 150 | 47 | 178 | 86 | 10 | 0 | 96.43
17:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 304 |  | 0 | 0 | 270 | 80 | 100 | 30 | 0 | 0 | 120 | 24 | 16 | 64 | 74 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 74 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 49 | 8 | 11 | 50 | 20 | 10 | 0 | 0 | 0 | 170 | 250 | 160 | 8 | 102 | 3 | 0 | 0 | 51 | 0 | 16 | 0 | 18 | 8 | 33 | 21 | 84 | 100 | 41 | 20 | 0 | 30 | 0 | 14 | 20 | 110 | 0 | 0 | 71 | 0 | 164 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 267 | 0 | 0 | 130 | 0 | 133 | 1 | 60 | 0 | 20 | 0 | 0 | 50 | 17 | 0 | 180 | 3 | 0 | 0 | 85 | 60 | 100 | 91 | 0 | 72 | 0 | 100 |  | 720 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 8 | 0 | 8 | 21 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 366 | 95 | 0 | 0 | 15 | 102 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 5053 | 2198 | 7251 | 2084 | 720 | 1476 | 2474 | 150 | 74 | 188 | 84 | 1 | 0 | 96.43
18:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 337 |  | 0 | 0 | 265 | 80 | 101 | 35 | 0 | 0 | 145 | 50 | 16 | 115 | 74 | 0 | 0 | 10 | 54 | 35 | 55 | 22 | 25 | 17 | 17 | 33 | 8 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 0 | 102 | 10 | 11 | 50 | 20 | 23 | 0 | 0 | 0 | 175 | 250 | 209 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 32 | 5 | 18 | 8 | 33 | 21 | 102 | 104 | 35 | 20 | 0 | 30 | 0 | 51 | 40 | 110 | 0 | 0 | 70 | 0 | 162 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 264 | 70 | 0 | 148 | 0 | 115 | 0 | 100 | 10 | 18 | 0 | 17 | 82 | 17 | 0 | 280 | 52 | 0 | 0 | 85 | 100 | 122 | 91 | 0 | 108 | 0 | 100 |  | 860 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 21 | 67 | 0 | 0 | 0 | 50 | 0 | 104 | 25 | 25 | 0 | 52 | 22 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1 | 0 | 0 | 370 | 95 | 0 | 0 | 50 | 103 | 0 | 0 | 70 | 0 | 0 | 0 | 18 |  | 5866 | 2765 | 8631 | 2262 | 860 | 1597 | 3142 | 150 | 68 | 450 | 102 | 0 | 0 | 96.43
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 366 |  | 0 | 0 | 240 | 100 | 101 | 50 | 0 | 0 | 180 | 100 | 16 | 115 | 75 | 0 | 0 | 12 | 54 | 35 | 55 | 22 | 25 | 31 | 17 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 10 | 11 | 50 | 20 | 25 | 0 | 0 | 0 | 175 | 250 | 216 | 8 | 92 | 6 | 0 | 0 | 51 | 0 | 33 | 16 | 18 | 8 | 33 | 21 | 102 | 106 | 52 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 18 | 0 | 9 | 295 | 8 | 11 | 0 | 250 | 158 | 0 | 200 | 0 | 114 | 0 | 100 | 17 | 16 | 0 | 16 | 90 | 34 | 0 | 286 | 54 | 0 | 0 | 85 | 100 | 130 | 91 | 0 | 126 | 0 | 100 |  | 907 | 0 | 405 | 0 | 115 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 22 | 96 | 0 | 0 | 0 | 50 | 0 | 104 | 25 | 50 | 0 | 52 | 22 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 60 | 5 | 0 | 372 | 95 | 0 | 0 | 67 | 103 | 0 | 0 | 94 | 0 | 0 | 0 | 35 |  | 6274 | 3004 | 9278 | 2314 | 907 | 1682 | 3603 | 150 | 69 | 451 | 102 | 0 | 0 | 96.42
19:30 | 0 | 0 | 0 | 170 | 0 | 107 | 0 | 0 | 366 |  | 0 | 0 | 285 | 100 | 101 | 50 | 0 | 0 | 190 | 100 | 16 | 100 | 74 | 0 | 0 | 0 | 54 | 37 | 55 | 22 | 25 | 32 | 17 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 175 | 250 | 213 | 8 | 101 | 6 | 0 | 0 | 51 | 0 | 33 | 0 | 18 | 8 | 33 | 21 | 100 | 104 | 82 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 250 | 51 | 0 | 200 | 0 | 131 | 0 | 100 | 17 | 20 | 0 | 0 | 90 | 17 | 0 | 286 | 54 | 0 | 0 | 85 | 100 | 138 | 91 | 0 | 126 | 0 | 100 |  | 909 | 0 | 395 | 0 | 115 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 23 | 96 | 0 | 0 | 0 | 50 | 0 | 104 | 25 | 50 | 0 | 52 | 23 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 12 | 0 | 428 | 95 | 0 | 0 | 67 | 102 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 6103 | 3041 | 9144 | 2345 | 909 | 1745 | 3423 | 150 | 69 | 403 | 100 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 366 |  | 0 | 0 | 240 | 100 | 101 | 55 | 0 | 0 | 186 | 100 | 16 | 100 | 74 | 0 | 0 | 0 | 54 | 37 | 55 | 22 | 25 | 32 | 17 | 33 | 8 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 0 | 0 | 0 | 20 | 30 | 0 | 0 | 0 | 175 | 250 | 207 | 8 | 92 | 6 | 0 | 0 | 51 | 0 | 33 | 0 | 19 | 8 | 33 | 21 | 102 | 106 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 140 | 0 | 0 | 73 | 0 | 163 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 254 | 53 | 0 | 200 | 0 | 131 | 0 | 100 | 17 | 20 | 0 | 0 | 90 | 17 | 0 | 303 | 54 | 0 | 0 | 85 | 100 | 143 | 91 | 0 | 126 | 0 | 100 |  | 909 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 23 | 96 | 0 | 0 | 0 | 50 | 0 | 104 | 25 | 50 | 0 | 52 | 23 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 9 | 0 | 391 | 95 | 0 | 0 | 67 | 103 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 6069 | 2997 | 9066 | 2327 | 909 | 1698 | 3407 | 150 | 70 | 403 | 102 | 0 | 0 | 96.42
21:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 367 |  | 0 | 0 | 240 | 100 | 101 | 30 | 0 | 0 | 185 | 60 | 102 | 100 | 74 | 0 | 0 | 0 | 54 | 37 | 55 | 22 | 25 | 28 | 17 | 33 | 8 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 0 | 0 | 20 | 30 | 0 | 0 | 0 | 175 | 250 | 187 | 8 | 96 | 6 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 96 | 106 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 140 | 0 | 0 | 73 | 0 | 163 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 267 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 17 | 20 | 0 | 0 | 90 | 17 | 0 | 306 | 54 | 0 | 0 | 85 | 100 | 230 | 91 | 0 | 126 | 0 | 100 |  | 908 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 23 | 96 | 0 | 0 | 0 | 36 | 0 | 104 | 25 | 16 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 9 | 0 | 392 | 95 | 0 | 0 | 50 | 105 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 6048 | 2861 | 8909 | 2374 | 908 | 1700 | 3312 | 150 | 70 | 299 | 96 | 0 | 0 | 96.42
22:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 327 |  | 0 | 0 | 240 | 70 | 100 | 15 | 0 | 0 | 185 | 60 | 58 | 84 | 70 | 0 | 0 | 0 | 54 | 37 | 35 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 0 | 170 | 250 | 198 | 8 | 99 | 6 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 92 | 106 | 82 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 19 | 0 | 9 | 285 | 8 | 11 | 0 | 269 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 17 | 20 | 0 | 0 | 72 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 200 | 91 | 0 | 126 | 0 | 100 |  | 908 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 8 | 7 | 8 | 0 | 23 | 96 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 14 | 0 | 321 | 95 | 0 | 0 | 15 | 105 | 0 | 0 | 95 | 0 | 0 | 0 | 17 |  | 5784 | 2557 | 8341 | 2350 | 908 | 1580 | 2970 | 150 | 71 | 220 | 92 | 0 | 0 | 96.41
23:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 326 |  | 0 | 0 | 305 | 60 | 100 | 15 | 0 | 0 | 190 | 45 | 24 | 48 | 74 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 170 | 250 | 221 | 8 | 102 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 105 | 48 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 19 | 0 | 9 | 285 | 8 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 82 | 0 | 50 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 200 | 91 | 0 | 126 | 0 | 100 |  | 860 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 28 | 0 | 226 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 |  | 5506 | 2196 | 7702 | 2391 | 860 | 1488 | 2488 | 150 | 70 | 167 | 88 | 0 | 0 | 96.41
24:00 | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 367 |  | 0 | 0 | 270 | 24 | 100 | 15 | 0 | 0 | 190 | 24 | 24 | 16 | 71 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 170 | 250 | 224 | 8 | 98 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 80 | 105 | 8 | 22 | 0 | 30 | 0 | 50 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 19 | 0 | 9 | 310 | 8 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 50 | 0 | 50 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 36 | 100 | 200 | 91 | 0 | 126 | 0 | 90 |  | 625 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 19 | 0 | 130 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 5201 | 1832 | 7033 | 2372 | 625 | 1456 | 2151 | 150 | 70 | 129 | 80 | 0 | 0 | 96.41
KWH | 0 | 0 | 0 | 3181500 | 0 | 2544636 | 0 | 0 | 8238000 |  | 0 | 0 | 6367738 | 1670400 | 1973304 | 571318 | 0 | 0 | 3052000 | 1166400 | 1063152 | 1463520 | 1545722 | 0 | 0 | 34176 | 821880 | 474803 | 1228324 | 458064 | 600000 | 688320 | 421500 | 837500 | 36480 | 0 | 1253444 | 0 | 0 | 0 | 313603 | 0 | 0 | 0 | 0 |  | 519360 | 0 | 819550 | 140520 | 192960 | 743040 | 440112 | 576480 | 0 | 0 | 0 | 4033000 | 6126000 | 4033000 | 217454 | 2332730 | 63720 | 0 | 0 | 1173343 | 0 | 221728 | 26333 | 435564 | 191880 | 780210 | 50400 | 2029440 | 2450560 | 972480 | 494892 | 10950 | 712000 | 0 | 894000 | 721008 | 3187800 | 0 | 0 | 1708800 | 0 | 4366980 | 445000 | 0 | 207720 | 7395000 | 293328 | 233000 | 0 | 5866252 | 748291 | 0 | 4012800 | 0 | 2173680 | 115830 | 2027520 | 120000 | 702545 | 0 | 207600 | 997140 | 358798 | 27600 | 6541200 | 343637 | 0 | 0 | 1632960 | 2244480 | 2009900 | 1970880 | 16670 | 2545920 | 0 | 2396000 |  | 16612363 | 0 | 9253152 | 0 | 2350080 | 0 | 0 | 0 | 275040 | 39808 | 415125 | 0 | 456400 | 1179840 | 0 | 0 | 0 | 551024 | 0 | 778608 | 364460 | 491732 | 0 | 578880 | 212604 | 494160 | 0 | 237718 | 0 | 0 | 3667500 | 0 | 0 | 0 | 0 | 0 | 0 | 1843789 | 264960 | 743100 | 0 | 8479054 | 1774080 | 0 | 0 | 688032 | 951360 | 0 | 25613 | 1204032 | 0 | 355036 | 0 | 160800 |  | 126305829 | 54448350 | 180754179 | 51361130 | 16612363 | 38492680 | 62779077 | 3667500 | 1253444 | 4361882 | 2029440 | 196663 | 0
Fuel Cost | 0 | 0 | 0 | 4676805 | 0 | 3358919.52 | 0 | 0 | 8485140 |  | 0 | 0 | 7068189.18 | 12678336 | 13596064.56 | 4833350.28 | 0 | 0 | 5279960 | 8782992 | 9695946.24 | 14401036.8 | 14251556.84 | 0 | 0 | 310659.84 | 5999724 | 3670227.19 | 12111274.64 | 343548 | 450000 | 0 | 0 | 0 | 352761.6 | 0 | 338429.88 | 0 | 0 | 0 | 2913371.87 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7949635 | 1341966 | 1678752 | 5884876.8 | 554541.12 | 1712145.6 | 0 | 0 | 0 | 2984420 | 6126000 | 3710360 | 280515.66 | 2682639.5 | 72003.6 | 0 | 0 | 2006416.53 | 0 | 2239452.8 | 251480.15 | 553166.28 | 143910 | 1365367.5 | 37800 | 15220800 | 2597593.6 | 8830118.4 | 628512.84 | 174543 | 1167680 | 0 | 1591320 | 1124772.48 | 3634092 | 0 | 0 | 3263808 | 0 | 7554875.4 | 974550 | 0 | 423748.8 | 7468950 | 219996 | 177080 | 0 | 44348865.12 | 12705981.18 | 0 | 20866560 | 0 | 21389011.2 | 1354052.7 | 16524288 | 1302000 | 4952942.25 | 0 | 1893312 | 9422973 | 3125130.58 | 0 | 49451472 | 2993078.27 | 0 | 0 | 13994467.2 | 14948236.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95687210.88 | 0 | 9715809.6 | 0 | 18471628.8 | 0 | 0 | 0 | 2885169.6 | 417187.84 | 4325602.5 | 0 | 707420 | 11515238.4 | 0 | 0 | 0 | 5422076.16 | 0 | 6890680.8 | 2806342 | 6648216.64 | 0 | 5609347.2 | 2062258.8 | 948787.2 | 0 | 179952.526 | 0 | 0 | 19877850 | 0 | 0 | 0 | 0 | 0 | 0 | 2765683.5 | 4506969.6 | 869427 | 0 | 8394263.46 | 18521395.2 | 0 | 0 | 6495022.08 | 7382553.6 | 0 | 283023.65 | 8897796.48 | 0 | 0 | 0 | 0 |  | 449498552.8 | 252286913.516 | 701785466.316 | 53065997.966 | 95687210.88 | 46165982.75 | 427350077.69 | 19877850 | 338429.88 | 42267497.8 | 15220800 | 1811619.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 0 | 364 |  | 0 | 0 | 280 | 100 | 100 | 15 | 0 | 0 | 90 | 70 | 102 | 100 | 62 | 0 | 0 | 0 | 54 | 35 | 55 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 10 | 24 | 46 | 18 | 5 | 0 | 0 | 0 | 150 | 250 | 161 | 8 | 100 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 18 | 8 | 33 | 20 | 88 | 104 | 49 | 22 | 2 | 30 | 0 | 13 | 20 | 110 | 0 | 0 | 69 | 0 | 163 | 18 | 0 | 9 | 290 | 8 | 0 | 0 | 263 | 31 | 0 | 200 | 0 | 149 | 18 | 100 | 0 | 21 | 0 | 16 | 48 | 34 | 4 | 270 | 0 | 0 | 0 | 103 | 100 | 50 | 91 | 0 | 108 | 0 | 100 |  | 720 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 13 | 0 | 40 | 0 | 18 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 52 | 13 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 419 | 72 | 0 | 0 | 50 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 0 |  | 7893 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 366 | 0 | 0 | 0 | 240 | 100 | 101 | 50 | 0 | 0 | 180 | 100 | 16 | 115 | 75 | 0 | 0 | 12 | 54 | 35 | 55 | 22 | 25 | 31 | 17 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 102 | 10 | 11 | 50 | 20 | 25 | 0 | 0 | 0 | 175 | 250 | 216 | 8 | 92 | 6 | 0 | 0 | 51 | 0 | 33 | 16 | 18 | 8 | 33 | 21 | 102 | 106 | 52 | 22 | 0 | 30 | 0 | 51 | 50 | 140 | 0 | 0 | 73 | 0 | 162 | 18 | 0 | 9 | 295 | 8 | 11 | 0 | 250 | 158 | 0 | 200 | 0 | 114 | 0 | 100 | 17 | 16 | 0 | 16 | 90 | 34 | 0 | 286 | 54 | 0 | 0 | 85 | 100 | 130 | 91 | 0 | 126 | 0 | 100 |  | 907 | 0 | 405 | 0 | 115 | 0 | 0 | 0 | 18 | 7 | 40 | 0 | 22 | 96 | 0 | 0 | 0 | 50 | 0 | 104 | 25 | 50 | 0 | 52 | 22 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 60 | 5 | 0 | 372 | 95 | 0 | 0 | 67 | 103 | 0 | 0 | 94 | 0 | 0 | 0 | 35 |  | 9278 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 50 | 22 | 25 | 135 | 0 | 0 | 0 | 350 | 180 | 8 | 100 | 5 | 0 | 0 | 51 | 0 | 50 | 52 | 20 | 11 | 33 | 22 | 147 | 110 | 92 | 22 | 0 | 30 | 0 | 50 | 50 | 163 | 0 | 0 | 73 | 0 | 100 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 20 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 0 | 100 |  | 885 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 90 | 200 | 0 | 100 | 113 | 0 | 0 | 113 | 0 | 0 |  | 0
Forecast for Day | 0 | 0 | 0 | 170 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 50 | 22 | 15 | 135 | 0 | 0 | 0 | 350 | 180 | 8 | 100 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 20 | 11 | 33 | 20 | 135 | 110 | 92 | 22 | 1.6 | 30 | 0 | 50 | 50 | 163 | 0 | 0 | 73 | 0 | 0 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 20 | 0 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 0 | 100 |  | 741 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 50 | 220 | 0 | 0 | 90 | 100 | 0 | 100 | 113 | 0 | 8 | 113 | 0 | 0 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 0 | 110 | 0 | 0 | 366 | 0 | 0 | 0 | 335 | 12 | 48 | 16 | 0 | 0 | 185 | 6 | 75 | 64 | 85 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 25 | 32 | 17 |  | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 105 | 330 | 223 | 8 | 100 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 0 | 21 | 72 | 106 | 17 | 22 | 0 | 30 | 0 | 51 | 50 | 163 | 0 | 0 | 69 | 0 | 162 | 19 | 0 | 9 | 325 | 8 | 11 | 0 | 250 | 0 | 0 | 195 | 0 | 59 | 5 | 90 | 0 | 20 | 0 | 8 | 8 | 0 | 1 | 305 | 0 | 0 | 0 | 8 | 100 | 200 | 85 | 2 | 126 | 0 | 100 | 0 | 728 | 0 | 445 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 89 | 0 | 136 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5675 | 5:00
| Highest Generation |  | 9278 | 19:00
| Day Peak Generation |  | 7893 | 12:00
| Evening Peak Generation |  | 9278 | 19:00
| HVDC Max Flow |  | 909 | 19:30
| HVDC EvPeak Flow |  | 907 | 19:00
| Load factor L.F |  | 81.18%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-26
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7893 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5815 | MW
Evening Peak Generation : |  | 9278 | MW Hour : | 19:00 | Available Max Generation : |  | 12269 | MW
E.P. Demand (at gen end) : |  | 9278 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9278 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2769 | MW
Total Gen. (MKWH) : |  | 180.7542 | System Load Factor : | 81.18% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -330 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-26
Actual : | 96.39 | Ft.(MSL) , | Rule curve : | 98.2 | Ft.( MSL )
Gas Consumed : | Total = | 799.27 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 99231980.716
: |  | Coal : | 19877850 | Oil : | 469617575.49 | Total : | 588727406.206
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3368.8572 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1141.3995 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1021.908 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 923.1145 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 834.3517 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 673.2817 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 381.8687 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 173.4949 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 519.2424 |  |  | 0 | 0%
Total | 0 |  | 9037.5184 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-4,5
|  |  |  | 2) Baghabari-71 &100 MW | 11) Haripur 412 MW
3) Ghorasal Unit-1,2,3,4
4) Shahjibazar 330 MW
5) Kaptai-1,2,3,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,3 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Siddhirganj GT-2 was synchronized at 12:42.
b) Baroirhat 132/33 kV T-2 transformer was switched on at 12:40.
c) Mirpur 132/33 kV T-3 transformer was under shut down from 09:05 to 17:46 for A/M.
d) Sreemangal-Shahjibazar 132 kV Ckt-1 was under shutdown from 10:00 to 16:40 for A/M.
e) Sylhet-Fenchuganj PP 132 kV Ckt was under shutdown from 09:15 to 15:53 for A/M.
f) Comilla(N)-Ashuganj 230 kV Ckt-1 was under shutdown from 09:43 to 17:16 for A/W.
g) Ramganj-Desh Energy PP 132 kV Ckt-1 was under shutdown from 09:32 to 18:35 for D/W.
h) Sherpur 132/33 kV T-2 transformer was under shut down from 10:42 to 13:25 for C/M.
i) Tongi-New Tongi 132 kV Ckt-1 was under shut down from 10:57 to 11:37 for C/M.
j) Mymensingh 132 kV Bus-A was under shut down from 10:52 to 16:58 for C/M.
k) Mymensingh-Sutiakhali Solar132 kV Ckt was under shut down from 10:07 to 18:18 for C/M.
l) Mymensingh-Valuka 132 kV Ckt was under shut down from 10:32 to 17:35 for C/M.
m) Rampura 230/132 kV T-1 transformer was under shut down from 08:15 to 16:17 for C/M.
n) Kishoreganj 132/33 kV T-3 transformer was under shut down from 10:51 to 16:18 for Painting.
o) Maniknagar 132/33 kV T-1 transformer was under shut down from 09:42 to 16:20 for A/M.
p) Rajshahi(N)-Bheramara HVDC 230 kV Ckt-2 was under shut down from 12:04 to 16:37 for D/W.
q) Gopalganj 400/132 kV T-2 transformer was under shut down from 09:13 to 16:22 for A/M.
r) Jashore-Benapole 132 kV Ckt-1 was under shut down from 08:50 to 12:47 for C/M.
s) Kurigram 132/33 kV T-1 transformer was under shut down from 11:48 to 14:30 for D/W.
t) Ghorashal-Ishurdi 230 kV Ckt-1 was under shut down from 09:47 to 18:40 for A/M.
u) Kabirpur 132/33 kV T-2 transformer was under shut down from 13:38 to 14:50 for C/M.
v) Khulna(C) 132/33 kV T-3 transformer tripped at 13:41 showing Int E/F relay and was switched on at 13:53. |  |  |  |  | About 20 MW power interruption occurred under Barisal S/S area
from 13:41 to 13:53.
w) Kurigram 132/33 kV T-2 transformer was under shut down from 15:06 to 15:56 for telecom work.
x) Kabirpur 132/33 kV T-3 transformer was under shut down from 16:20 to 17:50 for 33 kV PT oil leakage. |  |  |  |  | About 90 MW power interruption occurred under Barisal S/S area
y) Kabirpur 132/33 kV T-2 transformer was under shut down from 16:18 to 17:52 for 33 kV PT oil leakage. |  |  |  |  | from 16:20 to17:52.
z) Rajshahi-Bheramara HVDC 230 kV Ckt-1 was under shut down from 16:45 to 21:54 for protection work.
aa) Sirajganj unit-3 GT was synchronize at 18:12 and STG was synchronized at 21:21.
ab) Sirajganj unit-4 STG was shut down at 00:36(26/01/2021) and GT was shut down at 00:42 for maint. work.
ac) Sirajganj unit-2 GT was synchronize at 01:16(26/01/2021) and STG was synchronized at 02:20.
ad) Shahjibazar 132/3 kV T-6 transformer was shut down at 07:50(26/01/2021).
ae) Comilla(N) 132/33 kV T-3 transformer tripped at 00:14(26/01/2021) showing O/C,E/F relay due to 33 kV
Balutopa feeder fault and was switched on at 00:38.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 3181500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 2544636
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 366 | 8238000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1670400
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6367738 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 101 | 1973304
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 50 | 571318
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 75 | 1545722 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 458064
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3052000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1166400
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 1063152 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 12 | 34176 | High Voltage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 821880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1463520 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 474803 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1228324
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1288320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 421500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 837500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 36480 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 250 | 5866252 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 158 | 748291 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 114 | 2173680 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 997140 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 1970880 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2545920 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2744 | 52740900
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 313603
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115830
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 743040
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 69 | 1253444 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 358798 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 819550
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 140520 | High Voltage.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2027520
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 440112
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 576480
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 11 | 192960 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27600
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 286 | 6541200
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 343637
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2244480
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 886 | 16138774
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4033000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 175 | 4033000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6126000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 6 | 63720 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1173343
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 16 | 702545 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 221728
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2332730 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 120000 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 435564
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 191880 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2029440
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 780210
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 26333 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 50400
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 85 | 1632960 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1147 | 24170307
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2450560 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 494892
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 52 | 972480 | High Voltage.
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10950
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4012800 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 16 | 207600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 16670
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 519360
| Mymensingh Area Total |  |  |  | 709 | 420 | 8685312
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 712000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3187800 | Frequency control
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 894000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 721008
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 233000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1708800 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 2396000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 4366980
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 445000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 293328 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7395000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Gas shortage & Bibiyana south test
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 207720
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 130 | 2009900 | On test
| Sylhet Area Total |  |  |  | 1988 | 1077 | 24570536
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 16612363
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2350080
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 18 | 275040 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 7 | 39808 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 405 | 9253152
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 415125
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 60 | 264960 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 1774080 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 67 | 688032 | High Voltage.
| Khulna Area Total |  |  |  | 2284 | 1714 | 31672640
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 1179840
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 456400 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 1843789
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 0 | Under maint.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 355036 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 35 | 160800 | On test.
| Barisal Area Total |  |  |  | 1676 | 241 | 3995865
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 551024
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 364460 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 491732 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 5 | 743100 | Sync at 18:12
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 8479054 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 212604
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 494160
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 237718
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 578880
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 104 | 778608
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Under maint.
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 94 | 1204032 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 796 | 14135372
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3667500
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 103 | 951360 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25613
| Rangpur Area Total |  |  |  | 605 | 253 | 4644473
| Total |  |  |  | 20748 | 9278 | 180754179
| Eastern Grid Total |  |  |  | 14000 | 6274 | 126305829
| Western Grid Total |  |  |  | 6748 | 3004 | 54448350
| National Grid Total |  |  |  | 20748 | 9278 | 180754179
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-25
| (a) ENTIRE EASTERN GRID : |  | 5793 | MW | (b) ENTIRE WESTERN GRID : |  | 3022 | MW
| i) Dhaka area |  | 3017 | MW | i) Khulna area |  | 1100 | MW
| ii) Chittagong area |  | 907 | MW | ii) Rajshahi area |  | 982 | MW
| iii) Comilla area |  | 753 | MW | iii) Barisal area |  | 238 | MW
| iv) Mymensingh area |  | 780 | MW | iv) Rangpur area |  | 702 | MW
| v) Sylhet area |  | 336 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8815 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 100 | 15:00 | Jamalpur | 89 | 18:00 | Benapol | 36 | 18:30
| Munsiganj | 86 | 21:00 | Sherpur | 100 | 22:00 | Jhenida | 84 | 18:30
| Sonargaon | 65 | 20:00 | Srimongal | 27 | 19:00 | Bottail | 96 | 18:30
| Shyampur | 170 | 10:00 | Shahjibazar | 89 | 21:00 | G.K Project | 40 | 18:30
| Bhulta | 161 | 21:00 | Fenchuganj | 28 | 20:00 | Faridpur | 134 | 19:00
| Madanganj | 42 | 1:00 | Kulawara | 27 | 18:00 | Madaripur | 63 | 20:00
| Shitalakhya | 92 | 12:00 | Sylhet | 88 | 18:30 | Sariatpur | 42 | 20:00
| Rahim steel | 25 | 13:00 | Chatak | 20 | 18:30 | Gopalganj | 60 | 19:30
| Matuail | 48 | 10:00 | Sunamganj | 30 | 20:00 | Bagerhat | 83 | 18:30
| Ghorasal | 66 | 19:00 | Biani Bazar | 37 | 18:30 | Mongla | 38 | 21:00
| Narsingdi | 123 | 21:00 | Comilla (S) | 104 | 18:30 | Satkhira | 69 | 18:30
| Haripur (SBU) | 94 | 11:00 | Comilla(N) | 83 | 19:00 | Gallamari | 20 | 19:30
| Ullon | 44 | 13:00 | Chandpur | 58 | 19:00 | Magura | 40 | 18:30
| Hasnabad | 100 | 12:00 | Feni | 78 | 20:00 | Norail | 24 | 18:30
| Magbazar | 69 | 18:00 | Chowmuhani | 122 | 20:00 | Chuadanga | 62 | 18:30
| Maniknagar | 56 | 18:00 | Ashuganj | 40 | 19:00 | Barisal(N) | 27 | 20:00
| Bangabhaban | 16 | 12:00 | Daudkandi | 85 | 20:00 | Barisal (S) | 74 | 19:00
| Narinda | 66 | 12:00 | B.Baria | 100 | 18:30 | Patuakhali | 79 | 19:30
| Dhanmondi | 93 | 13:00 | Ramganj | 72 | 20:00 | Bhandaria | 40 | 21:00
| Lalbag | 70 | 13:00 | Chaddagram | 24 | 18:30 | Borhan Uddin | 27 | 21:00
| Madartek | 43 | 21:00 | PHP | 10 | 1:00 | Ishurdi | 45 | 18:30
| Dhaka University |  |  | Madunaghat | 44 | 18:30 | Ruppur Paromanobik | 2 | 1:00
| Aftabnagar | 6 | 0.54167 | Hathazari | 66 | 0.77083 | Natore | 86 | 0.77083
| Fatullah | 39 | 23:00 | Khulshi | 158 | 14:00 | Bogra | 117 | 19:00
| Mirpur | 71 | 18:30 | Halishahar | 95 | 18:00 | Noagaon | 91 | 20:00
| Kalyanpur | 72 | 18:30 | Baraulia | 151 | 10:00 | Rajshahi | 107 | 20:00
| Gulshan | 74 | 13:00 | Sikalbaha | 23 | 18:30 | Rajshahi New | 11 | 18:00
| Uttara | 64 | 18:00 | Dohazari | 60 | 18:30 | C.Nawabganj | 64 | 18:30
| Uttara New | 22 | 18:00 | Cox'sbazar | 86 | 18:00 | Amnura | 40 | 18:30
| Kamrangirchar | 73 | 13:00 | Chandraghona | 22 | 19:00 | Pabna | 65 | 18:30
| Savar | 117 | 12:00 | Kaptai | 3.5 | 19:00 | Shahjadpur | 78 | 18:30
| Bhasantec | 98 | 13:00 | A. Khaer Stl. | 8 | 3:00 | Serajganj | 75 | 9:00
| Agargaon | 45 | 13:00 | Bakulia | 72 | 18:00 | Niyamatpur | 66 | 18:30
| Satmosjid | 54 | 0.54167 | Julda | 21 | 0.58333 | Joypurhat | 56 | 0.77083
| Tongi | 77 | 19:00 | TK chemical | 18.6 | 18:30 | Sherpur(Bogura) | 44 | 19:00
| Kabirpur | 182 | 10:00 | Modern Steel | 0 | 1:00 | Mohastangor | 38 | 18:30
| Basundhara | 88 | 18:00 | Shahmirpur | 17.5 | 18:00 | Bangura | 15 | 18:30
| Manikganj | 44 | 20:00 | Khagrachhari | 20 | 6:00 | Rangpur | 123 | 18:30
| Joydevpur | 115 | 18:30 | Matarbari | 26 | 19:00 | Lalmonirhat | 57 | 13:00
| New Tongi | 83 | 12:00 | Baroiar Hat | 25 | 18:00 | Saidpur | 105 | 18:30
| Kodda | 153 | 18:30 | Rangamati | 9 | 18:00 | Purbasadipur | 98 | 18:30
| Dhamrai | 78 | 19:00 | Abul Khair 230 | 143 | 11:00 | Thakurgaon | 68 | 18:30
| Rajendrapur | 72 | 19:00 | BSRM | 104 | 16:00 | Palashbari | 106 | 19:00
| Valuka | 100 | 18:00 | GPH Ispat | 72 | 18:00 | Barapukuria | 51 | 18:30
| Tangail | 164 | 19:00 | Goalpara | 20 | 13:00 | Panchagar | 46 | 19:30
| Mymensing | 158 | 18:30 | Central s/s | 75 | 18:30 | Joldhaka | 25 | 19:00
| Kishorganj | 94 | 18:30 | Noapara | 54 | 18:30 | Kurigram | 44 | 19:00
| Netrokona | 108 | 20:00 | Jessore | 88 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 419 | 2:00 | 411 | 11:00 | Kaliakoir | 414 | 0.625 | 400 | 0.5
| Bheramara | 411 | 3:00 | 390 | 20:00 | Bhulta | 401 | 0.083333 | 387 | 0.5
| Ashuganj(N) | 404 | 2:00 | 393 | 13:00 | Gopalganj | 405 | 0.625 | 387 | 24:00
| Payra | 0 | 3:00 | 0 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 0 | 10:00 | Hathazari | 233 | 19:00 | 221 | 11:00
| Ishurdi | 243 | 3:00 | 233 | 18:30 | Megnaghat | 243 | 6:00 | 238 | 11:00
| Ashuganj | 247 | 5:00 | 240 | 11:00 | Fenchuganj | 247 | 1:00 | 242 | 16:00
| Serajganj | 234 | 1:00 | 226 | 12:00 | Siddhirganj | 243 | 5:00 | 235 | 12:00
| Baghabari | 241 | 3:00 | 230 | 12:00 | Maniknagar | 243 | 6:00 | 237 | 17:00
| Barapukuria | 233 | 2:00 | 222 | 12:00 | Agargaon | 244 | 9:00 | 234 | 11:00
| Bogra | 235 | 1:00 | 222 | 9:00 | Barisal | 252 | 3:00 | 242 | 15:00
| Rajshahi | 240 | 1:00 | 227 | 8:00 | Bhola 225 MW | 256 | 15:00 | 244 | 16:00
| Khulna South | 244 | 2:00 | 233 | 18:30 | AKSML | 234 | 3:00 | 221 | 11:00
| Rampura | 238 | 2:00 | 231 | 12:00 | BSRM | 236 | 19:00 | 225 | 11:00
| Haripur | 241 | 1:00 | 235 | 12:00 | Bibiyana | 248 | 6:00 | 241 | 12:00
| Hasnabad | 240 | 3:00 | 235 | 18:00 | Bhulta | 243 | 6:00 | 237 | 13:00
| Shyampur | 241 | 3:00 | 220 | 11:00 | Ashuganj (S) | 245 | 4:00 | 237 | 12:00
| Aminbazar | 244 | 1:00 | 234 | 12:00 | Kaliakoir | 242 | 2:00 | 232 | 12:00
| Tongi | 237 | 4:00 | 230 | 11:00 | GPH | 236 | 16:00 | 223 | 18:30
| Comilla (N) | 247 | 2:00 | 241 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 142 | 2:00 | 137 | 12:00 | Madanhat | 142 | 0.33333 | 137 | 0.5
| Munsiganj | 142 | 13:00 | 139 | 10:00 | Hathazari | 142 | 0.79167 | 136 | 0.45833
| Sonargaon | 138 | 1:00 | 136 | 7:00 | Khulshi | 139 | 0.79167 | 133 | 0.45833
| Shyampur | 135 | 1:00 | 130 | 11:00 | Halishahar | 141 | 0.79167 | 134 | 0.33333
| Bhulta | 138 | 4:00 | 131 | 12:00 | Baraulia | 139 | 0.77083 | 133 | 0.5
| Madanganj | 140 | 6:00 | 134 | 11:00 | Sikalbaha | 143 | 0.16667 | 135 | 0.33333
| Shitalakhya | 143 | 21:00 | 136 | 17:00 | Dohazari | 140 | 0.5 | 132 | 0.95833
| Rahim steal | 141 | 1:00 | 138 | 10:00 | Cox'sbazar | 135 | 0.25 | 126 | 0.95833
| Matuail | 142 | 2:00 | 137 | 12:00 | Chandraghona | 141 | 0.20833 | 136 | 0.29167
| Ghorasal | 142 | 1:00 | 140 | 15:00 | Kaptai | 140 | 0.91667 | 135 | 0.16667
| Narsinghdi | 138 | 18:00 | 134 | 11:00 | A. Khaer Stl. | 139 | 0.041667 | 135 | 0.25
| Haripur (SBU) | 141 | 7:00 | 138 | 11:00 | Bakulia | 140 | 0.375 | 134 | 0.5
| Ullon | 137 | 6:00 | 129 | 11:00 | Julda | 140 | 0.375 | 136 | 0.45833
| Hasnabad | 140 | 3:00 | 135 | 17:00 | TK Chemical | 141 | 0.77083 | 135 | 0.29167
| Magbazar | 135 | 1:00 | 130 | 11:00 | Modern Steel | 140 | 0.625 | 136 | 0.33333
| Maniknagar | 140 | 1:00 | 135 | 11:00 | Shahmirpur | 142 | 0.625 | 135 | 0.70833
| Bangabhaban | 140 | 1:00 | 135 | 11:00 | Khagrachhari | 139 | 0.25 | 134 | 0.45833
| Narinda | 140 | 1:00 | 135 | 11:00 | Matarbari | 137 | 0.58333 | 130 | 0.75
| Dhanmondi | 137 | 6:00 | 129 | 11:00 | Baroiar Hat | 141 | 0.041667 | 138 | 0.45833
| Lalbag | 141 | 6:00 | 134 | 11:00 | Rangamati | 140 | 19:00 | 135 | 12:00
| Madartek | 137 | 6:00 | 129 | 11:00 | Goalpara S/S | 139 | 1:00 | 134 | 18:30
| Dhaka University |  |  |  |  | Khulna Central S/S | 140 | 3:00 | 133 | 0.77083
| Aftabnagar | 136 | 1:00 | 129 | 1200 | Noapara | 137 | 4:00 | 132 | 0.33333
| Fatuiiah | 136 | 5:00 | 130 | 11:00 | Jessore | 135 | 1:00 | 128 | 0.33333
| Mirpur | 141 | 6;00 | 135 | 14;00 | Benapol | 135 | 0.041667 | 128 | 0.33333
| Kalyanpur | 140 | 6:00 | 135 | 11:00 | Jhenida | 135 | 1:00 | 127 | 0.33333
| Gulshan | 135 | 6:00 | 128 | 12:00 | Bottail | 137 | 0.041667 | 131 | 0.77083
| Uttara | 141 | 6:00 | 135 | 11:00 | G.K Project | 142 | 0.16667 | 138 | 0.54167
| Uttara New | 142 | 2:00 | 136 | 11:00 | Faridpur | 137 | 0.125 | 132 | 0.91667
| Kamrangirchar | 138 | 6:00 | 132 | 12:00 | Madaripur | 139 | 0.375 | 134 | 0.625
| Savar | 141 | 1:00 | 135 | 11:00 | Shariyatpur S/S | 140 | 15:00 | 134 | 0.95833
| Bhasantec | 140 | 6:00 | 133 | 11:00 | Gopalganj | 145 | 0.625 | 137 | 0.33333
| Agargaon | 140 | 6:00 | 135 | 12:00 | Bagerhat | 137 | 2:00 | 131 | 18:.00
| Satmosjid | 139 | 6:00 | 134 | 12:00 | Mongla | 136 | 1:00 | 132 | 0.8125
| Tongi | 143 | 21:00 | 139 | 12:00 | Satkhira | 139 | 3:00 | 131 | 18:30
| Kabirpur | 138 | 8:00 | 130 | 12:00 | Gallamari | 139 | 0.125 | 133 | 0.77083
| Basundhara | 141 | 21:00 | 137 | 12:00 | Magura | 135 | 1:00 | 125 | 0.77083
| Manikganj | 148 | 6:00 | 141 | 18:00 | Narail | 134 | 0.041667 | 125 | 0.77083
| Joydevpur | 140 | 7:00 | 135 | 17:00 | Chuadanga | 134 | 2:00 | 121 | 0.77083
| New Tongi | 142 | 22:00 | 136 | 11:00 | Barisal(N) | 142 | 21:00 | 138 | 15:00
| Kodda | 141 | 21:00 | 134 | 11:00 | Barisal (S) | 142 | 0.625 | 137 | 0.70833
| Dhamrai | 138 | 1:00 | 130 | 12:00 | Patuakhali(S) | 140 | 0.79167 | 137 | 0.083333
| Rajendrapur | 142 | 6:00 | 136 | 13:00 | Bhandaria | 140 | 0.625 | 134 | 0.77083
| Valuka | 131 | 1:00 | 118 | 17:00 | Ishurdi | 140 | 3:00 | 135 | 8:00
| Tangail | 137 | 1:00 | 128 | 12:00 | Ruppur Paromanobik | 139 | 1:00 | 136 | 12:00
| Mymensing | 132 | 1:00 | 126 | 13:00 | Natore | 139 | 3:00 | 133 | 8:00
| Kishorganj | 134 | 4:00 | 128 | 11:00 | Bogra | 139 | 3:00 | 128 | 8:00
| Netrokona | 133 | 6:00 | 123 | 12:00 | Noagaon | 132 | 4:00 | 121 | 9:00
| Jamalpur | 140 | 9:00 | 131 | 17:00 | Rajshahi | 138 | 1:00 | 132 | 12:00
| Sherpur | 139 | 19:00 | 130 | 5:00 | Rajshahi New | 137 | 1:00 | 129 | 8:00
| Srimongal | 139 | 23:00 | 137 | 4:00 | C.Nawabganj | 137 | 1:00 | 130 | 13:00
| Shahjibazar | 139 | 5:00 | 132 | 18:30 | Amnura | 138 | 19:00 | 131 | 7:00
| Fenchuganj | 142 | 6:00 | 138 | 8:00 | Pabna | 140 | 1:00 | 134 | 11:00
| Khulawara | 141 | 6:00 | 138 | 16:00 | Shahjadpur | 144 | 4:00 | 138 | 9:00
| Sylhet | 138 | 5:00 | 136 | 11:00 | Serajganj | 137 | 1:00 | 130 | 9:00
| Chatak | 138 | 6:00 | 135 | 20:00 | Niyamatpur | 133 | 3:00 | 119 | 13:00
| Sunamganj | 137 | 3:00 | 135 | 8:00 | Joypurhat | 133 | 2:00 | 118 | 10:00
| Biani Bazar | 139 | 3:00 | 135 | 18:30 | Sherpur(Bogura) | 138 | 4:00 | 127 | 12:00
| Comilla(s) | 131 | 6:00 | 126 | 18:00 | Mohastangor | 137 | 3:00 | 125 | 12:00
| Comilla(n) | 146 | 7:00 | 143 | 10:00 | Bangura | 141 | 1:00 | 136 | 9:00
| Chandpur | 145 | 12:00 | 143 | 20:00 | Rangpur | 129 | 7:00 | 116 | 9:00
| Feni | 142 | 9:00 | 138 | 12:00 | Lalmonirhat | 131 | 3:00 | 113 | 13:00
| Chowmuhani | 139 | 15:00 | 132 | 12:00 | Saidpur | 130 | 16:00 | 116 | 18:30
| Ashuganj | 142 | 5:00 | 137 | 12:00 | Purbasadipur | 130 | 5:00 | 114 | 11:00
| Daudkandi | 142 | 14:00 | 139 | 17:00 | Thakurgaon | 129 | 2:00 | 113 | 12:00
| B.Baria | 136 | 7:00 | 131 | 12:00 | Palashbari | 134 | 5:00 | 118 | 12:00
| Ramganj | 139 | 23:00 | 136 | 12:00 | Barapukuria | 133 | 2:00 | 122 | 12:00
| Chaddagram | 142 | 7:00 | 139 | 13:00 | Panchagar | 130 | 4:00 | 111 | 12:00

## L-Curve
Date | 2021-01-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 330 | 5201 | 1832 | 7033 |  |  |  | QF-LDC-11
0:30 | 259.5 | 4877 | 1823.5 | 6700.5 | Date: | 2021-01-25
1:00 | 189 | 4553 | 1815 | 6368
1:30 | 196.5 | 4531 | 1779.5 | 6310.5
2:00 | 204 | 4509 | 1744 | 6253
2:30 | 164 | 4382.5 | 1714.5 | 6097 | [5 empty] | Gen. at Eve. Peak | 9278 | 9500 MW (19:30 )
3:00 | 124 | 4256 | 1685 | 5941 | [6 empty] | 19:00
3:30 | 103.5 | 4200.5 | 1651.5 | 5852 | [5 empty] | Gen. at Day Peak | 7893 | 7952.5 MW (12:00 )
4:00 | 83 | 4145 | 1618 | 5763 | [6 empty] | 12:00
4:30 | 80 | 4091.5 | 1627.5 | 5719 | [5 empty] | Highest Generation | 9278
5:00 | 77 | 4038 | 1637 | 5675 | [6 empty] | 19:00
5:30 | 83.5 | 4083.5 | 1673 | 5756.5
6:00 | 90 | 4129 | 1709 | 5838
6:30 | 97.5 | 4261.5 | 1845 | 6106.5
7:00 | 105 | 4394 | 1981 | 6375
7:30 | 124.5 | 4614 | 2120 | 6734
8:00 | 144 | 4834 | 2259 | 7093
8:30 | 194.5 | 5103 | 2265 | 7368
9:00 | 245 | 5372 | 2271 | 7643
9:30 | 187.5 | 5407 | 2262.5 | 7669.5
10:00 | 130 | 5442 | 2254 | 7696
10:30 | 125 | 5447.5 | 2286 | 7733.5
11:00 | 120 | 5453 | 2318 | 7771
11:30 | 100 | 5496.5 | 2335.5 | 7832
12:00 | 80 | 5540 | 2353 | 7893
12:30 | 125 | 5662 | 2361.5 | 8023.5
13:00 | 170 | 5784 | 2370 | 8154
13:30 | 145 | 5682.5 | 2293.5 | 7976
14:00 | 120 | 5581 | 2217 | 7798
14:30 | 105 | 5556 | 2182 | 7738
15:00 | 90 | 5531 | 2147 | 7678
15:30 | 60 | 5438.5 | 2128.5 | 7567
16:00 | 30 | 5346 | 2110 | 7456
16:30 | 45 | 5199.5 | 2154 | 7353.5
17:00 | 60 | 5053 | 2198 | 7251
17:30 | 100 | 5459.5 | 2481.5 | 7941
18:00 | 140 | 5866 | 2765 | 8631
18:30 | 134.5 | 6070 | 2884.5 | 8954.5
19:00 | 129 | 6274 | 3004 | 9278
19:30 | 103 | 6103 | 3041 | 9144
20:00 | 136 | 6069 | 2997 | 9066 |  |  |  | Executive Engineer
20:30 | 139.5 | 6058.5 | 2929 | 8987.5 |  |  |  | Network Operation Division
21:00 | 143 | 6048 | 2861 | 8909
21:30 | 167 | 5916 | 2709 | 8625
22:00 | 191 | 5784 | 2557 | 8341 |  |  |  |  | Page 6 of 7
22:30 | 191 | 5645 | 2376.5 | 8021.5
23:00 | 191 | 5506 | 2196 | 7702
23:30 | 260.5 | 5353.5 | 2014 | 7367.5
24:00 | 330 | 5201 | 1832 | 7033
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-25 |  | Energy | 180754179
[11 empty] | 2021-01-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2372 | 625 | 1456 | 2488 | 150 | 70 | 129 | 0 | 80 | 0
0:30 | 2202 | 531 | 1518 | 2233.5 | 149 | 58 | 100.5 | 0 | 77 | 0 | Date: | 2021-01-25
1:00 | 2032 | 437 | 1580 | 1979 | 148 | 46 | 72 | 0 | 74 | 0
1:30 | 2015 | 437 | 1670.5 | 1858.5 | 148.5 | 46 | 62 | 0 | 73 | 0 | [7 empty] | Total Energy | 180.7542 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 1998 | 437 | 1761 | 1738 | 149 | 46 | 52 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 1999 | 437 | 1754.5 | 1608.5 | 149 | 46.5 | 30.5 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 180.7542
3:00 | 2000 | 437 | 1748 | 1479 | 149 | 47 | 9 | 0 | 72 | 0
3:30 | 1990 | 437 | 1740.5 | 1407.5 | 149 | 47 | 9 | 0 | 72 | 0 | [6 empty] | Shortage
4:00 | 1980 | 437 | 1733 | 1336 | 149 | 47 | 9 | 0 | 72 | 0
4:30 | 1966 | 436.5 | 1719 | 1320.5 | 149 | 47 | 9 | 0 | 72 | 0
5:00 | 1952 | 436 | 1705 | 1305 | 149 | 47 | 9 | 0 | 72 | 0
5:30 | 1942.5 | 468 | 1653.5 | 1415 | 149.5 | 47 | 9 | 0 | 72 | 0
6:00 | 1933 | 500 | 1602 | 1525 | 150 | 47 | 9 | 0 | 72 | 0
6:30 | 1960.5 | 552 | 1641 | 1676.5 | 150 | 47 | 9 | 0 | 70 | 0.5 |  |  |  |  | Coal
7:00 | 1988 | 604 | 1680 | 1828 | 150 | 47 | 9 | 0 | 68 | 1
7:30 | 2016.5 | 662 | 1723.5 | 2043.5 | 150 | 47 | 14.5 | 0 | 71 | 6 |  |  |  | Oil |  |  |  | ,
8:00 | 2045 | 720 | 1767 | 2259 | 150 | 47 | 20 | 0 | 74 | 11
8:30 | 1977.5 | 720 | 1655 | 2603 | 150 | 47 | 123 | 0 | 76 | 16.5
9:00 | 1910 | 720 | 1543 | 2947 | 150 | 47 | 226 | 0 | 78 | 22
9:30 | 1906 | 719.5 | 1503 | 3012.5 | 150 | 47 | 228.5 | 0 | 80 | 23
10:00 | 1902 | 719 | 1463 | 3078 | 150 | 47 | 231 | 0 | 82 | 24
10:30 | 1911.5 | 719 | 1480.5 | 3078.5 | 150 | 47 | 239 | 0 | 84 | 24
11:00 | 1921 | 719 | 1498 | 3079 | 150 | 47 | 247 | 0 | 86 | 24
11:30 | 1929 | 719.5 | 1540.5 | 3080.5 | 150 | 46.5 | 253.5 | 0 | 87 | 25.5
12:00 | 1937 | 720 | 1583 | 3082 | 150 | 46 | 260 | 0 | 88 | 27
12:30 | 2029 | 719.5 | 1569.5 | 3137.5 | 150 | 46 | 256 | 0 | 89 | 27
13:00 | 2121 | 719 | 1556 | 3193 | 150 | 46 | 252 | 0 | 90 | 27
13:30 | 2121 | 719 | 1556 | 3193 | 150 | 46 | 252 | 0 | 90 | 27
14:00 | 2121 | 719 | 1556 | 3193 | 150 | 46 | 252 | 0 | 90 | 27
14:30 | 2150 | 719.5 | 1475 | 3025 | 150 | 45.5 | 241 | 0 | 88 | 22
15:00 | 2179 | 720 | 1394 | 2857 | 150 | 45 | 230 | 0 | 86 | 17
15:30 | 2172 | 719.5 | 1371.5 | 2804.5 | 150 | 46 | 204 | 0 | 86 | 13.5
16:00 | 2165 | 719 | 1349 | 2752 | 150 | 47 | 178 | 0 | 86 | 10
16:30 | 2124.5 | 719.5 | 1412.5 | 2613 | 150 | 60.5 | 183 | 0 | 85 | 5.5
17:00 | 2084 | 720 | 1476 | 2474 | 150 | 74 | 188 | 0 | 84 | 1
17:30 | 2173 | 790 | 1536.5 | 2808 | 150 | 71 | 319 | 0 | 93 | 0.5
18:00 | 2262 | 860 | 1597 | 3142 | 150 | 68 | 450 | 0 | 102 | 0
18:30 | 2288 | 883.5 | 1639.5 | 3372.5 | 150 | 68.5 | 450.5 | 0 | 102 | 0
19:00 | 2314 | 907 | 1682 | 3603 | 150 | 69 | 451 | 0 | 102 | 0
19:30 | 2345 | 909 | 1745 | 3423 | 150 | 69 | 403 | 0 | 100 | 0
20:00 | 2327 | 909 | 1698 | 3407 | 150 | 70 | 403 | 0 | 102 | 0
20:30 | 2350.5 | 908.5 | 1699 | 3359.5 | 150 | 70 | 351 | 0 | 99 | 0
21:00 | 2374 | 908 | 1700 | 3312 | 150 | 70 | 299 | 0 | 96 | 0
21:30 | 2362 | 908 | 1640 | 3141 | 150 | 70.5 | 259.5 | 0 | 94 | 0
22:00 | 2350 | 908 | 1580 | 2970 | 150 | 71 | 220 | 0 | 92 | 0
22:30 | 2370.5 | 884 | 1534 | 2729 | 150 | 70.5 | 193.5 | 0 | 90 | 0
23:00 | 2391 | 860 | 1488 | 2488 | 150 | 70 | 167 | 0 | 88 | 0
23:30 | 2381.5 | 742.5 | 1472 | 2488 | 150 | 70 | 148 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 26.0° C
24:00 | 2372 | 625 | 1456 | 2488 | 150 | 70 | 129 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 45 | 47 | 74 | 68 |  | 69 | 69 | 70 | 70 | 71 | 70 | 70 | 1253444
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 17 | 17 | 17 |  |  |  | 313603
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 18 | 17 | 16 | 11 | 7 | 1 | [9 empty] | 115830
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 68 | 68 | 68 | 68 | 51 | 51 | 51 | 36 | 49 | 102 |  | 102 | 68 | 68 | 34 | 17 |  |  | 819550
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 5 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 |  | 34 | 17 | 17 | 17 |  |  |  | 358798
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [10 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 33 | 33 | 33 |  |  |  |  | 221728
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 90 | 90 | 88 | 89 | 40 | 65 | 40 | 90 | 90 | 90 | 90 | 90 | 150 | 155 | 155 | 145 | 120 | 145 |  | 180 | 190 | 186 | 185 | 185 | 190 | 190 | 3052000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 195 | 145 | 145 | 145 | 167 | 230 | 230 | 245 | 253 | 253 | 263 | 268 | 270 | 270 | 267 | 267 | 264 |  | 250 | 250 | 254 | 267 | 269 | 270 | 268 | 5866252
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 70 | 110 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3181500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3 | 3 | 3 | 3 |  | 6 | 6 | 6 | 6 | 6 | 3 | 3 | 63720
33 | Ashuganj 225 MW CCPP | 161 | 154 | 152 | 149 | 133 | 136 | 131 | 120 | 120 | 120 | 128 | 161 | 181 | 187 | 200 | 190 | 160 | 209 |  | 216 | 213 | 207 | 187 | 198 | 221 | 224 | 4033000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6126000
| Ashuganj 450 MW CCPP(North) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 165 | 175 | 170 | 175 |  | 175 | 175 | 175 | 175 | 170 | 170 | 170 | 4033000
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP | 100 | 101 | 93 | 101 | 100 | 92 | 100 | 100 | 93 | 100 | 100 | 100 | 100 | 100 | 92 | 99 | 102 | 100 |  | 92 | 101 | 92 | 96 | 99 | 102 | 98 | 2332730
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 355 | 363 | 363 | 363 | 365 | 314 | 340 | 364 | 364 | 363 | 363 | 364 | 364 | 305 | 304 | 304 | 304 | 337 |  | 366 | 366 | 366 | 367 | 327 | 326 | 367 | 8238000
42 | RPCL 210MW CCPP | 108 | 110 | 110 | 103 | 103 | 103 | 102 | 102 | 99 | 99 | 99 | 104 | 102 | 102 | 101 | 101 | 100 | 104 |  | 106 | 104 | 106 | 106 | 106 | 105 | 105 | 2450560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 4 | 9 | 5 | [16 empty] | 16670
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 712000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 74 | 74 | 74 | 68 | 69 | 68 | 68 | 69 | 69 | 68 | 70 | 70 | 70 | 71 | 70 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1708800
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 2396000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 222 | 222 | 222 | 222 | 222 | 208 | 215 | 215 | 180 | 162 | 163 | 163 | 163 | 163 | 163 | 162 | 164 | 162 |  | 162 | 162 | 163 | 163 | 162 | 162 | 162 | 4366980
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 445000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 207720
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 5 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 233000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 31 | 31 | 48 | 48 | 14 | 11 | 13 | 16 | 14 | 14 | 14 | 14 | 51 |  | 51 | 51 | 48 | 48 | 51 | 51 | 50 | 894000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 293328
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 300 | 300 | 305 | 300 | 315 | 330 | 300 | 290 | 300 | 290 | 320 | 280 | 290 | 285 | 300 | 300 |  | 295 | 310 | 290 | 290 | 285 | 285 | 310 | 7395000
| Bibiyana South 400 MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 46 | 55 | 83 | 100 | 122 |  | 130 | 138 | 143 | 230 | 200 | 200 | 200 | 2009900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 46 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 1228324
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 519360
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 19 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 440112
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 |  | 16 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 458064
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494892
63 | Impoprt (Tripura) | 74 | 72 | 72 | 72 | 72 | 72 | 68 | 74 | 78 | 82 | 86 | 88 | 90 | 94 | 86 | 86 | 84 | 102 |  | 102 | 100 | 102 | 96 | 92 | 88 | 80 | 2029440
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 42 | 42 | 42 | 42 | 39 | 12 | 5 | 2 | 5 | 5 | 14 | 6 | 4 | 7 | 10 | 23 |  | 25 | 20 | 30 | 30 | 35 | 38 | 38 | 576480
65 | Feni 22MW PP (Doreen) | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 18 | 21 | 21 | 21 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 435564
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191880
67 | Jangalia 33MW PP (Summit) | 33 | 25 | 33 | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 780210
68 | Cumilla 25 MW PP (Summit) | 22 | 18 | 18 | 18 | 18 | 18 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 50400
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 26 | 26 | 26 | 26 | 32 | 32 | 32 | 32 | 32 | 31 | 28 | 28 | 23 | 31 | 17 |  | 31 | 32 | 32 | 28 | 31 | 31 | 31 | 688320
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 421500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 837500
73 | Ghorashal 108MW PP (Regent) |  | 109 | 110 | 110 | 110 | 109 | 106 | 107 | 107 | 106 | 107 | 107 | 106 | 110 | 106 | 107 | 110 | 110 |  | 110 | 107 | 110 | 110 | 110 | 110 | 110 | 2544636
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 16 | 16 | 8 | 8 | 8 | 20 | 24 | 24 | 72 | 109 | 107 | 103 | 100 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 36 | 1632960
| Manikgonj 162MW PP(MPGL) | 144 | 126 | 108 | 108 | 108 |  | 40 | 126 | 126 | 108 | 108 | 108 | 90 | 90 | 72 | 72 | 72 | 108 |  | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 2545920
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 7 | 36 | 60 | 60 | 70 | 100 | 100 | 100 | 50 | 24 | 50 |  | 100 | 100 | 100 | 60 | 60 | 45 | 24 | 1166400
78 | Gazipur 52 MW PP | [17 empty] | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 36480
79 | Kodda 150MW PP | [7 empty] | 16 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 64 | 64 | 115 |  | 115 | 100 | 100 | 100 | 84 | 48 | 16 | 1463520
80 | Jamalpur 95 MW PP(Powerpac) | [5 empty] | 2 | 24 | 24 | 54 | 53 | 49 | 49 | 64 | 65 | 57 | 52 | 41 | 35 |  | 52 | 82 | 82 | 82 | 82 | 48 | 8 | 972480
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 5 |  | 16 | [6 empty] | 26333
| Gazipur 100 MW PP | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 48 | 71 | 90 | 90 | 50 | 50 | 82 |  | 90 | 90 | 90 | 90 | 72 |  |  | 997140
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 27600
| Jodiac Power | [16 empty] | 3 | 52 |  | 54 | 54 | 54 | 54 | 54 | 54 |  | 343637
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 48 | 48 | 48 | 30 | 30 | 35 | 64 | 64 | 64 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 |  | 101 | 101 | 101 | 101 | 100 | 100 | 100 | 1973304
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 62 | 62 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 60 | 62 | 65 | 74 | 75 | 75 | 74 | 74 |  | 75 | 74 | 74 | 74 | 70 | 74 | 71 | 1545722
86 | Meghnaghat CCPP(Summit) | 285 | 260 | 260 | 260 | 285 | 260 | 260 | 260 | 260 | 275 | 270 | 280 | 260 | 265 | 265 | 255 | 270 | 265 |  | 240 | 285 | 240 | 240 | 240 | 305 | 270 | 6367738
87 | Meghnaghat 100 MW(IEL) | 70 | 25 | 7 | 7 | 7 | 20 | 40 | 40 | 72 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 |  | 100 | 100 | 100 | 100 | 70 | 60 | 24 | 1670400
| Meghnaghat 104 MW PP (OPCL) | 91 | 91 | 60 | 54 | 54 | 54 | 53 | 53 | 84 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 1970880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 |  | 8 | 10 |  | 10 | [6 empty] | 140520
92 | Fenchuganj 44MW (Energyprima) | 47 | 50 | 50 | 50 | 50 | 30 | 30 | 44 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 721008
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 35 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1173343
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 48 | 48 | 32 | 32 | 32 | 40 | 40 | 74 | 102 | 102 | 102 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 102 | 58 | 24 | 24 | 1063152
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 27 | 25 | 25 | 36 | 45 | 45 | 46 | 46 | 46 | 46 | 50 | 50 | 50 |  | 50 | [6 empty] | 743040
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 1 | 7 | 13 | 24 | 26 | 30 | 31 | 15 | 11 | 11 |  | 11 | [6 empty] | 192960
97 | katpotti 52 MW | [17 empty] | 10 |  | 12 | [6 empty] | 34176
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 55 | 55 | 55 | 30 | 35 |  | 50 | 50 | 55 | 30 | 15 | 15 | 15 | 571318
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 |  | 35 | 37 | 37 | 37 | 37 |  |  | 474803
101 | Kushiara 163 MW CCPP (KP) | 110 | 140 | 140 | 140 | 110 | 140 | 110 | 140 | 110 | 110 | 110 | 110 | 140 | 110 | 110 | 110 | 110 | 110 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3187800
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | [10 empty] | 10950
103 | Kamalaghat 54 MW PP(Banco Energy) | [5 empty] | 17 | 17 | 17 | 54 | 54 | 45 | 54 | 54 | 54 | 54 | 54 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 | 17 | 821880
104 | Keranigonj 300 MW PP (APR) | [8 empty] | 162 | 54 | 30 | 31 | 174 | 53 |  |  |  | 70 |  | 158 | 51 | 53 |  |  |  |  | 748291
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 100 | 70 | 50 | 50 | 67 | 85 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 130 | 148 |  | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 4012800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 10 | 30 | 58 | 102 | 149 | 149 | 149 | 149 | 149 | 147 | 147 | 133 | 115 |  | 114 | 131 | 131 | 131 | 130 | 82 | 50 | 2173680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 60 | 60 | 60 | 30 | 30 | 60 | 76 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 2027520
116 | Chandpur 200MW (Desh energy) | [17 empty] | 10 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 120000
117 | Ashuganj 150MW PP (Midland) | 41 | 40 | 38 | 40 | 40 | 40 | 41 | 40 | 40 | 41 | 40 | 21 | 20 | 20 | 20 | 20 | 20 | 18 |  | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 702545
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 17 |  | 16 | [6 empty] | 207600
| Anwara 300 MW PP (United) | 290 | 275 | 256 | 253 | 197 | 288 | 301 | 306 | 290 | 287 | 305 | 270 | 271 | 215 | 215 | 215 | 180 | 280 |  | 286 | 286 | 303 | 306 | 307 | 307 | 307 | 6541200
| Juldah unit-2 (Acorn) | 100 | 100 | 60 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 92 | 100 | 90 | 100 | 100 | 100 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2244480
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4553 | 4509 | 4256 | 4145 | 4038 | 4129 | 4394 | 4834 | 5372 | 5442 | 5453 | 5540 | 5784 | 5581 | 5531 | 5346 | 5053 | 5866 |  | 6274 | 6103 | 6069 | 6048 | 5784 | 5506 | 5201 | 126305829
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 97 | 83 | 83 | 49 | 49 | 83 | 99 | 115 | 115 | 99 | 99 | 115 | 99 | 99 | 99 | 99 | 99 | 99 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2350080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 4 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 18 |  | 18 | 18 | 18 | 18 | 8 | 8 | 9 | 275040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 17 | 17 | 35 | 35 | 90 | 90 | 90 | 90 | 72 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 90 | 90 | 1774080
130
131
132 | United Payra Power Ltd. | [17 empty] | 18 |  | 35 | 35 | 35 | 35 | 17 | 17 |  | 160800
133 | Bhola Nutan Biddut BD LTD (GAS) | 57 | 57 | 57 | 57 | 22 | 17 | 20 | 40 | [18 empty] | 355036
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [5 empty] | 16 | 16 | 32 | 64 | 64 | 64 | 64 | 64 | 48 | 48 | 48 | 48 | 67 |  | 96 | 96 | 96 | 96 | 96 | 64 | 64 | 1179840
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 79 | 84 | 86 | 86 | 86 | 86 | 86 | 34 | 65 | 75 |  | 88 | 87 | 87 | 87 | 75 | 76 | 76 | 1843789
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 19 | 19 | 19 | 21 | 17 | 20 | 18 | 17 | 18 | 18 | 18 | 18 | 15 | 16 | 16 | 21 |  | 22 | 23 | 23 | 23 | 23 | 23 | 22 | 456400
141 | Noapara 100 MW PP (Bangla Trac) | [8 empty] | 62 | 45 | 30 | [6 empty] | 1 |  | 60 | 30 | 30 |  |  |  |  | 264960
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 16 | 33 | 33 | 40 | 40 | 40 | 8 | 8 |  |  | 40 |  | 40 | 40 | 40 | 40 | 8 |  |  | 415125
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 39808
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [8 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 32 | 15 | 15 | 50 |  | 67 | 67 | 67 | 50 | 15 |  |  | 688032
146 | Bheramara HVDC | 437 | 437 | 437 | 437 | 436 | 500 | 604 | 720 | 720 | 719 | 719 | 720 | 719 | 720 | 720 | 719 | 720 | 860 |  | 907 | 909 | 909 | 908 | 908 | 860 | 625 | 16612363
147 | Bheramara 410 MW CCPP | 400 | 345 | 345 | 345 | 370 | 345 | 415 | 430 | 340 | 345 | 385 | 345 | 435 | 400 | 400 | 370 | 330 | 410 |  | 405 | 395 | 390 | 370 | 360 | 360 | 360 | 9253152
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 148 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3667500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [8 empty] | 45 | 50 | 50 | 50 | 50 | 28 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 36 |  |  |  | 551024
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [19 empty] | 5 | 12 | 9 | 9 | 14 | 28 | 19 | 743100
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 370 | 395 | 380 | 365 | 395 | 362 | 442 | 430 | 308 | 311 | 331 | 419 | 330 | 305 | 285 | 292 | 366 | 370 |  | 372 | 428 | 391 | 392 | 321 | 226 | 130 | 8479054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 237718
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 |  |  |  | 364460
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 16 | 42 | 42 | 50 | 50 | 50 | 50 | 25 | 8 | 8 | 25 |  | 50 | 50 | 50 | 16 |  |  |  | 491732
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [11 empty] | 13 | 22 | 25 | 25 | 24 | 21 | 22 |  | 22 | 23 | 23 |  |  |  |  | 212604
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 19 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 8 | 8 | 52 |  | 52 | 52 | 52 | 52 | 8 |  |  | 578880
170 | Chapainawabganj 100 MW Peaking PP | 63 | 43 | [15 empty] | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 778608
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 70 |  | 94 | 95 | 95 | 95 | 95 | 35 | 35 | 1204032
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 35 | [7 empty] | 65 | 102 | 103 |  | 103 | 102 | 103 | 105 | 105 |  |  | 951360
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 25613
178
178