## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-01-30 | Saturday
|  |  | Date (day): | 2021-01-30 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12247.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13722 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-29 | 2021-01-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 109 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2021-07-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 340 | 357 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 280 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 75 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 36 | 49 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 10 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 120 | 193 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 40 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 6 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 |  |  | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 41 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 55 | 137 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 214 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 49 | 65 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 53 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 1714 | 2198 | 3311 | 3561 | 108 | 2267
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 43 | 43 | 43
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 52 | 55 | 68 | 68 | 162 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 36 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 20 | 42 | 25 | 40
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 97 | 97 |  | 11 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 216 | 251 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 455 | 674 | 1154 | 1244 | 897 | 126
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 199 | 200 | 200
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 350 | 350 | 350
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 |  | 19 | Machine problem
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 108 | 120 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 94 | 100 | 100 |  | 63 | ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 15 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 20
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 48 | 102 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 22 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 8 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1084 | 1165 | 1690 | 1952 | 500 | 442
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 98 | 98 | 161 | 161 | 41 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 64 | 90 | 90 |  |  | Engine problem
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 24 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 27 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 385 | 432 | 661.6 | 610 | 41 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 160 |  |  | Gas shortage
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 48 | 50 | 50
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under maint
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 71 | 73 | 73 |  | 13 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 100 | 100 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 50 | 120 | 50 | 120 |  | 111
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 325 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 15 | 320 | 320 |  | 400
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 9 | 9
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 417 | 415 | 415 | 415 |  |  | On test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1088 | 1193 | 1477 | 1707 | 0 | 911
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 520 | 801 | 716 | 908
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 360 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 70 | 95 | 95 |  | 10 | Engine problem
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 67 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 965 | 1462 | 1621 | 2099 | 0 | 78
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 82 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 25 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 34 | 75 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 470 | 0 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 41 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 525 | 223 | 932 | 1032 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 12 | 25 | 25 |  | 25 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 179 | 220 | 220 | 220
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 205 | 220 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint. |  | 13/2/2021
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 25 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 34 | 102 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 92 | 113 | 113 |  | 113 | Under maint.
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 542 | 740 | 1130 | 1254 | 821 | 552
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 4 | 112 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 158 | 261 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 6916 | 8348 | 12247.6 | 13722 | 2491 | 4791
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6577.1591 | 7939 | 11647.5439 | 13049.7075
| A. |  | 2021-01-29 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 8348 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5736 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8348 | MW
| 3 | Day peak Generation : |  |  | 6916 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7939 | MW
| 4 | Evening peak Generation : |  |  | 8348 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 167.7166 | MKWHr | By Solar | 0.38542 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 97.6565 | MKWHr |  | By Oil: | 41.0748 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.9117 | MKWHr |  | By Hydro: | 1.2925 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2491 | MW | Dhaka | 2448 | 2448 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4791 | MW | Chittagong | 854 | 854 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7282 | MW | Khulna | 1033 | 1033 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 805.32 | MMCFD |  |  | Rajshahi | 916 | 916 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 102680380.308 | ii) Oil : | Taka | 239487825.71 | Comilla | 719 | 719 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 56073184 | Total | Taka | 398241390.018 | Mymensingh | 753 | 753 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.2345 | MKWHr. | Sylhet | 315 | 315 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -328 | MW (E to W) at | 19:00 | hrs | Barisal | 224 | 224 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -405 | MW at | 8:00 | hrs | Rangpur | 677 | 677 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.4° C |  |  | Total | 7939 | 7939 |  | 0
| B. |  | 2021-01-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13722 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
| 4 | Reserve(Generation end) |  |  |  | 4422 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 186.8429 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5459 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.7185 | MKWHr. | ii) HVDC Flow at Peak Time |  | 801 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6771 | MKWHr. | iii) Maximum HVDC Flow : |  | 802 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.04 |  | (b) Today: | 95.92 |  | (c) Rule Curve: |  | 97.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 352 |  | 0 | 0 | 240 | 0 | 64 | 15 | 0 | 0 | 182 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 78 | 102 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 72 | 0 | 151 | 19 | 0 | 7 | 275 | 8 | 11 | 0 | 80 | 0 | 0 | 160 | 0 | 0 | 0 | 70 | 17 | 128 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 70 | 397 | 22 | 0 | 144 | 0 | 100 |  | 473 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 33 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 470 | 17 | 0 | 0 |  | 4673 | 1931 | 6604 | 2890 | 473 | 1119 | 1366 | 620 | 58 | 0 | 78 | 0 | 0 | 96.07
2:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 353 |  | 0 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 185 | 8 | 92 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 72 | 102 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 72 | 0 | 150 | 19 | 0 | 7 | 290 | 8 | 11 | 0 | 80 | 0 | 0 | 120 | 0 | 0 | 0 | 40 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 50 | 405 | 0 | 0 | 108 | 0 | 100 |  | 473 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 32 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 470 | 23 | 0 | 0 |  | 4324 | 1931 | 6255 | 2844 | 473 | 1132 | 1059 | 619 | 56 | 0 | 72 | 0 | 0 | 96.06
3:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 353 |  | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 68 | 102 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 72 | 0 | 150 | 19 | 0 | 7 | 290 | 8 | 11 | 0 | 45 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 50 | 405 | 0 | 0 | 72 | 0 | 100 |  | 474 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 21 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 440 | 18 | 0 | 0 |  | 4040 | 1893 | 5933 | 2847 | 474 | 1116 | 783 | 590 | 55 | 0 | 68 | 0 | 0 | 96.06
4:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 354 |  | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 95 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 68 | 103 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 73 | 0 | 150 | 19 | 0 | 7 | 300 | 8 | 11 | 0 | 45 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 50 | 405 | 0 | 0 | 54 | 0 | 100 |  | 474 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 31 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 400 | 17 | 0 | 0 |  | 3959 | 1822 | 5781 | 2807 | 474 | 1137 | 692 | 550 | 53 | 0 | 68 | 0 | 0 | 96.05
5:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 354 |  | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 70 | 103 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 73 | 0 | 150 | 19 | 0 | 7 | 310 | 8 | 11 | 0 | 45 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 50 | 405 | 0 | 0 | 54 | 0 | 100 |  | 473 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 31 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 340 | 18 | 0 | 0 |  | 3966 | 1770 | 5736 | 2825 | 473 | 1147 | 677 | 490 | 54 | 0 | 70 | 0 | 0 | 96.05
6:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 353 |  | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 30 | 100 | 0 | 0 | 0 | 350 | 197 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 70 | 103 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 73 | 0 | 150 | 19 | 0 | 5 | 310 | 8 | 11 | 0 | 45 | 0 | 0 | 62 | 0 | 0 | 0 | 10 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 90 | 390 | 0 | 0 | 108 | 0 | 100 |  | 473 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 31 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 330 | 0 | 0 | 0 |  | 4138 | 1826 | 5964 | 2965 | 473 | 1116 | 805 | 480 | 55 | 0 | 70 | 0 | 0 | 96.04
7:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 290 |  | 0 | 0 | 240 | 0 | 22 | 3 | 0 | 0 | 125 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 20 | 30 | 100 | 0 | 0 | 0 | 350 | 187 | 8 | 95 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 64 | 103 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 73 | 0 | 150 | 19 | 0 | 5 | 300 | 8 | 11 | 0 | 80 | 0 | 0 | 120 | 0 | 0 | 1 | 50 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 15 | 90 | 385 | 24 | 0 | 144 | 0 | 100 |  | 473 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 32 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 330 | 0 | 0 | 0 |  | 4263 | 1766 | 6029 | 2803 | 473 | 1043 | 1110 | 480 | 55 | 0 | 64 | 1 | 0 | 96.04
8:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 359 |  | 0 | 0 | 240 | 6 | 48 | 20 | 0 | 0 | 125 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 17 | 20 | 28 | 80 | 0 | 0 | 0 | 350 | 202 | 8 | 95 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 60 | 104 | 2 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 71 | 0 | 150 | 19 | 0 | 0 | 320 | 8 | 11 | 0 | 81 | 0 | 0 | 144 | 0 | 9 | 5 | 70 | 0 | 102 | 0 | 0 | 0 | 0 | 1 | 213 | 0 | 0 | 0 | 26 | 90 | 390 | 72 | 4 | 144 | 0 | 100 |  | 520 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 32 | 0 | 178 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 360 | 0 | 0 | 0 |  | 4631 | 1942 | 6573 | 2868 | 520 | 1122 | 1426 | 510 | 57 | 0 | 60 | 10 | 0 | 96.03
9:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 360 |  | 0 | 0 | 240 | 7 | 54 | 40 | 0 | 0 | 95 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 80 | 0 | 0 | 0 | 350 | 183 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 42 | 104 | 23 | 22 | 1 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 71 | 0 | 150 | 19 | 0 | 0 | 300 | 0 | 11 | 0 | 77 | 0 | 0 | 182 | 0 | 74 | 11 | 70 | 0 | 103 | 0 | 0 | 0 | 0 | 2 | 213 | 0 | 0 | 0 | 26 | 90 | 405 | 91 | 9 | 144 | 0 | 100 |  | 521 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 36 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 32 | 0 | 165 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 0 | 2 | 0 | 460 | 0 | 0 | 0 |  | 4762 | 2025 | 6787 | 2748 | 521 | 1104 | 1680 | 610 | 57 | 0 | 42 | 25 | 0 | 96.03
10:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 280 |  | 0 | 0 | 270 | 7 | 98 | 40 | 0 | 0 | 78 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 24 | 14 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 80 | 0 | 0 | 0 | 350 | 184 | 8 | 94 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 42 | 104 | 16 | 22 | 2 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 71 | 0 | 150 | 0 | 0 | 0 | 290 | 3 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 95 | 14 | 30 | 0 | 97 | 0 | 0 | 0 | 0 | 4 | 212 | 0 | 0 | 0 | 26 | 80 | 415 | 91 | 16 | 144 | 0 | 100 |  | 520 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 31 | 0 | 162 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 0 | 3 | 0 | 470 | 0 | 0 | 0 |  | 4738 | 2050 | 6788 | 2733 | 520 | 1006 | 1771 | 620 | 57 | 0 | 42 | 39 | 0 | 96.02
11:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 280 |  | 0 | 0 | 255 | 7 | 90 | 40 | 0 | 0 | 72 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 15 | 17 | 33 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 87 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 48 | 102 | 16 | 22 | 2 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 71 | 0 | 80 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 75 | 0 | 0 | 200 | 0 | 86 | 16 | 30 | 0 | 103 | 0 | 0 | 0 | 0 | 4 | 214 | 0 | 0 | 0 | 26 | 80 | 417 | 91 | 44 | 144 | 0 | 100 |  | 521 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 32 | 0 | 160 | 0 | 0 | 70 | 0 | 3 | 0 | 4 | 0 | 4 | 35 | 470 | 0 | 0 | 0 |  | 4675 | 2101 | 6776 | 2661 | 521 | 1006 | 1764 | 620 | 52 | 34 | 48 | 70 | 0 | 96.02
12:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 340 |  | 0 | 0 | 280 | 7 | 80 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 8 | 17 | 33 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 100 | 0 | 0 | 0 | 350 | 186 | 8 | 95 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 48 | 98 | 16 | 22 | 3 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 71 | 0 | 50 | 0 | 0 | 0 | 300 | 8 | 11 | 0 | 55 | 0 | 0 | 200 | 0 | 49 | 17 | 36 | 0 | 108 | 0 | 0 | 0 | 0 | 4 | 216 | 0 | 0 | 0 | 26 | 90 | 417 | 91 | 27 | 144 | 0 | 100 |  | 520 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 34 | 0 | 177 | 0 | 0 | 70 | 0 | 35 | 0 | 4 | 0 | 4 | 35 | 470 | 0 | 0 | 0 |  | 4726 | 2190 | 6916 | 2734 | 520 | 1077 | 1776 | 620 | 52 | 34 | 48 | 55 | 0 | 96.02
13:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 357 |  | 0 | 0 | 235 | 41 | 80 | 40 | 0 | 0 | 185 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 17 | 17 | 55 | 10 | 25 | 8 | 17 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 20 | 0 | 0 | 20 | 20 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 86 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 58 | 99 | 36 | 22 | 1 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 71 | 0 | 100 | 0 | 0 | 0 | 310 | 8 | 11 | 0 | 55 | 0 | 0 | 200 | 0 | 68 | 16 | 90 | 0 | 108 | 0 | 5 | 0 | 0 | 4 | 305 | 0 | 0 | 0 | 26 | 90 | 410 | 91 | 42 | 144 | 0 | 100 |  | 520 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 49 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 78 | 0 | 220 | 0 | 0 | 70 | 0 | 35 | 0 | 4 | 0 | 5 | 35 | 500 | 0 | 0 | 0 |  | 5070 | 2288 | 7358 | 2824 | 520 | 1153 | 1992 | 650 | 59 | 34 | 58 | 68 | 7358 | 96.01
14:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 250 |  | 0 | 0 | 280 | 14 | 48 | 40 | 0 | 0 | 95 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 17 | 17 | 10 | 25 | 7 | 17 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 0 | 0 | 20 | 31 | 80 | 0 | 0 | 0 | 350 | 185 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 58 | 99 | 16 | 20 | 1 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 71 | 0 | 80 | 0 | 0 | 0 | 260 | 8 | 11 | 0 | 52 | 0 | 0 | 200 | 0 | 72 | 16 | 10 | 0 | 108 | 0 | 8 | 0 | 0 | 4 | 198 | 0 | 0 | 0 | 26 | 20 | 412 | 72 | 20 | 144 | 0 | 100 |  | 521 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 55 | 0 | 159 | 0 | 0 | 53 | 0 | 35 | 0 | 4 | 0 | 5 | 35 | 480 | 0 | 0 | 0 |  | 4432 | 2104 | 6536 | 2636 | 521 | 977 | 1575 | 630 | 59 | 34 | 58 | 46 | 0 | 96
15:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 300 |  | 0 | 0 | 280 | 0 | 32 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 17 | 17 | 17 | 10 | 25 | 7 | 17 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 80 | 0 | 0 | 0 | 350 | 183 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 50 | 98 | 16 | 22 | 1 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 71 | 0 | 80 | 0 | 0 | 0 | 280 | 8 | 11 | 0 | 52 | 0 | 0 | 140 | 0 | 23 | 12 | 10 | 0 | 50 | 0 | 0 | 0 | 0 | 3 | 160 | 0 | 0 | 0 | 8 | 20 | 415 | 17 | 21 | 138 | 0 | 100 |  | 519 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 54 | 0 | 159 | 0 | 0 | 17 | 0 | 35 | 0 | 4 | 0 | 3 | 35 | 450 | 0 | 0 | 0 |  | 4141 | 2039 | 6180 | 2685 | 519 | 1044 | 1149 | 600 | 59 | 34 | 50 | 40 | 0 | 96
16:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 300 |  | 0 | 0 | 245 | 0 | 32 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 17 | 17 | 17 | 10 | 25 | 12 | 17 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 0 | 350 | 184 | 8 | 86 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 48 | 97 | 8 | 22 | 1 | 30 | 0 | 50 | 50 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 280 | 8 | 11 | 0 | 55 | 0 | 0 | 140 | 0 | 16 | 7 | 10 | 0 | 50 | 0 | 0 | 0 | 0 | 2 | 160 | 0 | 0 | 0 | 8 | 20 | 415 | 17 | 15 | 108 | 0 | 100 |  | 519 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 52 | 0 | 159 | 0 | 0 | 17 | 0 | 35 | 0 | 8 | 0 | 2 | 56 | 420 | 0 | 0 | 0 |  | 4029 | 2004 | 6033 | 2656 | 519 | 1016 | 1105 | 569 | 59 | 34 | 48 | 27 | 0 | 95.99
17:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 300 |  | 0 | 0 | 310 | 2 | 32 | 15 | 0 | 0 | 190 | 2 | 3 | 0 | 48 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 25 | 12 | 17 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 1 | 0 | 20 | 38 | 80 | 0 | 0 | 0 | 350 | 209 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 68 | 96 | 8 | 22 | 0 | 30 | 0 | 19 | 20 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 295 | 8 | 11 | 0 | 57 | 0 | 0 | 140 | 0 | 16 | 1 | 10 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 160 | 4 | 0 | 0 | 8 | 20 | 415 | 17 | 3 | 108 | 0 | 100 |  | 519 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 182 | 0 | 0 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 72 | 0 | 0 | 0 | 0 |  | 4205 | 1661 | 5866 | 2842 | 519 | 918 | 1273 | 149 | 58 | 34 | 68 | 5 | 0 | 95.99
18:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 356 |  | 0 | 0 | 310 | 7 | 35 | 16 | 0 | 0 | 187 | 10 | 7 | 0 | 49 | 0 | 0 | 0 | 35 | 35 | 55 | 10 | 25 | 12 | 17 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 34 | 0 | 11 | 6 | 20 | 38 | 80 | 0 | 0 | 0 | 350 | 224 | 8 | 93 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 88 | 97 | 13 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 71 | 0 | 80 | 0 | 0 | 0 | 350 | 8 | 11 | 0 | 110 | 0 | 0 | 178 | 0 | 19 | 0 | 84 | 0 | 71 | 0 | 45 | 0 | 0 | 0 | 251 | 17 | 0 | 0 | 8 | 100 | 415 | 17 | 0 | 144 | 0 | 100 |  | 707 | 0 | 420 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 0 | 101 | 12 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 212 | 0 | 0 | 28 | 0 | 65 | 0 | 55 | 0 | 0 | 95 | 0 | 0 | 0 | 0 |  | 5013 | 2144 | 7157 | 2933 | 707 | 1129 | 1957 | 150 | 58 | 135 | 88 | 0 | 0 | 95.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 |  | 0 | 0 | 280 | 7 | 75 | 40 | 0 | 0 | 193 | 40 | 7 | 16 | 49 | 0 | 0 | 6 | 35 | 35 | 55 | 10 | 25 | 16 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 12 | 43 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 199 | 8 | 94 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 102 | 98 | 64 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 71 | 0 | 120 | 0 | 0 | 0 | 325 | 8 | 11 | 0 | 137 | 214 | 0 | 200 | 0 | 65 | 0 | 100 | 15 | 120 | 15 | 24 | 0 | 0 | 0 | 251 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 801 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 75 | 0 | 205 | 0 | 0 | 70 | 0 | 92 | 67 | 112 | 0 | 0 | 95 | 0 | 0 | 0 | 41 |  | 5662 | 2686 | 8348 | 2921 | 801 | 1188 | 2971 | 149 | 55 | 161 | 102 | 0 | 0 | 95.97
19:30 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 |  | 0 | 0 | 275 | 7 | 101 | 40 | 0 | 0 | 193 | 40 | 7 | 48 | 49 | 0 | 0 | 6 | 35 | 35 | 55 | 16 | 25 | 31 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 34 | 0 | 12 | 45 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 95 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 99 | 82 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 71 | 0 | 50 | 0 | 0 | 0 | 320 | 8 | 11 | 0 | 142 | 152 | 0 | 200 | 0 | 65 | 0 | 100 | 17 | 130 | 120 | 0 | 0 | 0 | 0 | 251 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 801 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 96 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 169 | 0 | 79 | 0 | 198 | 0 | 0 | 70 | 0 | 92 | 32 | 112 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 5721 | 2621 | 8342 | 2963 | 801 | 1192 | 2894 | 149 | 55 | 184 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 |  | 0 | 0 | 290 | 7 | 101 | 40 | 0 | 0 | 192 | 40 | 7 | 48 | 50 | 0 | 0 | 6 | 35 | 35 | 55 | 16 | 25 | 32 | 17 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 34 | 0 | 12 | 46 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 201 | 8 | 95 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 99 | 82 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 71 | 0 | 30 | 0 | 0 | 0 | 310 | 8 | 11 | 0 | 143 | 51 | 0 | 200 | 0 | 65 | 0 | 100 | 17 | 132 | 120 | 0 | 0 | 0 | 0 | 251 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 801 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 173 | 0 | 81 | 0 | 195 | 0 | 0 | 70 | 0 | 92 | 32 | 112 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 5614 | 2633 | 8247 | 2955 | 801 | 1185 | 2813 | 149 | 56 | 184 | 104 | 0 | 0 | 95.97
21:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 358 |  | 0 | 0 | 280 | 7 | 101 | 40 | 0 | 0 | 193 | 40 | 7 | 48 | 39 | 0 | 0 | 6 | 35 | 35 | 55 | 16 | 25 | 29 | 20 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 12 | 48 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 192 | 8 | 95 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 104 | 100 | 82 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 70 | 0 | 30 | 0 | 0 | 0 | 320 | 8 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 65 | 0 | 100 | 17 | 133 | 120 | 0 | 0 | 0 | 0 | 252 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 801 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 86 | 0 | 201 | 0 | 0 | 70 | 0 | 92 | 15 | 112 | 0 | 0 | 95 | 0 | 0 | 0 | 35 |  | 5552 | 2609 | 8161 | 2941 | 801 | 1200 | 2726 | 149 | 56 | 184 | 104 | 0 | 0 | 95.97
22:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 |  | 0 | 0 | 280 | 0 | 100 | 15 | 0 | 0 | 190 | 30 | 0 | 10 | 36 | 0 | 0 | 6 | 35 | 0 | 17 | 19 | 25 | 32 | 15 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 44 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 186 | 8 | 95 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 100 | 101 | 35 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 70 | 0 | 30 | 0 | 0 | 0 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 50 | 0 | 100 | 17 | 135 | 120 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 802 | 0 | 340 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 173 | 0 | 32 | 0 | 185 | 0 | 0 | 70 | 0 | 92 | 0 | 112 | 0 | 0 | 95 | 40 | 0 | 0 | 0 |  | 5230 | 2332 | 7562 | 2898 | 802 | 1125 | 2279 | 189 | 57 | 112 | 100 | 0 | 0 | 95.96
23:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 358 |  | 0 | 0 | 285 | 0 | 98 | 22 | 0 | 0 | 125 | 7 | 0 | 0 | 53 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 32 | 15 | 33 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 45 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 188 | 8 | 95 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 92 | 102 | 8 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 70 | 0 | 30 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 110 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 17 | 135 | 120 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 8 | 100 | 415 | 60 | 0 | 144 | 0 | 100 |  | 635 | 0 | 340 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 32 | 0 | 186 | 0 | 0 | 70 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 180 | 0 | 0 | 0 |  | 5030 | 2068 | 7098 | 2836 | 635 | 1114 | 1935 | 330 | 54 | 102 | 92 | 0 | 0 | 95.96
24:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 |  | 0 | 0 | 260 | 0 | 80 | 15 | 0 | 0 | 125 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 15 | 33 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 95 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 82 | 102 | 0 | 22 | 0 | 30 | 0 | 53 | 50 | 0 | 0 | 0 | 71 | 0 | 30 | 0 | 0 | 0 | 300 | 8 | 11 | 0 | 67 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 17 | 100 | 120 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 100 | 415 | 52 | 0 | 108 | 0 | 100 |  | 519 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 31 | 0 | 186 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 230 | 0 | 0 | 0 |  | 4691 | 1792 | 6483 | 2831 | 519 | 1123 | 1460 | 380 | 54 | 34 | 82 | 0 | 0 | 95.95
KWH | 0 | 0 | 0 | 4378500 | 0 | 2566590 | 0 | 0 | 7926000 |  | 0 | 0 | 6584524 | 164160 | 1389144 | 584610 | 0 | 0 | 3606000 | 187200 | 38160 | 126720 | 820254 | 0 | 0 | 27648 | 390600 | 340981 | 643621 | 376524 | 600000 | 540000 | 421000 | 829700 | 0 | 0 | 1292482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 347280 | 0 | 135020 | 22800 | 52800 | 419040 | 467568 | 874560 | 2353868 | 0 | 0 | 0 | 8471000 | 4638000 | 217454 | 2208030 | 523296 | 141120 | 0 | 1241952 | 0 | 0 | 0 | 473760 | 231840 | 821300 | 529920 | 1677120 | 2384320 | 543360 | 517536 | 10350 | 713000 | 0 | 1198800 | 1168200 | 0 | 0 | 0 | 1654080 | 0 | 2474100 | 170000 | 0 | 51840 | 7472050 | 184200 | 2580500 | 0 | 1999745 | 333990 | 0 | 3928800 | 0 | 807840 | 116235 | 1272960 | 129120 | 2213018 | 579000 | 92400 | 0 | 0 | 27000 | 4995600 | 86500 | 0 | 0 | 436800 | 1777920 | 9777400 | 1082880 | 202080 | 3088800 | 0 | 2400000 |  | 13718545 | 0 | 8529984 | 0 | 444480 | 0 | 0 | 0 | 6350 | 0 | 63000 | 0 | 449400 | 421440 | 0 | 0 | 0 | 0 | 0 | 903424 | 244440 | 0 | 0 | 279360 | 0 | 518160 | 0 | 178344 | 0 | 0 | 3670700 | 0 | 0 | 0 | 0 | 4448264 | 0 | 976730 | 0 | 4648336 | 0 | 0 | 988800 | 0 | 713376 | 130752 | 640320 | 0 | 29754 | 1058400 | 8241000 | 144273 | 0 | 116400 |  | 116152570 | 51564032 | 167716602 | 71055290 | 13718545 | 26601209 | 39903323 | 11911700 | 1292482 | 1171514 | 1677120 | 385419 | 0
Fuel Cost | 0 | 0 | 0 | 6436395 | 0 | 3387898.8 | 0 | 0 | 8163780 |  | 0 | 0 | 7308821.64 | 1245974.4 | 9571202.16 | 4945800.6 | 0 | 0 | 6238380 | 1409616 | 348019.2 | 1246924.8 | 7562741.88 | 0 | 0 | 251320.32 | 2851380 | 2635783.13 | 6346103.06 | 282393 | 450000 | 0 | 0 | 0 | 0 | 0 | 348970.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1309694 | 217740 | 459360 | 3318796.8 | 589135.68 | 2597443.2 | 3483724.64 | 0 | 0 | 0 | 8471000 | 4266960 | 280515.66 | 2539234.5 | 591324.48 | 197568 | 0 | 2123737.92 | 0 | 0 | 0 | 601675.2 | 173880 | 1437275 | 397440 | 12578400 | 2527379.2 | 4933708.8 | 657270.72 | 164979 | 1169320 | 0 | 2133864 | 1822392 | 0 | 0 | 0 | 3159292.8 | 0 | 4280193 | 372300 | 0 | 105753.6 | 7546770.5 | 138150 | 1961180 | 0 | 15118072.2 | 5671150.2 | 0 | 20429760 | 0 | 7949145.6 | 1358787.15 | 10374624 | 1400952 | 15601776.9 | 538470 | 842688 | 0 | 0 | 0 | 37766736 | 753415 | 0 | 0 | 3743376 | 11840947.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 79018819.2 | 0 | 8956483.2 | 0 | 3493612.8 | 0 | 0 | 0 | 66611.5 | 0 | 656460 | 0 | 696570 | 4113254.4 | 0 | 0 | 0 | 0 | 0 | 7995302.4 | 1882188 | 0 | 0 | 2706998.4 | 0 | 994867.2 | 0 | 135006.408 | 0 | 0 | 19895194 | 0 | 0 | 0 | 0 | 5871708.48 | 0 | 1465095 | 0 | 5438553.12 | 0 | 0 | 10323072 | 0 | 6769938.24 | 1234298.88 | 4968883.2 | 0 | 328781.7 | 7821576 | 36177990 | 0 | 0 | 0 |  | 281028863.08 | 211011264.128 | 492040127.208 | 68004831.628 | 79018819.2 | 34675548.68 | 228869293.01 | 56073184 | 348970.14 | 10618532.7 | 12578400 | 1852547.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 340 |  | 0 | 0 | 280 | 7 | 80 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 17 | 17 | 55 | 16 | 25 | 8 | 17 | 33 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 100 | 0 | 0 | 0 | 350 | 186 | 8 | 95 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 22 | 48 | 98 | 16 | 22 | 3 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 71 | 0 | 50 | 0 | 0 | 0 | 300 | 8 | 11 | 0 | 55 | 0 | 0 | 200 | 0 | 49 | 17 | 36 | 0 | 108 | 0 | 0 | 0 | 0 | 4 | 216 | 0 | 0 | 0 | 26 | 90 | 417 | 91 | 27 | 144 | 0 | 100 |  | 520 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 34 | 0 | 177 | 0 | 0 | 70 | 0 | 35 | 0 | 4 | 0 | 4 | 35 | 470 | 0 | 0 | 0 |  | 6916 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 357 | 0 | 0 | 0 | 280 | 7 | 75 | 40 | 0 | 0 | 193 | 40 | 7 | 16 | 49 | 0 | 0 | 6 | 35 | 35 | 55 | 10 | 25 | 16 | 17 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 34 | 0 | 12 | 43 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 199 | 8 | 94 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 102 | 98 | 64 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 71 | 0 | 120 | 0 | 0 | 0 | 325 | 8 | 11 | 0 | 137 | 214 | 0 | 200 | 0 | 65 | 0 | 100 | 15 | 120 | 15 | 24 | 0 | 0 | 0 | 251 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 801 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 75 | 0 | 205 | 0 | 0 | 70 | 0 | 92 | 67 | 112 | 0 | 0 | 95 | 0 | 0 | 0 | 41 |  | 8348 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 97 | 43 | 22 | 40 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 100 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 20 | 11 | 33 | 22 | 147 | 161 | 90 | 22 | 0 | 30 | 0 | 50 | 50 | 160 | 0 | 0 | 73 | 0 | 120 | 20 | 0 | 9 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 320 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 0 | 162 | 0 | 100 |  | 908 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 35 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 97 | 43 | 22 | 25 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 100 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 20 | 11 | 33 | 22 | 135 | 161 | 90 | 22 | 1.6 | 30 | 0 | 50 | 50 | 0 | 0 | 0 | 73 | 0 | 50 | 20 | 0 | 9 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 320 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 50 | 162 | 0 | 100 |  | 716 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 50 | 220 | 0 | 0 | 95 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 35 |  | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 310 | 0 | 0 | 0 | 245 | 10 | 34 | 15 | 0 | 0 | 150 | 7 | 0 | 0 | 85 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 32 | 0 |  | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 26 | 20 | 18 | 100 | 0 | 0 | 0 | 300 | 190 | 8 | 95 | 23 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 33 | 20 | 84 | 161 | 5 | 22 | 0 | 30 | 0 | 5 | 5 | 0 | 0 | 0 | 71 | 0 | 30 | 0 | 0 | 0 | 330 | 0 | 11 | 0 | 32 | 0 | 0 | 173 | 0 | 52 | 5 | 20 | 0 | 100 | 120 | 0 | 0 | 0 | 1 | 214 | 0 | 0 | 0 | 26 | 100 | 415 | 55 | 7 | 144 | 0 | 100 | 0 | 700 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 32 | 0 | 174 | 0 | 0 | 72 | 0 | 0 | 0 | 4 | 0 | 0 | 35 | 350 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5736 | 5:00
| Highest Generation |  | 8348 | 19:00
| Day Peak Generation |  | 6916 | 12:00
| Evening Peak Generation |  | 8348 | 19:00
| HVDC Max Flow |  | 802 | 22:00
| HVDC EvPeak Flow |  | 801 | 19:00
| Load factor L.F |  | 83.71%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-01-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6916 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5459 | MW
Evening Peak Generation : |  | 8348 | MW Hour : | 19:00 | Available Max Generation : |  | 13722 | MW
E.P. Demand (at gen end) : |  | 8348 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 8348 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4422 | MW
Total Gen. (MKWH) : |  | 167.7166 | System Load Factor : | 83.71% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -405 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-01-30
Actual : | 95.92 | Ft.(MSL) , | Rule curve : | 97.6 | Ft.( MSL )
Gas Consumed : | Total = | 805.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 102680380.308
: |  | Coal : | 56073184 | Oil : | 239487825.71 | Total : | 398241390.018
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3302.0672 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1118.203 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1001.0384 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 904.2264 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 817.2997 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 659.5201 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 374.797 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.9682 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 508.6258 |  |  | 0 | 0%
Total | 0 |  | 8855.7457 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-4,5
|  |  |  | 2) Baghabari-71 &100 MW | 11) Haripur 412 MW
3) Ghorasal Unit-1,2,3,4
4) Shahjibazar 330 MW
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,4 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tangail-Kaliakoir 132KV Ckt-1 was under shut down from 08:39 to 18:00 for A/M.
b) Ishurdi-Natore 132 KV Ckt-2 was under shut down from 08:42 to 15:34 for A/M.
c) Bogura-Natore 132 KV Ckt-1,2 were under shut down from 08:32 to 15:40 due to O/V of Ishurdi-
Natore 132 KV Ckt-1
d) Khagrachari-Rangamati 132 KV Ckt-2 was under shut down from 09:22 to 16:34 for A/M.
e) Aminbazar-Meghnaghat 230 kV Ckt-2 was under shut down from 09:45 to 18:17 for A/M.
f) Bhaluka 132/33KV T-1 transformer was under shut down from 10:07 to 17:22 for A/M.
g) Mymensingh-Bhaluka 132 kV Ckt-1 was under shut down from 10:12 to 17:51 for A/M.
h) Rampura-Bhulta 230 kV Ckt-1 was under shut down from 10:08 to 18:32 for A/M.
i) Rampura-Bhulta 230 kV Ckt-2 was under shut down from 10:18 to 18:40 for A/M.
j) Hasnabad 132/33KV T-2 transformer was shut down at 10:50 for A/M.
k) Kishoreganj 132/33KV T-3 transformer was under shut down from 10:38 to 17:10 for A/M.
l) After maintenance Kaliakoir-Bibiyana 400 kV Ckt-2 was switched on at 11:43.
m) Shahjibazar-Bibiyana 230 kV Ckt-1 was under shut down from 11:59 to 15:09 for A/M.
n) Ullon-Haripur 132 KV Ckt was under shut down from 12:52 to 18:19 for work by WASA
o) Sylhet 132/33KV T-1 transformer was under shut down from 08:09 to 09:37 for C/M.
p) Bagerhat 132/33KV T-3 transformer was under shut down from 08:12 to 09:15 for C/M.
q) Faridpur-Bheramara 132 kV Ckt-1,2 tripped at 16:20 from Faridpur end showing dist B phase,Z1 |  |  |  |  | About 286 MW power interruption occurred under Barisal Zone &
at Faridpur end and were switched on at 16:48,17:20 respectively. |  |  |  |  | Faridpur, Madaripur & Shariatpur S/S areas from 16:20 to 16:55.
r) Madaripur-Gopalganj(N) 132 kV Ckt-1,2,3 tripped at 16:21 from Madaripur end showing dist 3 phase
O/V at Madaripur end and were switched on at 17:03,17:16,18:18 respectively.
s) Payra Unit #02 tripped at 16:17 due to over frequency and was synchronized at 21:31.
t) Bhola Aggreko 95 MW tripped at 16:20 due to over frequency.
u) Shahjibazar-Bibiyana 230 kV Ckt-2 was under shut down from 15:16 to 17:49 for A/M.
v) Bibiyana #03 was synchronized at 18:56.
w) Sikalbaha-TK Chemical 132 kV Ckt was under shut down since 07:31(30-01-2021) for D/W.
x) Sylhet 132 kV bus section 1 & 2 was under shut down since 07:17(30-01-2021) for C/M. |  |  |  |  | About 40 MW power interruption occurred under Sylhet S/S
areas since 07:17 to till now.
y) Rangpur 132/33KV T-2 transformer & 33 kV bus section-2 was under shut down from 07:28 to 08:49 |  |  |  |  | About 35 MW power interruption occurred under Rangpur S/S
(30-01-21) for C/M. |  |  |  |  | areas from 07:28 to 08:49.
z) Mymensing 132/33KV T-3 transformer & 33 kV bus section was under shut down from 07:48 to |  |  |  |  | About 42 MW power interruption occurred under Mymensing S/S
10:35(30-01-21) for C/M. |  |  |  |  | areas from 07:48 to 10:35.
About 08 MW power interruption occurred under Kulaura S/S area
since 05:33(29/01/2021) to

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 109 | 2566590
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 357 | 7926000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 164160 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6584524 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 75 | 1389144 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 584610 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 49 | 820254 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 376524
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 193 | 3606000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 40 | 187200 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 38160 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 6 | 27648 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 390600 | High Voltage.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 126720 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 340981 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 643621
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 1140000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 421000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 829700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 137 | 1999745 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 214 | 333990 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 65 | 807840 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 1082880 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3088800 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2198 | 39855191
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 116235
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 419040 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 55 | 1292482 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 135020
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 22800 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1272960
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 467568
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 874560
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 52800 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27000
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 251 | 4995600 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 86500 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1777920
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 674 | 11540485
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2353868 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4638000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 350 | 8471000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 523296 | Machine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 141120 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1241952
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 2213018 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 2208030 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 15 | 129120 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 473760
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231840 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1677120
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 529920 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 436800 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1165 | 26307598
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 98 | 2384320 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 517536
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 64 | 543360 | High Voltage.
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10350
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3928800 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 24 | 92400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 202080
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 347280
| Mymensingh Area Total |  |  |  | 709 | 432 | 8026126
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 713000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1198800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1168200
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 2580500
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1654080 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 2400000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2474100
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 170000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 184200 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7472050 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 15 | 579000 | synchronized at 18:56
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 51840 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 415 | 9777400 | On test
| Sylhet Area Total |  |  |  | 1988 | 1193 | 30423170
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 801 | 13718545
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 444480
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 6350
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8529984 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 63000
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 988800 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 67 | 130752 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1462 | 23881911
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 82 | 421440 | Engine problem
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 449400 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 976730 | Auxiliary fail
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 8241000 | Tripped at 16:17
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 144273 | On test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 41 | 116400 | On test.
| Barisal Area Total |  |  |  | 1676 | 223 | 10349243
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 244440 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4448264 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 205 | 4648336 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 518160
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178344 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 279360 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 903424
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 92 | 713376 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1058400 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 740 | 12992104
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3670700
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 640320
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29754
| Rangpur Area Total |  |  |  | 605 | 261 | 4340774
| Total |  |  |  | 20748 | 8348 | 167716602
| Eastern Grid Total |  |  |  | 14000 | 5662 | 116152570
| Western Grid Total |  |  |  | 6748 | 2686 | 51564032
| National Grid Total |  |  |  | 20748 | 8348 | 167716602
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-29
| (a) ENTIRE EASTERN GRID : |  | 5089 | MW | (b) ENTIRE WESTERN GRID : |  | 2850 | MW
| i) Dhaka area |  | 2448 | MW | i) Khulna area |  | 1033 | MW
| ii) Chittagong area |  | 854 | MW | ii) Rajshahi area |  | 916 | MW
| iii) Comilla area |  | 719 | MW | iii) Barisal area |  | 224 | MW
| iv) Mymensingh area |  | 753 | MW | iv) Rangpur area |  | 677 | MW
| v) Sylhet area |  | 315 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7939 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 80 | 1:00 | Jamalpur | 97 | 7:00 | Benapol | 40 | 18:30
| Munsiganj | 82 | 9:00 | Sherpur | 100 | 18:30 | Jhenida | 79 | 18:30
| Sonargaon | 61 | 20:00 | Srimongal | 27 | 19:00 | Bottail | 82 | 18:30
| Shyampur | 144 | 10:00 | Shahjibazar | 83 | 20:00 | G.K Project | 38 | 18:30
| Bhulta | 155 | 1:00 | Fenchuganj | 23 | 19:30 | Faridpur | 121 | 18:30
| Madanganj | 42 | 13:00 | Kulawara | 27 | 18:00 | Madaripur | 66 | 18:30
| Shitalakhya | 76 | 2:00 | Sylhet | 77 | 18:00 | Sariatpur | 42 | 19:30
| Rahim steel | 16 | 19:00 | Chatak | 19 | 18:30 | Gopalganj | 59 | 19:00
| Matuail | 36 | 1:00 | Sunamganj | 29 | 20:00 | Bagerhat | 75 | 19:00
| Ghorasal | 60 | 10:00 | Biani Bazar | 40 | 18:00 | Mongla | 34 | 1:00
| Narsingdi | 118 | 22:00 | Comilla (S) | 104 | 19:30 | Satkhira | 68 | 19:00
| Haripur (SBU) | 87 | 22:00 | Comilla(N) | 59 | 18:30 | Gallamari | 23 | 13:00
| Ullon | 42 | 19:00 | Chandpur | 43 | 20:00 | Magura | 42 | 18:30
| Hasnabad | 95 | 18:00 | Feni | 79 | 20:00 | Norail | 24 | 19:00
| Magbazar | 60 | 13:00 | Chowmuhani | 116 | 20:00 | Chuadanga | 61 | 19:00
| Maniknagar | 50 | 12:00 | Ashuganj | 39 | 20:00 | Barisal(N) | 34 | 18:00
| Bangabhaban | 8 | 12:00 | Daudkandi | 90 | 20:00 | Barisal (S) | 68 | 20:00
| Narinda | 48 | 11:00 | B.Baria | 100 | 18:30 | Patuakhali | 79 | 19:00
| Dhanmondi | 67 | 18:00 | Ramganj | 52 | 19:30 | Bhandaria | 42 | 19:00
| Lalbag | 50 | 1:00 | Chaddagram | 32 | 13:00 | Borhan Uddin | 26 | 19:30
| Madartek | 47 | 13:00 | PHP | 10 | 11:00 | Ishurdi | 49 | 20:00
| Dhaka University |  |  | Madunaghat | 38 | 18:30 | Ruppur Paromanobik | 2 | 20:00
| Aftabnagar | 6 | 0.5 | Hathazari | 61 | 0.8125 | Natore | 90 | 0.77083
| Fatullah | 32 | 2:00 | Khulshi | 128 | 19:30 | Bogra | 108 | 19:00
| Mirpur | 65 | 13:00 | Halishahar | 79 | 20:00 | Noagaon | 94 | 20:00
| Kalyanpur | 54 | 13:00 | Baraulia | 133 | 1:00 | Rajshahi | 90 | 20:00
| Gulshan | 62 | 13:00 | Sikalbaha | 20 | 20:00 | Rajshahi New | 12 | 20:00
| Uttara | 62 | 13:00 | Dohazari | 56 | 18:00 | C.Nawabganj | 67 | 12:00
| Uttara New | 17 | 13:00 | Cox'sbazar | 75 | 18:00 | Amnura | 44 | 19:00
| Kamrangirchar | 52 | 13:00 | Chandraghona | 24 | 12:00 | Pabna | 56 | 19:00
| Savar | 91 | 12:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 66 | 19:00
| Bhasantec | 91 | 13:00 | A. Khaer Stl. | 17 | 2:00 | Serajganj | 59 | 8:00
| Agargaon | 42 | 13:00 | Bakulia | 57 | 13:00 | Niyamatpur | 67 | 9:00
| Satmosjid | 57 | 0.54167 | Julda | 18 | 0.45833 | Joypurhat | 50 | 0.375
| Tongi | 68 | 9:00 | TK chemical | 17.9 | 19:00 | Sherpur(Bogura) | 44 | 19:00
| Kabirpur | 145 | 19:00 | Modern Steel | 0 | 1:00 | Mohastangor | 38 | 18:30
| Basundhara | 79 | 13:00 | Shahmirpur | 16 | 18:00 | Bangura | 15 | 20:00
| Manikganj | 40 | 21:00 | Khagrachhari | 20 | 9:00 | Rangpur | 108 | 18:30
| Joydevpur | 83 | 20:00 | Matarbari | 26 | 19:00 | Lalmonirhat | 51 | 19:00
| New Tongi | 50 | 1:00 | Baroiar Hat | 24 | 18:00 | Saidpur | 95 | 10:00
| Kodda | 107 | 8:00 | Rangamati | 10 | 18:00 | Purbasadipur | 104 | 13:00
| Dhamrai | 54 | 19:30 | Abul Khair 230 | 137 | 2:00 | Thakurgaon | 66 | 19:00
| Rajendrapur | 56 | 19:30 | BSRM | 103 | 15:00 | Palashbari | 111 | 19:00
| Valuka | 84 | 9:00 | GPH Ispat | 75 | 10:00 | Barapukuria | 49 | 9:00
| Tangail | 140 | 19:30 | Goalpara | 16 | 13:00 | Panchagar | 46 | 18:30
| Mymensing | 165 | 19:00 | Central s/s | 69 | 19:00 | Joldhaka | 24 | 19:00
| Kishorganj | 98 | 20:00 | Noapara | 47 | 19:30 | Kurigram | 48 | 19:00
| Netrokona | 108 | 9:00 | Jessore | 67 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 421 | 13:00 | 413 | 11:00 | Kaliakoir | 420 | 0.79167 | 410 | 0.33333
| Bheramara | 405 | 9:00 | 392 | 18:30 | Bhulta | 395 | 0.75 | 387 | 0.125
| Ashuganj(N) | 695 | 21:00 | 386 | 4:00 | Gopalganj | 411 | 0.625 | 0 | 0.70833
| Payra | 416 | 19:00 | 0 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 236 | 22:00 | 226 | 6:00
| Ishurdi | 244 | 5:00 | 229 | 8:00 | Megnaghat | 243 | 13:00 | 240 | 1:00
| Ashuganj | 245 | 14:00 | 240 | 3:00 | Fenchuganj | 247 | 18:30 | 243 | 8:00
| Serajganj | 235 | 1:00 | 225 | 8:00 | Siddhirganj | 241 | 13:00 | 237 | 4:00
| Baghabari | 241 | 6:00 | 232 | 9:00 | Maniknagar | 240 | 19:00 | 235 | 4:00
| Barapukuria | 235 | 4:00 | 225 | 9:00 | Agargaon | 241 | 2:00 | 235 | 4:00
| Bogra | 235 | 22:00 | 215 | 9:00 | Barisal | 254 | 21:00 | 243 | 8:00
| Rajshahi | 241 | 13:00 | 222 | 8:00 | Bhola 225 MW | 255 | 1:00 | 246 | 12:00
| Khulna South | 243 | 5:00 | 227 | 8:00 | AKSML | 238 | 21:00 | 227 | 2:00
| Rampura | 236 | 21:00 | 232 | 10:00 | BSRM | 239 | 21:00 | 228 | 4:00
| Haripur | 239 | 18:00 | 236 | 1:00 | Bibiyana | 248 | 13:00 | 245 | 3:00
| Hasnabad | 240 | 16:00 | 234 | 1:00 | Bhulta | 241 | 13:00 | 236 | 4:00
| Shyampur | 241 | 19:00 | 220 | 6:00 | Ashuganj (S) | 242 | 19:00 | 237 | 4:00
| Aminbazar | 242 | 18:30 | 237 | 3:00 | Kaliakoir | 240 | 21:00 | 234 | 4:00
| Tongi | 233 | 4:00 | 232 | 1:00 | GPH | 237 | 20:00 | 225 | 4:00
| Comilla (N) | 240 | 20:00 | 235 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 9:00 | 138 | 1:00 | Madanhat | 141 | 0.375 | 135 | 0.625
| Munsiganj | 141 | 10:00 | 138 | 20:00 | Hathazari | 140 | 0.33333 | 134 | 0.25
| Sonargaon | 138 | 13:00 | 135 | 17:00 | Khulshi | 139 | 0.83333 | 132 | 0.625
| Shyampur | 136 | 19:00 | 130 | 4:00 | Halishahar | 140 | 0.8125 | 133 | 0.58333
| Bhulta | 135 | 10:00 | 132 | 1:00 | Baraulia | 140 | 0.29167 | 133 | 0.45833
| Madanganj | 142 | 11:00 | 134 | 3:00 | Sikalbaha | 141 | 0.875 | 136 | 0.625
| Shitalakhya | 141 | 18:30 | 133 | 4:00 | Dohazari | 138 | 0.83333 | 132 | 0.58333
| Rahim steal | 141 | 18:00 | 138 | 1:00 | Cox'sbazar | 131 | 0.66667 | 126 | 0.5
| Matuail | 141 | 9:00 | 138 | 1:00 | Chandraghona | 142 | 0.54167 | 135 | 0.25
| Ghorasal | 142 | 23:00 | 140 | 2:00 | Kaptai | 140 | 0.041667 | 137 | 0.54167
| Narsinghdi | 139 | 13:00 | 136 | 1:00 | A. Khaer Stl. | 138 | 0.875 | 132 | 0.625
| Haripur (SBU) | 142 | 13:00 | 134 | 1:00 | Bakulia | 139 | 0.79167 | 132 | 0.66667
| Ullon | 136 | 24:00 | 132 | 1:00 | Julda | 139 | 0.79167 | 135 | 0.58333
| Hasnabad | 138 | 18:30 | 134 | 4:00 | TK Chemical | 141 | 0.95833 | 134 | 0.5
| Magbazar | 136 | 24:00 | 131 | 12:00 | Modern Steel | 139 | 0.375 | 134 | 0.70833
| Maniknagar | 138 | 4:00 | 136 | 12:00 | Shahmirpur | 140 | 0.79167 | 134 | 0.625
| Bangabhaban | 138 | 4:00 | 136 | 12:00 | Khagrachhari | 140 | 0.375 | 134 | 0.58333
| Narinda | 138 | 4:00 | 136 | 12:00 | Matarbari | 134 | 0.91667 | 130 | 0.29167
| Dhanmondi | 136 | 24:00 | 132 | 1:00 | Baroiar Hat | 141 | 0.375 | 138 | 0.041667
| Lalbag | 139 | 9:00 | 133 | 4:00 | Rangamati | 140 | 9:00 | 135 | 15:00
| Madartek | 136 | 13:00 | 131 | 12:00 | Goalpara S/S | 139 | 5:00 | 129 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 19:00 | 129 | 0.29167
| Aftabnagar | 136 | 21:00 | 132 | 10:00 | Noapara | 137 | 16:00 | 127 | 0.29167
| Fatuiiah | 136 | 19:00 | 132 | 1:00 | Jessore | 137 | 16:00 | 127 | 0.75
| Mirpur | 140 | 19:00 | 137 | 12:00 | Benapol | 137 | 0.66667 | 126 | 0.33333
| Kalyanpur | 140 | 19;30 | 138 | 12:00 | Jhenida | 135 | 2:00 | 124 | 0.33333
| Gulshan | 135 | 19:00 | 131 | 12:00 | Bottail | 138 | 0.20833 | 132 | 0.75
| Uttara | 140 | 19:00 | 138 | 6:00 | G.K Project | 143 | 0.16667 | 137 | 0.33333
| Uttara New | 138 | 19:00 | 136 | 12:00 | Faridpur | 141 | 0.20833 | 131 | 0.75
| Kamrangirchar | 141 | 19:00 | 134 | 12:00 | Madaripur | 144 | 0.041667 | 136 | 0.77083
| Savar | 137 | 19:00 | 138 | 12:00 | Shariyatpur S/S | 144 | 5:00 | 131 | 0.70833
| Bhasantec | 138 | 19:00 | 134 | 12:00 | Gopalganj | 147 | 0.25 | 127 | 0.70833
| Agargaon | 138 | 19:00 | 135 | 12:00 | Bagerhat | 138 | 14:00 | 128 | 0.33333
| Satmosjid | 140 | 19:00 | 135 | 12:00 | Mongla | 137 | 14:00 | 128 | 0.33333
| Tongi | 141 | 21:00 | 139 | 11:00 | Satkhira | 138 | 5:00 | 130 | 18:00
| Kabirpur | 139 | 13:00 | 135 | 8:00 | Gallamari | 139 | 0.20833 | 130 | 0.33333
| Basundhara | 140 | 21:00 | 137 | 12:00 | Magura | 135 | 3:00 | 125 | 0.33333
| Manikganj | 145 | 13:00 | 140 | 6:00 | Narail | 133 | 0.625 | 124 | 0.33333
| Joydevpur | 140 | 21:00 | 137 | 8:00 | Chuadanga | 133 | 2:00 | 122 | 0.33333
| New Tongi | 141 | 19:00 | 139 | 22:00 | Barisal(N) | 145 | 4:00 | 126 | 17:00
| Kodda | 140 | 13:00 | 135 | 15:00 | Barisal (S) | 144 | 0.16667 | 130 | 0.70833
| Dhamrai | 138 | 21:00 | 134 | 8:00 | Patuakhali(S) | 140 | 0.16667 | 126 | 0.70833
| Rajendrapur | 141 | 21:00 | 137 | 13:00 | Bhandaria | 143 | 0.16667 | 131
| Valuka | 131 | 18:00 | 122 | 17:00 | Ishurdi | 140 | 6:00 | 135 | 12:00
| Tangail | 137 | 23:00 | 130 | 8:00 | Ruppur Paromanobik | 140 | 17:00 | 133 | 8:00
| Mymensing | 133 | 1:00 | 127 | 12:00 | Natore | 138 | 5:00 | 128 | 8:00
| Kishorganj | 134 | 4:00 | 129 | 17:00 | Bogra | 137 | 6:00 | 123 | 9:00
| Netrokona | 132 | 4:00 | 124 | 17:00 | Noagaon | 133 | 5:00 | 115 | 9:00
| Jamalpur | 140 | 18:00 | 129 | 4:00 | Rajshahi | 137 | 20:00 | 126 | 8:00
| Sherpur | 138 | 13:00 | 128 | 17:00 | Rajshahi New | 138 | 13:00 | 126 | 8:00
| Srimongal | 140 | 3:00 | 138 | 19:30 | C.Nawabganj | 137 | 20:00 | 123 | 8:00
| Shahjibazar | 138 | 5:00 | 136 | 15:00 | Amnura | 137 | 20:00 | 130 | 8:00
| Fenchuganj | 142 | 13:00 | 137 | 17:00 | Pabna | 141 | 5:00 | 132 | 11:00
| Khulawara | 141 | 24:00 | 139 | 1:00 | Shahjadpur | 141 | 17:00 | 135 | 10:00
| Sylhet | 138 | 9:00 | 136 | 10:00 | Serajganj | 137 | 6:00 | 128 | 9:00
| Chatak | 137 | 4:00 | 135 | 10:00 | Niyamatpur | 131 | 5:00 | 112 | 8:00
| Sunamganj | 137 | 7:00 | 135 | 18:00 | Joypurhat | 134 | 3:00 | 113 | 8:00
| Biani Bazar | 138 | 4:00 | 136 | 12:00 | Sherpur(Bogura) | 137 | 20:00 | 127 | 9:00
| Comilla(s) | 132 | 1:00 | 129 | 18:00 | Mohastangor | 136 | 20:00 | 120 | 9:00
| Comilla(n) | 145 | 7:00 | 143 | 16:00 | Bangura | 142 | 4:00 | 132 | 8:00
| Chandpur | 143 | 23:00 | 142 | 18:00 | Rangpur | 134 | 5:00 | 117 | 9:00
| Feni | 141 | 9:00 | 138 | 17:00 | Lalmonirhat | 130 | 6:00 | 112 | 7:00
| Chowmuhani | 139 | 7:00 | 135 | 18:00 | Saidpur | 131 | 6:00 | 117 | 9:00
| Ashuganj | 140 | 11:00 | 138 | 8:00 | Purbasadipur | 132 | 6:00 | 114 | 9:00
| Daudkandi | 141 | 13:00 | 138 | 7:00 | Thakurgaon | 133 | 5:00 | 115 | 8:00
| B.Baria | 136 | 7:00 | 134 | 18:30 | Palashbari | 131 | 17:00 | 118 | 9:00
| Ramganj | 138 | 7:00 | 137 | 14:00 | Barapukuria | 135 | 4:00 | 125 | 9:00
| Chaddagram | 142 | 8:00 | 139 | 15:00 | Panchagar | 133 | 5:00 | 115 | 9:00

## L-Curve
Date | 2021-01-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 228 | 4691 | 1792 | 6483 |  |  |  | QF-LDC-11
0:30 | 175.5 | 4682 | 1861.5 | 6543.5 | Date: | 2021-01-29
1:00 | 123 | 4673 | 1931 | 6604
1:30 | 69.5 | 4498.5 | 1931 | 6429.5
2:00 | 16 | 4324 | 1931 | 6255
2:30 | 9.5 | 4182 | 1912 | 6094 | [5 empty] | Gen. at Eve. Peak | 8348 | 8348 MW (19:00 )
3:00 | 3 | 4040 | 1893 | 5933 | [6 empty] | 19:00
3:30 | 5.5 | 3999.5 | 1857.5 | 5857 | [5 empty] | Gen. at Day Peak | 6916 | 6916 MW (12:00 )
4:00 | 8 | 3959 | 1822 | 5781 | [6 empty] | 12:00
4:30 | 15.5 | 3962.5 | 1796 | 5758.5 | [5 empty] | Highest Generation | 8348
5:00 | 23 | 3966 | 1770 | 5736 | [6 empty] | 19:00
5:30 | 27.5 | 4052 | 1798 | 5850
6:00 | 32 | 4138 | 1826 | 5964
6:30 | 166.5 | 4200.5 | 1796 | 5996.5
7:00 | 301 | 4263 | 1766 | 6029
7:30 | 353 | 4447 | 1854 | 6301
8:00 | 405 | 4631 | 1942 | 6573
8:30 | 333 | 4696.5 | 1983.5 | 6680
9:00 | 261 | 4762 | 2025 | 6787
9:30 | 244 | 4750 | 2037.5 | 6787.5
10:00 | 227 | 4738 | 2050 | 6788
10:30 | 167.5 | 4706.5 | 2075.5 | 6782
11:00 | 108 | 4675 | 2101 | 6776
11:30 | 94.5 | 4700.5 | 2145.5 | 6846
12:00 | 81 | 4726 | 2190 | 6916
12:30 | 147.5 | 4898 | 2239 | 7137
13:00 | 214 | 5070 | 2288 | 7358
13:30 | 128 | 4751 | 2196 | 6947
14:00 | 42 | 4432 | 2104 | 6536
14:30 | 100 | 4286.5 | 2071.5 | 6358
15:00 | 158 | 4141 | 2039 | 6180
15:30 | 155.5 | 4085 | 2021.5 | 6106.5
16:00 | 153 | 4029 | 2004 | 6033
16:30 | 77.5 | 4117 | 1832.5 | 5949.5
17:00 | 2 | 4205 | 1661 | 5866
17:30 | 111 | 4609 | 1902.5 | 6511.5
18:00 | 220 | 5013 | 2144 | 7157
18:30 | 274 | 5337.5 | 2415 | 7752.5
19:00 | 328 | 5662 | 2686 | 8348
19:30 | 354 | 5721 | 2621 | 8342
20:00 | 288 | 5614 | 2633 | 8247 |  |  |  | Executive Engineer
20:30 | 272.5 | 5583 | 2621 | 8204 |  |  |  | Network Operation Division
21:00 | 257 | 5552 | 2609 | 8161
21:30 | 208 | 5391 | 2470.5 | 7861.5
22:00 | 159 | 5230 | 2332 | 7562 |  |  |  |  | Page 6 of 7
22:30 | 190 | 5130 | 2200 | 7330
23:00 | 221 | 5030 | 2068 | 7098
23:30 | 224.5 | 4860.5 | 1930 | 6790.5
24:00 | 228 | 4691 | 1792 | 6483
8348 MW (19:00 )
6916 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-29 |  | Energy | 167716602
[11 empty] | 2021-01-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2831 | 519 | 1123 | 1935 | 380 | 54 | 34 | 0 | 82 | 0
0:30 | 2860.5 | 496 | 1121 | 1650.5 | 500 | 56 | 17 | 0 | 80 | 0 | Date: | 2021-01-29
1:00 | 2890 | 473 | 1119 | 1366 | 620 | 58 | 0 | 0 | 78 | 0
1:30 | 2867 | 473 | 1125.5 | 1212.5 | 619.5 | 57 | 0 | 0 | 75 | 0 | [7 empty] | Total Energy | 167.7166 | Total Energy Gen 167.717 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.717 MKWHr
2:00 | 2844 | 473 | 1132 | 1059 | 619 | 56 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2845.5 | 473.5 | 1124 | 921 | 604.5 | 55.5 | 0 | 0 | 70 | 0 | [7 empty] | Energy Requirement | 167.7166
3:00 | 2847 | 474 | 1116 | 783 | 590 | 55 | 0 | 0 | 68 | 0
3:30 | 2827 | 474 | 1126.5 | 737.5 | 570 | 54 | 0 | 0 | 68 | 0 | [6 empty] | Shortage
4:00 | 2807 | 474 | 1137 | 692 | 550 | 53 | 0 | 0 | 68 | 0
4:30 | 2816 | 473.5 | 1142 | 684.5 | 520 | 53.5 | 0 | 0 | 69 | 0
5:00 | 2825 | 473 | 1147 | 677 | 490 | 54 | 0 | 0 | 70 | 0
5:30 | 2895 | 473 | 1131.5 | 741 | 485 | 54.5 | 0 | 0 | 70 | 0
6:00 | 2965 | 473 | 1116 | 805 | 480 | 55 | 0 | 0 | 70 | 0
6:30 | 2884 | 473 | 1079.5 | 957.5 | 480 | 55 | 0 | 0 | 67 | 0.5 |  |  |  |  | Coal
7:00 | 2803 | 473 | 1043 | 1110 | 480 | 55 | 0 | 0 | 64 | 1
7:30 | 2835.5 | 496.5 | 1082.5 | 1268 | 495 | 56 | 0 | 0 | 62 | 5.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2868 | 520 | 1122 | 1426 | 510 | 57 | 0 | 0 | 60 | 10
8:30 | 2808 | 520.5 | 1113 | 1553 | 560 | 57 | 0 | 0 | 51 | 17.5
9:00 | 2748 | 521 | 1104 | 1680 | 610 | 57 | 0 | 0 | 42 | 25
9:30 | 2740.5 | 520.5 | 1055 | 1725.5 | 615 | 57 | 0 | 0 | 42 | 32
10:00 | 2733 | 520 | 1006 | 1771 | 620 | 57 | 0 | 0 | 42 | 39
10:30 | 2697 | 520.5 | 1006 | 1767.5 | 620 | 54.5 | 17 | 0 | 45 | 54.5
11:00 | 2661 | 521 | 1006 | 1764 | 620 | 52 | 34 | 0 | 48 | 70
11:30 | 2697.5 | 520.5 | 1041.5 | 1770 | 620 | 52 | 34 | 0 | 48 | 62.5
12:00 | 2734 | 520 | 1077 | 1776 | 620 | 52 | 34 | 0 | 48 | 55
12:30 | 2779 | 520 | 1115 | 1884 | 635 | 55.5 | 34 | 0 | 53 | 61.5
13:00 | 2824 | 520 | 1153 | 1992 | 650 | 59 | 34 | 0 | 58 | 68
13:30 | 2824 | 520 | 1153 | 1992 | 650 | 59 | 34 | 0 | 58 | 68
14:00 | 2824 | 520 | 1153 | 1992 | 650 | 59 | 34 | 0 | 58 | 68
14:30 | 2754.5 | 519.5 | 1098.5 | 1570.5 | 625 | 59 | 34 | 0 | 54 | 54
15:00 | 2685 | 519 | 1044 | 1149 | 600 | 59 | 34 | 0 | 50 | 40
15:30 | 2670.5 | 519 | 1030 | 1127 | 584.5 | 59 | 34 | 0 | 49 | 33.5
16:00 | 2656 | 519 | 1016 | 1105 | 569 | 59 | 34 | 0 | 48 | 27
16:30 | 2749 | 519 | 967 | 1189 | 359 | 58.5 | 34 | 0 | 58 | 16
17:00 | 2842 | 519 | 918 | 1273 | 149 | 58 | 34 | 0 | 68 | 5
17:30 | 2887.5 | 613 | 1023.5 | 1615 | 149.5 | 58 | 84.5 | 0 | 78 | 2.5
18:00 | 2933 | 707 | 1129 | 1957 | 150 | 58 | 135 | 0 | 88 | 0
18:30 | 2927 | 754 | 1158.5 | 2464 | 149.5 | 56.5 | 148 | 0 | 95 | 0
19:00 | 2921 | 801 | 1188 | 2971 | 149 | 55 | 161 | 0 | 102 | 0
19:30 | 2963 | 801 | 1192 | 2894 | 149 | 55 | 184 | 0 | 104 | 0
20:00 | 2955 | 801 | 1185 | 2813 | 149 | 56 | 184 | 0 | 104 | 0
20:30 | 2948 | 801 | 1192.5 | 2769.5 | 149 | 56 | 184 | 0 | 104 | 0
21:00 | 2941 | 801 | 1200 | 2726 | 149 | 56 | 184 | 0 | 104 | 0
21:30 | 2919.5 | 801.5 | 1162.5 | 2502.5 | 169 | 56.5 | 148 | 0 | 102 | 0
22:00 | 2898 | 802 | 1125 | 2279 | 189 | 57 | 112 | 0 | 100 | 0
22:30 | 2867 | 718.5 | 1119.5 | 2107 | 259.5 | 55.5 | 107 | 0 | 96 | 0
23:00 | 2836 | 635 | 1114 | 1935 | 330 | 54 | 102 | 0 | 92 | 0
23:30 | 2833.5 | 577 | 1118.5 | 1935 | 355 | 54 | 68 | 0 | 87 | 0 | Max Temp. in Dhaka |  | 25.4° C
24:00 | 2831 | 519 | 1123 | 1935 | 380 | 54 | 34 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 167.717 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.717 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 58 | 56 | 55 | 53 | 54 | 55 | 55 | 57 | 57 | 57 | 52 | 52 | 59 | 59 | 59 | 59 | 58 | 58 |  | 55 | 55 | 56 | 56 | 57 | 54 | 54 | 1292482
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 11 | 14 | 16 | 17 | 16 | 16 | 12 | 7 | 1 | [9 empty] | 116235
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 0 | [7 empty] | 34 |  | 34 | 34 | 34 | 34 |  |  |  | 135020
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 182 | 121 | 125 | 125 | 127 | 190 | 125 | 125 | 95 | 78 | 72 | 120 | 185 | 95 | 120 | 120 | 190 | 187 |  | 193 | 193 | 192 | 193 | 190 | 125 | 125 | 3606000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 80 | 80 | 45 | 45 | 45 | 45 | 80 | 81 | 77 | 80 | 75 | 55 | 55 | 52 | 52 | 55 | 57 | 110 |  | 137 | 142 | 143 | 145 | 145 | 110 | 67 | 1999745
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2353868
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 5 | 5 | 5 | 20 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 523296
33 | Ashuganj 225 MW CCPP | 183 | 185 | 184 | 200 | 184 | 197 | 187 | 202 | 183 | 184 | 183 | 186 | 183 | 185 | 183 | 184 | 209 | 224 |  | 199 | 200 | 201 | 192 | 186 | 188 | 184 | 4638000
34 | Ashuganj 450 MW CCPP(South) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8471000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 141120
36 | Chandpur 150 MW CCPP | 90 | 92 | 90 | 95 | 96 | 96 | 95 | 95 | 91 | 94 | 87 | 95 | 86 | 96 | 96 | 86 | 96 | 93 |  | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 2208030
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 352 | 353 | 353 | 354 | 354 | 353 | 290 | 359 | 360 | 280 | 280 | 340 | 357 | 250 | 300 | 300 | 300 | 356 |  | 357 | 357 | 357 | 358 | 357 | 358 | 357 | 7926000
42 | RPCL 210MW CCPP | 102 | 102 | 102 | 103 | 103 | 103 | 103 | 104 | 104 | 104 | 102 | 98 | 99 | 99 | 98 | 97 | 96 | 97 |  | 98 | 99 | 99 | 100 | 101 | 102 | 102 | 2384320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 4 | 9 | 16 | 44 | 27 | 42 | 20 | 21 | 15 | 3 | [9 empty] | 202080
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 713000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 40 | 40 | 71 |  | 71 | 71 | 71 | 70 | 70 | 70 | 71 | 1654080
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 80 | 50 | 100 | 80 | 80 | 80 | 80 | 80 |  | 120 | 50 | 30 | 30 | 30 | 30 | 30 | 2474100
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [17 empty] | 170000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 5 | 5 | [19 empty] | 51840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 2580500
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 48 | 48 | 50 | 19 | 45 |  | 48 | 53 | 53 | 53 | 53 | 53 | 53 | 1198800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 184200
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 290 | 300 | 310 | 310 | 300 | 320 | 300 | 290 | 290 | 300 | 310 | 260 | 280 | 280 | 295 | 350 |  | 325 | 320 | 310 | 320 | 300 | 290 | 300 | 7472050
| Bibiyana South 400 MW | 397 | 405 | 405 | 405 | 405 | 390 | 385 | 390 | 405 | 415 | 417 | 417 | 410 | 412 | 415 | 415 | 415 | 415 |  | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 9777400
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 17 | 35 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 17 | 17 |  | 643621
59 | Tangail Palli Power Gen 22 MW | 24 | 0 |  |  |  |  | 6 | 23 | 20 | 18 | 19 | 19 | 18 | 19 | 16 | 6 | 6 | 10 |  | 24 | 18 | 20 | 24 | 24 | 25 |  | 347280
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467568
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 16 | 16 | 16 | 19 | 19 | 19 | 376524
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 517536
63 | Impoprt (Tripura) | 78 | 72 | 68 | 68 | 70 | 70 | 64 | 60 | 42 | 42 | 48 | 48 | 58 | 58 | 50 | 48 | 68 | 88 |  | 102 | 104 | 104 | 104 | 100 | 92 | 82 | 1677120
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 30 | 30 | 28 | 26 | 22 | 22 | 20 | 20 | 31 | 35 | 38 | 38 | 38 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 874560
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 16 | 18 | 18 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 473760
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 231840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 529920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 15 | 8 | 8 | 7 | 7 | 12 | 12 | 12 |  | 16 | 31 | 32 | 29 | 32 | 32 | 32 | 540000
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 20 | 15 | 15 | 15 | 421000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 829700
73 | Ghorashal 108MW PP (Regent) | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 106 | 106 | 104 | 104 | 108 | 108 | 105 | 105 | 108 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2566590
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [6 empty] | 15 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 436800
| Manikgonj 162MW PP(MPGL) | 144 | 108 | 72 | 54 | 54 | 108 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 138 | 108 | 108 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 108 | 3088800
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 10 |  | 40 | 40 | 40 | 40 | 30 | 7 |  | 187200
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [19 empty] | 16 | 48 | 48 | 48 | 10 |  |  | 126720
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 2 | 23 | 16 | 16 | 16 | 36 | 16 | 16 | 8 | 8 | 13 |  | 64 | 82 | 82 | 82 | 35 | 8 |  | 543360
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 27000
| Jodiac Power | [16 empty] | 4 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 86500
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 64 | 16 |  |  |  |  | 22 | 48 | 54 | 98 | 90 | 80 | 80 | 48 | 32 | 32 | 32 | 35 |  | 75 | 101 | 101 | 101 | 100 | 98 | 80 | 1389144
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 24 | 21 | 22 | 0 | 0 | 10 | 22 | 26 | 33 | 36 | 37 | 36 | 33 | 35 | 18 | 36 | 48 | 49 |  | 49 | 49 | 50 | 39 | 36 | 53 | 70 | 820254
86 | Meghnaghat CCPP(Summit) | 240 | 300 | 295 | 310 | 295 | 275 | 240 | 240 | 240 | 270 | 255 | 280 | 235 | 280 | 280 | 245 | 310 | 310 |  | 280 | 275 | 290 | 280 | 280 | 285 | 260 | 6584524
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 6 | 7 | 7 | 7 | 7 | 41 | 14 |  |  | 2 | 7 |  | 7 | 7 | 7 | 7 |  |  |  | 164160
| Meghnaghat 104 MW PP (OPCL) | 22 | 0 |  |  |  |  | 24 | 72 | 91 | 91 | 91 | 91 | 91 | 72 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 60 | 52 | 1082880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 20 | 10 | [12 empty] | 22800
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1168200
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1241952
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 3 | 7 |  | 7 | 7 | 7 | 7 |  |  |  | 38160
95 | Patenga 50MW PP (Baraka) | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 17 | [9 empty] | 6 |  | 43 | 45 | 46 | 48 | 44 | 45 | 25 | 419040
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 1 | 11 |  | 12 | 12 | 12 | 12 |  |  |  | 52800
97 | katpotti 52 MW | [19 empty] | 6 | 6 | 6 | 6 | 6 |  |  | 27648
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | 0 |  |  |  |  | 3 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 15 | 16 |  | 40 | 40 | 40 | 40 | 15 | 22 | 15 | 584610
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 340981
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 10350
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 390600
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 214 | 152 | 51 |  |  |  |  | 333990
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 160 | 120 | 80 | 50 | 50 | 62 | 120 | 144 | 182 | 200 | 200 | 200 | 200 | 200 | 140 | 140 | 140 | 178 |  | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 3928800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 9 | 74 | 95 | 86 | 49 | 68 | 72 | 23 | 16 | 16 | 19 |  | 65 | 65 | 65 | 65 | 50 |  |  | 807840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 70 | 40 | 10 | 10 | 10 | 10 | 50 | 70 | 70 | 30 | 30 | 36 | 90 | 10 | 10 | 10 | 10 | 84 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1272960
116 | Chandpur 200MW (Desh energy) | 17 | 0 | [17 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 129120
117 | Ashuganj 150MW PP (Midland) | 128 | 70 | 10 | 10 | 10 | 25 | 76 | 102 | 103 | 97 | 103 | 108 | 108 | 108 | 50 | 50 | 50 | 71 |  | 120 | 130 | 132 | 133 | 135 | 135 | 100 | 2213018
118 | Bibiyana-III 400 MW CCPP | [19 empty] | 15 | 120 | 120 | 120 | 120 | 120 | 120 | 579000
| Jamalpur 115 MW PP (United) | [12 empty] | 5 | 8 |  |  | 8 | 45 |  | 24 | [6 empty] | 92400
| Anwara 300 MW PP (United) | 251 | 197 | 142 | 106 | 106 | 122 | 160 | 213 | 213 | 212 | 214 | 216 | 305 | 198 | 160 | 160 | 160 | 251 |  | 251 | 251 | 251 | 252 | 252 | 252 | 252 | 4995600
| Juldah unit-2 (Acorn) | 70 | 50 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 80 | 80 | 90 | 90 | 20 | 20 | 20 | 20 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1777920
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4673 | 4324 | 4040 | 3959 | 3966 | 4138 | 4263 | 4631 | 4762 | 4738 | 4675 | 4726 | 5070 | 4432 | 4141 | 4029 | 4205 | 5013 |  | 5662 | 5721 | 5614 | 5552 | 5230 | 5030 | 4691 | 116152570
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 39 |  | 115 | 115 | 115 | 115 | 36 | 26 |  | 444480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 9 | [6 empty] | 6350
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 70 | 70 | 70 | 70 | 70 | 70 | 53 | 17 | 17 | 17 | 28 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 988800
130
131
132 | United Payra Power Ltd. | [19 empty] | 41 | 35 | 35 | 35 |  |  |  | 116400
133 | Bhola Nutan Biddut BD LTD (GAS) | 17 | 23 | 18 | 17 | 18 | 0 | [20 empty] | 144273
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 12 |  | 82 | 96 | 110 | 110 | 48 | 48 |  | 421440
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 33 | 32 | 21 | 31 | 31 | 31 | 32 | 32 | 32 | 31 | 32 | 34 | 78 | 55 | 54 | 52 |  |  |  | 75 | 79 | 81 | 86 | 32 | 32 | 31 | 976730
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 15 | 15 | 15 | 14 | 16 | 15 | 14 | 20 | 19 | 20 | 21 | 22 | 18 | 15 | 15 | 12 | 24 |  | 25 | 25 | 26 | 26 | 26 | 24 | 24 | 449400
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 24 | 8 |  |  |  |  | 63000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 67 | 32 | 32 | 15 |  |  |  | 130752
146 | Bheramara HVDC | 473 | 473 | 474 | 474 | 473 | 473 | 473 | 520 | 521 | 520 | 521 | 520 | 520 | 521 | 519 | 519 | 519 | 707 |  | 801 | 801 | 801 | 801 | 802 | 635 | 519 | 13718545
147 | Bheramara 410 MW CCPP | 340 | 340 | 345 | 300 | 300 | 380 | 350 | 390 | 345 | 350 | 345 | 375 | 340 | 345 | 340 | 345 | 390 | 420 |  | 360 | 360 | 370 | 345 | 340 | 340 | 340 | 8529984
148 | Payra 1320 MW | 470 | 470 | 440 | 400 | 340 | 330 | 330 | 360 | 460 | 470 | 470 | 470 | 500 | 480 | 450 | 420 | [7 empty] | 40 | 180 | 230 | 8241000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 |  | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 3670700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 175 | 177 | 177 | 180 | 185 | 185 | 179 | 192 | 176 | 173 | 173 | 181 | 171 | 155 | 182 | 151 | 165 | 186 |  | 179 | 169 | 173 | 188 | 173 | 175 | 177 | 4448264
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 186 | 187 | 189 | 193 | 195 | 168 | 178 | 165 | 162 | 160 | 177 | 220 | 159 | 159 | 159 | 182 | 212 |  | 205 | 198 | 195 | 201 | 185 | 186 | 186 | 4648336
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [26 empty] | 0
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 518160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 178344
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 14 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  |  | 244440
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 2 | 36 | 43 | 25 | 25 | 49 |  |  |  | 8 | 8 |  | 25 | 25 | 25 | 25 |  |  |  | 279360
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 101 |  | 102 | 102 | 102 | 102 | 102 | 102 | 34 | 903424
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 3 | 35 | 35 | 35 | 35 | 35 | 35 | 65 |  | 92 | 92 | 92 | 92 | 92 |  |  | 713376
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 35 | 35 | 35 | 35 | 35 | 56 | 72 | 95 |  | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 1058400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8 | 35 | 55 |  | 112 | 112 | 112 | 112 | 112 | 35 | 4 | 640320
177 | Sympa Solar Power 8MW | [8 empty] | 2 | 3 | 4 | 4 | 5 | 5 | 3 | 2 | 1 | [9 empty] | 29754
178
178