## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-01 | Monday
|  |  | Date (day): | 2021-02-01 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11863.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12962 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-01-31 | 2021-02-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 105 | 107 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2021-07-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 276 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 24 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 260 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 98 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 73 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 170 | 150 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 60 | 24 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 40 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 82 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 17 | 35 | 35 |  |  | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 135 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 130 | 117 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 50 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 70 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  |  | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2051 | 2130 | 3293 | 3543 | 108 | 2267
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 27 | 5 | 46 | 46
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 61 | 42 | 68 | 68 | 162 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 102 | 85 | 102 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 8 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 28 | 25 | 40
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 97 | 97 |  | 11 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 307 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 44 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 671 | 811 | 1157 | 1264 | 897 | 126
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 130 | 130
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 233 | 184 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 350 | 350
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 23 | 26 | 26 |  | 19 | Machine problem
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 8 | 8 | 47 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 137 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 81 | 70 | 100 | 100 |  | 63 | ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 34 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 19 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 104 | 135 | 146
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 22 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 4 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 26 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1111 | 1152 | 1750 | 2011 | 497 | 442
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 92 | 99 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 81 | 81 | 81 | 81 |  |  | Engine problem
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 24 | 45 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 17 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 484 | 470 | 601.6 | 550 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 20 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 30 |  |  | Under maint.
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 48 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under maint
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 66 | 69 | 74 | 74 |  | 12 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 100 | 100 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 251 | 252 | 320 | 320 |  | 400
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 415 | 415 | 415 | 415 |  |  | RRT
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1301 | 1300 | 1418 | 1448 | 0 | 1022
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 703 | 891 | 441 | 441
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 3 | 12 | 70 | 70 |  | 39
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 380 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 100 | 105 | 95 | 95 |  | 10
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1187 | 1537 | 1346 | 1632 | 0 | 78
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 27 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 72 | 83 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 530 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Machine problem.
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 544 | 656 | 897 | 997 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 14 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 162 | 220 | 220 | 220
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 179 | 220 | 220 | 220
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint. |  | 13/2/2021
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 481 | 869 | 1130 | 1254 | 821 | 439
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 5 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 159 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7989 | 9188 | 11863.6 | 12962 | 2539 | 4789
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7642.9375 | 8790 | 11349.7 | 12400.5202
| A. |  | 2021-01-31 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 9188 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5628 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9188 | MW
| 3 | Day peak Generation : |  |  | 7989 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8790 | MW
| 4 | Evening peak Generation : |  |  | 9188 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 179.7854 | MKWHr | By Solar | 0.44304 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 95.205 | MKWHr |  | By Oil: | 49.5038 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.3826 | MKWHr |  | By Hydro: | 1.2327 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2539 | MW | Dhaka | 2964 | 2964 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4789 | MW | Chittagong | 899 | 899 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7328 | MW | Khulna | 1113 | 1113 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 811.91 | MMCFD |  |  | Rajshahi | 989 | 989 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 96676525.024 | ii) Oil : | Taka | 306512513.77 | Comilla | 730 | 730 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 66910959 | Total | Taka | 470099997.794 | Mymensingh | 793 | 793 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.488 | MKWHr. | Sylhet | 333 | 333 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 126 | MW (E to W) at | 19:00 | hrs | Barisal | 247 | 247 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -367 | MW at | 9:00 | hrs | Rangpur | 722 | 722 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 22.1° C |  |  | Total | 8790 | 8790 |  | 0
| B. |  | 2021-02-01 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 24.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12962 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7900 | MW
| 4 | Reserve(Generation end) |  |  |  | 3762 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 180.0203 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5589 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.8727 | MKWHr. | ii) HVDC Flow at Peak Time |  | 891 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1456 | MKWHr. | iii) Maximum HVDC Flow : |  | 895 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.92 |  | (b) Today: | 95.68 |  | (c) Rule Curve: |  | 97
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-01-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 326 |  | 0 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 100 | 0 | 0 | 0 | 350 | 175 | 8 | 85 | 25 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 82 | 109 | 0 | 20 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 305 | 16 | 11 | 0 | 37 | 0 | 0 | 160 | 0 | 0 | 0 | 50 | 17 | 80 | 200 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 8 | 70 | 416 | 0 | 0 | 126 | 0 | 100 |  | 514 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 57 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 440 | 0 | 0 | 0 |  | 4413 | 1919 | 6332 | 2843 | 514 | 1081 | 1168 | 590 | 54 | 0 | 82 | 0 | 0 | 95.95
2:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 325 |  | 0 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 90 | 25 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 80 | 109 | 0 | 20 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 32 | 0 | 0 | 160 | 0 | 0 | 0 | 50 | 17 | 80 | 200 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 8 | 70 | 415 | 0 | 0 | 126 | 0 | 100 |  | 513 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 260 | 0 | 0 | 0 |  | 4426 | 1627 | 6053 | 2800 | 513 | 1048 | 1149 | 410 | 53 | 0 | 80 | 0 | 0 | 95.94
3:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 288 |  | 0 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 189 | 8 | 85 | 25 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 80 | 109 | 0 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 20 | 17 | 30 | 200 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 8 | 70 | 415 | 0 | 0 | 126 | 0 | 100 |  | 514 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 250 | 0 | 0 | 0 |  | 4162 | 1620 | 5782 | 2766 | 514 | 1015 | 955 | 400 | 52 | 0 | 80 | 0 | 0 | 95.94
4:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 288 |  | 0 | 0 | 275 | 0 | 16 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 17 | 33 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 178 | 8 | 90 | 25 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 78 | 109 | 0 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 20 | 17 | 30 | 200 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 8 | 20 | 415 | 0 | 0 | 126 | 0 | 100 |  | 513 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 250 | 0 | 0 | 0 |  | 4027 | 1620 | 5647 | 2752 | 513 | 1015 | 838 | 400 | 51 | 0 | 78 | 0 | 0 | 95.93
5:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 290 |  | 0 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 190 | 8 | 90 | 22 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 78 | 109 | 0 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 20 | 17 | 30 | 200 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 8 | 20 | 416 | 0 | 0 | 126 | 0 | 100 |  | 513 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 250 | 0 | 0 | 0 |  | 4033 | 1595 | 5628 | 2751 | 513 | 1003 | 833 | 400 | 50 | 0 | 78 | 0 | 0 | 95.93
6:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 315 |  | 0 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 196 | 8 | 90 | 22 | 8 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 76 | 108 | 0 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 320 | 16 | 11 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 20 | 17 | 34 | 200 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 8 | 20 | 415 | 0 | 0 | 126 | 0 | 100 |  | 513 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 250 | 0 | 0 | 0 |  | 4203 | 1736 | 5939 | 2972 | 513 | 1049 | 879 | 400 | 50 | 0 | 76 | 0 | 0 | 95.92
7:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 329 |  | 0 | 0 | 300 | 0 | 30 | 3 | 0 | 0 | 155 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 18 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 20 | 13 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 89 | 22 | 8 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 80 | 109 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 32 | 0 | 0 | 140 | 0 | 0 | 1 | 20 | 17 | 78 | 270 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 8 | 35 | 415 | 13 | 1 | 126 | 0 | 100 |  | 607 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 280 | 0 | 0 | 0 |  | 4497 | 1834 | 6331 | 3020 | 607 | 1006 | 1136 | 430 | 50 | 0 | 80 | 2 | 0 | 95.8
8:00 | 0 | 0 | 0 | 180 | 0 | 109 | 0 | 0 | 329 |  | 0 | 0 | 300 | 4 | 48 | 20 | 0 | 0 | 155 | 6 | 0 | 0 | 53 | 0 | 0 | 0 | 17 | 17 | 11 | 22 | 25 | 20 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 18 | 100 | 0 | 0 | 0 | 350 | 200 | 8 | 95 | 22 | 8 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 84 | 108 | 2 | 0 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 32 | 0 | 0 | 192 | 0 | 16 | 0 | 50 | 17 | 127 | 280 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 8 | 60 | 415 | 45 | 11 | 126 | 0 | 100 |  | 703 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 179 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 310 | 0 | 0 | 35 |  | 4859 | 2167 | 7026 | 3109 | 703 | 1021 | 1588 | 460 | 50 | 0 | 84 | 11 | 0 | 95.91
9:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 363 |  | 0 | 0 | 300 | 7 | 64 | 40 | 0 | 0 | 190 | 30 | 3 | 32 | 60 | 0 | 0 | 0 | 54 | 17 | 43 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 52 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 7 | 100 | 0 | 0 | 0 | 350 | 189 | 8 | 85 | 26 | 8 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 88 | 109 | 25 | 0 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 32 | 0 | 0 | 200 | 0 | 76 | 0 | 100 | 17 | 128 | 280 | 14 | 2 | 0 | 2 | 305 | 4 | 0 | 0 | 21 | 76 | 415 | 62 | 24 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 185 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 1 | 35 | 390 | 0 | 0 | 0 |  | 5394 | 2168 | 7562 | 3049 | 703 | 1049 | 2023 | 539 | 52 | 32 | 88 | 27 | 0 | 95.9
10:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 319 |  | 0 | 0 | 260 | 7 | 84 | 55 | 0 | 0 | 145 | 60 | 24 | 48 | 60 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 24 | 17 | 25 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 11 | 0 | 13 | 0 | 0 | 25 | 17 | 7 | 80 | 0 | 0 | 0 | 325 | 184 | 8 | 85 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 88 | 107 | 74 | 22 | 2 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 37 | 0 | 0 | 200 | 0 | 109 | 12 | 88 | 17 | 125 | 225 | 40 | 17 | 0 | 3 | 266 | 17 | 0 | 0 | 26 | 95 | 415 | 73 | 36 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 164 | 0 | 0 | 90 | 0 | 0 | 0 | 5 | 0 | 1 | 35 | 450 | 0 | 0 | 0 |  | 5384 | 2242 | 7626 | 2824 | 703 | 960 | 2287 | 599 | 50 | 61 | 88 | 54 | 0 | 95.9
11:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 319 |  | 0 | 0 | 285 | 7 | 98 | 55 | 0 | 0 | 145 | 60 | 24 | 48 | 60 | 0 | 0 | 0 | 54 | 17 | 36 | 22 | 25 | 24 | 17 | 25 | 0 | 0 | 59 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 25 | 17 | 7 | 80 | 0 | 0 | 0 | 300 | 186 | 8 | 83 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 90 | 108 | 78 | 22 | 2 | 30 | 0 | 47 | 47 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 7 | 300 | 16 | 11 | 0 | 47 | 0 | 0 | 200 | 0 | 113 | 15 | 90 | 17 | 123 | 223 | 24 | 17 | 0 | 4 | 255 | 17 | 0 | 0 | 26 | 100 | 415 | 72 | 40 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 163 | 0 | 0 | 100 | 0 | 0 | 0 | 5 | 0 | 2 | 35 | 480 | 0 | 0 | 0 |  | 5425 | 2285 | 7710 | 2788 | 703 | 1010 | 2302 | 630 | 59 | 65 | 90 | 63 | 0 | 95.9
12:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 322 |  | 0 | 0 | 260 | 7 | 98 | 55 | 0 | 0 | 170 | 60 | 24 | 48 | 68 | 0 | 0 | 0 | 54 | 35 | 36 | 22 | 25 | 32 | 17 | 25 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 27 | 20 | 5 | 80 | 0 | 0 | 0 | 300 | 233 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 96 | 92 | 81 | 22 | 2 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 305 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 130 | 15 | 90 | 17 | 128 | 251 | 24 | 17 | 0 | 4 | 307 | 17 | 0 | 0 | 26 | 100 | 415 | 72 | 46 | 144 | 0 | 100 |  | 703 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 72 | 0 | 172 | 0 | 0 | 100 | 0 | 0 | 0 | 5 | 0 | 4 | 35 | 450 | 0 | 0 | 0 |  | 5618 | 2371 | 7989 | 2920 | 703 | 1090 | 2380 | 600 | 61 | 68 | 96 | 71 | 0 | 95.89
13:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 302 |  | 0 | 0 | 245 | 41 | 98 | 55 | 0 | 0 | 155 | 83 | 40 | 48 | 72 | 0 | 0 | 0 | 54 | 35 | 36 | 22 | 25 | 32 | 17 | 25 | 0 | 0 | 60 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 17 | 0 | 51 | 0 | 0 | 33 | 20 | 5 | 80 | 0 | 0 | 0 | 320 | 184 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 96 | 86 | 81 | 20 | 2 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 130 | 14 | 90 | 17 | 128 | 252 | 45 | 17 | 0 | 4 | 307 | 39 | 0 | 0 | 42 | 100 | 415 | 72 | 44 | 144 | 0 | 100 |  | 704 | 0 | 345 | 0 | 39 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 80 | 0 | 213 | 0 | 0 | 102 | 0 | 0 | 0 | 5 | 0 | 5 | 35 | 420 | 0 | 0 | 0 |  | 5707 | 2418 | 8125 | 2906 | 704 | 1074 | 2541 | 570 | 60 | 105 | 96 | 69 | 8125 | 95.89
14:00 | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 309 |  | 0 | 0 | 260 | 65 | 99 | 55 | 0 | 0 | 70 | 100 | 40 | 0 | 73 | 0 | 0 | 0 | 54 | 17 | 36 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 62 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 0 | 51 | 0 | 12 | 44 | 20 | 5 | 80 | 0 | 0 | 0 | 280 | 184 | 8 | 73 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 96 | 85 | 81 | 22 | 2 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 130 | 12 | 100 | 17 | 128 | 193 | 35 | 0 | 0 | 3 | 307 | 54 | 0 | 0 | 46 | 100 | 416 | 72 | 40 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 65 | 0 | 217 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 4 | 35 | 400 | 0 | 0 | 0 |  | 5540 | 2288 | 7828 | 2696 | 703 | 1050 | 2551 | 550 | 62 | 59 | 96 | 61 | 0 | 95.88
15:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 310 |  | 0 | 0 | 275 | 60 | 99 | 55 | 0 | 0 | 75 | 77 | 0 | 0 | 61 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 34 | 0 | 0 | 0 | 20 | 5 | 100 | 0 | 0 | 0 | 280 | 184 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 92 | 86 | 81 | 22 | 1 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 130 | 9 | 100 | 17 | 123 | 124 | 35 | 0 | 0 | 2 | 307 | 54 | 0 | 0 | 46 | 100 | 415 | 72 | 33 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 35 | 0 | 162 | 0 | 0 | 105 | 0 | 27 | 0 | 5 | 0 | 3 | 35 | 400 | 0 | 0 | 0 |  | 5283 | 2183 | 7466 | 2594 | 703 | 1013 | 2362 | 550 | 63 | 41 | 92 | 48 | 0 | 95.88
16:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 287 |  | 0 | 0 | 260 | 0 | 99 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 17 | 33 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 0 | 20 | 8 | 100 | 0 | 0 | 0 | 280 | 184 | 8 | 72 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 90 | 85 | 81 | 22 | 1 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 117 | 5 | 50 | 17 | 125 | 191 | 16 | 0 | 0 | 1 | 307 | 17 | 0 | 0 | 26 | 100 | 415 | 70 | 17 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 36 | 0 | 161 | 0 | 0 | 70 | 0 | 69 | 0 | 70 | 0 | 1 | 92 | 400 | 0 | 0 | 0 |  | 4974 | 2299 | 7273 | 2649 | 703 | 999 | 2172 | 550 | 63 | 22 | 90 | 25 | 0 | 95.87
17:00 | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 288 |  | 0 | 0 | 285 | 0 | 99 | 40 | 0 | 0 | 75 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 17 | 0 | 0 | 0 | 20 | 16 | 100 | 0 | 0 | 0 | 280 | 184 | 8 | 76 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 8 | 33 | 21 | 84 | 103 | 64 | 22 | 0 | 30 | 0 | 50 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 101 | 1 | 50 | 17 | 128 | 190 | 16 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 26 | 100 | 415 | 53 | 3 | 144 | 0 | 100 |  | 703 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 37 | 0 | 159 | 0 | 0 | 70 | 0 | 108 | 0 | 70 | 0 | 0 | 113 | 400 | 0 | 0 | 0 |  | 4980 | 2347 | 7327 | 2680 | 703 | 1022 | 2201 | 549 | 62 | 22 | 84 | 4 | 0 | 95.87
18:00 | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 289 |  | 0 | 0 | 285 | 13 | 99 | 40 | 0 | 0 | 75 | 12 | 7 | 64 | 73 | 0 | 0 | 0 | 54 | 17 | 25 | 22 | 25 | 18 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 10 | 17 | 0 | 20 | 16 | 100 | 0 | 0 | 0 | 280 | 193 | 8 | 76 | 5 | 5 | 0 | 51 | 0 | 42 | 4 | 19 | 11 | 33 | 21 | 106 | 105 | 65 | 22 | 0 | 30 | 0 | 50 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 112 | 0 | 0 | 200 | 0 | 100 | 0 | 50 | 20 | 125 | 150 | 16 | 9 | 0 | 0 | 307 | 17 | 0 | 17 | 26 | 100 | 415 | 53 | 0 | 144 | 0 | 100 |  | 890 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 35 | 10 | 86 | 25 | 0 | 0 | 16 | 6 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 50 | 0 | 159 | 0 | 0 | 105 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 410 | 0 | 0 | 0 |  | 5328 | 2965 | 8293 | 2662 | 890 | 1032 | 2650 | 560 | 42 | 351 | 106 | 0 | 0 | 95.86
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 276 |  | 0 | 0 | 260 | 24 | 100 | 55 | 0 | 0 | 150 | 24 | 40 | 82 | 73 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 8 | 30 | 5 | 20 | 28 | 100 | 0 | 0 | 0 | 280 | 184 | 8 | 70 | 23 | 5 | 0 | 51 | 0 | 42 | 0 | 19 | 11 | 33 | 21 | 104 | 99 | 81 | 22 | 0 | 20 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 135 | 0 | 0 | 200 | 0 | 117 | 0 | 100 | 34 | 137 | 252 | 45 | 50 | 0 | 0 | 307 | 44 | 0 | 4 | 26 | 100 | 415 | 70 | 0 | 144 | 0 | 100 |  | 891 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 10 | 12 | 24 | 0 | 27 | 16 | 0 | 0 | 0 | 50 | 14 | 100 | 25 | 0 | 0 | 52 | 28 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 83 | 0 | 179 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 0 | 0 | 0 |  | 5863 | 3325 | 9188 | 2895 | 891 | 1093 | 3043 | 680 | 42 | 440 | 104 | 0 | 0 | 95.85
19:30 | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 278 |  | 0 | 0 | 285 | 24 | 100 | 55 | 0 | 0 | 100 | 24 | 40 | 98 | 73 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 0 | 0 | 18 | 20 | 29 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 70 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 106 | 106 | 81 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 167 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 34 | 146 | 252 | 25 | 17 | 0 | 0 | 307 | 17 | 0 | 0 | 26 | 100 | 416 | 72 | 0 | 144 | 0 | 100 |  | 892 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 28 | 48 | 0 | 0 | 0 | 50 | 0 | 100 | 25 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 83 | 0 | 188 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 5824 | 3309 | 9133 | 2919 | 892 | 1097 | 3007 | 700 | 47 | 365 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 279 |  | 0 | 0 | 285 | 24 | 100 | 55 | 0 | 0 | 100 | 24 | 16 | 98 | 73 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 0 | 0 | 18 | 20 | 31 | 100 | 0 | 0 | 0 | 350 | 190 | 8 | 70 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 102 | 81 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 148 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 34 | 144 | 255 | 25 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 26 | 100 | 416 | 73 | 0 | 144 | 0 | 100 |  | 891 | 0 | 350 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 100 | 25 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 83 | 0 | 190 | 0 | 0 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 5698 | 3183 | 8881 | 2933 | 891 | 1091 | 2851 | 700 | 47 | 266 | 102 | 0 | 0 | 95.85
21:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 277 |  | 0 | 0 | 270 | 24 | 100 | 55 | 0 | 0 | 100 | 21 | 0 | 64 | 73 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 51 | 0 | 0 | 19 | 20 | 36 | 100 | 0 | 0 | 0 | 350 | 191 | 8 | 70 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 98 | 72 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 320 | 16 | 11 | 0 | 168 | 0 | 0 | 200 | 0 | 125 | 0 | 100 | 34 | 148 | 258 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 26 | 100 | 415 | 72 | 0 | 144 | 0 | 100 |  | 894 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 85 | 0 | 198 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 5572 | 3100 | 8672 | 2957 | 894 | 1102 | 2655 | 700 | 47 | 215 | 102 | 0 | 0 | 95.85
22:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 277 |  | 0 | 0 | 245 | 0 | 100 | 30 | 0 | 0 | 95 | 0 | 0 | 16 | 75 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 19 | 20 | 39 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 64 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 94 | 48 | 22 | 0 | 30 | 0 | 48 | 47 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 170 | 0 | 0 | 200 | 0 | 55 | 0 | 100 | 34 | 148 | 252 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 415 | 70 | 0 | 144 | 0 | 100 |  | 895 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 83 | 0 | 188 | 0 | 0 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 15 | 0 | 0 |  | 5234 | 2957 | 8191 | 2900 | 895 | 1107 | 2312 | 700 | 59 | 116 | 102 | 0 | 0 | 95.84
23:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 277 |  | 0 | 0 | 260 | 0 | 100 | 15 | 0 | 0 | 95 | 0 | 0 | 16 | 67 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 100 | 0 | 0 | 0 | 350 | 185 | 8 | 72 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 90 | 94 | 8 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 52 | 0 | 0 | 200 | 0 | 15 | 0 | 100 | 34 | 150 | 252 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 415 | 29 | 0 | 144 | 0 | 100 |  | 895 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 86 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 510 | 28 | 0 | 0 |  | 4943 | 2588 | 7531 | 2884 | 895 | 1104 | 1741 | 660 | 61 | 96 | 90 | 0 | 0 | 95.84
24:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 303 |  | 0 | 0 | 245 | 0 | 48 | 0 | 0 | 0 | 95 | 0 | 0 | 16 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 63 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 82 | 96 | 8 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 295 | 16 | 11 | 0 | 31 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 34 | 150 | 252 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 415 | 0 | 0 | 144 | 0 | 100 |  | 610 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 88 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 470 | 33 | 0 | 0 |  | 4778 | 2123 | 6901 | 2842 | 610 | 1153 | 1493 | 620 | 61 | 40 | 82 | 0 | 0 | 95.83
KWH | 0 | 0 | 0 | 4299750 | 0 | 2528954 | 0 | 0 | 7274000 |  | 0 | 0 | 6634036 | 328320 | 1699320 | 773131 | 0 | 0 | 3017000 | 598080 | 266112 | 586560 | 1392603 | 0 | 0 | 0 | 802440 | 217229 | 438424 | 495684 | 600000 | 641160 | 574600 | 801400 | 0 | 0 | 1232722 | 0 | 0 | 0 | 143933 | 0 | 0 | 0 | 0 |  | 291120 | 0 | 542981 | 16440 | 72000 | 406560 | 464400 | 603360 | 2412184 | 0 | 0 | 0 | 7977000 | 4607000 | 200727 | 1911180 | 390888 | 166560 | 0 | 1243498 | 0 | 59288 | 12010 | 465372 | 255420 | 821300 | 465560 | 2145600 | 2415400 | 1042560 | 483336 | 12050 | 715000 | 0 | 1144200 | 1168200 | 0 | 0 | 0 | 1674240 | 0 | 0 | 0 | 0 | 125820 | 7450950 | 392448 | 264000 | 0 | 1492908 | 0 | 0 | 4212000 | 0 | 1618560 | 88020 | 1695360 | 537600 | 2721527 | 5400000 | 403200 | 174900 | 0 | 24600 | 6498545 | 353316 | 0 | 22800 | 541800 | 1961280 | 10112300 | 1062720 | 294000 | 3401280 | 0 | 2400000 |  | 16872727 | 0 | 8528256 | 0 | 441600 | 0 | 0 | 0 | 5760 | 47232 | 27000 | 0 | 373800 | 122496 | 0 | 0 | 0 | 94896 | 18242 | 559288 | 237280 | 0 | 0 | 398880 | 31154 | 520320 | 0 | 204012 | 0 | 0 | 3661500 | 0 | 0 | 0 | 0 | 4113809 | 0 | 949273 | 0 | 4487355 | 0 | 0 | 1394400 | 0 | 817344 | 0 | 850560 | 0 | 24368 | 1395936 | 10721100 | 65236 | 0 | 40800 |  | 122780826 | 57004624 | 179785450 | 69715814 | 16872727 | 25489138 | 47558410 | 14382600 | 1232722 | 1945401 | 2145600 | 443038 | 0
Fuel Cost | 0 | 0 | 0 | 6320632.5 | 0 | 3338219.28 | 0 | 0 | 7492220 |  | 0 | 0 | 7363779.96 | 2491948.8 | 11708314.8 | 6540688.26 | 0 | 0 | 5219410 | 4503542.4 | 2426941.44 | 5771750.4 | 12839799.66 | 0 | 0 | 0 | 5857812 | 1679180.17 | 4322860.64 | 371763 | 450000 | 0 | 0 | 0 | 0 | 0 | 332834.94 | 0 | 0 | 0 | 1337137.57 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5266915.7 | 157002 | 626400 | 3219955.2 | 585144 | 1791979.2 | 3570032.32 | 0 | 0 | 0 | 7977000 | 4238440 | 258937.83 | 2197857 | 441703.44 | 233184 | 0 | 2126381.58 | 0 | 598808.8 | 114695.5 | 591022.44 | 191565 | 1437275 | 349170 | 16092000 | 2560324 | 9466444.8 | 613836.72 | 192077 | 1172600 | 0 | 2036676 | 1822392 | 0 | 0 | 0 | 3197798.4 | 0 | 0 | 0 | 0 | 256672.8 | 7525459.5 | 294336 | 200640 | 0 | 11286384.48 | 0 | 0 | 21902400 | 0 | 15926630.4 | 1028953.8 | 13817184 | 5832960 | 19186765.35 | 5022000 | 3677184 | 1652805 | 0 | 0 | 49129000.2 | 3077382.36 | 0 | 227544 | 4643226 | 13062124.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97186907.52 | 0 | 8954668.8 | 0 | 3470976 | 0 | 0 | 0 | 60422.4 | 494991.36 | 281340 | 0 | 579390 | 1195560.96 | 0 | 0 | 0 | 933776.64 | 185338.72 | 4949698.8 | 1827056 | 0 | 0 | 3865147.2 | 302193.8 | 999014.4 | 0 | 154437.084 | 0 | 0 | 19845330 | 0 | 0 | 0 | 0 | 5430227.88 | 0 | 1423909.5 | 0 | 5250205.35 | 0 | 0 | 14557536 | 0 | 7756594.56 | 0 | 6600345.6 | 0 | 269266.4 | 10315967.04 | 47065629 | 0 | 0 | 0 |  | 341246106.44 | 243955931.014 | 585202037.454 | 63594290.534 | 97186907.52 | 33082234.49 | 287948617.15 | 66910959 | 332834.94 | 18563896.62 | 16092000 | 1490297.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 322 |  | 0 | 0 | 260 | 7 | 98 | 55 | 0 | 0 | 170 | 60 | 24 | 48 | 68 | 0 | 0 | 0 | 54 | 35 | 36 | 22 | 25 | 32 | 17 | 25 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 27 | 20 | 5 | 80 | 0 | 0 | 0 | 300 | 233 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 16 | 96 | 92 | 81 | 22 | 2 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 305 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 130 | 15 | 90 | 17 | 128 | 251 | 24 | 17 | 0 | 4 | 307 | 17 | 0 | 0 | 26 | 100 | 415 | 72 | 46 | 144 | 0 | 100 |  | 703 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 72 | 0 | 172 | 0 | 0 | 100 | 0 | 0 | 0 | 5 | 0 | 4 | 35 | 450 | 0 | 0 | 0 |  | 7989 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 107 | 0 | 0 | 276 | 0 | 0 | 0 | 260 | 24 | 100 | 55 | 0 | 0 | 150 | 24 | 40 | 82 | 73 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 8 | 30 | 5 | 20 | 28 | 100 | 0 | 0 | 0 | 280 | 184 | 8 | 70 | 23 | 5 | 0 | 51 | 0 | 42 | 0 | 19 | 11 | 33 | 21 | 104 | 99 | 81 | 22 | 0 | 20 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 135 | 0 | 0 | 200 | 0 | 117 | 0 | 100 | 34 | 137 | 252 | 45 | 50 | 0 | 0 | 307 | 44 | 0 | 4 | 26 | 100 | 415 | 70 | 0 | 144 | 0 | 100 |  | 891 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 10 | 12 | 24 | 0 | 27 | 16 | 0 | 0 | 0 | 50 | 14 | 100 | 25 | 0 | 0 | 52 | 28 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 83 | 0 | 179 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 0 | 0 | 0 |  | 9188 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 46 | 22 | 40 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 100 | 26 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 146 | 110 | 81 | 22 | 0 | 30 | 30 | 51 | 50 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 320 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 0 | 144 | 0 | 100 |  | 441 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 68 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 97 | 46 | 22 | 25 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 100 | 26 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 22 | 135 | 110 | 81 | 22 | 1.6 | 30 | 0 | 51 | 50 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 320 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 50 | 144 | 0 | 100 |  | 441 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 50 | 220 | 0 | 0 | 95 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 0 |  | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 310 | 0 | 0 | 0 | 305 | 0 | 48 | 15 | 0 | 0 | 120 | 1 | 3 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 28 | 0 |  | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 19 | 20 | 15 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 74 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 78 | 105 | 20 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 320 | 8 | 11 | 0 | 30 | 0 | 0 | 140 | 0 | 36 | 5 | 50 | 17 | 110 | 308 | 4 | 1 | 0 | 1 | 304 | 17 | 0 | 0 | 0 | 100 | 380 | 35 | 3 | 84 | 0 | 100 | 0 | 559 | 0 | 431 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 103 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 480 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5628 | 5:00
| Highest Generation |  | 9188 | 19:00
| Day Peak Generation |  | 7989 | 12:00
| Evening Peak Generation |  | 9188 | 19:00
| HVDC Max Flow |  | 895 | 22:00
| HVDC EvPeak Flow |  | 891 | 19:00
| Load factor L.F |  | 81.53%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-01-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7989 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5589 | MW
Evening Peak Generation : |  | 9188 | MW Hour : | 19:00 | Available Max Generation : |  | 12962 | MW
E.P. Demand (at gen end) : |  | 9188 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9188 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3762 | MW
Total Gen. (MKWH) : |  | 179.7854 | System Load Factor : | 81.53% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -367 | MW at | 9:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-01
Actual : | 95.68 | Ft.(MSL) , | Rule curve : | 97 | Ft.( MSL )
Gas Consumed : | Total = | 811.91 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 96676525.024
: |  | Coal : | 66910959 | Oil : | 306512513.77 | Total : | 470099997.794
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3285.7925 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1112.5507 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 995.9531 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 899.624 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 813.1446 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 656.1668 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 373.0738 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.1088 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 506.0389 |  |  | 0 | 0%
Total | 0 |  | 8811.4533 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-4,5
|  |  |  | 2) Baghabari-71 &100 MW | 11) Haripur 412 MW
3) Ghorasal Unit-1,2,3,4
4) Shahjibazar 330 MW
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,4 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tangail 132/33KV T-1 & T2 transformer tripped at 07:50 due to Y phase CT burst of 33 kV Betka & |  |  |  |  | About 80 MW power interruption occurred under Tangail S/S area
Kochuadanga feeder and were switched on at 08:20, 08:56 respectively. |  |  |  |  | from 07:50 to 08:20.
b) Barisal-Patuakhali 132 kV Ckt was under shut down from 08:48 to 16:30 for C/M.
c) Srimangal-Shahjibazar 132 KV Ckt-2 was under shut down from 08:55 to 14:55 for A/M.
d) Tongi-Kaliakoir 230 KV Ckt-2 was under shut down from 09:04 to 16:07 for A/M.
e) Mogbazar 132/33KV T-1 transformer was under shut down from 08:35 to 14:48 for A/M.
f) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 09:19 to 16:38 for A/M.
g) Ashuganj-Kishoreganj 132 kV Ckt-1 was under shut down from 09:04 to 16:19 for A/M.
h) Hathazari-Baroierhat 132 kV Ckt-1 was under shut down from 09:53 to 19:07 for A/M.
i) Chowmuhoni-Ramganj 132 kV Ckt-2 was under shut down from 09:32 to 16:39 for D/W.
j) Khulsi-AKSML 132 kV Ckt was under shut down from 08:43 to 19:01 for A/M.
k) Madanganj-Munshiganj 132 kV Ckt-1 was under shut down from 09:08 to 16:12 for A/M.
l) Baroirhat 132/33KV T-1 transformer was under shut down from 09:22 to 21:15 for D/W.
m) After maintenance Madanganj 132/33 kV transformer was switched on at 10:30.
n) After maintenance Haripur S/S-Haripur 412 MW Ckt was switched on at 08:38.
o) Ghorasal-Joydevpur 132 KV Ckt-2 was under shut down from 09:35 to 11:11 for C/M.
p) Ghorasal-Joydevpur 132 KV Ckt-1 was under shut down from 11:12 to 12:05 for C/M.
q) Kishoreganj 132/33KV T-3 transformer was under shut down from 12:05 to 14:18 for C/M.
r) Joydevpur 132/33KV T-2 transformer was under shut down from 12:15 to 14:40 for C/M. |  |  |  |  | About 19 MW power interruption occurred under Joydevpur S/S area
from 12:15 to 14:40.
s) Borguna 132/33KV T-1,2 transformer were switched on at 17:41,17:50 respectively.
t) Khulsi-Halishahar 132 kV Ckt-3 tripped at 17:20 showing instantaneous E/F relay and was switched on at 19:04.
u) Sylhet-Fenchuganj 132 kV Ckt tripped at 20:57 from both end showing dist A phase Z2, E/F relay |  |  |  |  | About 40 MW power interruption occurred under Biyanibazar S/S area
and was switched on at 21:18. |  |  |  |  | from 20:57 to 21:18.
v) After maintenance HVDC 400 kV main bus was switched on at 21:15.
w) After maintenance Bhola Notun Biddut was synchronized at 21:17.
x) Ghorasal-Tongi 230 KV Ckt-1 was under shut down since 07:20(01-02-2021) for A/M.
y) Sikalbaha-TK Chemical 132 KV Ckt was under shut down since 07:28(01-02-2021) for D/W.
z) Barisal(O)-Patuakhali 132 kV Ckt was under shut down since 08:48(01-02-2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-01-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4299750
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 2528954
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 276 | 7274000 | Gas Shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 24 | 328320 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6634036 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1699320
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 773131
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 73 | 1392603 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 495684
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3017000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 598080 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 266112 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 802440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 586560 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 217229 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 438424 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1241160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 574600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 135 | 1492908 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 117 | 1618560 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 50 | 174900 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1062720 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3401280 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2130 | 41719171
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 143933
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 88020
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 5 | 406560 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 42 | 1232722 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 542981
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 8 | 16440 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1695360
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 464400
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 603360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 72000 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24600
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 6498545
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 44 | 353316 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1961280
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0 | on test
| Chattogram area Total |  |  |  | 2266 | 811 | 14103517
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2412184
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4607000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7977000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 390888 | Machine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 166560 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1243498
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 2721527 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 59288
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1911180 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 537600 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 465372
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255420
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2145600
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 12010 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 465560
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 4 | 22800 | Low demand
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 541800 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1152 | 26957314
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 2415400 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483336
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 81 | 1042560 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12050
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4212000 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 45 | 403200 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 294000
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 291120
| Mymensingh Area Total |  |  |  | 709 | 470 | 9153666
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 715000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1144200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1168200
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 69 | 1674240 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 2400000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 392448 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7450950 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 252 | 5400000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 125820 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 415 | 10112300 | RRT
| Sylhet Area Total |  |  |  | 1988 | 1300 | 30847158
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 891 | 16872727
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 441600
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 5760 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 12 | 47232 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 380 | 8528256 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 27000 | Low demand
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1394400
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1537 | 27316975
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 122496 | Engine problem
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 373800 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 83 | 949273
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 10721100
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 65236 | High Voltage.
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 40800 | High Voltage.
| Barisal Area Total |  |  |  | 1676 | 656 | 12272705
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 94896
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 14 | 18242 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 237280 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 162 | 4113809 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 179 | 4487355 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 31154 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 520320
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 204012
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 398880
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 559288
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 817344
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1395936
| Rajshahi Area Total |  |  |  | 2183 | 869 | 12878516
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3661500
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 850560
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24368
| Rangpur Area Total |  |  |  | 605 | 263 | 4536428
| Total |  |  |  | 20748 | 9188 | 179785450
| Eastern Grid Total |  |  |  | 14000 | 5863 | 122780826
| Western Grid Total |  |  |  | 6748 | 3325 | 57004624
| National Grid Total |  |  |  | 20748 | 9188 | 179785450
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-01-31
| (a) ENTIRE EASTERN GRID : |  | 5719 | MW | (b) ENTIRE WESTERN GRID : |  | 3071 | MW
| i) Dhaka area |  | 2964 | MW | i) Khulna area |  | 1113 | MW
| ii) Chittagong area |  | 899 | MW | ii) Rajshahi area |  | 989 | MW
| iii) Comilla area |  | 730 | MW | iii) Barisal area |  | 247 | MW
| iv) Mymensingh area |  | 793 | MW | iv) Rangpur area |  | 722 | MW
| v) Sylhet area |  | 333 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8790 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 92 | 11:00 | Sherpur | 110 | 18:30 | Jhenida | 82 | 18:30
| Munsiganj | 84 | 20:00 | Srimongal | 30 | 18:00 | Bottail | 106 | 18:30
| Sonargaon | 59 | 2:00 | Shahjibazar | 85 | 19:00 | G.K Project | 32 | 19:00
| Shyampur | 174 | 11:00 | Fenchuganj | 24 | 18:00 | Faridpur | 134 | 18:30
| Bhulta | 152 | 12:00 | Kulawara | 27 | 19:30 | Madaripur | 64 | 21:00
| Madanganj | 57 | 19:00 | Sylhet | 82 | 19:00 | Sariatpur | 44 | 20:00
| Shitalakhya | 99 | 13:00 | Chatak | 20 | 18:30 | Gopalganj | 60 | 19:00
| Rahim steel | 20 | 8:00 | Sunamganj | 29 | 20:00 | Bagerhat | 84 | 19:00
| Matuail | 48 | 10:00 | Biani Bazar | 44 | 18:00 | Mongla | 40 | 17:00
| Ghorasal | 61 | 22:00 | Comilla (S) | 106 | 18:00 | Satkhira | 73 | 18:30
| Narsingdi | 123 | 22:00 | Comilla(N) | 79 | 20:00 | Gallamari | 16 | 1:00
| Haripur (SBU) | 102 | 19:00 | Chandpur | 39 | 20:00 | Magura | 40 | 18:30
| Ullon | 50 | 13:00 | Feni | 87 | 18:00 | Norail | 24 | 18:30
| Hasnabad | 98 | 19:00 | Chowmuhani | 116 | 20:00 | Chuadanga | 65 | 18:30
| Magbazar | 58 | 15:00 | Ashuganj | 40 | 21:00 | Barisal(N) | 29 | 19:00
| Maniknagar | 60 | 4:00 | Daudkandi | 80 | 19:30 | Barisal (S) | 68 | 19:00
| Bangabhaban | 14 | 13:00 | B.Baria | 98 | 20:00 | Patuakhali | 93 | 19:30
| Narinda | 64 | 12:00 | Ramganj | 52 | 19:30 | Bhandaria | 40 | 19:00
| Dhanmondi | 88 | 13:00 | Chaddagram | 26 | 20:00 | Borhan Uddin | 26 | 20:00
| Lalbag | 70 | 13:00 | PHP | 10 | 8:00 | Ishurdi | 51 | 19:30
| Madartek | 46 | 21:00 | Kochua | 43 | 20:00 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Madunaghat | 45 | 18:00 | Natore | 94 | 18:30
| Aftabnagar | 6 | 0.54167 | Hathazari | 63 | 0.77083 | Bogra | 121 | 0.79167
| Fatullah | 39 | 12:00 | Khulshi | 151 | 11:00 | Noagaon | 94 | 13:00
| Mirpur | 68 | 18:30 | Halishahar | 85 | 18:00 | Rajshahi | 94 | 19:00
| Kalyanpur | 57 | 18:30 | Baraulia | 136 | 11:00 | Rajshahi New | 13 | 19:00
| Gulshan | 70 | 13:00 | Sikalbaha | 20 | 18:30 | C.Nawabganj | 65 | 13:00
| Uttara | 63 | 18:30 | Dohazari | 58 | 18:00 | Amnura | 42 | 19:00
| Uttara New | 22 | 18:30 | Cox'sbazar | 84 | 19:00 | Pabna | 64 | 19:00
| Kamrangirchar | 66 | 13:00 | Chandraghona | 22 | 18:00 | Shahjadpur | 72 | 19:00
| Savar | 116 | 19:00 | Kaptai | 3.6 | 18:00 | Serajganj | 77 | 19:00
| Bhasantec | 97 | 18:30 | A. Khaer Stl. | 15 | 0:00 | Niyamatpur | 66 | 13:00
| Agargaon | 43 | 13:00 | Bakulia | 70 | 18:30 | Joypurhat | 58 | 9:00
| Satmosjid | 57 | 0.54167 | Julda | 20 | 0.5 | Sherpur(Bogura) | 48 | 0.77083
| Tongi | 89 | 12:00 | TK chemical | 18.5 | 18:30 | Mohastangor | 38 | 19:00
| Kabirpur | 177 | 18:30 | Modern Steel | 0 | 1:00 | Bangura | 15 | 20:00
| Basundhara | 90 | 18:00 | Shahmirpur | 17 | 19:00 | Rangpur | 114 | 18:30
| Manikganj | 40 | 21:00 | Khagrachhari | 20 | 5:00 | Lalmonirhat | 54 | 18:30
| Joydevpur | 112 | 19:30 | Matarbari | 27 | 18:30 | Saidpur | 104 | 19:00
| New Tongi | 73 | 11:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 106 | 19:00
| Korda | 144 | 12:00 | Rangamati | 8 | 12:00 | Thakurgaon | 72 | 19:00
| Dhamrai | 80 | 19:00 | Abul Khair 230 | 156 | 8:00 | Palashbari | 114 | 18:30
| Rajendrapur | 72 | 19:00 | BSRM | 102 | 8:00 | Barapukuria | 51 | 9:00
| Valuka | 82 | 9:00 | GPH Ispat | 12 | 18:00 | Panchagar | 48 | 19:30
| Tangail | 142 | 18:30 | Goalpara | 17 | 13:00 | Joldhaka | 24 | 19:00
| Mymensing | 186 | 19:00 | Central s/s | 78 | 18:30 | Kurigram | 50 | 18:30
| Kishorganj | 100 | 20:00 | Noapara | 51 | 19:00
| Netrokona | 101 | 18:00 | Jessore | 86 | 18:30
| Jamalpur | 99 | 18:30 | Benapol | 42 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 2:00 | 406 | 19:30 | Kaliakoir | 409 | 0.125 | 399 | 0.5
| Bheramara | 407 | 4:00 | 389 | 19:30 | Bhulta | 394 | 0.20833 | 386 | 0.45833
| Ashuganj(N) | 397 | 4:00 | 388 | 11:00 | Gopalganj | 413 | 0.625 | 385 | 0.77083
| Payra | 417 | 1:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 238 | 7:00 | Hathazari | 236 | 2:00 | 224 | 11:00
| Ishurdi | 244 | 4:00 | 230 | 9:00 | Megnaghat | 241 | 1:00 | 237 | 16:00
| Ashuganj | 245 | 1:00 | 240 | 10:00 | Fenchuganj | 242 | 1:00 | 239 | 18:30
| Serajganj | 237 | 4:00 | 225 | 9:00 | Siddhirganj | 241 | 2:00 | 235 | 15:00
| Baghabari | 240 | 2:00 | 228 | 9:00 | Maniknagar | 239 | 5:00 | 234 | 11:00
| Barapukuria | 236 | 22:00 | 225 | 8:00 | Agargaon | 241 | 16:00 | 235 | 16:00
| Bogra | 235 | 22:00 | 218 | 9:00 | Barisal | 253 | 1:00 | 239 | 18:30
| Rajshahi | 240 | 5:00 | 224 | 8:00 | Bhola 225 MW | 257 | 24:00 | 238 | 18:00
| Khulna South | 245 | 4:00 | 229 | 8:00 | AKSML | 236 | 1:00 | 225 | 11:00
| Rampura | 236 | 6:00 | 232 | 12:00 | BSRM | 237 | 1:00 | 229 | 11:00
| Haripur | 239 | 4:00 | 234 | 16:00 | Bibiyana | 245 | 1:00 | 238 | 17:00
| Hasnabad | 240 | 21:00 | 234 | 15:00 | Bhulta | 241 | 4:00 | 235 | 11:00
| Shyampur | 239 | 1:00 | 220 | 16:00 | Ashuganj (S) | 242 | 5:00 | 236 | 13:00
| Aminbazar | 240 | 1:00 | 236 | 15:00 | Kaliakoir | 239 | 2:00 | 228 | 12:00
| Tongi | 236 | 4:00 | 228 | 15:00 | GPH | 237 | 1:00 | 227 | 11:00
| Comilla (N) | 244 | 1:00 | 235 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 14:00 | 138 | 12:00 | Madanhat | 141 | 0.79167 | 134 | 0.45833
| Munsiganj | 142 | 10:00 | 137 | 1:00 | Hathazari | 140 | 0.041667 | 134 | 0.45833
| Sonargaon | 139 | 14:00 | 135 | 7:00 | Khulshi | 138 | 0.25 | 132 | 0.41667
| Shyampur | 135 | 2:00 | 131 | 11:00 | Halishahar | 139 | 0.041667 | 134 | 0.45833
| Bhulta | 135 | 6:00 | 132 | 11:00 | Baraulia | 138 | 0.54167 | 132 | 0.45833
| Madanganj | 139 | 11:00 | 133 | 1:00 | Sikalbaha | 141 | 0.77083 | 134 | 0.70833
| Shitalakhya | 140 | 14:00 | 134 | 15:00 | Dohazari | 136 | 0.77083 | 132 | 0.45833
| Rahim steal | 140 | 8:00 | 137 | 16:00 | Cox'sbazar | 131 | 0.33333 | 126 | 0.5
| Matuail | 141 | 14:00 | 138 | 12:00 | Chandraghona | 140 | 0.33333 | 136 | 0.41667
| Ghorasal | 142 | 2:00 | 140 | 11:00 | Kaptai | 138 | 0.041667 | 135 | 0.41667
| Narsinghdi | 137 | 18:30 | 135 | 1:00 | A. Khaer Stl. | 137 | 0.083333 | 132 | 0.45833
| Haripur (SBU) | 140 | 3:00 | 137 | 15:00 | Bakulia | 140 | 0.54167 | 134 | 0.41667
| Ullon | 136 | 5:00 | 132 | 11:00 | Julda | 140 | 0.75 | 134 | 0.5
| Hasnabad | 138 | 2:00 | 135 | 11:00 | TK Chemical | 139 | 0.79167 | 134 | 0.66667
| Magbazar | 136 | 24:00 | 133 | 11:00 | Modern Steel | 138 | 0.083333 | 133 | 0.41667
| Maniknagar | 139 | 1:00 | 135 | 12:00 | Shahmirpur | 139 | 0.58333 | 134 | 0.5
| Bangabhaban | 139 | 1:00 | 135 | 12:00 | Khagrachhari | 139 | 0.20833 | 133 | 0.41667
| Narinda | 139 | 1:00 | 135 | 12:00 | Matarbari | 135 | 0.29167 | 130 | 0.041667
| Dhanmondi | 136 | 5:00 | 132 | 11:00 | Baroiar Hat | 140 | 0.29167 | 137 | 0.5
| Lalbag | 138 | 7:00 | 134 | 16:00 | Rangamati | 139 | 5:00 | 133 | 11:00
| Madartek | 136 | 1:00 | 132 | 11:00 | Goalpara S/S | 139 | 18:00 | 130 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 18:00 | 130 | 0.375
| Aftabnagar | 136 | 1:00 | 132 | 11:00 | Noapara | 139 | 5:00 | 128 | 0.375
| Fatullah | 135 | 2:00 | 130 | 16:00 | Jessore | 136 | 6:00 | 127 | 0.5
| Mirpur | 141 | 5:00 | 137 | 12:00 | Benapol | 139 | 0.125 | 126 | 0.33333
| Kalyanpur | 140 | 5:00 | 137 | 12:00 | Jhenida | 136 | 6:00 | 125 | 0.54167
| Gulshan | 136 | 3:00 | 131 | 12:00 | Bottail | 139 | 0.125 | 130 | 0.375
| Uttara | 140 | 5:00 | 135 | 16:00 | G.K Project | 142 | 0.16667 | 135 | 0.5
| Uttara New | 140 | 6:00 | 134 | 16:00 | Faridpur | 140 | 0.16667 | 133 | 0.77083
| Kamrangirchar | 136 | 19:30 | 131 | 16:00 | Madaripur | 144 | 0.625 | 136 | 0.77083
| Savar | 141 | 5:00 | 137 | 16:00 | Shariyatpur S/S | 144 | 4:00 | 135 | 0.75
| Bhasantec | 139 | 5:00 | 134 | 16:00 | Gopalganj | 147 | 0.25 | 138 | 0.79167
| Agargaon | 139 | 5:00 | 135 | 16:00 | Bagerhat | 137 | 18:00 | 130 | 0.33333
| Satmosjid | 138 | 5:00 | 135 | 16:00 | Mongla | 138 | 21:00 | 129 | 0.33333
| Tongi | 142 | 0:00 | 137 | 15:00 | Satkhira | 138 | 5:00 | 129 | 8:00
| Kabirpur | 136 | 1:00 | 131 | 18:00 | Gallamari | 140 | 0.20833 | 131 | 0.33333
| Basundhara | 140 | 1:00 | 136 | 13:00 | Magura | 136 | 2:00 | 125 | 0.5
| Manikganj | 147 | 9:00 | 140 | 23:00 | Narail | 136 | 0.20833 | 125 | 0.5
| Joydevpur | 140 | 22:00 | 135 | 12:00 | Chuadanga | 134 | 4:00 | 122 | 0.54167
| New Tongi | 140 | 0:00 | 136 | 16:00 | Barisal(N) | 147 | 13:00 | 138 | 9:00
| Kodda | 138 | 19:00 | 134 | 17:00 | Barisal (S) | 144 | 0.20833 | 132 | 0.75
| Dhamrai | 136 | 1:00 | 130 | 17:00 | Patuakhali(S) | 139 | 0.70833 | 127 | 0.75
| Rajendrapur | 141 | 5:00 | 135 | 11:00 | Bhandaria | 141 | 0.083333 | 130 | 0.75
| Valuka | 131 | 3:00 | 124 | 14:00 | Ishurdi | 141 | 2:00 | 134 | 8:00
| Tangail | 135 | 3:00 | 130 | 15:00 | Ruppur Paromanobik | 140 | 4:00 | 134 | 9:00
| Mymensing | 132 | 4:00 | 127 | 12:00 | Natore | 138 | 2:00 | 130 | 12:00
| Kishorganj | 133 | 23:00 | 128 | 11:00 | Bogra | 138 | 2:00 | 124 | 9:00
| Netrokona | 131 | 1:00 | 125 | 9:00 | Noagaon | 131 | 19:30 | 116 | 9:00
| Jamalpur | 140 | 16:00 | 132 | 5:00 | Rajshahi | 138 | 5:00 | 129 | 8:00
| Sherpur | 139 | 16:00 | 130 | 8:00 | Rajshahi New | 137 | 4:00 | 128 | 13:00
| Srimongal | 140 | 1:00 | 138 | 19:00 | C.Nawabganj | 135 | 18:00 | 126 | 9:00
| Shahjibazar | 138 | 24:00 | 135 | 11:00 | Amnura | 137 | 20:00 | 125 | 8:00
| Fenchuganj | 140 | 4:00 | 137 | 18:00 | Pabna | 141 | 3:00 | 130 | 8:00
| Khulawara | 140 | 4:00 | 136 | 18:00 | Shahjadpur | 144 | 5:00 | 135 | 9:00
| Sylhet | 138 | 5:00 | 134 | 11:00 | Serajganj | 137 | 1:00 | 128 | 9:00
| Chatak | 136 | 1:00 | 130 | 21:00 | Niyamatpur | 131 | 2:00 | 115 | 9:00
| Sunamganj | 136 | 3:00 | 131 | 18:30 | Joypurhat | 134 | 1:00 | 115 | 9:00
| Biani Bazar | 138 | 3:00 | 132 | 18:00 | Sherpur(Bogura) | 138 | 2:00 | 126 | 12:00
| Comilla(s) | 132 | 24:00 | 126 | 18:00 | Mohastangor | 136 | 1:00 | 123 | 9:00
| Comilla(n) | 145 | 9:00 | 142 | 11:00 | Bangura | 143 | 5:00 | 133 | 8:00
| Chandpur | 144 | 7:00 | 142 | 18:00 | Rangpur | 132 | 4:00 | 118 | 10:00
| Feni | 140 | 7:00 | 138 | 20:00 | Lalmonirhat | 132 | 3:00 | 115 | 9:00
| Chowmuhani | 140 | 20:00 | 137 | 12:00 | Saidpur | 132 | 4:00 | 120 | 8:00
| Ashuganj | 141 | 12:00 | 139 | 18:00 | Purbasadipur | 131 | 3:00 | 115 | 9:00
| Daudkandi | 142 | 19:00 | 138 | 11:00 | Thakurgaon | 133 | 2:00 | 116 | 9:00
| B.Baria | 136 | 12:00 | 133 | 18:00 | Palashbari | 134 | 4:00 | 119 | 12:00
| Ramganj | 139 | 14:00 | 135 | 18:00 | Barapukuria | 135 | 6:00 | 125 | 8:00
| Chaddagram | 141 | 7:00 | 140 | 14:00 | Panchagar | 133 | 5:00 | 112 | 13:00

## L-Curve
Date | 2021-01-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 35 | 4778 | 2123 | 6901 |  |  |  | QF-LDC-11
0:30 | 54 | 4595.5 | 2021 | 6616.5 | Date: | 2021-01-31
1:00 | 73 | 4413 | 1919 | 6332
1:30 | 113 | 4419.5 | 1773 | 6192.5
2:00 | 153 | 4426 | 1627 | 6053
2:30 | 128 | 4294 | 1623.5 | 5917.5 | [5 empty] | Gen. at Eve. Peak | 9188 | 9188 MW (19:00 )
3:00 | 103 | 4162 | 1620 | 5782 | [6 empty] | 19:00
3:30 | 80 | 4094.5 | 1620 | 5714.5 | [5 empty] | Gen. at Day Peak | 7989 | 7989 MW (12:00 )
4:00 | 57 | 4027 | 1620 | 5647 | [6 empty] | 12:00
4:30 | 56 | 4030 | 1607.5 | 5637.5 | [5 empty] | Highest Generation | 9188
5:00 | 55 | 4033 | 1595 | 5628 | [6 empty] | 19:00
5:30 | 50.5 | 4118 | 1665.5 | 5783.5
6:00 | 46 | 4203 | 1736 | 5939
6:30 | 136.5 | 4350 | 1785 | 6135
7:00 | 227 | 4497 | 1834 | 6331
7:30 | 272.5 | 4678 | 2000.5 | 6678.5
8:00 | 318 | 4859 | 2167 | 7026
8:30 | 342.5 | 5126.5 | 2167.5 | 7294
9:00 | 367 | 5394 | 2168 | 7562
9:30 | 283 | 5389 | 2205 | 7594
10:00 | 199 | 5384 | 2242 | 7626
10:30 | 170 | 5404.5 | 2263.5 | 7668
11:00 | 141 | 5425 | 2285 | 7710
11:30 | 130.5 | 5521.5 | 2328 | 7849.5
12:00 | 120 | 5618 | 2371 | 7989
12:30 | 154 | 5662.5 | 2394.5 | 8057
13:00 | 188 | 5707 | 2418 | 8125
13:30 | 182.5 | 5623.5 | 2353 | 7976.5
14:00 | 177 | 5540 | 2288 | 7828
14:30 | 95.5 | 5411.5 | 2235.5 | 7647
15:00 | 14 | 5283 | 2183 | 7466
15:30 | 120.5 | 5128.5 | 2241 | 7369.5
16:00 | 227 | 4974 | 2299 | 7273
16:30 | 200 | 4977 | 2323 | 7300
17:00 | 173 | 4980 | 2347 | 7327
17:30 | 205 | 5154 | 2656 | 7810
18:00 | 237 | 5328 | 2965 | 8293
18:30 | 181.5 | 5595.5 | 3145 | 8740.5
19:00 | 126 | 5863 | 3325 | 9188
19:30 | 122 | 5824 | 3309 | 9133
20:00 | 68 | 5698 | 3183 | 8881 |  |  |  | Executive Engineer
20:30 | 93.5 | 5635 | 3141.5 | 8776.5 |  |  |  | Network Operation Division
21:00 | 119 | 5572 | 3100 | 8672
21:30 | 200 | 5403 | 3028.5 | 8431.5
22:00 | 281 | 5234 | 2957 | 8191 |  |  |  |  | Page 6 of 7
22:30 | 249.5 | 5088.5 | 2772.5 | 7861
23:00 | 218 | 4943 | 2588 | 7531
23:30 | 126.5 | 4860.5 | 2355.5 | 7216
24:00 | 35 | 4778 | 2123 | 6901
9188 MW (19:00 )
7989 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-01-31 |  | Energy | 179785450
[11 empty] | 2021-01-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2842 | 610 | 1153 | 1741 | 620 | 61 | 40 | 0 | 82 | 0
0:30 | 2842.5 | 562 | 1117 | 1454.5 | 605 | 57.5 | 20 | 0 | 82 | 0 | Date: | 2021-01-31
1:00 | 2843 | 514 | 1081 | 1168 | 590 | 54 | 0 | 0 | 82 | 0
1:30 | 2821.5 | 513.5 | 1064.5 | 1158.5 | 500 | 53.5 | 0 | 0 | 81 | 0 | [7 empty] | Total Energy | 179.7854 | Total Energy Gen 179.785 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 179.785 MKWHr
2:00 | 2800 | 513 | 1048 | 1149 | 410 | 53 | 0 | 0 | 80 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2783 | 513.5 | 1031.5 | 1052 | 405 | 52.5 | 0 | 0 | 80 | 0 | [7 empty] | Energy Requirement | 179.7854
3:00 | 2766 | 514 | 1015 | 955 | 400 | 52 | 0 | 0 | 80 | 0
3:30 | 2759 | 513.5 | 1015 | 896.5 | 400 | 51.5 | 0 | 0 | 79 | 0 | [6 empty] | Shortage
4:00 | 2752 | 513 | 1015 | 838 | 400 | 51 | 0 | 0 | 78 | 0
4:30 | 2751.5 | 513 | 1009 | 835.5 | 400 | 50.5 | 0 | 0 | 78 | 0
5:00 | 2751 | 513 | 1003 | 833 | 400 | 50 | 0 | 0 | 78 | 0
5:30 | 2861.5 | 513 | 1026 | 856 | 400 | 50 | 0 | 0 | 77 | 0
6:00 | 2972 | 513 | 1049 | 879 | 400 | 50 | 0 | 0 | 76 | 0
6:30 | 2996 | 560 | 1027.5 | 1007.5 | 415 | 50 | 0 | 0 | 78 | 1 |  |  |  |  | Coal
7:00 | 3020 | 607 | 1006 | 1136 | 430 | 50 | 0 | 0 | 80 | 2
7:30 | 3064.5 | 655 | 1013.5 | 1362 | 445 | 50 | 0 | 0 | 82 | 6.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3109 | 703 | 1021 | 1588 | 460 | 50 | 0 | 0 | 84 | 11
8:30 | 3079 | 703 | 1035 | 1805.5 | 499.5 | 51 | 16 | 0 | 86 | 19
9:00 | 3049 | 703 | 1049 | 2023 | 539 | 52 | 32 | 0 | 88 | 27
9:30 | 2936.5 | 703 | 1004.5 | 2155 | 569 | 51 | 46.5 | 0 | 88 | 40.5
10:00 | 2824 | 703 | 960 | 2287 | 599 | 50 | 61 | 0 | 88 | 54
10:30 | 2806 | 703 | 985 | 2294.5 | 614.5 | 54.5 | 63 | 0 | 89 | 58.5
11:00 | 2788 | 703 | 1010 | 2302 | 630 | 59 | 65 | 0 | 90 | 63
11:30 | 2854 | 703 | 1050 | 2341 | 615 | 60 | 66.5 | 0 | 93 | 67
12:00 | 2920 | 703 | 1090 | 2380 | 600 | 61 | 68 | 0 | 96 | 71
12:30 | 2913 | 703.5 | 1082 | 2460.5 | 585 | 60.5 | 86.5 | 0 | 96 | 70
13:00 | 2906 | 704 | 1074 | 2541 | 570 | 60 | 105 | 0 | 96 | 69
13:30 | 2906 | 704 | 1074 | 2541 | 570 | 60 | 105 | 0 | 96 | 69
14:00 | 2906 | 704 | 1074 | 2541 | 570 | 60 | 105 | 0 | 96 | 69
14:30 | 2750 | 703.5 | 1043.5 | 2451.5 | 560 | 61.5 | 73 | 0 | 94 | 58.5
15:00 | 2594 | 703 | 1013 | 2362 | 550 | 63 | 41 | 0 | 92 | 48
15:30 | 2621.5 | 703 | 1006 | 2267 | 550 | 63 | 31.5 | 0 | 91 | 36.5
16:00 | 2649 | 703 | 999 | 2172 | 550 | 63 | 22 | 0 | 90 | 25
16:30 | 2664.5 | 703 | 1010.5 | 2186.5 | 549.5 | 62.5 | 22 | 0 | 87 | 14.5
17:00 | 2680 | 703 | 1022 | 2201 | 549 | 62 | 22 | 0 | 84 | 4
17:30 | 2671 | 796.5 | 1027 | 2425.5 | 554.5 | 52 | 186.5 | 0 | 95 | 2
18:00 | 2662 | 890 | 1032 | 2650 | 560 | 42 | 351 | 0 | 106 | 0
18:30 | 2778.5 | 890.5 | 1062.5 | 2846.5 | 620 | 42 | 395.5 | 0 | 105 | 0
19:00 | 2895 | 891 | 1093 | 3043 | 680 | 42 | 440 | 0 | 104 | 0
19:30 | 2919 | 892 | 1097 | 3007 | 700 | 47 | 365 | 0 | 106 | 0
20:00 | 2933 | 891 | 1091 | 2851 | 700 | 47 | 266 | 0 | 102 | 0
20:30 | 2945 | 892.5 | 1096.5 | 2753 | 700 | 47 | 240.5 | 0 | 102 | 0
21:00 | 2957 | 894 | 1102 | 2655 | 700 | 47 | 215 | 0 | 102 | 0
21:30 | 2928.5 | 894.5 | 1104.5 | 2483.5 | 700 | 53 | 165.5 | 0 | 102 | 0
22:00 | 2900 | 895 | 1107 | 2312 | 700 | 59 | 116 | 0 | 102 | 0
22:30 | 2892 | 895 | 1105.5 | 2026.5 | 680 | 60 | 106 | 0 | 96 | 0
23:00 | 2884 | 895 | 1104 | 1741 | 660 | 61 | 96 | 0 | 90 | 0
23:30 | 2863 | 752.5 | 1128.5 | 1741 | 640 | 61 | 68 | 0 | 86 | 0 | Max Temp. in Dhaka |  | 22.1° C
24:00 | 2842 | 610 | 1153 | 1741 | 620 | 61 | 40 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 179.785 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 179.785 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-01-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 54 | 53 | 52 | 51 | 50 | 50 | 50 | 50 | 52 | 50 | 59 | 61 | 60 | 62 | 63 | 63 | 62 | 42 |  | 42 | 47 | 47 | 47 | 59 | 61 | 61 | 1232722
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 1 | 8 | 8 | 8 | 17 | 25 |  |  |  | 13 |  | 25 | 25 | [5 empty] | 143933
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  |  | 12 | 15 | 15 | 14 | 12 | 9 | 5 | 1 | [9 empty] | 88020
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 13 | 17 | 17 | 51 | 51 | 34 | 17 | 17 | 102 |  | 102 | 85 | 68 | 51 |  |  |  | 542981
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 42 |  | 42 | [6 empty] | 59288
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 80 | 80 | 80 | 155 | 155 | 155 | 190 | 145 | 145 | 170 | 155 | 70 | 75 | 70 | 75 | 75 |  | 150 | 100 | 100 | 100 | 95 | 95 | 95 | 3017000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 37 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 37 | 47 | 45 | 45 | 45 | 45 | 45 | 45 | 112 |  | 135 | 167 | 148 | 168 | 170 | 52 | 31 | 1492908
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4299750
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2412184
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 22 | 22 | 22 | 22 | 26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 390888
33 | Ashuganj 225 MW CCPP | 175 | 184 | 189 | 178 | 190 | 196 | 200 | 200 | 189 | 184 | 186 | 233 | 184 | 184 | 184 | 184 | 184 | 193 |  | 184 | 184 | 190 | 191 | 183 | 185 | 184 | 4607000
34 | Ashuganj 450 MW CCPP(South) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 325 | 300 | 300 | 320 | 280 | 280 | 280 | 280 | 280 |  | 280 | 350 | 350 | 350 | 350 | 350 | 350 | 7977000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 166560
36 | Chandpur 150 MW CCPP | 85 | 90 | 85 | 90 | 90 | 90 | 89 | 95 | 85 | 85 | 83 | 81 | 80 | 73 | 80 | 72 | 76 | 76 |  | 70 | 70 | 70 | 70 | 64 | 72 | 63 | 1911180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | [26 empty] | 0
41 | Haripur 360MW CCPP(HPL) | 326 | 325 | 288 | 288 | 290 | 315 | 329 | 329 | 363 | 319 | 319 | 322 | 302 | 309 | 310 | 287 | 288 | 289 |  | 276 | 278 | 279 | 277 | 277 | 277 | 303 | 7274000
42 | RPCL 210MW CCPP | 109 | 109 | 109 | 109 | 109 | 108 | 109 | 108 | 109 | 107 | 108 | 92 | 86 | 85 | 86 | 85 | 103 | 105 |  | 99 | 106 | 102 | 98 | 94 | 94 | 96 | 2415400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 11 | 24 | 36 | 40 | 46 | 44 | 40 | 33 | 17 | 3 | [9 empty] | 294000
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 76 | 76 | 77 | 68 | 68 | 68 | 67 | 70 | 66 | 66 | 66 | 66 | 66 | 68 | 69 |  | 69 | 69 | 69 | 66 | 69 | 69 | 69 | 1674240
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [26 empty] | 0
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [8 empty] | 9 | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 |  | 9 | 9 | 9 | 125820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 47 | 47 | 48 | 48 | 48 | 45 | 45 | 50 | 50 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1144200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 392448
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 290 | 300 | 300 | 300 | 320 | 300 | 310 | 310 | 280 | 300 | 305 | 300 | 285 | 285 | 290 | 300 | 280 |  | 310 | 310 | 300 | 320 | 300 | 280 | 295 | 7450950
| Bibiyana South 400 MW | 416 | 415 | 415 | 415 | 416 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 416 | 415 | 415 | 415 | 415 |  | 415 | 416 | 416 | 415 | 415 | 415 | 415 | 10112300
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 11 | 43 | 55 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 25 |  | 35 | 35 | 17 |  |  |  |  | 438424
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 6 |  |  | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 23 |  | 23 | 23 | 23 | 19 | 23 | 21 |  | 291120
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 464400
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495684
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 483336
63 | Impoprt (Tripura) | 82 | 80 | 80 | 78 | 78 | 76 | 80 | 84 | 88 | 88 | 90 | 96 | 96 | 96 | 92 | 90 | 84 | 106 |  | 104 | 106 | 102 | 102 | 102 | 90 | 82 | 2145600
64 | Malancha, Ctg. EPZ (United) |  | 41 | 41 | 42 | 42 | 42 | 13 | 18 | 7 | 7 | 7 | 5 | 5 | 5 | 5 | 8 | 16 | 16 |  | 28 | 29 | 31 | 36 | 39 | 40 | 41 | 603360
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 16 | 17 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 465372
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 255420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821300
68 | Cumilla 25 MW PP (Summit) | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 465560
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 18 | 18 | 18 | 18 | 20 | 32 | 24 | 24 | 32 | 32 | 32 | 28 | 30 | 30 | 18 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 641160
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 |  | 25 | 25 | 25 | 25 | 20 | 17 | 17 | 574600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801400
73 | Ghorashal 108MW PP (Regent) | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 105 | 105 | 105 | 105 | 105 | 107 | 104 | 104 | 107 | 107 |  | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 2528954
| Feni Lanka Power | [17 empty] | 17 |  | 4 | [6 empty] | 22800
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 21 | 26 | 26 | 26 | 42 | 46 | 46 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 |  |  |  | 541800
| Manikgonj 162MW PP(MPGL) | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3401280
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 6 | 30 | 60 | 60 | 60 | 83 | 100 | 77 |  |  | 12 |  | 24 | 24 | 24 | 21 |  |  |  | 598080
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [8 empty] | 32 | 48 | 48 | 48 | 48 |  |  |  |  | 64 |  | 82 | 98 | 98 | 64 | 16 | 16 | 16 | 586560
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 2 | 25 | 74 | 78 | 81 | 81 | 81 | 81 | 81 | 64 | 65 |  | 81 | 81 | 81 | 72 | 48 | 8 | 8 | 1042560
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 4 | [8 empty] | 12010
| Gazipur 100 MW PP | [8 empty] | 2 | 17 | 17 | 17 | 17 |  |  |  |  | 9 |  | 50 | 17 | [5 empty] | 174900
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 24600
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 39 | 54 | 54 | 17 | 17 | 17 |  | 44 | 17 | 17 |  |  |  |  | 353316
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 30 | 48 | 64 | 84 | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 99 |  | 100 | 100 | 100 | 100 | 100 | 100 | 48 | 1699320
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 54 | 20 | 10 | 10 | 10 | 12 | 50 | 53 | 60 | 60 | 60 | 68 | 72 | 73 | 61 | 69 | 73 | 73 |  | 73 | 73 | 73 | 73 | 75 | 67 | 72 | 1392603
86 | Meghnaghat CCPP(Summit) | 270 | 290 | 305 | 275 | 270 | 300 | 300 | 300 | 300 | 260 | 285 | 260 | 245 | 260 | 275 | 260 | 285 | 285 |  | 260 | 285 | 285 | 270 | 245 | 260 | 245 | 6634036
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 4 | 7 | 7 | 7 | 7 | 41 | 65 | 60 |  |  | 13 |  | 24 | 24 | 24 | 24 |  |  |  | 328320
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 13 | 45 | 62 | 73 | 72 | 72 | 72 | 72 | 72 | 70 | 53 | 53 |  | 70 | 72 | 73 | 72 | 70 | 29 | 0 | 1062720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 8 | [6 empty] | 16440
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 1168200
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1243498
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 3 | 24 | 24 | 24 | 40 | 40 |  |  |  | 7 |  | 40 | 40 | 16 |  |  |  |  | 266112
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 6 | 6 | 6 | 6 | 6 | 14 | 25 | 25 | 25 | 27 | 33 | 44 | [5 empty] | 5 | 18 | 18 | 19 | 19 | 19 | 19 | 406560
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 12 |  |  |  | 17 |  | 30 | [6 empty] | 72000
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 3 | 20 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 |  | 55 | 55 | 55 | 55 | 30 | 15 |  | 773131
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 17 | 17 |  |  | 17 |  | 17 | [6 empty] | 217229
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 |  | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12050
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 |  | 802440
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 160 | 160 | 60 | 60 | 60 | 70 | 140 | 192 | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4212000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 16 | 76 | 109 | 113 | 130 | 130 | 130 | 130 | 117 | 101 | 100 |  | 117 | 131 | 131 | 125 | 55 | 15 |  | 1618560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 50 | 100 | 88 | 90 | 90 | 90 | 100 | 100 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1695360
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 537600
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 30 | 30 | 30 | 34 | 78 | 127 | 128 | 125 | 123 | 128 | 128 | 128 | 123 | 125 | 128 | 125 |  | 137 | 146 | 144 | 148 | 148 | 150 | 150 | 2721527
118 | Bibiyana-III 400 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 270 | 280 | 280 | 225 | 223 | 251 | 252 | 193 | 124 | 191 | 190 | 150 |  | 252 | 252 | 255 | 258 | 252 | 252 | 252 | 5400000
| Jamalpur 115 MW PP (United) | [8 empty] | 14 | 40 | 24 | 24 | 45 | 35 | 35 | 16 | 16 | 16 |  | 45 | 25 | 25 |  |  |  |  | 403200
| Anwara 300 MW PP (United) | 215 | 215 | 215 | 178 | 178 | 178 | 215 | 270 | 305 | 266 | 255 | 307 | 307 | 307 | 307 | 307 | 307 | 307 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 6498545
| Juldah unit-2 (Acorn) | 70 | 70 | 70 | 20 | 20 | 20 | 35 | 60 | 76 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1961280
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4413 | 4426 | 4162 | 4027 | 4033 | 4203 | 4497 | 4859 | 5394 | 5384 | 5425 | 5618 | 5707 | 5540 | 5283 | 4974 | 4980 | 5328 |  | 5863 | 5824 | 5698 | 5572 | 5234 | 4943 | 4778 | 122780826
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [8 empty] | 5 | 32 | 16 | 16 | 39 |  |  |  |  | 115 |  | 115 | 115 | 91 | 32 |  |  |  | 441600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 10 | [6 empty] | 5760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 0 | 70 | 70 | 90 | 100 | 100 | 102 | 105 | 105 | 70 | 70 | 105 |  | 105 | 105 | 105 | 105 | 35 |  |  | 1394400
130
131
132 | United Payra Power Ltd. | [7 empty] | 35 | [18 empty] | 40800
133 | Bhola Nutan Biddut BD LTD (GAS) | [23 empty] | 15 | 28 | 33 | 65236
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 48 | 48 | 48 | 16 |  |  | 122496
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 57 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 72 | 80 | 65 | 35 | 36 | 37 | 50 |  | 83 | 83 | 83 | 85 | 83 | 86 | 88 | 949273
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 21 | 15 | 14 | 0 | 0 |  |  |  |  | 22 | 22 | 23 | 20 | 18 | 18 | 11 | 26 |  | 27 | 28 | 28 | 26 | 26 | 24 | 23 | 373800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 24 | [6 empty] | 27000
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 3 | 6 | 8 | 7 | 5 | 5 | 6 |  | 12 | 12 | [5 empty] | 47232
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 514 | 513 | 514 | 513 | 513 | 513 | 607 | 703 | 703 | 703 | 703 | 703 | 704 | 703 | 703 | 703 | 703 | 890 |  | 891 | 892 | 891 | 894 | 895 | 895 | 610 | 16872727
147 | Bheramara 410 MW CCPP | 345 | 300 | 300 | 300 | 300 | 410 | 380 | 455 | 345 | 345 | 345 | 365 | 345 | 345 | 345 | 345 | 345 | 360 |  | 380 | 345 | 350 | 355 | 340 | 340 | 340 | 8528256
148 | Payra 1320 MW | 440 | 260 | 250 | 250 | 250 | 250 | 280 | 310 | 390 | 450 | 480 | 450 | 420 | 400 | 400 | 400 | 400 | 410 |  | 530 | 550 | 550 | 550 | 550 | 510 | 470 | 10721100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3661500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 35 |  | 50 | 50 | [5 empty] | 94896
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 153 | 157 | 158 | 154 | 170 | 172 | 184 | 189 | 158 | 154 | 164 | 181 | 148 | 146 | 149 | 147 | 147 |  | 162 | 174 | 176 | 185 | 187 | 175 | 152 | 4113809
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 167 | 163 | 167 | 168 | 161 | 176 | 178 | 179 | 185 | 164 | 163 | 172 | 213 | 217 | 162 | 161 | 159 | 159 |  | 179 | 188 | 190 | 198 | 188 | 186 | 168 | 4487355
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [26 empty] | 0
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 14 | [6 empty] | 18242
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 520320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 204012
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 12 |  |  | 25 |  | 25 | 25 | 25 |  |  |  |  | 237280
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 6 |  | 28 | 20 | [5 empty] | 31154
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 46 | 52 | 52 | 52 | 52 | 25 |  |  |  | 16 |  | 52 | 52 | 25 |  |  |  |  | 398880
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 86 |  | 100 | 100 | 100 | 100 | 100 | 80 | 24 | 559288
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [14 empty] | 27 | 69 | 108 | 113 |  | 113 | 113 | 113 | 113 | 113 |  |  | 817344
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 92 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 1395936
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 70 | 70 | 110 |  | 113 | 113 | 112 | 113 | 113 | 50 |  | 850560
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 1 | 1 | 2 | 4 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 24368
178
178