## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-02 | Tuesday
|  |  | Date (day): | 2021-02-02 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11760.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12933 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-01 | 2021-02-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 103 | 105 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2021-07-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 271 | 243 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 55 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 305 | 280 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 101 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 73 | 85 | 85
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 183 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 88 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  |  | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 208 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 75 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 122 | 102 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 62 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 91 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  |  | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2135 | 2664 | 3278 | 3528 | 108 | 2267
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 16 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 46 | 46
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 56 | 47 | 46 | 46 | 184 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 102 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 26 | 15 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 97 | 97 |  | 11 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 283 | 307 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 48 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 19 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 668 | 780 | 1125 | 1227 | 919 | 126
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 130 | 130 | 130 | 130
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 195 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 290 | 350 | 350
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Machine problem
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 90 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 51 | 50 | 50 |  | 113 | Gas shortage + ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 17 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 104 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 22 | 22
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 16 | 36 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1130 | 1082 | 1697 | 1959 | 500 | 492
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 95 | 85 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 82 | 82 | 82 |  |  | Engine problem
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 31 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 458 | 443 | 602.6 | 551 | 92 | 0
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 30 |  |  | Under maint.
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 105 | 105 |  | 225 | GT-2 & ST under maint.
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 46 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under maint
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 66 | 69 | 74 | 74 |  | 12 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 60 | 0 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 320 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 300 | 261 | 280 | 280
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 415 | 415 | 415 | 415 |  |  | RRT
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1292 | 1227 | 1483 | 1513 | 231 | 286
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 435 | 416 | 440 | 440
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 82 | 99 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 17 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 350 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 930 | 1027 | 1355 | 1641 | 0 | 68
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 22 | 22 |  | 11 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 36 | 87 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 510 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 12 | 4 | 0 | 0 |  |  | Machine problem.
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 508 | 658 | 897 | 997 | 0 | 205
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 43 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 157 | 180 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 114 | 183 | 220 | 220 |  |  | FGMO
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint. |  | 13/2/2021
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 31 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 100 | 35 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 491 | 900 | 1052 | 1254 | 381 | 439
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 281 | 180 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 5 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 289 | 293 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7901 | 9074 | 11760.6 | 12933 | 2355 | 4093
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7615.4007 | 8746 | 11335.4868 | 12465.5078
| A. |  | 2021-02-01 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9074 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5589 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9074 | MW
| 3 | Day peak Generation : |  |  | 7901 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8746 | MW
| 4 | Evening peak Generation : |  |  | 9074 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 178.3346 | MKWHr | By Solar | 0.40731 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 94.3849 | MKWHr |  | By Oil: | 52.6695 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.1999 | MKWHr |  | By Hydro: | 1.3601 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2355 | MW | Dhaka | 3025 | 3025 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4093 | MW | Chittagong | 844 | 844 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6448 | MW | Khulna | 1100 | 1100 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 818.02 | MMCFD |  |  | Rajshahi | 969 | 969 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 97774527.318 | ii) Oil : | Taka | 339747166.61 | Comilla | 740 | 740 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 75427596 | Total | Taka | 512949289.928 | Mymensingh | 805 | 805 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.709 | MKWHr. | Sylhet | 337 | 337 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -233 | MW (E to W) at | 19:00 | hrs | Barisal | 247 | 247 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -331 | MW at | 9:00 | hrs | Rangpur | 679 | 679 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 22.4° C |  |  | Total | 8746 | 8746 |  | 0
| B. |  | 2021-02-02 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 25.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12933 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
| 4 | Reserve(Generation end) |  |  |  | 3633 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 182.7763 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5579 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.2633 | MKWHr. | ii) HVDC Flow at Peak Time |  | 416 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0496 | MKWHr. | iii) Maximum HVDC Flow : |  | 621 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.68 |  | (b) Today: | 95.56 |  | (c) Rule Curve: |  | 96.86
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 260 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 71 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 74 | 96 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 285 | 8 | 11 | 0 | 31 | 0 | 0 | 95 | 0 | 0 | 0 | 85 | 34 | 50 | 252 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 415 | 0 | 0 | 144 | 0 | 100 |  | 521 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 30 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 460 | 33 | 0 | 0 |  | 4441 | 1933 | 6374 | 2833 | 521 | 1090 | 1185 | 610 | 61 | 0 | 74 | 0 | 0 | 95.71
2:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 275 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 190 | 8 | 72 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 72 | 101 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 31 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 10 | 255 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 30 | 416 | 0 | 0 | 18 | 0 | 100 |  | 521 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 460 | 33 | 0 | 0 |  | 4028 | 1919 | 5947 | 2865 | 521 | 1066 | 754 | 610 | 59 | 0 | 72 | 0 | 0 | 95.7
3:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 270 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 184 | 8 | 71 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 72 | 97 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 10 | 250 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 10 | 415 | 0 | 0 | 18 | 0 | 100 |  | 520 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 33 | 0 | 0 |  | 3923 | 1897 | 5820 | 2859 | 520 | 1075 | 626 | 610 | 58 | 0 | 72 | 0 | 0 | 95.7
4:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 270 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 70 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 70 | 108 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 10 | 250 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 17 | 0 | 100 |  | 519 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 33 | 0 | 0 |  | 3790 | 1854 | 5644 | 2824 | 519 | 1065 | 498 | 610 | 58 | 0 | 70 | 0 | 0 | 95.69
5:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 265 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 0 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 66 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 72 | 96 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 10 | 251 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 17 | 0 | 100 |  | 520 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 33 | 0 | 0 |  | 3768 | 1821 | 5589 | 2761 | 520 | 1075 | 493 | 610 | 58 | 0 | 72 | 0 | 0 | 95.69
6:00 | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 310 |  | 0 | 0 | 280 | 0 | 15 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 0 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 0 | 350 | 205 | 8 | 73 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 72 | 109 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 20 | 17 | 15 | 280 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 40 | 415 | 0 | 0 | 30 | 0 | 100 |  | 528 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 16 | 0 | 0 |  | 4026 | 1845 | 5871 | 2920 | 528 | 1069 | 614 | 610 | 58 | 0 | 72 | 0 | 0 | 95.68
7:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 310 |  | 0 | 0 | 280 | 0 | 25 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 25 | 28 | 0 | 33 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 18 | 20 | 40 | 100 | 0 | 0 | 0 | 350 | 183 | 8 | 70 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 72 | 96 | 0 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 26 | 0 | 0 | 94 | 0 | 4 | 1 | 20 | 17 | 26 | 252 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 40 | 400 | 21 | 0 | 60 | 0 | 100 |  | 621 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 117 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 0 | 25 | 460 | 0 | 0 | 0 |  | 4189 | 1964 | 6153 | 2788 | 621 | 1024 | 984 | 610 | 53 | 0 | 72 | 1 | 0 | 0
8:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 310 |  | 0 | 0 | 305 | 0 | 48 | 15 | 0 | 0 | 120 | 1 | 3 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 28 | 0 | 33 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 19 | 20 | 15 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 74 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 78 | 105 | 20 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 320 | 8 | 11 | 0 | 30 | 0 | 0 | 140 | 0 | 36 | 5 | 50 | 17 | 110 | 308 | 4 | 1 | 0 | 1 | 304 | 17 | 0 | 0 | 0 | 100 | 380 | 35 | 3 | 84 | 0 | 100 |  | 559 | 0 | 431 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 103 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 480 | 0 | 0 | 0 |  | 4807 | 2158 | 6965 | 2970 | 559 | 1018 | 1649 | 629 | 53 | 0 | 78 | 9 | 0 | 0
9:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 298 |  | 0 | 0 | 280 | 6 | 50 | 40 | 0 | 0 | 185 | 12 | 24 | 48 | 56 | 0 | 0 | 0 | 17 | 17 | 24 | 0 | 25 | 32 | 0 | 33 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 350 | 186 | 8 | 70 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 22 | 80 | 105 | 32 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 320 | 8 | 11 | 0 | 30 | 51 | 0 | 175 | 0 | 82 | 10 | 100 | 17 | 128 | 253 | 8 | 18 | 0 | 2 | 307 | 35 | 0 | 0 | 0 | 100 | 365 | 60 | 7 | 118 | 0 | 100 |  | 434 | 0 | 345 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 101 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 1 | 35 | 480 | 0 | 0 | 0 |  | 5191 | 2085 | 7276 | 2851 | 434 | 992 | 2168 | 629 | 54 | 48 | 80 | 20 | 0 | 0
10:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 288 |  | 0 | 0 | 275 | 45 | 64 | 55 | 0 | 0 | 184 | 30 | 40 | 48 | 60 | 0 | 0 | 0 | 17 | 35 | 13 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 19 | 18 | 8 | 130 | 0 | 0 | 0 | 350 | 185 | 8 | 70 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 80 | 105 | 57 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 49 | 0 | 0 | 200 | 0 | 108 | 14 | 100 | 17 | 128 | 250 | 12 | 34 | 0 | 4 | 307 | 35 | 0 | 0 | 15 | 100 | 332 | 72 | 9 | 144 | 9 | 108 |  | 434 | 0 | 345 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 36 | 0 | 112 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 2 | 35 | 460 | 0 | 0 | 0 |  | 5436 | 2180 | 7616 | 2876 | 434 | 1013 | 2421 | 610 | 55 | 98 | 80 | 29 | 0 | 0
11:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 278 |  | 0 | 0 | 230 | 50 | 75 | 55 | 0 | 0 | 170 | 32 | 40 | 48 | 60 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 350 | 185 | 8 | 48 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 82 | 99 | 72 | 22 | 1 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 120 | 0 | 0 | 200 | 0 | 126 | 16 | 100 | 17 | 125 | 252 | 24 | 34 | 0 | 4 | 307 | 35 | 0 | 0 | 16 | 100 | 295 | 72 | 22 | 144 | 19 | 100 |  | 434 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 52 | 12 | 22 | 0 | 11 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 172 | 0 | 36 | 0 | 113 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 3 | 35 | 440 | 0 | 0 | 0 |  | 5459 | 2219 | 7678 | 2789 | 434 | 977 | 2560 | 625 | 55 | 110 | 82 | 46 | 0 | 0
12:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 271 |  | 0 | 0 | 305 | 50 | 80 | 55 | 0 | 0 | 100 | 40 | 40 | 48 | 60 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 130 | 0 | 0 | 0 | 325 | 210 | 8 | 51 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 92 | 95 | 72 | 22 | 2 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 208 | 0 | 0 | 200 | 0 | 122 | 16 | 100 | 17 | 122 | 300 | 8 | 34 | 0 | 4 | 283 | 35 | 0 | 0 | 16 | 100 | 415 | 72 | 47 | 144 | 19 | 60 |  | 435 | 0 | 300 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 52 | 25 | 22 | 0 | 11 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 157 | 0 | 36 | 0 | 114 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 3 | 35 | 440 | 12 | 0 | 0 |  | 5683 | 2218 | 7901 | 2794 | 435 | 988 | 2620 | 721 | 56 | 123 | 92 | 72 | 0 | 0
13:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 261 |  | 0 | 0 | 300 | 44 | 82 | 55 | 0 | 0 | 153 | 40 | 40 | 48 | 60 | 0 | 0 | 0 | 35 | 35 | 36 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 19 | 20 | 12 | 130 | 0 | 0 | 0 | 280 | 189 | 8 | 50 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 88 | 82 | 72 | 22 | 2 | 29 | 0 | 45 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 330 | 16 | 11 | 0 | 250 | 0 | 0 | 200 | 0 | 110 | 14 | 100 | 17 | 122 | 262 | 8 | 34 | 0 | 4 | 301 | 35 | 0 | 0 | 16 | 100 | 415 | 72 | 47 | 144 | 18 | 100 |  | 435 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 0 | 5 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 171 | 0 | 36 | 0 | 163 | 0 | 0 | 105 | 0 | 0 | 0 | 80 | 0 | 4 | 35 | 440 | 5 | 0 | 0 |  | 5745 | 2332 | 8077 | 2886 | 435 | 1019 | 2754 | 635 | 56 | 133 | 88 | 71 | 8077 | 0
14:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 270 |  | 0 | 0 | 230 | 46 | 82 | 55 | 0 | 0 | 91 | 40 | 40 | 48 | 60 | 0 | 0 | 0 | 35 | 35 | 52 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 19 | 20 | 10 | 130 | 0 | 0 | 0 | 265 | 187 | 8 | 50 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 96 | 80 | 72 | 22 | 2 | 30 | 0 | 42 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 111 | 14 | 100 | 17 | 122 | 250 | 8 | 34 | 0 | 4 | 301 | 35 | 0 | 0 | 26 | 100 | 415 | 72 | 41 | 144 | 18 | 0 |  | 435 | 0 | 345 | 0 | 72 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 182 | 0 | 36 | 0 | 205 | 0 | 0 | 105 | 0 | 1 | 0 | 110 | 0 | 4 | 35 | 440 | 4 | 0 | 0 |  | 5519 | 2365 | 7884 | 2737 | 435 | 991 | 2747 | 619 | 56 | 138 | 96 | 65 | 0 | 95.64
15:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 292 |  | 0 | 0 | 250 | 20 | 82 | 55 | 0 | 0 | 90 | 40 | 7 | 16 | 60 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 265 | 187 | 8 | 45 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 90 | 80 | 40 | 22 | 1 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 85 | 11 | 100 | 17 | 120 | 252 | 8 | 0 | 0 | 3 | 307 | 35 | 0 | 0 | 36 | 100 | 415 | 84 | 30 | 144 | 0 | 0 |  | 435 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 8 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 166 | 0 | 36 | 0 | 197 | 0 | 0 | 70 | 0 | 27 | 0 | 113 | 0 | 3 | 35 | 410 | 4 | 0 | 0 |  | 5331 | 2190 | 7521 | 2709 | 435 | 992 | 2494 | 590 | 56 | 107 | 90 | 48 | 0 | 95.64
16:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 293 |  | 0 | 0 | 250 | 7 | 82 | 55 | 0 | 0 | 90 | 8 | 7 | 16 | 74 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 14 | 20 | 8 | 130 | 0 | 0 | 0 | 265 | 187 | 8 | 51 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 86 | 82 | 8 | 22 | 1 | 30 | 0 | 48 | 50 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 288 | 0 | 0 | 170 | 0 | 37 | 7 | 50 | 17 | 122 | 252 | 8 | 0 | 0 | 1 | 253 | 35 | 0 | 0 | 36 | 50 | 415 | 92 | 18 | 144 | 0 | 0 |  | 419 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 8 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 153 | 0 | 35 | 0 | 190 | 0 | 0 | 35 | 0 | 75 | 0 | 113 | 0 | 2 | 50 | 410 | 4 | 0 | 0 |  | 4986 | 2171 | 7157 | 2677 | 419 | 964 | 2229 | 590 | 56 | 107 | 86 | 29 | 0 | 95.63
17:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 267 |  | 0 | 0 | 280 | 7 | 97 | 55 | 0 | 0 | 123 | 8 | 7 | 16 | 73 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 4 | 19 | 20 | 21 | 130 | 0 | 0 | 0 | 290 | 199 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 82 | 81 | 8 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 286 | 0 | 0 | 170 | 0 | 32 | 2 | 50 | 17 | 122 | 270 | 8 | 0 | 0 | 0 | 195 | 35 | 0 | 0 | 36 | 50 | 415 | 92 | 4 | 144 | 0 | 0 |  | 416 | 0 | 370 | 0 | 3 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 12 | 0 | 0 | 8 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 157 | 0 | 34 | 0 | 176 | 0 | 0 | 35 | 0 | 113 | 0 | 113 | 0 | 1 | 50 | 410 | 4 | 0 | 0 |  | 5053 | 2229 | 7282 | 2793 | 416 | 964 | 2256 | 590 | 57 | 117 | 82 | 7 | 0 | 95.63
18:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 259 |  | 0 | 0 | 290 | 24 | 101 | 55 | 0 | 0 | 120 | 15 | 32 | 125 | 73 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 20 | 25 | 33 | 5 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 85 | 0 | 12 | 19 | 20 | 15 | 130 | 0 | 0 | 0 | 285 | 198 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 106 | 83 | 17 | 22 | 0 | 30 | 0 | 47 | 50 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 286 | 0 | 0 | 185 | 0 | 34 | 0 | 100 | 17 | 128 | 283 | 8 | 18 | 0 | 0 | 253 | 35 | 0 | 0 | 36 | 100 | 415 | 91 | 0 | 144 | 0 | 0 |  | 416 | 0 | 360 | 0 | 79 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 23 | 16 | 0 | 0 | 0 | 43 | 11 | 100 | 25 | 0 | 0 | 24 | 31 | 22 | 0 | 11 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 167 | 0 | 50 | 0 | 175 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 420 | 4 | 0 | 0 |  | 5617 | 2612 | 8229 | 2795 | 416 | 1024 | 2832 | 599 | 47 | 410 | 106 | 0 | 0 | 95.62
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 243 |  | 0 | 0 | 280 | 55 | 101 | 55 | 0 | 0 | 183 | 88 | 102 | 150 | 73 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 33 | 8 | 0 | 47 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 0 | 12 | 19 | 20 | 26 | 130 | 0 | 0 | 0 | 290 | 195 | 8 | 51 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 85 | 82 | 22 | 0 | 30 | 0 | 46 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 286 | 75 | 0 | 200 | 0 | 102 | 0 | 100 | 17 | 90 | 261 | 31 | 62 | 0 | 0 | 307 | 48 | 0 | 0 | 36 | 100 | 415 | 91 | 0 | 144 | 0 | 0 |  | 416 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 40 | 100 | 25 | 0 | 0 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 183 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 100 | 510 | 4 | 0 | 0 |  | 6196 | 2878 | 9074 | 2863 | 416 | 1062 | 3426 | 690 | 47 | 466 | 104 | 0 | 0 | 95.61
19:30 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 239 |  | 0 | 0 | 270 | 50 | 101 | 55 | 0 | 0 | 190 | 100 | 102 | 150 | 73 | 0 | 0 | 1 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 0 | 12 | 19 | 20 | 28 | 130 | 0 | 0 | 0 | 275 | 188 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 85 | 82 | 22 | 0 | 30 | 0 | 46 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 315 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 17 | 90 | 253 | 25 | 55 | 0 | 0 | 307 | 54 | 0 | 0 | 36 | 100 | 415 | 94 | 0 | 144 | 0 | 0 |  | 416 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 43 | 40 | 100 | 25 | 0 | 0 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 180 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 4 | 0 | 0 |  | 6124 | 2923 | 9047 | 2832 | 416 | 1064 | 3389 | 730 | 47 | 465 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 238 |  | 0 | 0 | 270 | 50 | 101 | 55 | 0 | 0 | 185 | 100 | 64 | 150 | 73 | 0 | 0 | 2 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 0 | 12 | 19 | 20 | 31 | 130 | 0 | 0 | 0 | 275 | 184 | 8 | 48 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 102 | 85 | 82 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 70 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 315 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 129 | 0 | 100 | 17 | 90 | 252 | 8 | 35 | 0 | 0 | 307 | 54 | 0 | 0 | 36 | 100 | 416 | 96 | 0 | 144 | 0 | 0 |  | 416 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 15 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 42 | 100 | 25 | 0 | 0 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 170 | 0 | 87 | 0 | 182 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 6111 | 2906 | 9017 | 2877 | 416 | 1064 | 3315 | 730 | 47 | 466 | 102 | 0 | 0 | 95.61
21:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 227 |  | 0 | 0 | 285 | 28 | 101 | 55 | 0 | 0 | 190 | 100 | 32 | 115 | 73 | 0 | 0 | 6 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 0 | 12 | 19 | 20 | 35 | 130 | 0 | 0 | 0 | 275 | 184 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 102 | 86 | 64 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 106 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 17 | 90 | 252 | 8 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 36 | 100 | 415 | 104 | 0 | 144 | 0 | 0 |  | 416 | 0 | 325 | 0 | 99 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 170 | 0 | 87 | 0 | 170 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 5933 | 2721 | 8654 | 2894 | 416 | 1043 | 3178 | 730 | 47 | 244 | 102 | 0 | 0 | 95.61
22:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 227 |  | 0 | 0 | 270 | 7 | 99 | 30 | 0 | 0 | 190 | 60 | 0 | 64 | 73 | 0 | 0 | 0 | 54 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 20 | 30 | 130 | 0 | 0 | 0 | 305 | 200 | 8 | 52 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 96 | 86 | 8 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 105 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 98 | 0 | 100 | 17 | 90 | 265 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 8 | 100 | 415 | 93 | 0 | 144 | 0 | 0 |  | 416 | 0 | 320 | 0 | 33 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 171 | 0 | 87 | 0 | 170 | 0 | 0 | 105 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 5508 | 2515 | 8023 | 2949 | 416 | 1037 | 2571 | 730 | 47 | 177 | 96 | 0 | 0 | 95.61
23:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 236 |  | 0 | 0 | 275 | 7 | 99 | 15 | 0 | 0 | 165 | 24 | 0 | 16 | 73 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 130 | 0 | 0 | 0 | 310 | 200 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 88 | 103 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 101 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 33 | 0 | 100 | 17 | 90 | 270 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 8 | 100 | 415 | 53 | 0 | 144 | 0 | 0 |  | 416 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 172 | 0 | 87 | 0 | 166 | 0 | 0 | 70 | 0 | 0 | 0 | 55 | 0 | 0 | 35 | 500 | 0 | 0 | 0 |  | 5293 | 2159 | 7452 | 2931 | 416 | 1065 | 2105 | 680 | 47 | 120 | 88 | 0 | 0 | 95.6
24:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 242 |  | 0 | 0 | 280 | 7 | 81 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 130 | 0 | 0 | 0 | 280 | 185 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 80 | 104 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 106 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 305 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 17 | 90 | 252 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 415 | 14 | 0 | 144 | 0 | 0 |  | 416 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 171 | 0 | 62 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 500 | 0 | 0 | 0 |  | 4942 | 1906 | 6848 | 2847 | 416 | 1044 | 1725 | 679 | 47 | 10 | 80 | 0 | 0 | 95.59
KWH | 0 | 0 | 0 | 4410000 | 0 | 2477727 | 0 | 0 | 6678000 |  | 0 | 0 | 6484160 | 485760 | 1625352 | 809275 | 0 | 0 | 3539000 | 686400 | 512352 | 943680 | 1248757 | 0 | 0 | 14304 | 630360 | 419098 | 564787 | 430776 | 600000 | 706320 | 444800 | 786300 | 15200 | 0 | 1360145 | 0 | 0 | 0 | 143240 | 0 | 0 | 0 | 0 |  | 308880 | 0 | 265407 | 0 | 56640 | 364320 | 468672 | 590400 | 3054774 | 0 | 0 | 0 | 7674000 | 4687000 | 217454 | 1397760 | 597600 | 138720 | 0 | 1145078 | 0 | 0 | 0 | 464148 | 252180 | 796200 | 543650 | 2049600 | 2123400 | 765120 | 527940 | 10000 | 714000 | 0 | 1117800 | 1183824 | 0 | 410000 | 0 | 1597440 | 0 | 0 | 0 | 0 | 206100 | 7573000 | 303930 | 264000 | 0 | 3916689 | 158740 | 0 | 3688800 | 0 | 1404000 | 110295 | 1675200 | 445920 | 2146109 | 6301000 | 192000 | 370176 | 0 | 23113 | 6627513 | 603768 | 0 | 0 | 438480 | 1886400 | 9666400 | 1304640 | 232720 | 2787840 | 107890 | 1290000 |  | 11263273 | 0 | 8436672 | 0 | 969600 | 0 | 0 | 0 | 0 | 118656 | 233250 | 0 | 493500 | 127680 | 0 | 0 | 0 | 521154 | 94039 | 661504 | 330270 | 0 | 0 | 506880 | 272527 | 517920 | 0 | 203994 | 0 | 0 | 4184500 | 0 | 0 | 0 | 0 | 4219945 | 0 | 896406 | 0 | 3974282 | 0 | 0 | 1570992 | 0 | 816576 | 0 | 1162560 | 0 | 31180 | 1170912 | 12015400 | 262827 | 0 | 15600 |  | 123262523 | 55072099 | 178334622 | 69288743 | 11263273 | 25096196 | 49792490 | 16199900 | 1360145 | 2876967 | 2049600 | 407308 | 0
Fuel Cost | 0 | 0 | 0 | 6482700 | 0 | 3270599.64 | 0 | 0 | 6878340 |  | 0 | 0 | 7197417.6 | 3686918.4 | 11198675.28 | 6846466.5 | 0 | 0 | 6122470 | 5168592 | 4672650.24 | 9285811.2 | 11513539.54 | 0 | 0 | 130023.36 | 4601628 | 3239627.54 | 5568799.82 | 323082 | 450000 | 0 | 0 | 0 | 146984 | 0 | 367239.15 | 0 | 0 | 0 | 1330699.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2574447.9 | 0 | 492768 | 2885414.4 | 590526.72 | 1753488 | 4521065.52 | 0 | 0 | 0 | 7674000 | 4312040 | 280515.66 | 1607424 | 675288 | 194208 | 0 | 1958083.38 | 0 | 0 | 0 | 589467.96 | 189135 | 1393350 | 407737.5 | 15372000 | 2250804 | 6947289.6 | 670483.8 | 159400 | 1170960 | 0 | 1989684 | 1846765.44 | 0 | 426400 | 0 | 3051110.4 | 0 | 0 | 0 | 0 | 420444 | 7648730 | 227947.5 | 200640 | 0 | 29610168.84 | 2695405.2 | 0 | 19181760 | 0 | 13815360 | 1289348.55 | 13652880 | 4838232 | 15130068.45 | 5859930 | 1751040 | 3498163.2 | 0 | 0 | 50103998.28 | 5258819.28 | 0 | 0 | 3757773.6 | 12563424 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64876452.48 | 0 | 8858505.6 | 0 | 7621056 | 0 | 0 | 0 | 0 | 1243514.88 | 2430465 | 0 | 764925 | 1246156.8 | 0 | 0 | 0 | 5128155.36 | 955436.24 | 5854310.4 | 2543079 | 0 | 0 | 4911667.2 | 2643511.9 | 994406.4 | 0 | 154423.458 | 0 | 0 | 22679990 | 0 | 0 | 0 | 0 | 5570327.4 | 0 | 1344609 | 0 | 4649909.94 | 0 | 0 | 16401156.48 | 0 | 7749306.24 | 0 | 9021465.6 | 0 | 344539 | 8653039.68 | 52747606 | 0 | 0 | 0 |  | 355970254.05 | 239388015.058 | 595358269.108 | 65378618.398 | 64876452.48 | 32395908.92 | 312061978.73 | 75427596 | 367239.15 | 27685187.88 | 15372000 | 1793287.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 271 |  | 0 | 0 | 305 | 50 | 80 | 55 | 0 | 0 | 100 | 40 | 40 | 48 | 60 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 130 | 0 | 0 | 0 | 325 | 210 | 8 | 51 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 22 | 92 | 95 | 72 | 22 | 2 | 30 | 0 | 45 | 50 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 208 | 0 | 0 | 200 | 0 | 122 | 16 | 100 | 17 | 122 | 300 | 8 | 34 | 0 | 4 | 283 | 35 | 0 | 0 | 16 | 100 | 415 | 72 | 47 | 144 | 19 | 60 |  | 435 | 0 | 300 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 52 | 25 | 22 | 0 | 11 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 157 | 0 | 36 | 0 | 114 | 0 | 0 | 105 | 0 | 0 | 0 | 5 | 0 | 3 | 35 | 440 | 12 | 0 | 0 |  | 7901 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 243 | 0 | 0 | 0 | 280 | 55 | 101 | 55 | 0 | 0 | 183 | 88 | 102 | 150 | 73 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 32 | 25 | 33 | 8 | 0 | 47 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 85 | 0 | 12 | 19 | 20 | 26 | 130 | 0 | 0 | 0 | 290 | 195 | 8 | 51 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 104 | 85 | 82 | 22 | 0 | 30 | 0 | 46 | 50 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 286 | 75 | 0 | 200 | 0 | 102 | 0 | 100 | 17 | 90 | 261 | 31 | 62 | 0 | 0 | 307 | 48 | 0 | 0 | 36 | 100 | 415 | 91 | 0 | 144 | 0 | 0 |  | 416 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 40 | 100 | 25 | 0 | 0 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 183 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 100 | 510 | 4 | 0 | 0 |  | 9074 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 97 | 46 | 22 | 25 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 147 | 110 | 82 | 22 | 0 | 30 | 30 | 51 | 50 | 0 | 105 | 0 | 74 | 0 | 0 | 0 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 280 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 0 | 144 | 0 | 100 |  | 440 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 97 | 46 | 22 | 15 | 130 | 0 | 0 | 0 | 350 | 225 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 22 | 135 | 110 | 82 | 22 | 1.6 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 74 | 0 | 0 | 0 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 280 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 50 | 144 | 0 | 100 |  | 440 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 50 | 220 | 0 | 0 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 35 | 620 | 0 |  | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 318 | 0 | 0 | 0 | 260 | 7 | 36 | 15 | 0 | 0 | 190 | 10 | 16 | 0 | 85 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 28 | 20 |  | 0 | 0 | 46 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 51 | 0 | 0 | 18 | 20 | 15 | 130 | 0 | 0 | 0 | 285 | 184 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 78 | 106 | 23 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 107 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 65 | 0 | 0 | 180 | 0 | 49 | 5 | 60 | 17 | 90 | 253 | 18 | 0 | 0 | 0 | 308 | 17 | 0 | 0 | 8 | 100 | 415 | 55 | 8 | 130 | 0 | 0 | 0 | 434 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 35 | 0 | 166 | 0 | 0 | 90 | 0 | 0 | 0 | 92 | 0 | 1 | 35 | 450 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5589 | 5:00
| Highest Generation |  | 9074 | 19:00
| Day Peak Generation |  | 7901 | 12:00
| Evening Peak Generation |  | 9074 | 19:00
| HVDC Max Flow |  | 621 | 7:00
| HVDC EvPeak Flow |  | 416 | 19:00
| Load factor L.F |  | 81.89%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7901 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5579 | MW
Evening Peak Generation : |  | 9074 | MW Hour : | 19:00 | Available Max Generation : |  | 12933 | MW
E.P. Demand (at gen end) : |  | 9074 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9074 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3633 | MW
Total Gen. (MKWH) : |  | 178.3346 | System Load Factor : | 81.89% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -331 | MW at | 9:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-02
Actual : | 95.56 | Ft.(MSL) , | Rule curve : | 96.86 | Ft.( MSL )
Gas Consumed : | Total = | 818.02 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 97774527.318
: |  | Coal : | 75427596 | Oil : | 339747166.61 | Total : | 512949289.928
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3344.7815 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1133.0379 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1014.3852 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 916.3059 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 828.205 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 668.3211 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 379.3195 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.2236 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 515.4155 |  |  | 0 | 0%
Total | 0 |  | 8971.9952 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-4,5
|  |  |  | 2) Baghabari-71 &100 MW | 11) Haripur 412 MW
3) Ghorasal Unit-1,2,3,4
4) Shahjibazar 330 MW
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,4 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Haripur-Bhulta 230 kV Ckt-1 was shut down at 08:22 for C/M.
b) Kaliakoir-Aminbazar 230 kV Ckt-1 was under shut down from 08:32 to 16:11 for A.M.
c) Kaliakoir-Tongi 230 kV Ckt-2 was under shut down from 08:45 to 16:40 for A.M.
d) Khulshi-AKSML 132 kV Ckt was under shut down from 09:10 to 16:50 for A/M.
e) Ramganj-Desh Energy 132 kV Ckt-1 was under shut down from 09:04 to 20:26 for D/W.
f) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 09:35 to 16:35 for A/M.
g) Khulna(C) T-1 & T-2 tripped at 08:15 due to 33 kV cable burst showing O/C, E/F relay and T-2 was switched |  |  |  |  | About 20 MW power interruption occurred under Khulna(C) S/S area
on at 09:36 and T-1 was switched on at 19:59. |  |  |  |  | from 08:15 to 08:40.
h) Bheramara HVDC block-1 was shut down at 10:21 for A/M.
i) Jamalpur 132/33 kV T-1 transformer was shut down at 09:15 for C/M.
j) Comilla(N)-Daudkandi 132 kV Ckt-1 was under shut down from 09:22 to 16:32 for A/M.
k) Ashugonj-Kishoreganj 132 kV Ckt-1 was under shut down from 09:29 to 17:48 for A/M.
l) Ramganj-Chowmuhoni 132 kV Ckt-1 was under shut down from 09:46 to 18:39 for A/M.
m) Hasnabad 230 kV Bay mid breaker was under shut down from 09:54 to 15:15 for C/M.
n) Madanganj-Munshiganj 132 kV Ckt-2 was under shut down from 09:55 to 16:33 for A/M.
o) Fenchuganj P/S-Fenchuganj S/S 132 kV Ckt-3 was under shut down from 10:21 to 13:53 for A/M.
p) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 10:17 to 13:28 for A/M.
q) Meghnaghat 230/0.66 kV start-up transformer was under shut down from 10:26 to 17:27 for A/M.
r) Uttara 132/33 kV Gt-1 transformer was shut down at 11:08 for A/M.
s) Kabirpur 132/33 kV T-2 transformer was under shut down from 11:15 to 15:29 for D/W.
t) Shahjibazar-Sreemangal 132 kV Ckt-2 was under shut down from 09:51 to 13:49 for A/M.
u) Haripur-Meghnaghat 230 kV Ckt-1 was under shut down from 15:26 to 17:22 for protection test.
v) Siddhirganj GT-2 was synchronized at 16:05.
w) Daudkandi 132/33 kV T-3 transformer tripped at 15:34 showing Diff. L1 at 132 kV side due to 33 kV
PBS Chandpur feeder fault and was switched on at 16:12. |  |  |  |  | from 15:34 to 16:12.
x) Shahjibazar 330 Gt-1 was synchronized at 19:41.
y) Hasnabad 132/33 kV T-1,T-2 & T-5 transformers tripped at 21:18 for 33 kV Zinzira 1,2 feeder fault and |  |  |  |  | About 100 MW power interruption occurred under Hasnabad S/S area
were switched on at 21:58. |  |  |  |  | from 21:18 to 21:58.
z) Fenchuganj S/S-Sylhet 132 kV Ckt tripped at 22:10 from both ends showing Dist. Z2 at Fenchuganj end |  |  |  |  | About 35 MW power interruption occurred under Biyanibazar S/S area
and Dist. Z1,A at Sylhet end and was switched on at 22:43. |  |  |  |  | from 22:10 to 22:43.
aa) Ullon-Siddhirganj 132 kV Ckt-1 was under shut down from 00:31(02/02/2021) to 01:41 for removing
GI wire from this Ckt.
ab) Sikalbaha-TK Chemical 132 kV Ckt was shut down at 07:01(02/02/2021) for D/W.
ac) Tongi-Ghorashal 230 kV Ckt-1 was shut down at 07:37(02/02/2021) for A/M.
ad) Khulna(C) 132/33 kV T-3 transformer was shut down at 07:38(02/02/2021) for R/H maint. at Bus isolator
of 33 kV Khalishpur feeder.
ae) Dohazari-Matarbari-Cox's bazar 132 kV Ckt-1 was shut down at 07:12(02/02/2021) for C/M. |  |  |  |  | About 16 MW power interruption occurred under Matarbari S/S area
from 07:12(02/02/2021) to 08:12.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4410000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2477727
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 243 | 6678000 | Gas Shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 55 | 485760 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6484160 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 101 | 1625352
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 809275
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 73 | 1248757 | High Voltage.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 430776
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 183 | 3539000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 88 | 686400 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 512352
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 14304 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 630360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 943680
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 419098 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 564787
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1306320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 444800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 786300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 15200 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 3916689
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 75 | 158740 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 102 | 1404000 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 62 | 370176 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 1304640 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2787840 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2664 | 44454493
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 143240
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110295
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 364320 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 47 | 1360145 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 265407 | High Voltage.
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1675200
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 468672
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 590400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 56640 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23113
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 6627513
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 48 | 603768 | Engine problem
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1886400
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 107890 | on test
| Chattogram area Total |  |  |  | 2266 | 780 | 14283003
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 130 | 3054774
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 195 | 4687000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7674000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 597600 | Machine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138720 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1145078
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 90 | 2146109 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1397760 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 445920 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 464148
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2049600
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 796200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 543650
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 36 | 438480 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1082 | 26048673
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 85 | 2123400 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 527940
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 82 | 765120 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10000
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3688800 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 31 | 192000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 232720
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 308880
| Mymensingh Area Total |  |  |  | 709 | 443 | 7848860
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 714000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 410000 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 46 | 1117800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1183824
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 69 | 1597440 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 1290000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 303930 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7573000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 261 | 6301000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 206100 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 415 | 9666400 | RRT
| Sylhet Area Total |  |  |  | 1988 | 1227 | 30627494
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 416 | 11263273
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 969600 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 17 | 118656 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8436672 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 233250
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1570992
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1027 | 22592443
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 127680 | Engine problem
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 493500 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 87 | 896406
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 510 | 12015400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 4 | 262827 | High Voltage.
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 15600 | High Voltage.
| Barisal Area Total |  |  |  | 1676 | 658 | 13811413
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 521154
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 94039 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 330270 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4219945 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 3974282 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 272527 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 517920
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203994
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 506880
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 661504
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 816576
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 1170912 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 900 | 13290003
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4184500 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1162560
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31180
| Rangpur Area Total |  |  |  | 605 | 293 | 5378240
| Total |  |  |  | 20748 | 9074 | 178334622
| Eastern Grid Total |  |  |  | 14000 | 6196 | 123262523
| Western Grid Total |  |  |  | 6748 | 2878 | 55072099
| National Grid Total |  |  |  | 20748 | 9074 | 178334622
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-02-01
| (a) ENTIRE EASTERN GRID : |  | 5751 | MW | (b) ENTIRE WESTERN GRID : |  | 2995 | MW
| i) Dhaka area |  | 3025 | MW | i) Khulna area |  | 1100 | MW
| ii) Chittagong area |  | 844 | MW | ii) Rajshahi area |  | 969 | MW
| iii) Comilla area |  | 740 | MW | iii) Barisal area |  | 247 | MW
| iv) Mymensingh area |  | 805 | MW | iv) Rangpur area |  | 679 | MW
| v) Sylhet area |  | 337 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8746 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 92 | 19:00 | Sherpur | 112 | 18:30 | Jhenida | 84 | 18:30
| Munsiganj | 86 | 22:00 | Srimongal | 29 | 19:30 | Bottail | 112 | 18:30
| Sonargaon | 60 | 13:00 | Shahjibazar | 89 | 18:30 | G.K Project | 33 | 19:30
| Shyampur | 140 | 14:00 | Fenchuganj | 23 | 19:00 | Faridpur | 132 | 20:00
| Bhulta | 160 | 14:00 | Kulawara | 27 | 18:00 | Madaripur | 61 | 20:00
| Madanganj | 53 | 2:00 | Sylhet | 81 | 19:00 | Sariatpur | 42 | 19:30
| Shitalakhya | 98 | 13:00 | Chatak | 19 | 18:00 | Gopalganj | 66 | 18:30
| Rahim steel | 21 | 15:00 | Sunamganj | 30 | 18:30 | Bagerhat | 81 | 19:00
| Matuail | 48 | 13:00 | Biani Bazar | 42 | 20:00 | Mongla | 38 | 9:00
| Ghorasal | 64 | 20:00 | Comilla (S) | 108 | 18:30 | Satkhira | 71 | 18:30
| Narsingdi | 127 | 20:00 | Comilla(N) | 63 | 20:00 | Gallamari | 32 | 11:00
| Haripur (SBU) | 102 | 14:00 | Chandpur | 40 | 18:30 | Magura | 40 | 18:30
| Ullon | 50 | 14:00 | Feni | 79 | 19:30 | Norail | 24 | 18:30
| Hasnabad | 103 | 18:30 | Chowmuhani | 119 | 21:00 | Chuadanga | 65 | 19:00
| Magbazar | 63 | 18:30 | Ashuganj | 40 | 18:30 | Barisal(N) | 30 | 19:30
| Maniknagar | 56 | 11:00 | Daudkandi | 94 | 20:00 | Barisal (S) | 68 | 18:30
| Bangabhaban | 14 | 10:00 | B.Baria | 100 | 18:30 | Patuakhali | 92 | 19:30
| Narinda | 64 | 11:00 | Ramganj | 52 | 21:00 | Bhandaria | 40 | 19:30
| Dhanmondi | 90 | 13:00 | Chaddagram | 26 | 19:00 | Borhan Uddin | 25 | 19:00
| Lalbag | 70 | 13:00 | PHP | 9 | 9:00 | Ishurdi | 45 | 20:00
| Madartek | 51 | 18:30 | Kochua | 42 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Madunaghat | 43 | 19:30 | Natore | 93 | 18:30
| Aftabnagar | 6 | 0.54167 | Hathazari | 65 | 0.77083 | Bogra | 122 | 0.79167
| Fatullah | 39 | 18:30 | Khulshi | 149 | 15:00 | Noagaon | 99 | 19:00
| Mirpur | 68 | 18:00 | Halishahar | 85 | 19:00 | Rajshahi | 94 | 19:30
| Kalyanpur | 57 | 14:00 | Baraulia | 101 | 1:00 | Rajshahi New | 12 | 20:00
| Gulshan | 72 | 13:00 | Sikalbaha | 19 | 18:00 | C.Nawabganj | 63 | 19:30
| Uttara | 62 | 18:00 | Dohazari | 58 | 19:00 | Amnura | 52 | 11:00
| Uttara New | 22 | 18:00 | Cox'sbazar | 80 | 18:00 | Pabna | 63 | 19:00
| Kamrangirchar | 64 | 12:00 | Chandraghona | 30 | 18:00 | Shahjadpur | 74 | 19:00
| Savar | 122 | 18:30 | Kaptai | 2 | 7:00 | Serajganj | 75 | 19:30
| Bhasantec | 95 | 13:00 | A. Khaer Stl. | 13 | 8:00 | Niyamatpur | 65 | 13:00
| Agargaon | 44 | 13:00 | Bakulia | 67 | 13:00 | Joypurhat | 51 | 10:00
| Satmosjid | 57 | 0.58333 | Julda | 19 | 0.29167 | Sherpur(Bogura) | 44 | 0.79167
| Tongi | 87 | 12:00 | TK chemical | 19.6 | 20:00 | Mohastangor | 42 | 19:30
| Kabirpur | 198 | 15:00 | Modern Steel | 0 | 1:00 | Bangura | 16 | 19:00
| Basundhara | 94 | 14:00 | Shahmirpur | 16.5 | 20:00 | Rangpur | 114 | 19:00
| Manikganj | 50 | 21:00 | Khagrachhari | 22 | 1:00 | Lalmonirhat | 60 | 13:00
| Joydevpur | 113 | 18:30 | Matarbari | 26 | 18:00 | Saidpur | 104 | 12:00
| New Tongi | 68 | 12:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 102 | 13:00
| Korda | 138 | 12:00 | Rangamati | 10 | 19:00 | Thakurgaon | 70 | 19:00
| Dhamrai | 72 | 18:30 | Abul Khair 230 | 138 | 3:00 | Palashbari | 100 | 19:00
| Rajendrapur | 74 | 19:00 | BSRM | 99 | 13:00 | Barapukuria | 49 | 9:00
| Valuka | 100 | 11:00 | GPH Ispat | 12 | 18:00 | Panchagar | 48 | 18:30
| Tangail | 144 | 19:00 | Goalpara | 22 | 19:30 | Joldhaka | 25 | 18:30
| Mymensing | 163 | 18:30 | Central s/s | 76 | 13:00 | Kurigram | 52 | 18:30
| Kishorganj | 102 | 20:00 | Noapara | 52 | 19:00
| Netrokona | 93 | 13:00 | Jessore | 86 | 13:00
| Jamalpur | 106 | 19:00 | Benapol | 42 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 7:00 | 405 | 12:00 | Kaliakoir | 407 | 0.29167 | 398 | 0.5
| Bheramara | 412 | 5:00 | 405 | 11:00 | Bhulta | 395 | 0.29167 | 385 | 0.5
| Ashuganj(N) | 396 | 20:00 | 384 | 13:00 | Gopalganj | 400 | 0.625 | 388 | 0.79167
| Payra | 410 | 20:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 239 | 7:00 | 225 | 16:00
| Ishurdi | 241 | 5:00 | 233 | 13:00 | Megnaghat | 243 | 24:00 | 238 | 5:00
| Ashuganj | 243 | 18:00 | 240 | 3:00 | Fenchuganj | 243 | 20:00 | 238 | 12:00
| Serajganj | 234 | 1:00 | 228 | 8:00 | Siddhirganj | 241 | 7:00 | 235 | 11:00
| Baghabari | 239 | 19:30 | 232 | 11:00 | Maniknagar | 239 | 20:00 | 233 | 12:00
| Barapukuria | 235 | 3:00 | 228 | 10:00 | Agargaon | 241 | 10:00 | 234 | 12:00
| Bogra | 234 | 1:00 | 223 | 9:00 | Barisal | 252 | 7:00 | 243 | 22:00
| Rajshahi | 239 | 4:00 | 229 | 8:00 | Bhola 225 MW | 255 | 15:00 | 245 | 5:00
| Khulna South | 243 | 3:00 | 230 | 16:00 | AKSML | 236 | 7:00 | 228 | 3:00
| Rampura | 235 | 7:00 | 231 | 12:00 | BSRM | 238 | 20:00 | 228 | 17:00
| Haripur | 240 | 24:00 | 234 | 12:00 | Bibiyana | 247 | 5:00 | 238 | 17:00
| Hasnabad | 238 | 7:00 | 236 | 10:00 | Bhulta | 241 | 24:00 | 235 | 12:00
| Shyampur | 240 | 20:00 | 220 | 12:00 | Ashuganj (S) | 241 | 24:00 | 236 | 10:00
| Aminbazar | 242 | 23:00 | 236 | 10:00 | Kaliakoir | 236 | 21:00 | 229 | 10:00
| Tongi | 236 | 18:00 | 227 | 11:00 | GPH | 238 | 7:00 | 226 | 17:00
| Comilla (N) | 244 | 24:00 | 235 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 18:30 | 138 | 12:00 | Madanhat | 141 | 0.8125 | 135 | 0.5
| Munsiganj | 141 | 21:00 | 135 | 14:00 | Hathazari | 140 | 0.8125 | 134 | 0.66667
| Sonargaon | 138 | 11:00 | 135 | 1:00 | Khulshi | 138 | 0.041667 | 133 | 0.66667
| Shyampur | 135 | 8:00 | 131 | 12:00 | Halishahar | 140 | 0.041667 | 133 | 0.5
| Bhulta | 138 | 21:00 | 134 | 1:00 | Baraulia | 140 | 0.16667 | 134 | 0.5
| Madanganj | 140 | 22:00 | 134 | 2:00 | Sikalbaha | 140 | 0.041667 | 134 | 0.70833
| Shitalakhya | 142 | 19:00 | 134 | 2:00 | Dohazari | 137 | 0.041667 | 130 | 0.5
| Rahim steal | 141 | 21:00 | 137 | 12:00 | Cox'sbazar | 132 | 0.25 | 124 | 0.5
| Matuail | 141 | 18:30 | 138 | 12:00 | Chandraghona | 140 | 0.041667 | 134 | 0.5
| Ghorasal | 142 | 2:00 | 140 | 16:00 | Kaptai | 138 | 0.041667 | 138 | 0.041667
| Narsinghdi | 138 | 4:00 | 135 | 12:00 | A. Khaer Stl. | 139 | 0.16667 | 134 | 0.5
| Haripur (SBU) | 140 | 3:00 | 137 | 13:00 | Bakulia | 140 | 0.041667 | 131 | 0.66667
| Ullon | 136 | 4:00 | 131 | 11:00 | Julda | 140 | 0.79167 | 134 | 0.5
| Hasnabad | 140 | 22:00 | 135 | 1:00 | TK Chemical | 140 | 0.83333 | 134 | 0.45833
| Magbazar | 136 | 1:00 | 132 | 13:00 | Modern Steel | 140 | 0.79167 | 133 | 0.70833
| Maniknagar | 138 | 1:00 | 135 | 11:00 | Shahmirpur | 140 | 0.83333 | 133 | 0.70833
| Bangabhaban | 138 | 1:00 | 135 | 11:00 | Khagrachhari | 140 | 0.041667 | 133 | 0.5
| Narinda | 138 | 1:00 | 135 | 11:00 | Matarbari | 133 | 0.041667 | 132 | 0.16667
| Dhanmondi | 136 | 4:00 | 131 | 11:00 | Baroiar Hat | 140 | 0.29167 | 135 | 0.5
| Lalbag | 139 | 20:00 | 133 | 2:00 | Rangamati | 139 | 1:00 | 133 | 12:00
| Madartek | 136 | 5:00 | 131 | 13:00 | Goalpara S/S | 139 | 9:00 | 130 | 16:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 139 | 11:00 | 130 | 0.625
| Aftabnagar | 136 | 3:00 | 132 | 12:00 | Noapara | 137 | 1:00 | 128 | 0.70833
| Fatullah | 135 | 19:30 | 131 | 12:00 | Jessore | 134 | 6:00 | 126 | 0.54167
| Mirpur | 140 | 19:30 | 137 | 14:00 | Benapol | 137 | 0.083333 | 126 | 0.70833
| Kalyanpur | 141 | 20:00 | 137 | 12:00 | Jhenida | 136 | 1:00 | 124 | 0.77083
| Gulshan | 135 | 1:00 | 131 | 12:00 | Bottail | 137 | 0.16667 | 130 | 0.54167
| Uttara | 140 | 23:00 | 136 | 12:00 | G.K Project | 141 | 0.20833 | 137 | 0.33333
| Uttara New | 140 | 18:30 | 135 | 16:00 | Faridpur | 137 | 0.20833 | 133 | 0.77083
| Kamrangirchar | 137 | 18;30 | 132 | 12:00 | Madaripur | 143 | 0.375 | 138 | 0.77083
| Savar | 140 | 1:00 | 135 | 8:00 | Shariyatpur S/S | 142 | 1:00 | 136 | 0.79167
| Bhasantec | 138 | 1:00 | 134 | 12:00 | Gopalganj | 144 | 0.625 | 138 | 0.33333
| Agargaon | 139 | 24:00 | 134 | 12:00 | Bagerhat | 138 | 9:00 | 128 | 0.58333
| Satmosjid | 138 | 1:00 | 134 | 12:00 | Mongla | 137 | 18:00 | 127 | 0.70833
| Tongi | 142 | 19:00 | 137 | 15:00 | Satkhira | 138 | 11:00 | 129 | 17:00
| Kabirpur | 137 | 20:00 | 128 | 12:00 | Gallamari | 138 | 0.16667 | 130 | 0.70833
| Basundhara | 140 | 19:00 | 135 | 16:00 | Magura | 136 | 2:00 | 124 | 0.77083
| Manikganj | 145 | 20:00 | 140 | 17:00 | Narail | 135 | 0.041667 | 123 | 0.77083
| Joydevpur | 140 | 7:00 | 136 | 17:00 | Chuadanga | 135 | 1:00 | 120 | 0.77083
| New Tongi | 140 | 23:00 | 136 | 17:00 | Barisal(N) | 143 | 10:00 | 137 | 20:00
| Kodda | 141 | 19:00 | 134 | 16:00 | Barisal (S) | 142 | 0.125 | 136 | 0.875
| Dhamrai | 136 | 0:00 | 128 | 12:00 | Patuakhali(S) | 136 | 0.20833 | 133 | 0.83333
| Rajendrapur | 140 | 0:00 | 135 | 17:00 | Bhandaria | 140 | 0.41667 | 135 | 0.33333
| Valuka | 132 | 0:00 | 121 | 12:00 | Ishurdi | 139 | 6:00 | 135 | 16:00
| Tangail | 136 | 0:00 | 128 | 12:00 | Ruppur Paromanobik | 139 | 5:00 | 135 | 16:00
| Mymensing | 135 | 0:00 | 125 | 12:00 | Natore | 138 | 18:00 | 131 | 8:00
| Kishorganj | 135 | 0:00 | 126 | 13:00 | Bogra | 137 | 20:00 | 128 | 9:00
| Netrokona | 132 | 1:00 | 123 | 12:00 | Noagaon | 133 | 4:00 | 122 | 9:00
| Jamalpur | 140 | 19:30 | 132 | 2:00 | Rajshahi | 136 | 20:00 | 130 | 8:00
| Sherpur | 139 | 20:00 | 129 | 4:00 | Rajshahi New | 136 | 20:00 | 130 | 8:00
| Srimongal | 141 | 4:00 | 135 | 18:00 | C.Nawabganj | 136 | 20:00 | 127 | 8:00
| Shahjibazar | 138 | 1:00 | 134 | 12:00 | Amnura | 138 | 20:00 | 126 | 7:00
| Fenchuganj | 140 | 24:00 | 137 | 12:00 | Pabna | 139 | 5:00 | 134 | 8:00
| Khulawara | 140 | 5:00 | 136 | 12:00 | Shahjadpur | 140 | 18:00 | 135 | 13:00
| Sylhet | 138 | 1:00 | 133 | 12:00 | Serajganj | 137 | 5:00 | 128 | 9:00
| Chatak | 138 | 5:00 | 131 | 18:00 | Niyamatpur | 130 | 18:00 | 120 | 9:00
| Sunamganj | 137 | 3:00 | 131 | 18:30 | Joypurhat | 133 | 20:00 | 120 | 9:00
| Biani Bazar | 139 | 3:00 | 132 | 13:00 | Sherpur(Bogura) | 137 | 20:00 | 128 | 9:00
| Comilla(s) | 132 | 4:00 | 128 | 10:00 | Mohastangor | 136 | 20:00 | 127 | 12:00
| Comilla(n) | 145 | 20:00 | 142 | 13:00 | Bangura | 139 | 20:00 | 135 | 12:00
| Chandpur | 145 | 23:00 | 142 | 18:00 | Rangpur | 133 | 17:00 | 122 | 9:00
| Feni | 141 | 0:00 | 136 | 132:00 | Lalmonirhat | 132 | 5:00 | 120 | 12:00
| Chowmuhani | 139 | 7:00 | 135 | 18:00 | Saidpur | 133 | 5:00 | 121 | 12:00
| Ashuganj | 140 | 7:00 | 137 | 15:00 | Purbasadipur | 133 | 4:00 | 120 | 12:00
| Daudkandi | 141 | 18:00 | 137 | 12:00 | Thakurgaon | 133 | 5:00 | 120 | 12:00
| B.Baria | 136 | 23:00 | 133 | 11:00 | Palashbari | 133 | 5:00 | 122 | 12:00
| Ramganj | 140 | 9:00 | 137 | 23:00 | Barapukuria | 135 | 6:00 | 128 | 12:00
| Chaddagram | 141 | 7:00 | 138 | 12:00 | Panchagar | 133 | 5:00 | 120 | 13:00

## L-Curve
Date | 2021-02-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 205 | 4942 | 1906 | 6848 |  |  |  | QF-LDC-11
0:30 | 123.5 | 4691.5 | 1919.5 | 6611 | Date: | 2021-02-01
1:00 | 42 | 4441 | 1933 | 6374
1:30 | 56.5 | 4234.5 | 1926 | 6160.5
2:00 | 71 | 4028 | 1919 | 5947
2:30 | 77 | 3975.5 | 1908 | 5883.5 | [5 empty] | Gen. at Eve. Peak | 9074 | 9500 MW (19:30 )
3:00 | 83 | 3923 | 1897 | 5820 | [6 empty] | 19:00
3:30 | 97 | 3856.5 | 1875.5 | 5732 | [5 empty] | Gen. at Day Peak | 7901 | 7952.5 MW (12:00 )
4:00 | 111 | 3790 | 1854 | 5644 | [6 empty] | 12:00
4:30 | 103 | 3779 | 1837.5 | 5616.5 | [5 empty] | Highest Generation | 9074
5:00 | 95 | 3768 | 1821 | 5589 | [6 empty] | 19:00
5:30 | 87 | 3897 | 1833 | 5730
6:00 | 79 | 4026 | 1845 | 5871
6:30 | 123 | 4107.5 | 1904.5 | 6012
7:00 | 167 | 4189 | 1964 | 6153
7:30 | 219.5 | 4498 | 2061 | 6559
8:00 | 272 | 4807 | 2158 | 6965
8:30 | 301.5 | 4999 | 2121.5 | 7120.5
9:00 | 331 | 5191 | 2085 | 7276
9:30 | 281 | 5313.5 | 2132.5 | 7446
10:00 | 231 | 5436 | 2180 | 7616
10:30 | 204 | 5447.5 | 2199.5 | 7647
11:00 | 177 | 5459 | 2219 | 7678
11:30 | 209.5 | 5571 | 2218.5 | 7789.5
12:00 | 242 | 5683 | 2218 | 7901
12:30 | 227 | 5714 | 2275 | 7989
13:00 | 212 | 5745 | 2332 | 8077
13:30 | 158.5 | 5632 | 2348.5 | 7980.5
14:00 | 105 | 5519 | 2365 | 7884
14:30 | 64 | 5425 | 2277.5 | 7702.5
15:00 | 23 | 5331 | 2190 | 7521
15:30 | 55 | 5158.5 | 2180.5 | 7339
16:00 | 87 | 4986 | 2171 | 7157
16:30 | 90 | 5019.5 | 2200 | 7219.5
17:00 | 93 | 5053 | 2229 | 7282
17:30 | 91.5 | 5335 | 2420.5 | 7755.5
18:00 | 90 | 5617 | 2612 | 8229
18:30 | 161.5 | 5906.5 | 2745 | 8651.5
19:00 | 233 | 6196 | 2878 | 9074
19:30 | 208 | 6124 | 2923 | 9047
20:00 | 225 | 6111 | 2906 | 9017 |  |  |  | Executive Engineer
20:30 | 236 | 6022 | 2813.5 | 8835.5 |  |  |  | Network Operation Division
21:00 | 247 | 5933 | 2721 | 8654
21:30 | 192.5 | 5720.5 | 2618 | 8338.5
22:00 | 138 | 5508 | 2515 | 8023 |  |  |  |  | Page 6 of 7
22:30 | 144.5 | 5400.5 | 2337 | 7737.5
23:00 | 151 | 5293 | 2159 | 7452
23:30 | 178 | 5117.5 | 2032.5 | 7150
24:00 | 205 | 4942 | 1906 | 6848
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-01 |  | Energy | 178334622
[11 empty] | 2021-02-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2847 | 416 | 1044 | 2105 | 679 | 47 | 10 | 0 | 80 | 0
0:30 | 2840 | 468.5 | 1067 | 1645 | 644.5 | 54 | 5 | 0 | 77 | 0 | Date: | 2021-02-01
1:00 | 2833 | 521 | 1090 | 1185 | 610 | 61 | 0 | 0 | 74 | 0
1:30 | 2849 | 521 | 1078 | 969.5 | 610 | 60 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 178.3346 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 2865 | 521 | 1066 | 754 | 610 | 59 | 0 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2862 | 520.5 | 1070.5 | 690 | 610 | 58.5 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 178.3346
3:00 | 2859 | 520 | 1075 | 626 | 610 | 58 | 0 | 0 | 72 | 0
3:30 | 2841.5 | 519.5 | 1070 | 562 | 610 | 58 | 0 | 0 | 71 | 0 | [6 empty] | Shortage
4:00 | 2824 | 519 | 1065 | 498 | 610 | 58 | 0 | 0 | 70 | 0
4:30 | 2792.5 | 519.5 | 1070 | 495.5 | 610 | 58 | 0 | 0 | 71 | 0
5:00 | 2761 | 520 | 1075 | 493 | 610 | 58 | 0 | 0 | 72 | 0
5:30 | 2840.5 | 524 | 1072 | 553.5 | 610 | 58 | 0 | 0 | 72 | 0
6:00 | 2920 | 528 | 1069 | 614 | 610 | 58 | 0 | 0 | 72 | 0
6:30 | 2854 | 574.5 | 1046.5 | 799 | 610 | 55.5 | 0 | 0 | 72 | 0.5 |  |  |  |  | Coal
7:00 | 2788 | 621 | 1024 | 984 | 610 | 53 | 0 | 0 | 72 | 1
7:30 | 2879 | 590 | 1021 | 1316.5 | 619.5 | 53 | 0 | 0 | 75 | 5 |  |  |  | Oil |  |  |  | ,
8:00 | 2970 | 559 | 1018 | 1649 | 629 | 53 | 0 | 0 | 78 | 9
8:30 | 2910.5 | 496.5 | 1005 | 1908.5 | 629 | 53.5 | 24 | 0 | 79 | 14.5
9:00 | 2851 | 434 | 992 | 2168 | 629 | 54 | 48 | 0 | 80 | 20
9:30 | 2863.5 | 434 | 1002.5 | 2294.5 | 619.5 | 54.5 | 73 | 0 | 80 | 24.5
10:00 | 2876 | 434 | 1013 | 2421 | 610 | 55 | 98 | 0 | 80 | 29
10:30 | 2832.5 | 434 | 995 | 2490.5 | 617.5 | 55 | 104 | 0 | 81 | 37.5
11:00 | 2789 | 434 | 977 | 2560 | 625 | 55 | 110 | 0 | 82 | 46
11:30 | 2791.5 | 434.5 | 982.5 | 2590 | 673 | 55.5 | 116.5 | 0 | 87 | 59
12:00 | 2794 | 435 | 988 | 2620 | 721 | 56 | 123 | 0 | 92 | 72
12:30 | 2840 | 435 | 1003.5 | 2687 | 678 | 56 | 128 | 0 | 90 | 71.5
13:00 | 2886 | 435 | 1019 | 2754 | 635 | 56 | 133 | 0 | 88 | 71
13:30 | 2886 | 435 | 1019 | 2754 | 635 | 56 | 133 | 0 | 88 | 71
14:00 | 2886 | 435 | 1019 | 2754 | 635 | 56 | 133 | 0 | 88 | 71
14:30 | 2797.5 | 435 | 1005.5 | 2624 | 612.5 | 56 | 120 | 0 | 89 | 59.5
15:00 | 2709 | 435 | 992 | 2494 | 590 | 56 | 107 | 0 | 90 | 48
15:30 | 2693 | 427 | 978 | 2361.5 | 590 | 56 | 107 | 0 | 88 | 38.5
16:00 | 2677 | 419 | 964 | 2229 | 590 | 56 | 107 | 0 | 86 | 29
16:30 | 2735 | 417.5 | 964 | 2242.5 | 590 | 56.5 | 112 | 0 | 84 | 18
17:00 | 2793 | 416 | 964 | 2256 | 590 | 57 | 117 | 0 | 82 | 7
17:30 | 2794 | 416 | 994 | 2544 | 594.5 | 52 | 263.5 | 0 | 94 | 3.5
18:00 | 2795 | 416 | 1024 | 2832 | 599 | 47 | 410 | 0 | 106 | 0
18:30 | 2829 | 416 | 1043 | 3129 | 644.5 | 47 | 438 | 0 | 105 | 0
19:00 | 2863 | 416 | 1062 | 3426 | 690 | 47 | 466 | 0 | 104 | 0
19:30 | 2832 | 416 | 1064 | 3389 | 730 | 47 | 465 | 0 | 104 | 0
20:00 | 2877 | 416 | 1064 | 3315 | 730 | 47 | 466 | 0 | 102 | 0
20:30 | 2885.5 | 416 | 1053.5 | 3246.5 | 730 | 47 | 355 | 0 | 102 | 0
21:00 | 2894 | 416 | 1043 | 3178 | 730 | 47 | 244 | 0 | 102 | 0
21:30 | 2921.5 | 416 | 1040 | 2874.5 | 730 | 47 | 210.5 | 0 | 99 | 0
22:00 | 2949 | 416 | 1037 | 2571 | 730 | 47 | 177 | 0 | 96 | 0
22:30 | 2940 | 416 | 1051 | 2338 | 705 | 47 | 148.5 | 0 | 92 | 0
23:00 | 2931 | 416 | 1065 | 2105 | 680 | 47 | 120 | 0 | 88 | 0
23:30 | 2889 | 416 | 1054.5 | 2105 | 679.5 | 47 | 65 | 0 | 84 | 0 | Max Temp. in Dhaka |  | 22.4° C
24:00 | 2847 | 416 | 1044 | 2105 | 679 | 47 | 10 | 0 | 80 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 61 | 59 | 58 | 58 | 58 | 58 | 53 | 53 | 54 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 57 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1360145
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 25 | 25 | 8 |  |  | 0 | 143240
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 16 | 14 | 14 | 11 | 7 | 2 | [9 empty] | 110295
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 85 | 85 | 17 |  |  | 0 | 265407
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 95 | 95 | 95 | 95 | 95 | 150 | 120 | 120 | 185 | 184 | 170 | 100 | 153 | 91 | 90 | 90 | 123 | 120 |  | 183 | 190 | 185 | 190 | 190 | 165 | 145 | 3539000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 31 | 31 |  |  |  |  | 26 | 30 | 30 | 49 | 120 | 208 | 250 | 278 | 275 | 288 | 286 | 286 |  | 286 | 286 | 286 | 286 | 286 | 286 | 245 | 3916689
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4410000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3054774
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 597600
33 | Ashuganj 225 MW CCPP | 184 | 190 | 184 | 183 | 183 | 205 | 183 | 225 | 186 | 185 | 185 | 210 | 189 | 187 | 187 | 187 | 199 | 198 |  | 195 | 188 | 184 | 184 | 200 | 200 | 185 | 4687000
34 | Ashuganj 450 MW CCPP(South) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 325 | 280 | 265 | 265 | 265 | 290 | 285 |  | 290 | 275 | 275 | 275 | 305 | 310 | 280 | 7674000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138720
36 | Chandpur 150 MW CCPP | 71 | 72 | 71 | 70 | 66 | 73 | 70 | 74 | 70 | 70 | 48 | 51 | 50 | 50 | 45 | 51 | 51 | 51 |  | 51 | 51 | 48 | 51 | 52 | 50 | 50 | 1397760
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 298 | 288 | 278 | 271 | 261 | 270 | 292 | 293 | 267 | 259 |  | 243 | 239 | 238 | 227 | 227 | 236 | 242 | 6678000
42 | RPCL 210MW CCPP | 96 | 101 | 97 | 108 | 96 | 109 | 96 | 105 | 105 | 105 | 99 | 95 | 82 | 80 | 80 | 82 | 81 | 83 |  | 85 | 85 | 85 | 86 | 86 | 103 | 104 | 2123400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 7 | 9 | 22 | 47 | 47 | 41 | 30 | 18 | 4 | [9 empty] | 232720
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | [21 empty] | 70 | 106 | 105 | 101 | 106 | 410000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 67 | 67 | 67 | 64 | 66 | 68 | 68 | 68 | 30 | 30 | 68 |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 1597440
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 108 | 100 | 60 | 100 | [13 empty] | 1290000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 206100
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 42 | 45 | 48 | 47 | 47 |  | 46 | 46 | 48 | 48 | 48 | 48 | 51 | 1117800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 303930
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 300 | 290 | 300 | 310 | 300 | 320 | 320 | 310 | 290 | 290 | 330 | 300 | 290 | 290 | 300 | 310 |  | 320 | 315 | 315 | 300 | 300 | 310 | 305 | 7573000
| Bibiyana South 400 MW | 415 | 416 | 415 | 415 | 415 | 415 | 400 | 380 | 365 | 332 | 295 | 415 | 415 | 415 | 415 | 415 | 415 | 415 |  | 415 | 415 | 416 | 415 | 415 | 415 | 415 | 9666400
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 5 | 17 | 24 | 13 | 17 | 17 | 36 | 52 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 |  |  |  | 564787
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 8 | 22 | 18 | 17 | 16 | 12 | 13 | 16 | 17 | 14 | 12 | 17 |  | 23 | 23 | 24 | 22 | 24 | 24 | 0 | 308880
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 468672
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 430776
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 527940
63 | Impoprt (Tripura) | 74 | 72 | 72 | 70 | 72 | 72 | 72 | 78 | 80 | 80 | 82 | 92 | 88 | 96 | 90 | 86 | 82 | 106 |  | 104 | 104 | 102 | 102 | 96 | 88 | 80 | 2049600
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 41 | 41 | 42 | 42 | 40 | 15 | 5 | 8 | 5 | 8 | 12 | 10 | 5 | 8 | 21 | 15 |  | 26 | 28 | 31 | 35 | 30 | 40 | 41 | 590400
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 464148
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 796200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 543650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 706320
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 15 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 444800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 786300
73 | Ghorashal 108MW PP (Regent) | 108 | 108 | 108 | 108 | 108 | 108 | 105 | 105 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 |  | 105 | 105 | 106 | 106 | 106 | 106 | 106 | 2477727
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [9 empty] | 15 | 16 | 16 | 16 | 26 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 8 | 8 | 0 | 438480
| Manikgonj 162MW PP(MPGL) | 144 | 18 | 18 | 17 | 17 | 30 | 60 | 84 | 118 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2787840
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 1 | 12 | 30 | 32 | 40 | 40 | 40 | 40 | 8 | 8 | 15 |  | 88 | 100 | 100 | 100 | 60 | 24 | 0 | 686400
78 | Gazipur 52 MW PP | [17 empty] | 5 |  | 8 | [5 empty] | 0 | 15200
79 | Kodda 150MW PP | [8 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 125 |  | 150 | 150 | 150 | 115 | 64 | 16 | 0 | 943680
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 20 | 32 | 57 | 72 | 72 | 72 | 72 | 40 | 8 | 8 | 17 |  | 82 | 82 | 82 | 64 | 8 |  | 0 | 765120
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [7 empty] | 1 | 18 | 34 | 34 | 34 | 34 | 34 |  |  |  | 18 |  | 62 | 55 | 35 |  |  |  | 0 | 370176
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | [10 empty] | 23113
| Jodiac Power | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 48 | 54 | 54 | 54 | 17 | 17 | 0 | 603768
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 25 | 48 | 50 | 64 | 75 | 80 | 82 | 82 | 82 | 82 | 97 | 101 |  | 101 | 101 | 101 | 101 | 99 | 99 | 81 | 1625352
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 10 | [5 empty] | 42 | 54 | 56 | 60 | 60 | 60 | 60 | 60 | 60 | 74 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 70 | 1248757
86 | Meghnaghat CCPP(Summit) | 260 | 275 | 270 | 270 | 265 | 280 | 280 | 305 | 280 | 275 | 230 | 305 | 300 | 230 | 250 | 250 | 280 | 290 |  | 280 | 270 | 270 | 285 | 270 | 275 | 280 | 6484160
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 6 | 45 | 50 | 50 | 44 | 46 | 20 | 7 | 7 | 24 |  | 55 | 50 | 50 | 28 | 7 | 7 | 7 | 485760
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 21 | 35 | 60 | 72 | 72 | 72 | 72 | 72 | 84 | 92 | 92 | 91 |  | 91 | 94 | 96 | 104 | 93 | 53 | 14 | 1304640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1183824
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 |  | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 1145078
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 3 | 24 | 40 | 40 | 40 | 40 | 40 | 7 | 7 | 7 | 32 |  | 102 | 102 | 64 | 32 |  |  | 0 | 512352
95 | Patenga 50MW PP (Baraka) | 19 | [5 empty] | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 14 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 364320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 4 | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 56640
97 | katpotti 52 MW | [20 empty] | 1 | 2 | 6 |  |  | 0 | 14304
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 15 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 | 15 | 0 | 809275
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 17 |  | 0 | 419098
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 10000
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 630360
104 | Keranigonj 300 MW PP (APR) | [8 empty] | 51 | [10 empty] | 75 | [5 empty] | 0 | 158740
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 95 | 16 | 16 | 8 | 8 | 15 | 94 | 140 | 175 | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 170 | 185 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3688800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 4 | 36 | 82 | 108 | 126 | 122 | 110 | 111 | 85 | 37 | 32 | 34 |  | 102 | 132 | 129 | 131 | 98 | 33 | 0 | 1404000
115 | Juldah 100 MW PP Unit-3 (Acorn) | 85 |  |  |  |  | 20 | 20 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1675200
116 | Chandpur 200MW (Desh energy) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445920
117 | Ashuganj 150MW PP (Midland) | 50 | 10 | 10 | 10 | 10 | 15 | 26 | 110 | 128 | 128 | 125 | 122 | 122 | 122 | 120 | 122 | 122 | 128 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2146109
118 | Bibiyana-III 400 MW CCPP | 252 | 255 | 250 | 250 | 251 | 280 | 252 | 308 | 253 | 250 | 252 | 300 | 262 | 250 | 252 | 252 | 270 | 283 |  | 261 | 253 | 252 | 252 | 265 | 270 | 252 | 6301000
| Jamalpur 115 MW PP (United) | [7 empty] | 4 | 8 | 12 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 31 | 25 | 8 | 8 |  |  | 0 | 192000
| Anwara 300 MW PP (United) | 307 | 307 | 270 | 161 | 161 | 182 | 233 | 304 | 307 | 307 | 307 | 283 | 301 | 301 | 307 | 253 | 195 | 253 |  | 307 | 307 | 307 | 307 | 307 | 307 | 306 | 6627513
| Juldah unit-2 (Acorn) | 100 | 30 | 10 |  |  | 40 | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1886400
| Anlima Energy Ltd. | [9 empty] | 9 | 19 | 19 | 18 | 18 | [11 empty] | 0 | 107890
120 | Eastern Zone Total | 4441 | 4028 | 3923 | 3790 | 3768 | 4026 | 4189 | 4807 | 5191 | 5436 | 5459 | 5683 | 5745 | 5519 | 5331 | 4986 | 5053 | 5617 |  | 6196 | 6124 | 6111 | 5933 | 5508 | 5293 | 4942 | 123262523
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 35 | 91 | 100 | 115 | 82 | 83 | 72 |  |  | 3 | 79 |  | 99 | 99 | 99 | 99 | 33 |  | 0 | 969600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 35 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 35 | 35 | 105 |  | 105 | 105 | 105 | 105 | 105 | 70 | 0 | 1570992
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 15600
133 | Bhola Nutan Biddut BD LTD (GAS) | 33 | 33 | 33 | 33 | 33 | 16 | [5 empty] | 12 | 5 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 |  |  |  |  | 0 | 262827
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 32 | 32 | 32 | 32 | 16 |  | 0 | 127680
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 30 | [8 empty] | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 34 | 50 |  | 87 | 87 | 87 | 87 | 87 | 87 | 62 | 896406
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 21 | 21 | 20 | 20 | 17 | 19 | 17 | 19 | 19 | 20 | 22 | 21 | 12 | 16 | 13 | 23 |  | 25 | 26 | 25 | 26 | 25 | 24 | 23 | 493500
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 40 | 40 | 40 | 8 | 8 |  |  |  |  | 40 |  | 40 | 40 | 40 |  |  |  |  | 233250
143 | Gopalganj 100 MW Peaking PP | [12 empty] | 5 | 10 | 10 | 10 | 10 | 15 |  | 17 | 15 | 15 | 12 | 13 | 3 |  | 118656
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 521 | 521 | 520 | 519 | 520 | 528 | 621 | 559 | 434 | 434 | 434 | 435 | 435 | 435 | 435 | 419 | 416 | 416 |  | 416 | 416 | 416 | 416 | 416 | 416 | 416 | 11263273
147 | Bheramara 410 MW CCPP | 340 | 350 | 370 | 350 | 320 | 350 | 350 | 431 | 345 | 345 | 345 | 300 | 355 | 345 | 345 | 345 | 370 | 360 |  | 350 | 345 | 340 | 325 | 320 | 320 | 320 | 8436672
148 | Payra 1320 MW | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 480 | 480 | 460 | 440 | 440 | 440 | 440 | 410 | 410 | 410 | 420 |  | 510 | 550 | 550 | 550 | 550 | 500 | 500 | 12015400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 185 | 281 | 195 | 179 | 180 | 180 | 180 | 179 |  | 180 | 180 | 180 | 180 | 180 | 180 | 179 | 4184500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [9 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 43 |  | 43 | 43 | 43 |  |  |  |  | 521154
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 151 | 154 | 155 | 152 | 154 | 163 | 157 | 170 | 184 | 177 | 172 | 157 | 171 | 182 | 166 | 153 | 157 | 167 |  | 180 | 180 | 170 | 170 | 171 | 172 | 171 | 4219945
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 164 | 167 | 161 | 142 | 137 | 131 | 117 | 103 | 101 | 112 | 113 | 114 | 163 | 205 | 197 | 190 | 176 | 175 |  | 183 | 180 | 182 | 170 | 170 | 166 | 160 | 3974282
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [25 empty] | 0 | 0
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 11 |  | 40 | 40 | 42 |  |  |  |  | 94039
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 517920
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 203994
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 25 |  | 25 | 25 | 25 | 25 |  |  |  | 330270
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [10 empty] | 12 | 25 | 30 | 30 | 31 | 31 | 31 | 31 |  | 31 | 32 | 31 |  |  |  |  | 272527
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 25 | 43 | 52 | 52 | 52 | 52 | 43 | 8 | 8 | 8 | 24 |  | 52 | 52 | 52 | 52 |  |  | 0 | 506880
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 100 |  | 100 | 100 | 100 | 100 | 100 | 101 | 10 | 661504
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [13 empty] | 1 | 27 | 75 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 |  | 0 | 816576
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 50 | 70 |  | 100 | 113 | 113 | 113 | 113 | 35 | 35 | 1170912
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 80 | 110 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 70 | 55 | 0 | 1162560
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 1 | 2 | 3 | 3 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 31180
178
178