## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-03 | Wednesday
|  |  | Date (day): | 2021-02-03 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12063.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13211 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-02 | 2021-02-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 103 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2021-07-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 238 | 229 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 41 | 83 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 305 | 270 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 69 | 73 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 190 | 178 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 9 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 24 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 230 | 282 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 95 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 27 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 111 | 123 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 1 | 70 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6281 | 6057 | 2158 | 2724 | 3260 | 3512 | 108 | 2348
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 20 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 19 | 19 |  | 31 | Engine problem
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 58 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 85 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 24 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 24 | 15 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 17 | 44 | 100 | 100
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 307 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 17 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 746 | 870 | 1125 | 1210 | 895 | 146
| 58 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 130 | 100 | 100 | 100 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 216 | 185 | 225 | 225
| 60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 100 | 100 | 260 |  | Gas shortage
| 61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 285 | 350 | 350 |  |  | FGMO
| 62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Machine problem
| 63 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 20 | 5 | 5 | 50 |  | Gas shortage
| 64 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 66 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 90 | 60 | 150 | 150
| 67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
| 68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 46 | 50 | 50 |  | 113 | Gas shortage + ST under maint.
| 69 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 17 | 200 | 200
| 70 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 102 | 135 | 147
| 72 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 4 | 52 | 52
| 74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 19 | 19 | 19 |  | 6 | Engine problem
| 75 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 85 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1123 | 1115 | 1764 | 2026 | 795 | 138
| 78 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 82 | 102 | 110 | 110 | 92 |  | Gas shortage
| 79 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 80 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 24 | 82 | 82 |  | 13 | Engine problem
| 81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 50 | 115 | 115 | 115
| 84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 16 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 435 | 487 | 602.6 | 551 | 92 | 13
| 86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 100 | 120 | 43 |  | Gas shortage
| 89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 106 | 105 | 105 | 105 |  | 225 | GT-2 & ST under maint.
| 90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 51 | 51 | 51
| 91 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
| 92 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 94 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 68 | 74 | 74 | 74 |  | 12 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 150 | 150
| 96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 97 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 |  |  | FGMO
| 100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 302 | 252 | 280 | 280 |  |  | FGMO
| 101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 408 | 415 | 415 | 415 |  |  | RRT
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1365 | 1323 | 1733 | 1753 | 63 | 442
| 102 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 434 | 424 | 440 | 440
| 103 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 37 | 99 | 115 | 115
| 104 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 105 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 106 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 70 | 70 |  | 39 | Engine problem
| 107 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 270 | 410 | 410
| 108 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 109 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 50 | 100
| 110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 95 | 105 | 105
| 111 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 911 | 948 | 1355 | 1641 | 0 | 68
| 112 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 113 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 26 | 26 |  | 7 | Engine problem
| 114 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 115 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 37 | 70 | 95 | 95
| 116 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 460 | 520 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 1676 | 1676 | 515 | 648 | 901 | 1001 | 0 | 201
| 117 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 118 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 119 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 40
| 120 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 25 | 25 |  | 25 | Engine problem
| 121 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0
| 122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 167 | 220 | 220 |  |  | FGMO
| 125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 198 | 220 | 220 |  |  | FGMO
| 126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint. |  | 13/2/2021
| 127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 128 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 129 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 131 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 132 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 104 | 104
| 133 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 134 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 135 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 35 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 476 | 856 | 1052 | 1254 | 381 | 439
| 136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 107 | 113 | 113 | 113
| 141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 261 | 263 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21239 | 20748 | 7990 | 9234 | 12063.6 | 13211 | 2458 | 4005
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7571.2042 | 8750 | 11431.2865 | 12518.5456
| A. |  | 2021-02-02 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9234 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5579 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9234 | MW
| 3 | Day peak Generation : |  |  | 7990 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8750 | MW
| 4 | Evening peak Generation : |  |  | 9234 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 180.9305 | MKWHr | By Solar | 0.43787 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 94.1261 | MKWHr |  | By Oil: | 56.6057 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.1116 | MKWHr |  | By Hydro: | 1.1938 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2458 | MW | Dhaka | 2981 | 2981 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4005 | MW | Chittagong | 888 | 888 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6463 | MW | Khulna | 1108 | 1108 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 824.96 | MMCFD |  |  | Rajshahi | 963 | 963 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 99056450.16 | ii) Oil : | Taka | 363240707.26 | Comilla | 754 | 754 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 74518161 | Total | Taka | 536815318.42 | Mymensingh | 799 | 799 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.8815 | MKWHr. | Sylhet | 330 | 330 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -439 | MW (E to W) at | 19:00 | hrs | Barisal | 239 | 239 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -441 | MW at | 13:00 | hrs | Rangpur | 688 | 688 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 25.4° C |  |  | Total | 8750 | 8750 |  | 0
| B. |  | 2021-02-03 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 26.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13211 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
| 4 | Reserve(Generation end) |  |  |  | 3911 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 182.2237 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5643 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.3578 | MKWHr. | ii) HVDC Flow at Peak Time |  | 424 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0976 | MKWHr. | iii) Maximum HVDC Flow : |  | 435 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.56 |  | (b) Today: | 95.44 |  | (c) Rule Curve: |  | 96.72
.

## YesterdayGen
2021-02-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 293 |  | 0 | 0 | 255 | 7 | 48 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 130 | 0 | 0 | 0 | 285 | 184 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 74 | 104 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 295 | 16 | 11 | 0 | 95 | 0 | 0 | 140 | 0 | 0 | 0 | 30 | 17 | 90 | 252 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 100 | 415 | 0 | 0 | 144 | 0 | 0 |  | 434 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 173 | 0 | 35 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4486 | 1812 | 6298 | 2793 | 434 | 1054 | 1247 | 649 | 47 | 0 | 74 | 0 | 0 | 95.59
2:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 314 |  | 0 | 0 | 265 | 7 | 15 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 41 | 130 | 0 | 0 | 0 | 285 | 184 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 70 | 104 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 106 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 30 | 17 | 10 | 252 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 100 | 415 | 0 | 0 | 144 | 0 | 0 |  | 434 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4159 | 1812 | 5971 | 2774 | 434 | 1081 | 916 | 649 | 47 | 0 | 70 | 0 | 0 | 95.58
3:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 316 |  | 0 | 0 | 285 | 7 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 130 | 0 | 0 | 0 | 280 | 184 | 8 | 49 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 68 | 104 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 17 | 10 | 255 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 80 | 416 | 0 | 0 | 144 | 0 | 0 |  | 434 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 35 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4022 | 1797 | 5819 | 2790 | 434 | 1081 | 780 | 619 | 47 | 0 | 68 | 0 | 0 | 95.58
4:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 316 |  | 0 | 0 | 260 | 7 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 130 | 0 | 0 | 0 | 285 | 184 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 68 | 105 | 0 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 107 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 10 | 252 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 20 | 415 | 0 | 0 | 144 | 0 | 0 |  | 434 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 35 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 3842 | 1806 | 5648 | 2799 | 434 | 1091 | 589 | 620 | 47 | 0 | 68 | 0 | 0 | 95.57
5:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 316 |  | 0 | 0 | 295 | 7 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 130 | 0 | 0 | 0 | 295 | 191 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 68 | 105 | 0 | 22 | 0 | 30 | 0 | 48 | 50 | 0 | 106 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 10 | 260 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 10 | 415 | 0 | 0 | 90 | 0 | 0 |  | 434 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 35 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 3789 | 1790 | 5579 | 2828 | 434 | 1079 | 523 | 600 | 47 | 0 | 68 | 0 | 0 | 95.57
6:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 316 |  | 0 | 0 | 260 | 7 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 20 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 130 | 0 | 0 | 0 | 315 | 205 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 72 | 105 | 0 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 103 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 20 | 17 | 16 | 280 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 60 | 415 | 0 | 0 | 90 | 0 | 0 |  | 434 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 35 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 450 | 0 | 0 | 0 |  | 4072 | 1811 | 5883 | 2889 | 434 | 1104 | 737 | 600 | 47 | 0 | 72 | 0 | 0 | 95.56
7:00 | 0 | 0 | 0 | 180 | 0 | 106 | 0 | 0 | 316 |  | 0 | 0 | 285 | 7 | 2 | 4 | 0 | 0 | 80 | 4 | 3 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 16 | 16 | 25 | 28 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 13 | 0 | 13 | 0 | 0 | 14 | 20 | 38 | 130 | 0 | 0 | 0 | 290 | 192 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 74 | 105 | 8 | 22 | 0 | 30 | 0 | 44 | 50 | 0 | 105 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 25 | 0 | 0 | 122 | 0 | 17 | 1 | 20 | 17 | 90 | 252 | 0 | 0 | 0 | 0 | 248 | 14 | 0 | 0 | 8 | 100 | 416 | 25 | 1 | 126 | 0 | 0 |  | 434 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 35 | 0 | 148 | 0 | 0 | 35 | 0 | 0 | 0 | 49 | 0 | 0 | 35 | 450 | 0 | 0 | 0 |  | 4512 | 1940 | 6452 | 2826 | 434 | 1073 | 1384 | 600 | 46 | 13 | 74 | 2 | 0 | 95.56
8:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 318 |  | 0 | 0 | 260 | 7 | 36 | 15 | 0 | 0 | 190 | 10 | 16 | 0 | 71 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 28 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 0 | 0 | 18 | 20 | 15 | 130 | 0 | 0 | 0 | 285 | 184 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 78 | 106 | 23 | 22 | 0 | 30 | 0 | 45 | 50 | 0 | 107 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 65 | 0 | 0 | 180 | 0 | 49 | 5 | 60 | 17 | 90 | 253 | 18 | 0 | 0 | 0 | 308 | 17 | 0 | 0 | 8 | 100 | 415 | 55 | 8 | 130 | 0 | 0 |  | 434 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 35 | 0 | 166 | 0 | 0 | 90 | 0 | 0 | 0 | 92 | 0 | 1 | 35 | 450 | 0 | 0 | 0 |  | 5036 | 2165 | 7201 | 2950 | 434 | 1050 | 1978 | 600 | 46 | 51 | 78 | 14 | 0 | 95.55
9:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 290 |  | 0 | 0 | 245 | 7 | 48 | 25 | 0 | 0 | 190 | 32 | 24 | 0 | 67 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 47 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 51 | 3 | 0 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 285 | 189 | 8 | 50 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 18 | 84 | 104 | 81 | 20 | 1 | 30 | 0 | 45 | 50 | 0 | 105 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 190 | 0 | 0 | 200 | 0 | 107 | 10 | 80 | 17 | 97 | 255 | 55 | 0 | 0 | 3 | 306 | 17 | 0 | 0 | 8 | 100 | 420 | 73 | 19 | 144 | 0 | 0 |  | 433 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 36 | 0 | 171 | 0 | 0 | 90 | 0 | 0 | 0 | 102 | 0 | 1 | 35 | 480 | 0 | 0 | 0 |  | 5441 | 2208 | 7649 | 2962 | 433 | 1025 | 2383 | 630 | 47 | 51 | 84 | 34 | 0 | 95.55
10:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 269 |  | 0 | 0 | 265 | 10 | 55 | 55 | 0 | 0 | 160 | 32 | 32 | 0 | 60 | 0 | 0 | 0 | 35 | 35 | 0 | 16 | 25 | 32 | 25 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 51 | 10 | 5 | 19 | 20 | 4 | 130 | 0 | 0 | 0 | 280 | 184 | 8 | 45 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 22 | 88 | 105 | 81 | 20 | 2 | 30 | 0 | 45 | 50 | 0 | 107 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 116 | 14 | 90 | 17 | 107 | 251 | 45 | 0 | 0 | 4 | 304 | 22 | 0 | 0 | 8 | 100 | 426 | 104 | 31 | 144 | 0 | 0 |  | 434 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 36 | 0 | 190 | 0 | 0 | 90 | 0 | 0 | 0 | 107 | 0 | 2 | 35 | 460 | 0 | 0 | 0 |  | 5569 | 2213 | 7782 | 2940 | 434 | 982 | 2576 | 610 | 48 | 51 | 88 | 53 | 0 | 95.54
11:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 0 | 264 |  | 0 | 0 | 285 | 33 | 64 | 55 | 0 | 0 | 160 | 32 | 50 | 0 | 61 | 0 | 0 | 0 | 35 | 35 | 6 | 16 | 25 | 31 | 25 | 33 | 0 | 0 | 56 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 10 | 16 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 280 | 211 | 8 | 51 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 22 | 92 | 84 | 48 | 20 | 2 | 30 | 0 | 45 | 50 | 0 | 106 | 0 | 67 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 115 | 17 | 100 | 17 | 90 | 252 | 45 | 0 | 0 | 4 | 307 | 20 | 0 | 0 | 8 | 100 | 423 | 104 | 38 | 144 | 0 | 0 |  | 434 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 36 | 0 | 191 | 0 | 0 | 95 | 0 | 0 | 0 | 107 | 0 | 4 | 35 | 460 | 0 | 0 | 0 |  | 5649 | 2195 | 7844 | 2923 | 434 | 980 | 2633 | 610 | 56 | 51 | 92 | 65 | 0 | 95.54
12:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 238 |  | 0 | 0 | 305 | 41 | 64 | 55 | 0 | 0 | 190 | 40 | 50 | 16 | 69 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 0 | 34 | 24 | 17 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 340 | 216 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 94 | 82 | 24 | 20 | 2 | 30 | 0 | 45 | 50 | 0 | 106 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 111 | 17 | 100 | 17 | 90 | 302 | 50 | 1 | 0 | 5 | 305 | 17 | 0 | 0 | 8 | 100 | 408 | 104 | 41 | 144 | 0 | 0 |  | 434 | 0 | 310 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 37 | 0 | 184 | 0 | 0 | 90 | 0 | 0 | 0 | 107 | 0 | 4 | 35 | 460 | 0 | 0 | 0 |  | 5827 | 2163 | 7990 | 3024 | 434 | 977 | 2674 | 610 | 58 | 50 | 94 | 69 | 0 | 95.53
13:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 238 |  | 0 | 0 | 265 | 77 | 70 | 55 | 0 | 0 | 175 | 78 | 102 | 48 | 72 | 0 | 0 | 0 | 53 | 35 | 17 | 22 | 25 | 30 | 25 | 33 | 10 | 0 | 58 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 13 | 0 | 51 | 70 | 30 | 19 | 20 | 7 | 130 | 0 | 0 | 0 | 295 | 184 | 8 | 46 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 31 | 22 | 94 | 80 | 24 | 20 | 2 | 30 | 0 | 47 | 47 | 0 | 105 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 250 | 0 | 0 | 200 | 0 | 114 | 17 | 100 | 17 | 50 | 252 | 84 | 28 | 0 | 5 | 306 | 20 | 0 | 0 | 46 | 90 | 414 | 104 | 39 | 144 | 7 | 0 |  | 434 | 0 | 310 | 0 | 71 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 37 | 0 | 178 | 0 | 0 | 90 | 0 | 0 | 0 | 100 | 0 | 4 | 35 | 490 | 0 | 0 | 0 |  | 6014 | 2216 | 8230 | 2877 | 434 | 994 | 2963 | 640 | 58 | 103 | 94 | 67 | 8230 | 95.53
14:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 0 | 230 |  | 0 | 0 | 280 | 93 | 81 | 55 | 0 | 0 | 150 | 100 | 58 | 32 | 72 | 0 | 0 | 0 | 54 | 35 | 17 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 14 | 0 | 17 | 30 | 33 | 19 | 20 | 9 | 130 | 0 | 0 | 0 | 295 | 174 | 8 | 50 | 26 | 40 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 32 | 22 | 98 | 80 | 24 | 20 | 2 | 30 | 0 | 47 | 47 | 0 | 105 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 93 | 15 | 100 | 17 | 50 | 251 | 55 | 17 | 0 | 4 | 307 | 35 | 0 | 0 | 26 | 100 | 412 | 81 | 34 | 144 | 17 | 0 |  | 434 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 7 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 172 | 0 | 0 | 90 | 0 | 1 | 0 | 100 | 0 | 4 | 35 | 440 | 0 | 0 | 0 |  | 5836 | 2053 | 7889 | 2828 | 434 | 963 | 2803 | 590 | 58 | 56 | 98 | 59 | 0 | 95.52
15:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 234 |  | 0 | 0 | 260 | 93 | 90 | 55 | 0 | 0 | 150 | 100 | 58 | 16 | 73 | 0 | 0 | 0 | 54 | 35 | 17 | 22 | 25 | 30 | 17 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 13 | 0 | 17 | 0 | 32 | 19 | 20 | 4 | 130 | 0 | 0 | 0 | 275 | 175 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 32 | 22 | 94 | 78 | 24 | 20 | 1 | 30 | 0 | 47 | 47 | 0 | 106 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 80 | 11 | 100 | 17 | 50 | 213 | 55 | 0 | 0 | 3 | 307 | 47 | 0 | 0 | 26 | 100 | 411 | 71 | 25 | 144 | 0 | 0 |  | 434 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 168 | 0 | 0 | 95 | 0 | 24 | 0 | 105 | 0 | 3 | 35 | 420 | 0 | 0 | 0 |  | 5601 | 1945 | 7546 | 2741 | 434 | 913 | 2660 | 570 | 58 | 33 | 94 | 43 | 0 | 95.52
16:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 232 |  | 0 | 0 | 250 | 70 | 100 | 55 | 0 | 0 | 150 | 86 | 7 | 16 | 73 | 0 | 0 | 0 | 54 | 35 | 17 | 22 | 25 | 30 | 17 | 25 | 0 | 0 | 57 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 17 | 0 | 18 | 19 | 20 | 6 | 80 | 0 | 0 | 0 | 270 | 185 | 8 | 47 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 0 | 0 | 90 | 84 | 24 | 22 | 1 | 30 | 0 | 50 | 47 | 0 | 106 | 0 | 69 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 72 | 6 | 100 | 17 | 50 | 192 | 16 | 0 | 0 | 1 | 307 | 17 | 0 | 0 | 8 | 90 | 415 | 71 | 14 | 144 | 0 | 0 |  | 434 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 164 | 0 | 0 | 70 | 0 | 71 | 0 | 107 | 0 | 2 | 70 | 400 | 0 | 0 | 0 |  | 5261 | 1973 | 7234 | 2612 | 434 | 917 | 2517 | 550 | 57 | 33 | 90 | 24 | 0 | 95.51
17:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 0 | 237 |  | 0 | 0 | 240 | 50 | 99 | 55 | 0 | 0 | 120 | 60 | 7 | 40 | 73 | 0 | 0 | 0 | 54 | 35 | 25 | 22 | 25 | 31 | 17 | 33 | 0 | 0 | 57 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 17 | 0 | 16 | 19 | 20 | 12 | 80 | 0 | 0 | 0 | 270 | 186 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 0 | 0 | 88 | 84 | 24 | 22 | 0 | 30 | 0 | 50 | 50 | 0 | 106 | 0 | 70 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 51 | 1 | 100 | 17 | 50 | 188 | 16 | 1 | 0 | 0 | 307 | 17 | 0 | 0 | 8 | 100 | 417 | 72 | 3 | 144 | 0 | 0 |  | 435 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 178 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 380 | 0 | 0 | 0 |  | 5203 | 2071 | 7274 | 2607 | 435 | 932 | 2549 | 530 | 57 | 72 | 88 | 4 | 0 | 95.51
18:00 | 0 | 0 | 0 | 185 | 0 | 103 | 0 | 0 | 238 |  | 0 | 0 | 300 | 50 | 100 | 55 | 0 | 0 | 120 | 72 | 53 | 115 | 73 | 0 | 0 | 1 | 54 | 35 | 34 | 22 | 25 | 18 | 17 | 33 | 5 | 0 | 35 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 0 | 20 | 19 | 20 | 16 | 100 | 0 | 0 | 0 | 330 | 215 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 10 | 0 | 21 | 11 | 33 | 19 | 106 | 85 | 24 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 106 | 0 | 73 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 265 | 95 | 0 | 200 | 14 | 63 | 0 | 100 | 17 | 54 | 267 | 29 | 18 | 0 | 0 | 307 | 32 | 0 | 0 | 37 | 100 | 410 | 81 | 0 | 144 | 6 | 0 |  | 434 | 0 | 280 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 10 | 101 | 18 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 33 | 0 | 167 | 0 | 0 | 80 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 0 | 0 | 0 |  | 5982 | 2362 | 8344 | 2820 | 434 | 992 | 3031 | 570 | 70 | 321 | 106 | 0 | 0 | 95.5
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 103 | 0 | 0 | 229 |  | 0 | 0 | 270 | 83 | 100 | 55 | 0 | 0 | 178 | 100 | 102 | 115 | 73 | 0 | 0 | 9 | 54 | 35 | 35 | 22 | 25 | 32 | 17 | 33 | 24 | 0 | 35 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 10 | 44 | 19 | 20 | 24 | 100 | 0 | 0 | 0 | 285 | 185 | 8 | 46 | 26 | 20 | 0 | 51 | 0 | 42 | 4 | 21 | 11 | 33 | 19 | 102 | 102 | 24 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 74 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 282 | 95 | 0 | 200 | 27 | 123 | 0 | 100 | 17 | 60 | 252 | 115 | 70 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 415 | 104 | 0 | 144 | 17 | 0 |  | 424 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 43 | 10 | 102 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 70 | 20 | 198 | 0 | 0 | 95 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 6519 | 2715 | 9234 | 2837 | 424 | 1047 | 3687 | 670 | 70 | 397 | 102 | 0 | 0 | 95.49
19:30 | 0 | 0 | 0 | 185 | 0 | 103 | 0 | 0 | 223 |  | 0 | 0 | 275 | 93 | 101 | 55 | 0 | 0 | 185 | 100 | 68 | 115 | 73 | 0 | 0 | 18 | 54 | 0 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 10 | 44 | 19 | 20 | 28 | 90 | 0 | 0 | 0 | 330 | 191 | 8 | 51 | 26 | 20 | 0 | 51 | 0 | 42 | 0 | 21 | 11 | 33 | 19 | 106 | 102 | 48 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 74 | 0 | 0 | 0 | 0 | 9 | 325 | 16 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 127 | 0 | 100 | 17 | 60 | 280 | 35 | 35 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 414 | 104 | 0 | 144 | 17 | 0 |  | 424 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 27 | 102 | 25 | 0 | 0 | 52 | 10 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 81 | 0 | 206 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 6343 | 2775 | 9118 | 2926 | 424 | 1071 | 3420 | 670 | 70 | 431 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 103 | 0 | 0 | 225 |  | 0 | 0 | 270 | 93 | 101 | 55 | 0 | 0 | 178 | 100 | 68 | 115 | 74 | 0 | 0 | 18 | 54 | 0 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 10 | 44 | 19 | 20 | 33 | 80 | 0 | 0 | 0 | 290 | 180 | 8 | 46 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 106 | 102 | 81 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 106 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 305 | 16 | 11 | 0 | 287 | 0 | 0 | 200 | 0 | 124 | 0 | 100 | 17 | 60 | 252 | 8 | 35 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 420 | 104 | 0 | 144 | 17 | 0 |  | 424 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 41 | 102 | 25 | 0 | 0 | 52 | 16 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 85 | 0 | 206 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 0 | 0 | 0 |  | 6260 | 2804 | 9064 | 2907 | 424 | 1047 | 3421 | 680 | 70 | 409 | 106 | 0 | 0 | 95.49
21:00 | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 213 |  | 0 | 0 | 270 | 63 | 101 | 55 | 0 | 0 | 185 | 100 | 24 | 64 | 73 | 0 | 0 | 18 | 54 | 0 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 0 | 0 | 19 | 20 | 35 | 80 | 0 | 0 | 0 | 300 | 173 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 102 | 102 | 73 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 106 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 124 | 0 | 100 | 17 | 60 | 280 | 0 | 35 | 0 | 0 | 307 | 54 | 0 | 0 | 0 | 100 | 418 | 104 | 0 | 144 | 0 | 0 |  | 424 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 102 | 25 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 86 | 0 | 204 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 6003 | 2726 | 8729 | 2940 | 424 | 1054 | 3132 | 730 | 70 | 277 | 102 | 0 | 0 | 95.49
22:00 | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 213 |  | 0 | 0 | 270 | 55 | 100 | 55 | 0 | 0 | 178 | 100 | 0 | 64 | 73 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 44 | 0 | 0 | 19 | 20 | 36 | 80 | 0 | 0 | 0 | 260 | 202 | 8 | 52 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 96 | 102 | 48 | 22 | 0 | 30 | 0 | 48 | 50 | 30 | 107 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 287 | 0 | 0 | 200 | 0 | 120 | 0 | 100 | 17 | 60 | 254 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 0 | 100 | 420 | 104 | 0 | 144 | 0 | 0 |  | 424 | 0 | 250 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 102 | 18 | 0 | 0 | 0 | 27 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 88 | 0 | 185 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 5697 | 2557 | 8254 | 2872 | 424 | 1049 | 2786 | 720 | 70 | 237 | 96 | 0 | 0 | 95.48
23:00 | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 213 |  | 0 | 0 | 270 | 0 | 100 | 55 | 0 | 0 | 185 | 70 | 0 | 32 | 73 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 37 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 17 | 0 | 0 | 19 | 20 | 36 | 0 | 0 | 0 | 45 | 260 | 202 | 8 | 52 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 88 | 102 | 0 | 22 | 0 | 30 | 0 | 31 | 5 | 40 | 105 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 38 | 0 | 100 | 17 | 60 | 252 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 421 | 104 | 0 | 144 | 0 | 0 |  | 425 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 12 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 64 | 0 | 170 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 0 |  | 5256 | 2339 | 7595 | 2783 | 425 | 974 | 2441 | 690 | 72 | 122 | 88 | 0 | 0 | 95.48
24:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 0 | 213 |  | 0 | 0 | 250 | 0 | 85 | 15 | 0 | 0 | 120 | 0 | 0 | 16 | 73 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 17 | 33 | 0 | 0 | 37 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 19 | 20 | 38 | 0 | 0 | 0 | 105 | 260 | 187 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 82 | 105 | 0 | 22 | 0 | 30 | 0 | 8 | 5 | 30 | 105 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 17 | 60 | 252 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 420 | 70 | 0 | 144 | 0 | 0 |  | 425 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 55 | 0 | 170 | 0 | 0 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 0 |  | 4926 | 2199 | 7125 | 2767 | 425 | 932 | 2117 | 689 | 72 | 41 | 82 | 0 | 0 | 95.47
KWH | 0 | 0 | 0 | 4410000 | 0 | 2436954 | 0 | 0 | 6274000 |  | 0 | 0 | 6551069 | 929280 | 1542744 | 852068 | 0 | 0 | 3650000 | 1180800 | 632160 | 709920 | 1364016 | 0 | 0 | 69456 | 724320 | 420949 | 382211 | 444708 | 600000 | 690660 | 518500 | 829600 | 39276 | 0 | 949822 | 244000 | 0 | 0 | 291915 | 0 | 0 | 0 | 0 |  | 336960 | 0 | 772926 | 165360 | 292800 | 378720 | 487008 | 569760 | 2748308 | 0 | 0 | 121700 | 7048000 | 4647000 | 200727 | 1169830 | 553968 | 259680 | 0 | 1257194 | 0 | 70240 | 7349 | 502524 | 253080 | 728300 | 479830 | 2097600 | 2275560 | 648960 | 501372 | 12800 | 711000 | 0 | 1118400 | 1124712 | 69627 | 2469000 | 0 | 1682880 | 0 | 335350 | 0 | 0 | 208620 | 7574000 | 392064 | 264000 | 0 | 4548980 | 114108 | 0 | 4003200 | 29436 | 1553760 | 114615 | 1777920 | 428160 | 1527200 | 6113000 | 664800 | 260676 | 0 | 28971 | 6526145 | 527270 | 0 | 0 | 516600 | 2146560 | 9937900 | 1595520 | 251150 | 3398400 | 85309 | 0 |  | 10357818 | 0 | 7591968 | 0 | 721920 | 0 | 0 | 0 | 0 | 6144 | 356625 | 0 | 467600 | 126720 | 0 | 0 | 0 | 93689 | 57599 | 596104 | 123470 | 0 | 0 | 525600 | 82373 | 513840 | 0 | 210110 | 0 | 0 | 3677900 | 0 | 0 | 0 | 0 | 4345027 | 0 | 980310 | 28800 | 4358436 | 0 | 0 | 1607040 | 0 | 1011936 | 0 | 1853760 | 0 | 30332 | 1346400 | 12433700 | 0 | 0 | 0 |  | 127425317 | 53505221 | 180930538 | 69387803 | 10357818 | 24738304 | 54216728 | 16111600 | 1193822 | 2388995 | 2097600 | 437868 | 0
Fuel Cost | 0 | 0 | 0 | 6482700 | 0 | 3216779.28 | 0 | 0 | 6462220 |  | 0 | 0 | 7271686.59 | 7053235.2 | 10629506.16 | 7208495.28 | 0 | 0 | 6314500 | 8891424 | 5765299.2 | 6985612.8 | 12576227.52 | 0 | 0 | 631355.04 | 5287536 | 3253935.77 | 3768600.46 | 333531 | 450000 | 0 | 0 | 0 | 379798.92 | 0 | 256451.94 | 65880 | 0 | 0 | 2711890.35 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7497382.2 | 1579188 | 2547360 | 2999462.4 | 613630.08 | 1692187.2 | 4067495.84 | 0 | 0 | 90058 | 7048000 | 4275240 | 258937.83 | 1345304.5 | 625983.84 | 363552 | 0 | 2149801.74 | 0 | 709424 | 70182.95 | 638205.48 | 189810 | 1274525 | 359872.5 | 15732000 | 2412093.6 | 5892556.8 | 636742.44 | 204032 | 1166040 | 0 | 1990752 | 1754550.72 | 79374.78 | 2567760 | 0 | 3214300.8 | 0 | 580155.5 | 0 | 0 | 425584.8 | 7649740 | 294048 | 200640 | 0 | 34390288.8 | 1937553.84 | 0 | 20816640 | 492169.92 | 15288998.4 | 1339849.35 | 14490048 | 4645536 | 10766760 | 5685090 | 6062976 | 2463388.2 | 0 | 0 | 49337656.2 | 4592521.7 | 0 | 0 | 4427262 | 14296089.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 59661031.68 | 0 | 7971566.4 | 0 | 5674291.2 | 0 | 0 | 0 | 0 | 64389.12 | 3716032.5 | 0 | 724780 | 1236787.2 | 0 | 0 | 0 | 921899.76 | 585205.84 | 5275520.4 | 950719 | 0 | 0 | 5093064 | 799018.1 | 986572.8 | 0 | 159053.27 | 0 | 0 | 19934218 | 0 | 0 | 0 | 0 | 5735435.64 | 0 | 1470465 | 489888 | 5099370.12 | 0 | 0 | 16777497.6 | 0 | 9603272.64 | 0 | 14385177.6 | 0 | 335168.6 | 9949896 | 54583943 | 0 | 0 | 0 |  | 382225468.52 | 232184263.47 | 614409731.99 | 66616851.21 | 59661031.68 | 32439598.95 | 340402255.04 | 74518161 | 322331.94 | 22838452.22 | 15732000 | 1879049.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 238 |  | 0 | 0 | 305 | 41 | 64 | 55 | 0 | 0 | 190 | 40 | 50 | 16 | 69 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 58 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 0 | 34 | 24 | 17 | 19 | 20 | 5 | 130 | 0 | 0 | 0 | 340 | 216 | 8 | 51 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 94 | 82 | 24 | 20 | 2 | 30 | 0 | 45 | 50 | 0 | 106 | 0 | 68 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 111 | 17 | 100 | 17 | 90 | 302 | 50 | 1 | 0 | 5 | 305 | 17 | 0 | 0 | 8 | 100 | 408 | 104 | 41 | 144 | 0 | 0 |  | 434 | 0 | 310 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 37 | 0 | 184 | 0 | 0 | 90 | 0 | 0 | 0 | 107 | 0 | 4 | 35 | 460 | 0 | 0 | 0 |  | 7990 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 103 | 0 | 0 | 229 | 0 | 0 | 0 | 270 | 83 | 100 | 55 | 0 | 0 | 178 | 100 | 102 | 115 | 73 | 0 | 0 | 9 | 54 | 35 | 35 | 22 | 25 | 32 | 17 | 33 | 24 | 0 | 35 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 10 | 44 | 19 | 20 | 24 | 100 | 0 | 0 | 0 | 285 | 185 | 8 | 46 | 26 | 20 | 0 | 51 | 0 | 42 | 4 | 21 | 11 | 33 | 19 | 102 | 102 | 24 | 22 | 0 | 30 | 0 | 51 | 50 | 0 | 105 | 0 | 74 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 282 | 95 | 0 | 200 | 27 | 123 | 0 | 100 | 17 | 60 | 252 | 115 | 70 | 0 | 0 | 307 | 54 | 0 | 0 | 85 | 100 | 415 | 104 | 0 | 144 | 17 | 0 |  | 424 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 43 | 10 | 102 | 25 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 70 | 20 | 198 | 0 | 0 | 95 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 9234 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 102 | 149 | 85 | 0 | 0 | 50 | 54 | 35 | 35 | 22 | 25 | 33 | 17 | 33 | 52 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 100 | 19 | 22 | 25 | 100 | 0 | 0 | 100 | 350 | 225 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 110 | 82 | 22 | 0 | 30 | 0 | 51 | 50 | 120 | 105 | 0 | 74 | 0 | 150 | 0 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 280 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 0 | 144 | 0 | 100 |  | 440 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 35 | 35 | 22 | 25 | 33 | 17 | 33 | 52 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 100 | 19 | 22 | 15 | 100 | 0 | 0 | 100 | 350 | 225 | 8 | 50 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 110 | 82 | 22 | 1.6 | 30 | 0 | 51 | 50 | 100 | 105 | 0 | 74 | 0 | 150 | 0 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 280 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 415 | 104 | 50 | 144 | 0 | 100 |  | 440 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 70 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 50 | 220 | 0 | 0 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 35 | 620 | 0 |  | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 272 | 0 | 0 | 0 | 280 | 0 | 60 | 52 | 0 | 0 | 170 | 0 | 24 | 30 | 67 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 28 | 17 |  | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 100 | 300 | 178 | 8 | 51 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 80 | 106 | 22 | 22 | 0 | 30 | 0 | 8 | 50 | 30 | 105 | 0 | 70 | 0 | 80 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 262 | 0 | 0 | 173 | 0 | 23 | 5 | 100 | 17 | 115 | 275 | 20 | 0 | 0 | 1 | 306 | 18 | 0 | 0 | 8 | 100 | 410 | 70 | 8 | 100 | 0 | 0 | 0 | 423 | 0 | 360 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 130 | 0 | 0 | 90 | 0 | 37 | 0 | 90 | 0 | 1 | 35 | 510 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5579 | 5:00
| Highest Generation |  | 9234 | 19:00
| Day Peak Generation |  | 7990 | 12:00
| Evening Peak Generation |  | 9234 | 19:00
| HVDC Max Flow |  | 435 | 17:00
| HVDC EvPeak Flow |  | 424 | 19:00
| Load factor L.F |  | 81.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7990 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5643 | MW
Evening Peak Generation : |  | 9234 | MW Hour : | 19:00 | Available Max Generation : |  | 13211 | MW
E.P. Demand (at gen end) : |  | 9234 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9234 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3911 | MW
Total Gen. (MKWH) : |  | 180.9305 | System Load Factor : | 81.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -441 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-03
Actual : | 95.44 | Ft.(MSL) , | Rule curve : | 96.72 | Ft.( MSL )
Gas Consumed : | Total = | 824.96 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 99056450.16
: |  | Coal : | 74518161 | Oil : | 363240707.26 | Total : | 536815318.42
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3290.6917 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1114.2522 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 997.484 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 901.0094 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 814.3954 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 657.1763 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 373.5926 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.3675 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 506.8176 |  |  | 0 | 0%
Total | 0 |  | 8824.7868 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj-4,5
|  |  |  | 2) Baghabari-71 &100 MW | 11) Haripur 412 MW
3) Ghorasal Unit-1,2,3,4
4) Shahjibazar 330 MW
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1,2,4 CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Dohazari-Cox'sbazar 132 kV Ckt-1 was under shut down at 07:22 for A/M.
b) Tongi-Ghorasal 230 kV Ckt-1 was under shut down from 08:30 to 17:26 for A/M.
c) Cumilla(N)-Daudkandi 132 kV Ckt-1 was under shut down from 08:46 to 16:41 for A/M.
d) Kaliakoir-Aminbazar 230 kV Ckt-1 was under shut down from 10:12 to 15:29 for A/M.
e) Abul Khair-Baroaulia 132 kV Ckt-1 was under shut down from 09:25 to 17:22 for A/M.
f) Shahjibazar-Srimongal 132 kV Ckt-2 was under shut down from 09:22 to 15:40 for A/M.
g) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 09:15 to 17:17 for A/M.
h) Rangamati-Khagrachori 132 kV Ckt-2 was under shut down from 09:37 to 15:18 for A/M.
i) Cox'sbazar-Matarbari 132 kV Ckt was under shut down from 07:44 to 09:27 for A/M.
j) Kaliakoir-Tongi 230 kV Ckt-1 was under shut down from 08:53 to 15:44 for A/M.
k) Baroirhat 132/33 kV T-1 transformer was under shut down from 09:50 to 17:16 for A/M.
l) Rangpur 132/33 kV T-2 transformer was under shut down from 09:44 to 17:47 for SAS work.
m) Joydevpur 132/33 kV T-3 transformer was under shut down from 09:18 to 17:03 for A/M.
n) Mirpur 132/33 kV T-1 transformer was under shut down from 09:02 to 17:30 for A/M.
o) Biyanibazar 132 kV Bus-2 was under shut down from 10:49 to 17:52 for A/M.
p) Jhenaidah-Kustia 132 kV Ckt-1 was under shut down from 09:31 to 14:04 for A/M.
q) Barisal-Patuakhali 132 kV Ckt-1 was under shut down from 08:44 to 17:04 for A/M.
r) Khulna© 132/33 kV T-1 transformer was under shut down from 09:23 to 13:05 for C/M.
s) Bogura 132/33 kV T-3 transformer was under shut down at 08:38 for C/M.
t) Bashundhara-Tongi 132 kV Ckt-1 was under shut down from 11:49 to 15:32 for D/W.
u) Bheramara-Bahrampur 400 kV Ckt-2 was under shut down from 09:56 to 16:26 for C/M.
v) Hasnabad 132/33 kV T-1 transformer was under shut down from 11:34 to 21:01 for C/M.
w) Hasnabad 230/132 kV TR-1 transformer was under shut down at 09:37 for C/M.
x) Ishurdi 132/33 kV T-2 transformer was under shut down at 09:56 for oil centrifuging.
y) Shahjibazar 132/33 kV T-5 transformer was under shut down at 11:17 for C/M.
z) Mirpur 132 kV reserve Bus was under shut down from 12:32 to 17:29 for A/M.
aa) Khulna© 132/33 kV T-3 transformer was under shut down from 07:38 to 08:34 for C/M.
ab) Benapole 132/33 kV T-1 transformer was under shut down from 12:42 to 13:38 for C/M.
ac) Barisal 132/33 kV T-1 transformer was under shut down from 13:54 to 17:01 for bus coupling work. |  |  |  |  | About 53 MW power interruption occurred under Barisal S/S area
ad) Barisal 132/33 kV T-2 transformer was under shut down from 13:58 to 18:45 for maint.work. |  |  |  |  | from 13:54 to 17:01.
ae) Cumilla(N) 132/33 kV T-3 & T-4 transformers tripped at 15:31 showing E/F & O/C relays and were |  |  |  |  | About 40 MW power interruption occurred under Cumilla(N) S/S area
switched on at 15:57 & 16:45 respectively. |  |  |  |  | from 15:31 to 15:57.
af) Sylhet-225 MW CCPP GT was synchronized at 19:37.
ag) Kushiara-163 MW CCPP GT was synchronized at 21:31.
ah) Ashuganj North-450 MW CCPP GT was synchronized at 22:05.
ai) Ashuganj #3 was shut down at 22:50 for gas shortage.
aj) Kushiara-163 MW CCPP GT was synchronized at 21:31.
ak) Sikalbaha-TK Chemical 132 kV Ckt is under shut down at 07:02(3/2/21) for A/M.
al) Tongi-Ghorasal 230 kV Ckt-1 is under shut down at 07:34(3/2/21) for A/M.
am) Pabna-Shahjadpur 132 kV Ckt is under shut down at 07:42(3/2/21) for A/M.
an) Sirajganj #2 CCPP ST & GT were shut down at 07:35 & 07:40(3/2/21) for gas shortage.
ao) Sylhet 132/33 kV t-2 transformer is under shut down at 07:32(3/2/21) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4410000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2436954
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 229 | 6274000 | Gas Shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 83 | 929280 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6551069 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1542744
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 852068
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 73 | 1364016 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 444708
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 178 | 3650000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1180800
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 632160
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 9 | 69456 | High Voltage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 724320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 709920 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 420949 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 382211 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1290660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 518500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 829600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 24 | 39276 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 282 | 4548980
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 95 | 114108 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 27 | 29436 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 123 | 1553760 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 260676 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1595520
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3398400 | Engine problem
| Dhaka area Total |  |  |  | 6057 | 2724 | 46753571
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 20 | 291915
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 114615
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 378720 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1193822 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 772926 | High Voltage.
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 165360 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1777920
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 487008
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 569760
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 292800 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28971
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 6526145
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 527270
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2146560
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 17 | 85309 | on test
| Chattogram area Total |  |  |  | 2266 | 870 | 15359101
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2748308 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 185 | 4647000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 121700 | Under maint.
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 7048000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 553968 | Machine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 259680 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1257194
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 60 | 1527200 | Red hot at APSCL
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 70240
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 46 | 1169830 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 428160 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 502524
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 253080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2097600
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 728300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 4 | 7349 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 479830 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 85 | 516600 | High Voltage.
| Cumilla Area Total |  |  |  | 2980 | 1115 | 24617290
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 2275560 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 501372
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 648960 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12800
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4003200
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 664800 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 251150
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 336960
| Mymensingh Area Total |  |  |  | 709 | 487 | 8694802
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 711000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 69627 | Under maint.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 105 | 2469000 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1118400
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1124712
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1682880 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 335350 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 392064 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7574000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 252 | 6113000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 208620
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 415 | 9937900 | RRT
| Sylhet Area Total |  |  |  | 1988 | 1323 | 32000553
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 424 | 10357818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 721920 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 6144 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 270 | 7591968 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 356625
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 20 | 28800 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 1607040 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 948 | 20670315
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 126720 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 467600 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 70 | 980310 | Engine problem
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 12433700
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | High Voltage.
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | High Voltage.
| Barisal Area Total |  |  |  | 1676 | 648 | 14008330
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 93689
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 57599 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 123470 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 167 | 4345027 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 198 | 4358436 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 82373 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 513840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210110
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 525600
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 596104
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1011936
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1346400
| Rajshahi Area Total |  |  |  | 2183 | 856 | 13264584
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3677900 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1853760
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30332
| Rangpur Area Total |  |  |  | 605 | 263 | 5561992
| Total |  |  |  | 20748 | 9234 | 180930538
| Eastern Grid Total |  |  |  | 14000 | 6519 | 127425317
| Western Grid Total |  |  |  | 6748 | 2715 | 53505221
| National Grid Total |  |  |  | 20748 | 9234 | 180930538
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2021-02-02
| (a) ENTIRE EASTERN GRID : |  | 5752 | MW | (b) ENTIRE WESTERN GRID : |  | 2998 | MW
| i) Dhaka area |  | 2981 | MW | i) Khulna area |  | 1108 | MW
| ii) Chittagong area |  | 888 | MW | ii) Rajshahi area |  | 963 | MW
| iii) Comilla area |  | 754 | MW | iii) Barisal area |  | 239 | MW
| iv) Mymensingh area |  | 799 | MW | iv) Rangpur area |  | 688 | MW
| v) Sylhet area |  | 330 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8750 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 12:00 | Sherpur | 108 | 8:00 | Jhenida | 85 | 18:30
| Munsiganj | 88 | 19:30 | Srimongal | 29 | 18:30 | Bottail | 106 | 18:30
| Sonargaon | 64 | 10:00 | Shahjibazar | 86 | 18:30 | G.K Project | 30 | 18:30
| Shyampur | 160 | 10:00 | Fenchuganj | 22 | 19:00 | Faridpur | 134 | 18:30
| Bhulta | 154 | 13:00 | Kulawara | 27 | 19:00 | Madaripur | 67 | 20:00
| Madanganj | 52 | 11:00 | Sylhet | 82 | 19:30 | Sariatpur | 42 | 19:30
| Shitalakhya | 98 | 12:00 | Chatak | 19 | 18:00 | Gopalganj | 58 | 20:00
| Rahim steel | 28 | 13:00 | Sunamganj | 31 | 20:00 | Bagerhat | 85 | 19:00
| Matuail | 46 | 10:00 | Biani Bazar | 41 | 18:00 | Mongla | 34 | 18:30
| Ghorasal | 66 | 19:00 | Comilla (S) | 108 | 18:30 | Satkhira | 75 | 19:00
| Narsingdi | 128 | 20:00 | Comilla(N) | 77 | 19:30 | Gallamari | 33 | 7:00
| Haripur (SBU) | 99 | 12:00 | Chandpur | 45 | 20:00 | Magura | 40 | 18:30
| Ullon | 44 | 14:00 | Feni | 78 | 20:00 | Norail | 24 | 18:30
| Hasnabad | 91 | 18:00 | Chowmuhani | 124 | 19:00 | Chuadanga | 65 | 18:30
| Magbazar | 63 | 19:00 | Ashuganj | 40 | 21:00 | Barisal(N) | 30 | 19:30
| Maniknagar | 58 | 16:00 | Daudkandi | 88 | 18:30 | Barisal (S) | 76 | 20:00
| Bangabhaban | 14 | 15:00 | B.Baria | 102 | 18:00 | Patuakhali | 90 | 21:00
| Narinda | 66 | 12:00 | Ramganj | 52 | 19:00 | Bhandaria | 40 | 20:00
| Dhanmondi | 87 | 13:00 | Chaddagram | 26 | 18:00 | Borhan Uddin | 25 | 22:00
| Lalbag | 64 | 18:30 | PHP | 7 | 9:00 | Ishurdi | 46 | 19:30
| Madartek | 51 | 18:30 | Kochua | 40 | 20:00 | Ruppur Paromanobik | 2 | 18:00
| Dhaka University | 0 | #NUM! | Madunaghat | 44 | 19:00 | Natore | 89 | 19:30
| Aftabnagar | 6 | 12:00 | Hathazari | 64 | 18:00 | Bogra | 121 | 19:00
| Fatullah | 43 | 11:00 | Khulshi | 151 | 14:00 | Noagaon | 88 | 13:00
| Mirpur | 70 | 18:30 | Halishahar | 87 | 18:00 | Rajshahi | 100 | 20:00
| Kalyanpur | 72 | 13:00 | Baraulia | 134 | 9:00 | Rajshahi New | 12 | 18:30
| Gulshan | 74 | 14:00 | Sikalbaha | 19 | 18:00 | C.Nawabganj | 73 | 18:30
| Uttara | 64 | 13:00 | Dohazari | 58 | 18:30 | Amnura | 38 | 8:00
| Uttara New | 23 | 18:30 | Cox'sbazar | 79 | 20:00 | Pabna | 64 | 20:00
| Kamrangirchar | 66 | 18:30 | Chandraghona | 24 | 18:00 | Shahjadpur | 73 | 19:30
| Savar | 124 | 18:30 | Kaptai | 0 | 1:00 | Serajganj | 77 | 12:00
| Bhasantec | 98 | 14:00 | A. Khaer Stl. | 18 | 18:00 | Niyamatpur | 75 | 11:00
| Agargaon | 45 | 13:00 | Bakulia | 67 | 13:00 | Joypurhat | 61 | 9:00
| Satmosjid | 58 | 13:00 | Julda | 22 | 11:00 | Sherpur(Bogura) | 44 | 18:00
| Tongi | 84 | 17:00 | TK chemical | 19 | 18:30 | Mohastangor | 32 | 18:30
| Kabirpur | 194 | 18:30 | Modern Steel | 0 | 1:00 | Bangura | 15 | 18:30
| Basundhara | 90 | 13:00 | Shahmirpur | 19.5 | 18:00 | Rangpur | 120 | 18:30
| Manikganj | 52 | 20:00 | Khagrachhari | 20 | 1:00 | Lalmonirhat | 57 | 18:00
| Joydevpur | 115 | 18:00 | Matarbari | 27 | 18:30 | Saidpur | 104 | 9:00
| New Tongi | 81 | 12:00 | Baroiar Hat | 24 | 18:00 | Purbasadipur | 104 | 19:00
| Korda | 148 | 9:00 | Rangamati | 10 | 19:00 | Thakurgaon | 70 | 18:30
| Dhamrai | 78 | 10:00 | Abul Khair 230 | 158 | 15:00 | Palashbari | 108 | 18:30
| Rajendrapur | 76 | 18:00 | BSRM | 108 | 0:00 | Barapukuria | 50 | 9:00
| Valuka | 98 | 15:00 | GPH Ispat | 13 | 17:00 | Panchagar | 47 | 18:30
| Tangail | 150 | 18:30 | Goalpara | 18 | 13:00 | Joldhaka | 23 | 18:30
| Mymensing | 165 | 18:00 | Central s/s | 75 | 19:00 | Kurigram | 47 | 20:00
| Kishorganj | 102 | 20:00 | Noapara | 53 | 18:30
| Netrokona | 99 | 18:30 | Jessore | 85 | 19:00
| Jamalpur | 101 | 18:30 | Benapol | 44 | 8:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 24:00 | 404 | 12:00 | Kaliakoir | 410 | 0.66667 | 397 | 0.5
| Bheramara | 427 | 1:00 | 397 | 13:00 | Bhulta | 394 | 24:00 | 382 | 0.5
| Ashuganj(N) | 403 | 1:00 | 383 | 13:00 | Gopalganj | 403 | 0.625 | 386 | 0.875
| Payra | 411 | 19:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 236 | 19:30 | 230 | 22:00
| Ishurdi | 241 | 24:00 | 226 | 9:00 | Megnaghat | 241 | 24:00 | 240 | 2:00
| Ashuganj | 247 | 24:00 | 237 | 12:00 | Fenchuganj | 246 | 24:00 | 237 | 11:00
| Serajganj | 235 | 23:00 | 224 | 9:00 | Siddhirganj | 241 | 21:00 | 235 | 12:00
| Baghabari | 241 | 22:00 | 231 | 11:00 | Maniknagar | 237 | 24:00 | 233 | 12:00
| Barapukuria | 237 | 23:00 | 226 | 9:00 | Agargaon | 242 | 16:00 | 234 | 12:00
| Bogra | 238 | 24:00 | 218 | 9:00 | Barisal | 254 | 24:00 | 235 | 18:00
| Rajshahi | 240 | 22:00 | 219 | 9:00 | Bhola 225 MW | 258 | 22:00 | 236 | 18:00
| Khulna South | 242 | 21:00 | 227 | 12:00 | AKSML | 238 | 24:00 | 227 | 5:00
| Rampura | 236 | 23:00 | 231 | 10:00 | BSRM | 239 | 24:00 | 230 | 5:00
| Haripur | 240 | 1:00 | 233 | 12:00 | Bibiyana | 245 | 2:00 | 238 | 21:00
| Hasnabad | 241 | 23:00 | 235 | 13:00 | Bhulta | 242 | 20:00 | 234 | 12:00
| Shyampur | 240 | 19:00 | 220 | 12:00 | Ashuganj (S) | 243 | 24:00 | 236 | 10:00
| Aminbazar | 242 | 7:00 | 235 | 12:00 | Kaliakoir | 240 | 24:00 | 230 | 16:00
| Tongi | 236 | 4:00 | 227 | 13:00 | GPH | 237 | 1:00 | 228 | 17:00
| Comilla (N) | 244 | 1:00 | 232 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 19:00 | 137 | 12:00 | Madanhat | 141 | 0.041667 | 136 | 0.66667
| Munsiganj | 142 | 20:00 | 138 | 12:00 | Hathazari | 140 | 0.20833 | 137 | 0.45833
| Sonargaon | 137 | 4:00 | 135 | 0:00 | Khulshi | 138 | 0.25 | 130 | 0.20833
| Shyampur | 135 | 19:00 | 130 | 12:00 | Halishahar | 140 | 0.83333 | 135 | 0.75
| Bhulta | 137 | 18:00 | 133 | 10:00 | Baraulia | 140 | 0.83333 | 136 | 0.5
| Madanganj | 139 | 4:00 | 135 | 16:00 | Sikalbaha | 141 | 0.25 | 135 | 0.125
| Shitalakhya | 142 | 19:00 | 135 | 2:00 | Dohazari | 138 | 0.8125 | 130 | 0.16667
| Rahim steal | 140 | 1:00 | 137 | 11:00 | Cox'sbazar | 132 | 0.125 | 120 | 0.8125
| Matuail | 141 | 19:00 | 137 | 12:00 | Chandraghona | 140 | 0.041667 | 135 | 0.20833
| Ghorasal | 142 | 1:00 | 140 | 10:00 | Kaptai | 0 |  | 0
| Narsinghdi | 137 | 13:00 | 134 | 12:00 | A. Khaer Stl. | 140 | 0.041667 | 130 | 0.625
| Haripur (SBU) | 140 | 4:00 | 137 | 12:00 | Bakulia | 138 | 0.041667 | 132 | 0.20833
| Ullon | 135 | 23:00 | 130 | 12:00 | Julda | 140 | 0.625 | 136 | 0.45833
| Hasnabad | 138 | 21:00 | 135 | 3:00 | TK Chemical | 141 | 0.83333 | 136 | 0.95833
| Magbazar | 136 | 1:00 | 131 | 11:00 | Modern Steel | 139 | 0.79167 | 136 | 0.083333
| Maniknagar | 138 | 1:00 | 135 | 10:00 | Shahmirpur | 140 | 0.79167 | 135 | 0.75
| Bangabhaban | 138 | 1:00 | 135 | 10:00 | Khagrachhari | 139 | 0.041667 | 134 | 0.5
| Narinda | 138 | 1:00 | 135 | 10:00 | Matarbari | 135 | 0.29167 | 112 | 0.75
| Dhanmondi | 135 | 23:00 | 130 | 12:00 | Baroiar Hat | 141 | 0 | 137 | 0.41667
| Lalbag | 139 | 7:00 | 134 | 12:00 | Rangamati | 139 | 1:00 | 134 | 18:00
| Madartek | 136 | 1:00 | 130 | 12:00 | Goalpara S/S | 139 | 20:00 | 128 | 12:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Khulna Central S/S | 138 | 21:00 | 129 | 0.5
| Aftabnagar | 136 | 1:00 | 131 | 12:00 | Noapara | 137 | 18:00 | 126 | 0.5
| Fatullah | 135 | 7:00 | 130 | 12:00 | Jessore | 135 | 23:00 | 121 | 0.5
| Mirpur | 141 | 6:00 | 136 | 12:00 | Benapol | 135 | 0.83333 | 122 | 0.5
| Kalyanpur | 140 | 6:00 | 136 | 12:00 | Jhenida | 133 | 4:00 | 123 | 0.41667
| Gulshan | 135 | 6:00 | 130 | 12:00 | Bottail | 136 | 0.95833 | 128 | 0.375
| Uttara | 140 | 24:00 | 135 | 12:00 | G.K Project | 141 | 0.25 | 134 | 0.375
| Uttara New | 141 | 24:00 | 135 | 12:00 | Faridpur | 137 | 0.16667 | 131 | 0.375
| Kamrangirchar | 136 | 24:00 | 131 | 12:00 | Madaripur | 144 | 0.66667 | 133 | 0.77083
| Savar | 141 | 24:00 | 137 | 12:00 | Shariyatpur S/S | 136 | 5:00 | 136 | 0.8125
| Bhasantec | 139 | 24:00 | 133 | 12:00 | Gopalganj | 146 | 0.70833 | 137 | 0.77083
| Agargaon | 139 | 24:00 | 134 | 12:00 | Bagerhat | 137 | 13:00 | 128 | 0.5
| Satmosjid | 139 | 24:00 | 133 | 12:00 | Mongla | 136 | 13:00 | 127 | 0.5
| Tongi | 141 | 18:00 | 137 | 11:00 | Satkhira | 136 | 13:00 | 127 | 12:00
| Kabirpur | 137 | 24:00 | 127 | 12:00 | Gallamari | 136 | 0.83333 | 128 | 0.5
| Basundhara | 141 | 19:00 | 135 | 12:00 | Magura | 139 | 2:00 | 120 | 0.5
| Manikganj | 144 | 21:00 | 140 | 12:00 | Narail | 135 | 0.083333 | 120 | 0.5
| Joydevpur | 139 | 24:00 | 135 | 12:00 | Chuadanga | 132 | 4:00 | 117 | 0.5
| New Tongi | 141 | 24:00 | 135 | 12:00 | Barisal(N) | 143 | 14:00 | 133 | 18:00
| Kodda | 142 | 19:00 | 133 | 11:00 | Barisal (S) | 143 | 0.66667 | 131 | 0.75
| Dhamrai | 137 | 24:00 | 127 | 12:00 | Patuakhali(S) | 138 | 0.20833 | 125 | 0.75
| Rajendrapur | 140 | 24:00 | 134 | 12:00 | Bhandaria | 141 | 0.58333 | 131 | 0.75
| Valuka | 132 | 1:00 | 123 | 12:00 | Ishurdi | 138 | 3:00 | 131 | 12:00
| Tangail | 136 | 1:00 | 128 | 12:00 | Ruppur Paromanobik | 137 | 3:00 | 133 | 10:00
| Mymensing | 134 | 0:00 | 126 | 12:00 | Natore | 136 | 4:00 | 128 | 10:00
| Kishorganj | 135 | 1:00 | 126 | 12:00 | Bogra | 137 | 17:00 | 125 | 9:00
| Netrokona | 133 | 0:00 | 123 | 12:00 | Noagaon | 132 | 2:00 | 126 | 9:00
| Jamalpur | 141 | 19:00 | 134 | 4:00 | Rajshahi | 136 | 20:00 | 126 | 9:00
| Sherpur | 139 | 19:30 | 124 | 4:00 | Rajshahi New | 136 | 20:00 | 125 | 9:00
| Srimongal | 140 | 1:00 | 138 | 15:00 | C.Nawabganj | 137 | 20:00 | 125 | 9:00
| Shahjibazar | 138 | 1:00 | 134 | 12:00 | Amnura | 138 | 20:00 | 121 | 9:00
| Fenchuganj | 140 | 4:00 | 136 | 11:00 | Pabna | 138 | 4:00 | 130 | 9:00
| Khulawara | 140 | 1:00 | 133 | 12:00 | Shahjadpur | 140 | 5:00 | 132 | 10:00
| Sylhet | 138 | 1:00 | 133 | 12:00 | Serajganj | 136 | 4:00 | 125 | 13:00
| Chatak | 137 | 1:00 | 131 | 12:00 | Niyamatpur | 132 | 3:00 | 115 | 12:00
| Sunamganj | 137 | 3:00 | 131 | 12:00 | Joypurhat | 132 | 4:00 | 114 | 9:00
| Biani Bazar | 138 | 1:00 | 132 | 12:00 | Sherpur(Bogura) | 137 | 5:00 | 125 | 12:00
| Comilla(s) | 132 | 1:00 | 126 | 18:00 | Mohastangor | 136 | 17:00 | 123 | 9:00
| Comilla(n) | 146 | 0:00 | 142 | 11:00 | Bangura | 140 | 4:00 | 131 | 12:00
| Chandpur | 145 | 8:00 | 142 | 18:00 | Rangpur | 134 | 17:00 | 122 | 9:00
| Feni | 140 | 20:00 | 137 | 12:00 | Lalmonirhat | 132 | 17:00 | 123 | 9:00
| Chowmuhani | 138 | 7:00 | 135 | 11:00 | Saidpur | 133 | 5:00 | 117 | 9:00
| Ashuganj | 140 | 1:00 | 138 | 11:00 | Purbasadipur | 132 | 4:00 | 117 | 9:00
| Daudkandi | 141 | 7:00 | 137 | 11:00 | Thakurgaon | 131 | 4:00 | 116 | 8:00
| B.Baria | 135 | 7:00 | 133 | 20:00 | Palashbari | 134 | 17:00 | 122 | 9:00
| Ramganj | 137 | 19:30 | 136 | 15:00 | Barapukuria | 134 | 3:00 | 126 | 9:00
| Chaddagram | 143 | 20:00 | 139 | 12:00 | Panchagar | 131 | 4:00 | 114 | 9:00

## L-Curve
Date | 2021-02-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 17 | 4926 | 2199 | 7125 |  |  |  | QF-LDC-11
0:30 | 80 | 4706 | 2005.5 | 6711.5 | Date: | 2021-02-02
1:00 | 143 | 4486 | 1812 | 6298
1:30 | 99.5 | 4322.5 | 1812 | 6134.5
2:00 | 56 | 4159 | 1812 | 5971
2:30 | 42.5 | 4090.5 | 1804.5 | 5895 | [5 empty] | Gen. at Eve. Peak | 9234 | 9234 MW (19:00 )
3:00 | 29 | 4022 | 1797 | 5819 | [6 empty] | 19:00
3:30 | 34.5 | 3932 | 1801.5 | 5733.5 | [5 empty] | Gen. at Day Peak | 7990 | 7990 MW (12:00 )
4:00 | 40 | 3842 | 1806 | 5648 | [6 empty] | 12:00
4:30 | 40.5 | 3815.5 | 1798 | 5613.5 | [5 empty] | Highest Generation | 9234
5:00 | 41 | 3789 | 1790 | 5579 | [6 empty] | 19:00
5:30 | 57.5 | 3930.5 | 1800.5 | 5731
6:00 | 74 | 4072 | 1811 | 5883
6:30 | 179 | 4292 | 1875.5 | 6167.5
7:00 | 284 | 4512 | 1940 | 6452
7:30 | 355 | 4774 | 2052.5 | 6826.5
8:00 | 426 | 5036 | 2165 | 7201
8:30 | 389.5 | 5238.5 | 2186.5 | 7425
9:00 | 353 | 5441 | 2208 | 7649
9:30 | 283 | 5505 | 2210.5 | 7715.5
10:00 | 213 | 5569 | 2213 | 7782
10:30 | 202.5 | 5609 | 2204 | 7813
11:00 | 192 | 5649 | 2195 | 7844
11:30 | 251 | 5738 | 2179 | 7917
12:00 | 310 | 5827 | 2163 | 7990
12:30 | 375.5 | 5920.5 | 2189.5 | 8110
13:00 | 441 | 6014 | 2216 | 8230
13:30 | 370.5 | 5925 | 2134.5 | 8059.5
14:00 | 300 | 5836 | 2053 | 7889
14:30 | 235.5 | 5718.5 | 1999 | 7717.5
15:00 | 171 | 5601 | 1945 | 7546
15:30 | 86.5 | 5431 | 1959 | 7390
16:00 | 2 | 5261 | 1973 | 7234
16:30 | 4.5 | 5232 | 2022 | 7254
17:00 | 7 | 5203 | 2071 | 7274
17:30 | 128 | 5592.5 | 2216.5 | 7809
18:00 | 249 | 5982 | 2362 | 8344
18:30 | 344 | 6250.5 | 2538.5 | 8789
19:00 | 439 | 6519 | 2715 | 9234
19:30 | 366 | 6343 | 2775 | 9118
20:00 | 299 | 6260 | 2804 | 9064 |  |  |  | Executive Engineer
20:30 | 269.5 | 6131.5 | 2765 | 8896.5 |  |  |  | Network Operation Division
21:00 | 240 | 6003 | 2726 | 8729
21:30 | 173.5 | 5850 | 2641.5 | 8491.5
22:00 | 107 | 5697 | 2557 | 8254 |  |  |  |  | Page 6 of 7
22:30 | 75.5 | 5476.5 | 2448 | 7924.5
23:00 | 44 | 5256 | 2339 | 7595
23:30 | 30.5 | 5091 | 2269 | 7360
24:00 | 17 | 4926 | 2199 | 7125
9234 MW (19:00 )
7990 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-02 |  | Energy | 180930538
[11 empty] | 2021-02-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2767 | 425 | 932 | 2441 | 689 | 72 | 41 | 0 | 82 | 0
0:30 | 2780 | 429.5 | 993 | 1844 | 669 | 59.5 | 20.5 | 0 | 78 | 0 | Date: | 2021-02-02
1:00 | 2793 | 434 | 1054 | 1247 | 649 | 47 | 0 | 0 | 74 | 0
1:30 | 2783.5 | 434 | 1067.5 | 1081.5 | 649 | 47 | 0 | 0 | 72 | 0 | [7 empty] | Total Energy | 180.9305 | Total Energy Gen 180.931 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.931 MKWHr
2:00 | 2774 | 434 | 1081 | 916 | 649 | 47 | 0 | 0 | 70 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2782 | 434 | 1081 | 848 | 634 | 47 | 0 | 0 | 69 | 0 | [7 empty] | Energy Requirement | 180.9305
3:00 | 2790 | 434 | 1081 | 780 | 619 | 47 | 0 | 0 | 68 | 0
3:30 | 2794.5 | 434 | 1086 | 684.5 | 619.5 | 47 | 0 | 0 | 68 | 0 | [6 empty] | Shortage
4:00 | 2799 | 434 | 1091 | 589 | 620 | 47 | 0 | 0 | 68 | 0
4:30 | 2813.5 | 434 | 1085 | 556 | 610 | 47 | 0 | 0 | 68 | 0
5:00 | 2828 | 434 | 1079 | 523 | 600 | 47 | 0 | 0 | 68 | 0
5:30 | 2858.5 | 434 | 1091.5 | 630 | 600 | 47 | 0 | 0 | 70 | 0
6:00 | 2889 | 434 | 1104 | 737 | 600 | 47 | 0 | 0 | 72 | 0
6:30 | 2857.5 | 434 | 1088.5 | 1060.5 | 600 | 46.5 | 6.5 | 0 | 73 | 1 |  |  |  |  | Coal
7:00 | 2826 | 434 | 1073 | 1384 | 600 | 46 | 13 | 0 | 74 | 2
7:30 | 2888 | 434 | 1061.5 | 1681 | 600 | 46 | 32 | 0 | 76 | 8 |  |  |  | Oil |  |  |  | ,
8:00 | 2950 | 434 | 1050 | 1978 | 600 | 46 | 51 | 0 | 78 | 14
8:30 | 2956 | 433.5 | 1037.5 | 2180.5 | 615 | 46.5 | 51 | 0 | 81 | 24
9:00 | 2962 | 433 | 1025 | 2383 | 630 | 47 | 51 | 0 | 84 | 34
9:30 | 2951 | 433.5 | 1003.5 | 2479.5 | 620 | 47.5 | 51 | 0 | 86 | 43.5
10:00 | 2940 | 434 | 982 | 2576 | 610 | 48 | 51 | 0 | 88 | 53
10:30 | 2931.5 | 434 | 981 | 2604.5 | 610 | 52 | 51 | 0 | 90 | 59
11:00 | 2923 | 434 | 980 | 2633 | 610 | 56 | 51 | 0 | 92 | 65
11:30 | 2973.5 | 434 | 978.5 | 2653.5 | 610 | 57 | 50.5 | 0 | 93 | 67
12:00 | 3024 | 434 | 977 | 2674 | 610 | 58 | 50 | 0 | 94 | 69
12:30 | 2950.5 | 434 | 985.5 | 2818.5 | 625 | 58 | 76.5 | 0 | 94 | 68
13:00 | 2877 | 434 | 994 | 2963 | 640 | 58 | 103 | 0 | 94 | 67
13:30 | 2877 | 434 | 994 | 2963 | 640 | 58 | 103 | 0 | 94 | 67
14:00 | 2877 | 434 | 994 | 2963 | 640 | 58 | 103 | 0 | 94 | 67
14:30 | 2809 | 434 | 953.5 | 2811.5 | 605 | 58 | 68 | 0 | 94 | 55
15:00 | 2741 | 434 | 913 | 2660 | 570 | 58 | 33 | 0 | 94 | 43
15:30 | 2676.5 | 434 | 915 | 2588.5 | 560 | 57.5 | 33 | 0 | 92 | 33.5
16:00 | 2612 | 434 | 917 | 2517 | 550 | 57 | 33 | 0 | 90 | 24
16:30 | 2609.5 | 434.5 | 924.5 | 2533 | 540 | 57 | 52.5 | 0 | 89 | 14
17:00 | 2607 | 435 | 932 | 2549 | 530 | 57 | 72 | 0 | 88 | 4
17:30 | 2713.5 | 434.5 | 962 | 2790 | 550 | 63.5 | 196.5 | 0 | 97 | 2
18:00 | 2820 | 434 | 992 | 3031 | 570 | 70 | 321 | 0 | 106 | 0
18:30 | 2828.5 | 429 | 1019.5 | 3359 | 620 | 70 | 359 | 0 | 104 | 0
19:00 | 2837 | 424 | 1047 | 3687 | 670 | 70 | 397 | 0 | 102 | 0
19:30 | 2926 | 424 | 1071 | 3420 | 670 | 70 | 431 | 0 | 106 | 0
20:00 | 2907 | 424 | 1047 | 3421 | 680 | 70 | 409 | 0 | 106 | 0
20:30 | 2923.5 | 424 | 1050.5 | 3276.5 | 705 | 70 | 343 | 0 | 104 | 0
21:00 | 2940 | 424 | 1054 | 3132 | 730 | 70 | 277 | 0 | 102 | 0
21:30 | 2906 | 424 | 1051.5 | 2959 | 725 | 70 | 257 | 0 | 99 | 0
22:00 | 2872 | 424 | 1049 | 2786 | 720 | 70 | 237 | 0 | 96 | 0
22:30 | 2827.5 | 424.5 | 1011.5 | 2613.5 | 705 | 71 | 179.5 | 0 | 92 | 0
23:00 | 2783 | 425 | 974 | 2441 | 690 | 72 | 122 | 0 | 88 | 0
23:30 | 2775 | 425 | 953 | 2441 | 689.5 | 72 | 81.5 | 0 | 85 | 0 | Max Temp. in Dhaka |  | 25.4° C
24:00 | 2767 | 425 | 932 | 2441 | 689 | 72 | 41 | 0 | 82 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 180.931 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.931 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 47 | 48 | 56 | 58 | 58 | 58 | 58 | 57 | 57 | 35 |  | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 949822
2 | Karnaphuli Hydro PP Unit-4 & 5 | [17 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 244000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 4 | 15 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 |  | 20 | 25 | 25 | 25 |  |  |  | 291915
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 17 | 17 | 17 | 15 | 11 | 6 | 1 | [9 empty] | 114615
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [6 empty] | 13 | 51 | 51 | 51 | 51 | 34 | 51 | 17 | 17 | 17 | 17 | 85 |  | 85 | 85 | 85 | 85 | 44 | 17 | 0 | 772926
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 10 |  | 42 | 42 | [5 empty] | 70240
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 95 | 75 | 80 | 80 | 80 | 80 | 80 | 190 | 190 | 160 | 160 | 190 | 175 | 150 | 150 | 150 | 120 | 120 |  | 178 | 185 | 178 | 185 | 178 | 185 | 120 | 3650000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 0 |  |  |  | 0 | 25 | 65 | 190 | 230 | 230 | 230 | 250 | 265 | 265 | 265 | 265 | 265 |  | 282 | 285 | 287 | 285 | 287 | 286 | 286 | 4548980
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 180 | 4410000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 100 |  | 100 | 90 | 80 | 80 | 80 |  |  | 2748308
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 26 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 5 | 5 | 553968
33 | Ashuganj 225 MW CCPP | 184 | 184 | 184 | 184 | 191 | 205 | 192 | 184 | 189 | 184 | 211 | 216 | 184 | 174 | 175 | 185 | 186 | 215 |  | 185 | 191 | 180 | 173 | 202 | 202 | 187 | 4647000
34 | Ashuganj 450 MW CCPP(South) | 285 | 285 | 280 | 285 | 295 | 315 | 290 | 285 | 285 | 280 | 280 | 340 | 295 | 295 | 275 | 270 | 270 | 330 |  | 285 | 330 | 290 | 300 | 260 | 260 | 260 | 7048000
| Ashuganj 450 MW CCPP(North) | [24 empty] | 45 | 105 | 121700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 40 | 5 | 5 | 5 | 5 |  | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 259680
36 | Chandpur 150 MW CCPP | 50 | 50 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 51 | 51 | 46 | 50 | 50 | 47 | 50 | 51 |  | 46 | 51 | 46 | 51 | 52 | 52 | 50 | 1169830
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 293 | 314 | 316 | 316 | 316 | 316 | 316 | 318 | 290 | 269 | 264 | 238 | 238 | 230 | 234 | 232 | 237 | 238 |  | 229 | 223 | 225 | 213 | 213 | 213 | 213 | 6274000
42 | RPCL 210MW CCPP | 104 | 104 | 104 | 105 | 105 | 105 | 105 | 106 | 104 | 105 | 84 | 82 | 80 | 80 | 78 | 84 | 84 | 85 |  | 102 | 102 | 102 | 102 | 102 | 102 | 105 | 2275560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 19 | 31 | 38 | 41 | 39 | 34 | 25 | 14 | 3 | [9 empty] | 251150
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 711000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 105 | 106 | 105 | 107 | 106 | 103 | 105 | 107 | 105 | 107 | 106 | 106 | 105 | 105 | 106 | 106 | 106 | 106 |  | 105 | 105 | 106 | 106 | 107 | 105 | 105 | 2469000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 70 | 67 | 67 | 67 | 68 | 68 | 68 | 68 | 69 | 70 | 73 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1682880
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [21 empty] | 80 | 80 | 80 | 80 | 80 | 335350
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 208620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 48 | 45 | 44 | 45 | 45 | 45 | 45 | 45 | 47 | 47 | 47 | 50 | 50 | 51 |  | 51 | 51 | 51 | 51 | 48 | 31 | 8 | 1118400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 392064
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 300 | 300 | 310 | 300 | 325 | 300 | 310 | 320 | 300 | 300 | 320 | 320 | 310 | 300 | 300 | 300 | 310 |  | 310 | 325 | 305 | 320 | 285 | 290 | 290 | 7574000
| Bibiyana South 400 MW | 415 | 415 | 416 | 415 | 415 | 415 | 416 | 415 | 420 | 426 | 423 | 408 | 414 | 412 | 411 | 415 | 417 | 410 |  | 415 | 414 | 420 | 418 | 420 | 421 | 420 | 9937900
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 16 | 17 | 17 |  | 6 | 17 | 17 | 17 | 17 | 17 | 25 | 34 |  | 35 | 35 | 35 | 35 | 35 | 17 |  | 382211
59 | Tangail Palli Power Gen 22 MW |  |  |  |  | 0 | 1 | 13 | 18 | 19 | 14 | 18 | 16 | 13 | 14 | 13 | 18 | 19 | 24 |  | 24 | 24 | 24 | 24 | 24 | 20 | 19 | 336960
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 487008
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 444708
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501372
63 | Impoprt (Tripura) | 74 | 70 | 68 | 68 | 68 | 72 | 74 | 78 | 84 | 88 | 92 | 94 | 94 | 98 | 94 | 90 | 88 | 106 |  | 102 | 106 | 106 | 102 | 96 | 88 | 82 | 2097600
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 41 | 41 | 41 | 42 | 38 | 15 | 5 | 4 | 5 | 5 | 7 | 9 | 4 | 6 | 12 | 16 |  | 24 | 28 | 33 | 35 | 36 | 36 | 38 | 569760
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502524
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 31 | 32 | 32 |  |  | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 728300
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 479830
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 31 | 22 | 30 | 29 | 30 | 30 | 31 | 18 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 690660
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 518500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 829600
73 | Ghorashal 108MW PP (Regent) | 106 | 106 | 105 | 105 | 106 | 106 | 106 | 102 | 102 | 102 | 102 | 101 | 101 | 102 | 101 | 101 | 102 | 103 |  | 103 | 103 | 103 | 104 | 104 | 104 | 105 | 2436954
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 46 | 26 | 26 | 8 | 8 | 37 |  | 85 | 85 | 85 |  |  |  |  | 516600
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 90 | 90 | 126 | 130 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3398400
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 4 | 10 | 32 | 32 | 32 | 40 | 78 | 100 | 100 | 86 | 60 | 72 |  | 100 | 100 | 100 | 100 | 100 | 70 | 0 | 1180800
78 | Gazipur 52 MW PP | [12 empty] | 10 |  |  |  |  | 5 |  | 24 | [6 empty] | 39276
79 | Kodda 150MW PP | [11 empty] | 16 | 48 | 32 | 16 | 16 | 40 | 115 |  | 115 | 115 | 115 | 64 | 64 | 32 | 16 | 709920
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 8 | 23 | 81 | 81 | 48 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 48 | 81 | 73 | 48 |  |  | 648960
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 4 | [6 empty] | 7349
| Gazipur 100 MW PP | [11 empty] | 1 | 28 | 17 |  |  | 1 | 18 |  | 70 | 35 | 35 | 35 |  |  |  | 260676
| Kaptai 7 MW Solar PP | [8 empty] | 3 | 4 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 28971
| Jodiac Power | [6 empty] | 14 | 17 | 17 | 22 | 20 | 17 | 20 | 35 | 47 | 17 | 17 | 32 |  | 54 | 54 | 54 | 54 | 17 |  |  | 527270
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 48 | 15 | 0 |  |  |  | 2 | 36 | 48 | 55 | 64 | 64 | 70 | 81 | 90 | 100 | 99 | 100 |  | 100 | 101 | 101 | 101 | 100 | 100 | 85 | 1542744
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | 0 |  |  | 0 | 2 | 50 | 71 | 67 | 60 | 61 | 69 | 72 | 72 | 73 | 73 | 73 | 73 |  | 73 | 73 | 74 | 73 | 73 | 73 | 73 | 1364016
86 | Meghnaghat CCPP(Summit) | 255 | 265 | 285 | 260 | 295 | 260 | 285 | 260 | 245 | 265 | 285 | 305 | 265 | 280 | 260 | 250 | 240 | 300 |  | 270 | 275 | 270 | 270 | 270 | 270 | 250 | 6551069
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 33 | 41 | 77 | 93 | 93 | 70 | 50 | 50 |  | 83 | 93 | 93 | 63 | 55 |  |  | 929280
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 25 | 55 | 73 | 104 | 104 | 104 | 104 | 81 | 71 | 71 | 72 | 81 |  | 104 | 104 | 104 | 104 | 104 | 104 | 70 | 1595520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 3 | 10 | 10 | 24 | 70 | 30 | [5 empty] | 10 | 10 | 10 |  |  |  |  | 165360
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 1124712
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1257194
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 3 | 16 | 24 | 32 | 50 | 50 | 102 | 58 | 58 | 7 | 7 | 53 |  | 102 | 68 | 68 | 24 |  |  |  | 632160
95 | Patenga 50MW PP (Baraka) | 19 | 11 | 0 |  |  |  | 14 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 378720
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 5 | 16 | 17 | 30 | 33 | 32 | 18 | 16 | 20 |  | 44 | 44 | 44 |  |  |  |  | 292800
97 | katpotti 52 MW | [17 empty] | 1 |  | 9 | 18 | 18 | 18 |  |  |  | 69456
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 4 | 15 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 15 | 852068
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | [6 empty] | 420949
101 | Kushiara 163 MW CCPP (KP) | [23 empty] | 30 | 40 | 30 | 69627
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12800
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 10 | 17 | 17 | 35 | 35 | 35 | 53 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 724320
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 95 |  | 95 | [6 empty] | 114108
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 140 | 120 | 40 | 8 | 8 | 58 | 122 | 180 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4003200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 14 |  | 27 | [6 empty] | 29436
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 17 | 49 | 107 | 116 | 115 | 111 | 114 | 93 | 80 | 72 | 51 | 63 |  | 123 | 127 | 124 | 124 | 120 | 38 |  | 1553760
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 30 | 0 |  | 0 | 20 | 20 | 60 | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1777920
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 428160
117 | Ashuganj 150MW PP (Midland) | 90 | 10 | 10 | 10 | 10 | 16 | 90 | 90 | 97 | 107 | 90 | 90 | 50 | 50 | 50 | 50 | 50 | 54 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1527200
118 | Bibiyana-III 400 MW CCPP | 252 | 252 | 255 | 252 | 260 | 280 | 252 | 253 | 255 | 251 | 252 | 302 | 252 | 251 | 213 | 192 | 188 | 267 |  | 252 | 280 | 252 | 280 | 254 | 252 | 252 | 6113000
| Jamalpur 115 MW PP (United) | [7 empty] | 18 | 55 | 45 | 45 | 50 | 84 | 55 | 55 | 16 | 16 | 29 |  | 115 | 35 | 8 |  |  |  |  | 664800
| Anwara 300 MW PP (United) | 252 | 197 | 197 | 123 | 86 | 196 | 248 | 308 | 306 | 304 | 307 | 305 | 306 | 307 | 307 | 307 | 307 | 307 |  | 307 | 307 | 307 | 307 | 307 | 307 | 306 | 6526145
| Juldah unit-2 (Acorn) | 100 | 100 | 80 | 20 | 10 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2146560
| Anlima Energy Ltd. | [12 empty] | 7 | 17 |  |  |  | 6 |  | 17 | 17 | 17 |  |  |  |  | 85309
120 | Eastern Zone Total | 4486 | 4159 | 4022 | 3842 | 3789 | 4072 | 4512 | 5036 | 5441 | 5569 | 5649 | 5827 | 6014 | 5836 | 5601 | 5261 | 5203 | 5982 |  | 6519 | 6343 | 6260 | 6003 | 5697 | 5256 | 4926 | 127425317
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 32 | 32 | 32 | 32 | 37 | 71 | 49 |  |  |  | 73 |  | 99 | 115 | 115 | 115 | 40 |  |  | 721920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 35 | 90 | 90 | 90 | 95 | 90 | 90 | 90 | 95 | 70 | 70 | 80 |  | 95 | 105 | 105 | 105 | 105 | 105 | 17 | 1607040
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | [26 empty] | 0
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 32 | 32 | 32 | 32 | 32 |  |  | 126720
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 37 | 37 |  |  |  |  | 33 |  | 70 | 81 | 85 | 86 | 88 | 64 | 55 | 980310
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 20 | 20 | 19 | 19 | 19 | 20 | 19 | 10 | 15 | 14 | 16 | 18 | 19 | 20 | 17 | 17 | 16 | 23 |  | 26 | 26 | 26 | 26 | 26 | 24 | 23 | 467600
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 20 | [6 empty] | 28800
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  | 8 |  | 40 | 40 | 40 |  |  |  |  | 356625
143 | Gopalganj 100 MW Peaking PP | [12 empty] | 4 | 7 | [12 empty] | 6144
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 433 | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 435 | 434 |  | 424 | 424 | 424 | 424 | 424 | 425 | 425 | 10357818
147 | Bheramara 410 MW CCPP | 320 | 320 | 335 | 345 | 350 | 360 | 365 | 370 | 360 | 350 | 330 | 310 | 310 | 300 | 290 | 285 | 285 | 280 |  | 270 | 270 | 265 | 260 | 250 | 255 | 265 | 7591968
148 | Payra 1320 MW | 500 | 500 | 470 | 470 | 450 | 450 | 450 | 450 | 480 | 460 | 460 | 460 | 490 | 440 | 420 | 400 | 380 | 420 |  | 520 | 520 | 530 | 580 | 570 | 540 | 540 | 12433700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3677900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 50 | 50 |  |  |  |  | 93689
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 173 | 174 | 174 | 174 | 174 | 174 | 177 | 178 | 186 | 188 | 180 | 172 | 169 | 170 | 166 | 165 | 165 | 169 |  | 167 | 168 | 168 | 167 | 168 | 166 | 165 | 4345027
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 154 | 153 | 154 | 152 | 151 | 151 | 148 | 166 | 171 | 190 | 191 | 184 | 178 | 172 | 168 | 164 | 178 | 167 |  | 198 | 206 | 206 | 204 | 185 | 170 | 170 | 4358436
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 10 | 27 | 41 |  |  |  |  | 57599
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 513840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 210110
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 18 |  | 25 | 25 | 25 | 25 | 18 |  |  | 123470
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [20 empty] | 10 | 16 | 26 | 27 | 12 |  | 82373
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 16 | 52 | 44 | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 24 |  | 52 | 52 | 52 | 52 |  |  |  | 525600
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 15 | 101 |  | 102 | 102 | 102 | 102 | 102 | 61 | 25 | 596104
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [13 empty] | 1 | 24 | 71 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1011936
172 | Confidence Power Bogura Unit-1 113 MW |  |  |  |  | 0 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1346400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [5 empty] | 0 | 49 | 92 | 102 | 107 | 107 | 107 | 100 | 100 | 105 | 107 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1853760
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 30332
178
178