## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-10 | Wednesday
|  |  | Date (day): | 2021-02-10 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12455.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13820 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-09 | 2021-02-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 102 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 350 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 251 | 268 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 60 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 245 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 99 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 50 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 90 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 64 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 11 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 64 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | 33 kV feeder problem.
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 42 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 81 | 146 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 35 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 32 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 2389 | 2644 | 3545 | 3767 | 318 | 1808
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 19 | 19 |  | 31 | Engine problem
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 0 | 0 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 25 | 15 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 48 | 83 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 286 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 529 | 842 | 1243 | 1328 | 895 | 146
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 90 | 109 | 0 | 0 |  | 221 | Under S/D
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 365 | 365
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 26 | 26 | 45 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 46 | 80 | 80 |  | 83 | ST under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 34 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 93 | 106 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 5 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 70 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 19 | 0 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 883 | 989 | 1478 | 1740 | 745 | 310
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 90 | 107 | 150 | 150 | 52 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 24 | 82 | 82 |  | 13 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 184 | 200 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 103 | 65 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 20 | 25 | 25
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 494 | 438 | 645.6 | 594 | 52 | 13
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22 |  | 68 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 101 | 100 | 0 | 100 |  | 230 | GT-2 & ST under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 52 | 53 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 55 | 55 | 60 | 60 |  | 26 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 98 | 100 | 100 | 100
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | S/S maintenance work
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 422 | 426 | 400 | 400
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1286 | 1320 | 1268 | 1368 | 0 | 670
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 770 | 732 | 924
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 99 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 21 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 400 | 375 | 410
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 76 | 76 | 95 | 95 |  | 10 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1184 | 1390 | 1592 | 2105 | 0 | 88
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 85 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 470 | 480 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 560 | 602 | 1001 | 1001 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 12 | 25 | 25 |  | 25 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 8 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 197 | 200 | 220 |  |  | FGMO
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 163 | 200 | 220 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 400 | 400
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 101 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 40 | 113 | 35 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 586 | 876 | 1412 | 1654 | 431 | 25
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 93 | 105 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 247 | 255 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 8158 | 9356 | 12455.6 | 13820 | 2565 | 3471
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7816.1941 | 8964 | 11933.7322 | 13240.9662
| A. |  | 2021-02-09 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9356 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5854 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9356 | MW
| 3 | Day peak Generation : |  |  | 8158 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8964 | MW
| 4 | Evening peak Generation : |  |  | 9356 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 185.7334 | MKWHr | By Solar | 0.68575 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 98.0319 | MKWHr |  | By Oil: | 51.2219 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.3534 | MKWHr |  | By Hydro: | 1.692 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2565 | MW | Dhaka | 3080 | 3080 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3471 | MW | Chittagong | 961 | 961 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6036 | MW | Khulna | 1124 | 1124 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 812.39 | MMCFD |  |  | Rajshahi | 986 | 986 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 104085005.474 | ii) Oil : | Taka | 322602644.96 | Comilla | 738 | 738 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 71196873 | Total | Taka | 497884523.434 | Mymensingh | 820 | 820 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.738 | MKWHr. | Sylhet | 334 | 334 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -82 | MW (E to W) at | 19:00 | hrs | Barisal | 225 | 225 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -231 | MW at | 8:00 | hrs | Rangpur | 696 | 696 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.4° C |  |  | Total | 8964 | 8964 |  | 0
| B. |  | 2021-02-10 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 28.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13820 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
| 4 | Reserve(Generation end) |  |  |  | 4420 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 186.6068 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5888 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.648 | MKWHr. | ii) HVDC Flow at Peak Time |  | 770 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1005 | MKWHr. | iii) Maximum HVDC Flow : |  | 770 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.64 |  | (b) Today: | 94.52 |  | (c) Rule Curve: |  | 95.74
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 303 |  | 0 | 0 | 270 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 20 | 41 | 0 | 0 | 0 | 260 | 240 | 90 | 8 | 44 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 78 | 159 | 0 | 22 | 0 | 30 | 22 | 51 | 50 | 163 | 100 | 0 | 57 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 170 | 0 | 15 | 0 | 100 | 34 | 0 | 419 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 126 | 0 | 100 | 0 | 0 |  | 535 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 58 | 0 | 185 | 0 | 0 | 0 | 0 | 70 | 0 | 15 | 0 | 0 | 0 | 480 | 0 | 0 | 0 |  | 4585 | 2027 | 6612 | 2980 | 535 | 1160 | 1159 | 630 | 70 | 0 | 78 | 0 | 0 | 94.66
2:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 324 |  | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 41 | 0 | 0 | 0 | 260 | 240 | 92 | 8 | 48 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 76 | 162 | 0 | 22 | 0 | 30 | 22 | 51 | 50 | 140 | 99 | 0 | 57 | 0 | 0 | 0 | 0 | 9 | 275 | 16 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 90 | 0 | 100 | 0 | 0 |  | 535 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 36 | 0 | 186 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 0 |  | 4247 | 1954 | 6201 | 2984 | 535 | 1131 | 775 | 630 | 70 | 0 | 76 | 0 | 0 | 94.66
3:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 354 | 334 |  | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 41 | 0 | 0 | 0 | 260 | 240 | 95 | 8 | 44 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 74 | 160 | 0 | 22 | 0 | 30 | 22 | 51 | 50 | 140 | 100 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 72 | 0 | 100 | 0 | 0 |  | 534 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 35 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4085 | 1923 | 6008 | 2992 | 534 | 1146 | 572 | 620 | 70 | 0 | 74 | 0 | 0 | 94.65
4:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 349 | 353 |  | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 41 | 0 | 0 | 0 | 260 | 240 | 101 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 72 | 154 | 0 | 22 | 0 | 30 | 22 | 51 | 50 | 140 | 101 | 0 | 57 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 54 | 0 | 100 | 0 | 0 |  | 534 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 35 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 4008 | 1904 | 5912 | 2980 | 534 | 1163 | 494 | 599 | 70 | 0 | 72 | 0 | 0 | 94.65
5:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 349 | 363 |  | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 18 | 20 | 41 | 0 | 0 | 0 | 260 | 240 | 99 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 70 | 155 | 0 | 22 | 0 | 30 | 22 | 51 | 50 | 110 | 102 | 0 | 57 | 0 | 0 | 0 | 0 | 9 | 275 | 16 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 1 | 0 | 20 | 0 | 0 | 421 | 2 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 54 | 0 | 100 | 0 | 0 |  | 529 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 34 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 |  | 3991 | 1863 | 5854 | 2980 | 529 | 1137 | 508 | 560 | 70 | 0 | 70 | 0 | 0 | 94.64
6:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 378 | 363 |  | 0 | 0 | 260 | 0 | 10 | 13 | 0 | 0 | 0 | 4 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 0 | 0 | 0 | 260 | 240 | 95 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 66 | 163 | 7 | 22 | 0 | 30 | 22 | 51 | 50 | 110 | 101 | 0 | 54 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 60 | 0 | 18 | 0 | 30 | 0 | 0 | 421 | 8 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 54 | 0 | 100 | 0 | 0 |  | 611 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 34 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 380 | 0 | 0 | 0 |  | 4153 | 1913 | 6066 | 2978 | 611 | 1161 | 650 | 530 | 70 | 0 | 66 | 0 | 0 | 94.64
7:00 | 0 | 0 | 0 | 190 | 0 | 99 | 0 | 357 | 310 |  | 0 | 0 | 260 | 18 | 18 | 42 | 0 | 0 | 0 | 40 | 7 | 0 | 71 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 23 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 18 | 20 | 42 | 0 | 0 | 0 | 260 | 240 | 87 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 68 | 149 | 36 | 22 | 0 | 30 | 22 | 14 | 50 | 110 | 101 | 0 | 20 | 0 | 0 | 0 | 0 | 9 | 230 | 16 | 11 | 0 | 60 | 0 | 0 | 150 | 0 | 54 | 1 | 60 | 0 | 0 | 375 | 8 | 7 | 5 | 0 | 52 | 44 | 0 | 0 | 20 | 70 | 0 | 53 | 2 | 126 | 8 | 100 | 0 | 1 |  | 719 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 34 | 0 | 150 | 0 | 0 | 53 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 350 | 0 | 0 | 0 |  | 4574 | 2107 | 6681 | 2830 | 719 | 962 | 1477 | 500 | 70 | 51 | 68 | 4 | 0 | 94.63
8:00 | 0 | 0 | 0 | 190 | 0 | 99 | 0 | 370 | 329 |  | 0 | 0 | 255 | 16 | 50 | 55 | 0 | 0 | 0 | 40 | 7 | 0 | 72 | 0 | 0 | 0 | 17 | 11 | 28 | 22 | 25 | 29 | 15 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 10 | 12 | 19 | 20 | 12 | 0 | 0 | 0 | 260 | 240 | 90 | 8 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 78 | 130 | 41 | 22 | 1 | 30 | 22 | 42 | 50 | 163 | 102 | 0 | 52 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 125 | 0 | 0 | 180 | 0 | 80 | 0 | 90 | 7 | 0 | 421 | 9 | 17 | 17 | 1 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 59 | 13 | 126 | 19 | 100 | 0 | 9 |  | 718 | 0 | 375 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 33 | 0 | 158 | 0 | 0 | 70 | 0 | 0 | 0 | 102 | 0 | 1 | 0 | 410 | 0 | 0 | 0 |  | 5150 | 2374 | 7524 | 2990 | 718 | 1133 | 1900 | 559 | 70 | 51 | 78 | 25 | 0 | 94.63
9:00 | 0 | 0 | 0 | 190 | 0 | 99 | 0 | 356 | 290 |  | 0 | 0 | 265 | 16 | 75 | 55 | 0 | 0 | 0 | 40 | 7 | 0 | 72 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 18 | 19 | 20 | 3 | 0 | 0 | 0 | 260 | 240 | 87 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 82 | 111 | 64 | 22 | 1 | 30 | 22 | 42 | 50 | 130 | 101 | 0 | 52 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 81 | 0 | 100 | 17 | 0 | 423 | 24 | 17 | 17 | 3 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 26 | 126 | 46 | 100 | 0 | 18 |  | 719 | 0 | 375 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 53 | 0 | 156 | 0 | 0 | 70 | 0 | 43 | 0 | 94 | 0 | 2 | 0 | 470 | 0 | 0 | 0 |  | 5426 | 2466 | 7892 | 2955 | 719 | 1071 | 2301 | 619 | 70 | 25 | 82 | 50 | 0 | 94.62
10:00 | 0 | 0 | 0 | 190 | 0 | 99 | 0 | 355 | 290 |  | 0 | 0 | 285 | 16 | 99 | 55 | 0 | 0 | 0 | 40 | 7 | 16 | 74 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 12 | 19 | 20 | 3 | 0 | 0 | 0 | 260 | 240 | 87 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 87 | 91 | 24 | 22 | 2 | 30 | 22 | 42 | 50 | 130 | 101 | 0 | 52 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 281 | 0 | 0 | 193 | 0 | 81 | 0 | 100 | 17 | 0 | 425 | 65 | 17 | 17 | 4 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 37 | 126 | 53 | 100 | 1 | 26 |  | 719 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 53 | 0 | 163 | 0 | 0 | 70 | 0 | 50 | 0 | 84 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5479 | 2416 | 7895 | 2910 | 719 | 1059 | 2346 | 619 | 70 | 16 | 87 | 69 | 0 | 94.62
11:00 | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 354 | 260 |  | 0 | 0 | 285 | 16 | 99 | 55 | 0 | 0 | 0 | 40 | 7 | 16 | 73 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 13 | 19 | 20 | 4 | 0 | 0 | 0 | 260 | 240 | 95 | 8 | 51 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 86 | 91 | 24 | 22 | 2 | 30 | 22 | 46 | 50 | 110 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 286 | 0 | 0 | 194 | 0 | 81 | 14 | 100 | 17 | 0 | 427 | 103 | 17 | 17 | 4 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 46 | 126 | 17 | 80 | 13 | 30 |  | 719 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 55 | 0 | 162 | 0 | 0 | 76 | 0 | 70 | 0 | 91 | 0 | 5 | 35 | 470 | 0 | 0 | 0 |  | 5500 | 2480 | 7980 | 2881 | 719 | 1035 | 2452 | 620 | 70 | 16 | 86 | 101 | 0 | 94.61
12:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 367 | 251 |  | 0 | 0 | 295 | 16 | 99 | 55 | 0 | 0 | 0 | 40 | 7 | 16 | 70 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 10 | 48 | 19 | 20 | 4 | 0 | 0 | 0 | 260 | 240 | 90 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 93 | 90 | 24 | 22 | 2 | 30 | 22 | 52 | 50 | 110 | 101 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 286 | 0 | 0 | 184 | 0 | 81 | 15 | 90 | 17 | 0 | 422 | 103 | 17 | 17 | 5 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 48 | 126 | 17 | 98 | 19 | 32 |  | 719 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 77 | 0 | 177 | 0 | 0 | 76 | 0 | 113 | 0 | 93 | 0 | 5 | 40 | 470 | 0 | 0 | 0 |  | 5581 | 2577 | 8158 | 2926 | 719 | 1061 | 2547 | 619 | 70 | 16 | 93 | 107 | 0 | 94.61
13:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 366 | 257 |  | 0 | 0 | 255 | 40 | 99 | 55 | 0 | 0 | 0 | 60 | 24 | 32 | 56 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 22 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 66 | 15 | 20 | 6 | 0 | 0 | 0 | 260 | 240 | 76 | 8 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 93 | 90 | 24 | 20 | 2 | 30 | 22 | 52 | 50 | 130 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 286 | 0 | 0 | 193 | 0 | 121 | 15 | 100 | 30 | 0 | 430 | 85 | 17 | 17 | 4 | 51 | 54 | 0 | 0 | 46 | 100 | 0 | 104 | 47 | 126 | 17 | 100 | 20 | 33 |  | 719 | 0 | 280 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 65 | 0 | 210 | 0 | 0 | 76 | 0 | 113 | 0 | 85 | 0 | 5 | 50 | 470 | 0 | 0 | 0 |  | 5717 | 2548 | 8265 | 2880 | 719 | 1060 | 2685 | 620 | 70 | 32 | 93 | 106 |  | 94.6
14:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 353 | 274 |  | 0 | 0 | 240 | 18 | 99 | 55 | 0 | 0 | 0 | 64 | 40 | 32 | 49 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 59 | 15 | 20 | 4 | 0 | 0 | 0 | 260 | 240 | 79 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 98 | 88 | 24 | 20 | 2 | 30 | 22 | 52 | 50 | 110 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 13 | 50 | 34 | 0 | 400 | 85 | 17 | 17 | 4 | 52 | 54 | 0 | 0 | 46 | 100 | 0 | 104 | 42 | 126 | 17 | 100 | 4 | 29 |  | 719 | 0 | 250 | 0 | 49 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 65 | 0 | 159 | 0 | 0 | 76 | 0 | 113 | 0 | 83 | 0 | 5 | 55 | 470 | 0 | 0 | 0 |  | 5584 | 2430 | 8014 | 2755 | 719 | 1044 | 2579 | 620 | 70 | 34 | 98 | 95 | 0 | 94.6
15:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 359 | 272 |  | 0 | 0 | 250 | 16 | 99 | 55 | 0 | 0 | 0 | 64 | 40 | 0 | 50 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 51 | 19 | 20 | 3 | 0 | 0 | 0 | 275 | 240 | 95 | 8 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 95 | 104 | 24 | 22 | 2 | 30 | 22 | 52 | 50 | 110 | 102 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 109 | 10 | 50 | 34 | 0 | 385 | 55 | 0 | 17 | 3 | 52 | 54 | 0 | 0 | 46 | 100 | 0 | 54 | 33 | 126 | 17 | 100 | 2 | 20 |  | 719 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 61 | 0 | 159 | 0 | 0 | 76 | 0 | 113 | 0 | 70 | 0 | 4 | 55 | 450 | 0 | 0 | 0 |  | 5471 | 2365 | 7836 | 2816 | 719 | 1046 | 2413 | 600 | 70 | 5 | 95 | 72 | 0 | 94.59
16:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 358 | 272 |  | 0 | 0 | 260 | 16 | 99 | 55 | 0 | 0 | 0 | 64 | 7 | 0 | 49 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 51 | 19 | 20 | 4 | 0 | 0 | 0 | 275 | 240 | 101 | 8 | 67 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 25 | 22 | 90 | 102 | 24 | 22 | 1 | 30 | 22 | 52 | 50 | 110 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 73 | 6 | 50 | 34 | 0 | 353 | 16 | 0 | 0 | 2 | 52 | 54 | 0 | 0 | 46 | 100 | 0 | 53 | 19 | 126 | 0 | 100 | 3 | 13 |  | 718 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 35 | 0 | 158 | 0 | 0 | 35 | 0 | 113 | 0 | 70 | 0 | 3 | 111 | 450 | 0 | 0 | 0 |  | 5313 | 2320 | 7633 | 2798 | 718 | 1030 | 2274 | 600 | 70 | 9 | 90 | 44 | 0 | 94.59
17:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 355 | 268 |  | 0 | 0 | 270 | 16 | 99 | 55 | 0 | 0 | 0 | 64 | 7 | 0 | 53 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 51 | 14 | 20 | 9 | 0 | 0 | 0 | 275 | 240 | 99 | 8 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 89 | 104 | 24 | 22 | 0 | 30 | 22 | 52 | 50 | 110 | 101 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 66 | 6 | 50 | 34 | 0 | 352 | 16 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 46 | 100 | 0 | 53 | 5 | 126 | 0 | 100 | 0 | 4 |  | 719 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 7 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 34 | 0 | 157 | 0 | 0 | 35 | 0 | 113 | 0 | 70 | 0 | 1 | 113 | 380 | 0 | 0 | 0 |  | 5231 | 2261 | 7492 | 2779 | 719 | 1021 | 2247 | 530 | 70 | 21 | 89 | 16 | 0 | 94.58
18:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 339 | 268 |  | 0 | 0 | 295 | 32 | 100 | 55 | 0 | 0 | 0 | 75 | 16 | 32 | 51 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 85 | 10 | 59 | 17 | 20 | 13 | 0 | 0 | 0 | 275 | 240 | 100 | 8 | 51 | 10 | 0 | 0 | 0 | 0 | 38 | 0 | 21 | 11 | 33 | 21 | 112 | 104 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 103 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 288 | 0 | 0 | 200 | 0 | 73 | 0 | 70 | 34 | 0 | 347 | 19 | 2 | 0 | 0 | 248 | 54 | 0 | 0 | 46 | 100 | 0 | 80 | 0 | 144 | 0 | 100 | 5 | 0 |  | 770 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 8 | 52 | 13 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 35 | 0 | 158 | 0 | 0 | 76 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 380 | 0 | 0 | 0 |  | 5732 | 2606 | 8338 | 2831 | 770 | 1022 | 2760 | 530 | 70 | 243 | 112 | 0 | 0 | 94.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 268 |  | 0 | 0 | 245 | 60 | 100 | 55 | 0 | 0 | 0 | 90 | 64 | 64 | 50 | 0 | 0 | 11 | 54 | 55 | 35 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 85 | 0 | 83 | 19 | 20 | 25 | 0 | 0 | 0 | 275 | 240 | 109 | 8 | 46 | 10 | 0 | 0 | 0 | 0 | 0 | 5 | 21 | 11 | 33 | 21 | 106 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 0 | 100 | 34 | 0 | 426 | 65 | 35 | 0 | 0 | 286 | 54 | 0 | 0 | 70 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 0 | 21 | 24 | 0 | 21 | 16 | 0 | 0 | 0 | 50 | 0 | 101 | 12 | 0 | 8 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 85 | 0 | 163 | 0 | 0 | 76 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 480 | 0 | 0 | 0 |  | 6233 | 3123 | 9356 | 3053 | 770 | 1146 | 3218 | 630 | 70 | 363 | 106 | 0 | 0 | 94.56
19:30 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 357 | 263 |  | 0 | 0 | 285 | 60 | 101 | 55 | 0 | 0 | 0 | 100 | 72 | 64 | 50 | 0 | 0 | 12 | 54 | 55 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 0 | 45 | 19 | 20 | 25 | 0 | 0 | 0 | 275 | 240 | 102 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 108 | 106 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 315 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 34 | 0 | 427 | 65 | 0 | 0 | 0 | 286 | 54 | 0 | 0 | 74 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 101 | 12 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 84 | 0 | 164 | 0 | 0 | 76 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6237 | 3059 | 9296 | 3072 | 770 | 1169 | 3186 | 650 | 70 | 271 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 356 | 253 |  | 0 | 0 | 240 | 65 | 101 | 55 | 0 | 0 | 0 | 100 | 72 | 64 | 50 | 0 | 0 | 12 | 54 | 55 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 45 | 19 | 20 | 30 | 0 | 0 | 0 | 275 | 240 | 102 | 8 | 46 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 106 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 34 | 0 | 420 | 65 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 74 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 390 | 0 | 99 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 101 | 12 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 84 | 0 | 164 | 0 | 0 | 76 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6186 | 3042 | 9228 | 3044 | 770 | 1150 | 3167 | 650 | 70 | 271 | 106 | 0 | 0 | 94.57
21:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 351 | 254 |  | 0 | 0 | 260 | 65 | 80 | 55 | 0 | 0 | 0 | 100 | 16 | 64 | 50 | 0 | 0 | 12 | 35 | 55 | 35 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 19 | 20 | 30 | 0 | 0 | 0 | 275 | 240 | 102 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 106 | 108 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 101 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 34 | 0 | 418 | 35 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 74 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 101 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 88 | 0 | 163 | 0 | 0 | 76 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 5981 | 2919 | 8900 | 3020 | 770 | 1135 | 2950 | 650 | 70 | 199 | 106 | 0 | 0 | 94.56
22:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 351 | 253 |  | 0 | 0 | 245 | 50 | 80 | 55 | 0 | 0 | 0 | 60 | 0 | 64 | 49 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 32 | 25 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 20 | 37 | 0 | 0 | 0 | 275 | 240 | 107 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 109 | 35 | 22 | 0 | 30 | 22 | 53 | 50 | 130 | 101 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 34 | 0 | 380 | 8 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 74 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 101 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 63 | 0 | 158 | 0 | 0 | 53 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 5675 | 2784 | 8459 | 2952 | 770 | 1083 | 2651 | 650 | 70 | 183 | 100 | 0 | 0 | 94.56
23:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 261 |  | 0 | 0 | 275 | 16 | 80 | 15 | 0 | 0 | 0 | 7 | 0 | 32 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 0 | 0 | 0 | 275 | 240 | 115 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 92 | 110 | 8 | 22 | 0 | 30 | 22 | 53 | 50 | 130 | 102 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 55 | 0 | 100 | 34 | 0 | 381 | 0 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 36 | 100 | 0 | 70 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 66 | 0 | 152 | 0 | 0 | 17 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 5087 | 2685 | 7772 | 2958 | 770 | 1095 | 1986 | 650 | 70 | 151 | 92 | 0 | 0 | 94.55
24:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 269 |  | 0 | 0 | 245 | 16 | 80 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 0 | 0 | 0 | 275 | 240 | 121 | 8 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 88 | 108 | 0 | 22 | 0 | 30 | 22 | 52 | 50 | 130 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 25 | 0 | 100 | 34 | 0 | 380 | 0 | 0 | 0 | 0 | 52 | 17 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 63 | 0 | 155 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 50 | 500 | 0 | 0 | 0 |  | 4749 | 2435 | 7184 | 2949 | 770 | 1103 | 1499 | 649 | 70 | 56 | 88 | 0 | 0 | 94.55
KWH | 0 | 0 | 0 | 4536000 | 0 | 2388863 | 0 | 8679420 | 6916000 |  | 0 | 0 | 6423273 | 535680 | 1685664 | 950440 | 0 | 0 | 0 | 1109760 | 396288 | 446400 | 1244660 | 0 | 0 | 51408 | 529920 | 668121 | 521678 | 482256 | 600000 | 684360 | 462600 | 808100 | 0 | 0 | 0 | 1692000 | 0 | 0 | 225918 | 0 | 0 | 0 | 0 |  | 472320 | 0 | 223301 | 150840 | 586560 | 446400 | 480768 | 547200 | 0 | 0 | 0 | 6750000 | 5869000 | 2333000 | 217454 | 1206430 | 228096 | 0 | 0 | 0 | 0 | 34208 | 6173 | 488736 | 257040 | 646800 | 501280 | 2100480 | 2773720 | 514560 | 502128 | 14750 | 714000 | 524760 | 1179000 | 1187352 | 3375981 | 2354000 | 0 | 1297920 | 0 | 0 | 0 | 0 | 204120 | 7160500 | 385216 | 259000 | 0 | 5171234 | 0 | 0 | 4068000 | 0 | 1743840 | 75870 | 1806720 | 542880 | 0 | 9753000 | 818400 | 177564 | 160581 | 29760 | 2443855 | 960258 | 0 | 0 | 887880 | 2095680 | 0 | 1581120 | 315440 | 2916000 | 278509 | 2410000 | 69840 | 218893 |  | 16648000 | 0 | 8158176 | 0 | 672000 | 0 | 0 | 0 | 0 | 142336 | 24000 | 0 | 364000 | 96960 | 0 | 0 | 0 | 44304 | 0 | 689296 | 185820 | 0 | 8682 | 593760 | 67511 | 498480 | 0 | 223452 | 0 | 0 | 3684900 | 0 | 0 | 0 | 0 | 4064618 | 0 | 1298622 | 0 | 4260409 | 0 | 0 | 1133280 | 0 | 1861248 | 0 | 1576320 | 0 | 31036 | 1180416 | 11668500 | 0 | 0 | 0 |  | 126557226 | 59176126 | 185733352 | 71396365 | 16648000 | 26635492 | 49565828 | 15353400 | 1692000 | 1656038 | 2100480 | 685749 | 0
Fuel Cost | 0 | 0 | 0 | 6667920 | 0 | 3153299.16 | 0 | 8766214.2 | 7123480 |  | 0 | 0 | 7129833.03 | 4065811.2 | 11614224.96 | 8040722.4 | 0 | 0 | 0 | 8356492.8 | 3614146.56 | 4392576 | 11475765.2 | 0 | 0 | 467298.72 | 3868416 | 5164575.33 | 5143745.08 | 361692 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 456840 | 0 | 0 | 2098778.22 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2166019.7 | 1440522 | 5103072 | 3535488 | 605767.68 | 1625184 | 0 | 0 | 0 | 4995000 | 5869000 | 2146360 | 280515.66 | 1387394.5 | 257748.48 | 0 | 0 | 0 | 0 | 345500.8 | 58952.15 | 620694.72 | 192780 | 1131900 | 375960 | 15753600 | 2940143.2 | 4672204.8 | 637702.56 | 235115 | 1170960 | 839616 | 2098620 | 1852269.12 | 3848618.34 | 2448160 | 0 | 2479027.2 | 0 | 0 | 0 | 0 | 416404.8 | 7232105 | 288912 | 196840 | 0 | 39094529.04 | 0 | 0 | 21153600 | 0 | 17159385.6 | 886920.3 | 14724768 | 5890248 | 0 | 9070290 | 7463808 | 1677979.8 | 1398660.51 | 0 | 18475543.8 | 8363847.18 | 0 | 0 | 7609131.6 | 13957228.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95892480 | 0 | 8566084.8 | 0 | 5281920 | 0 | 0 | 0 | 0 | 1491681.28 | 250080 | 0 | 564200 | 946329.6 | 0 | 0 | 0 | 435951.36 | 0 | 6100269.6 | 1430814 | 0 | 84128.58 | 5753534.4 | 654856.7 | 957081.6 | 0 | 169153.164 | 0 | 0 | 19972158 | 0 | 0 | 0 | 0 | 5365295.76 | 0 | 1947933 | 0 | 4984678.53 | 0 | 0 | 11831443.2 | 0 | 17663243.52 | 0 | 12232243.2 | 0 | 342947.8 | 8723274.24 | 51224715 | 0 | 0 | 0 |  | 348585929.2 | 262866497.334 | 611452426.534 | 70506267.594 | 95892480 | 33578737.88 | 306931660.94 | 71196873 | 456840 | 15670984.02 | 15753600 | 1464983.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 367 | 251 |  | 0 | 0 | 295 | 16 | 99 | 55 | 0 | 0 | 0 | 40 | 7 | 16 | 70 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 32 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 10 | 48 | 19 | 20 | 4 | 0 | 0 | 0 | 260 | 240 | 90 | 8 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 93 | 90 | 24 | 22 | 2 | 30 | 22 | 52 | 50 | 110 | 101 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 286 | 0 | 0 | 184 | 0 | 81 | 15 | 90 | 17 | 0 | 422 | 103 | 17 | 17 | 5 | 52 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 48 | 126 | 17 | 98 | 19 | 32 |  | 719 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 77 | 0 | 177 | 0 | 0 | 76 | 0 | 113 | 0 | 93 | 0 | 5 | 40 | 470 | 0 | 0 | 0 |  | 8158 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 350 | 268 | 0 | 0 | 0 | 245 | 60 | 100 | 55 | 0 | 0 | 0 | 90 | 64 | 64 | 50 | 0 | 0 | 11 | 54 | 55 | 35 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 85 | 0 | 83 | 19 | 20 | 25 | 0 | 0 | 0 | 275 | 240 | 109 | 8 | 46 | 10 | 0 | 0 | 0 | 0 | 0 | 5 | 21 | 11 | 33 | 21 | 106 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 0 | 100 | 34 | 0 | 426 | 65 | 35 | 0 | 0 | 286 | 54 | 0 | 0 | 70 | 100 | 0 | 104 | 0 | 144 | 0 | 100 | 0 | 0 |  | 770 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 0 | 21 | 24 | 0 | 21 | 16 | 0 | 0 | 0 | 50 | 0 | 101 | 12 | 0 | 8 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 85 | 0 | 163 | 0 | 0 | 76 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 480 | 0 | 0 | 0 |  | 9356 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 25 | 0 | 0 | 0 | 365 | 300 | 0 | 8 | 80 | 26 | 0 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 150 | 82 | 22 | 0 | 30 | 22 | 51 | 44 | 163 | 100 | 0 | 60 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 144 | 116 | 100 |  |  |  | 924 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 15 | 0 | 0 | 0 | 365 | 300 | 0 | 8 | 80 | 26 | 0 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 150 | 82 | 22 | 1.6 | 30 | 22 | 51 | 44 | 163 | 0 | 0 | 60 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 0 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 50 | 144 | 116 | 100 |  | 30 |  | 732 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 95 | 100 | 113 | 100 | 113 | 0 | 8 | 35 | 620 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 384 | 329 | 0 | 0 | 0 | 260 | 9 | 48 | 32 | 0 | 0 | 0 | 20 | 3 | 16 | 35 | 0 | 0 | 0 | 17 | 0 | 25 | 22 | 25 | 27 | 20 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 19 | 20 | 15 | 0 | 0 | 0 | 365 | 295 | 0 | 8 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 10 | 80 | 111 | 24 | 22 | 1 | 30 | 22 | 53 | 50 | 130 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 180 | 0 | 0 | 197 | 0 | 37 | 0 | 100 | 17 | 0 | 422 | 4 | 0 | 0 | 1 | 52 | 29 | 0 | 0 | 16 | 100 | 0 | 80 | 14 | 112 | 0 | 100 | 0 | 7 | 0 | 719 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 83 | 0 | 205 | 0 | 62 | 70 | 0 | 55 | 0 | 97 | 0 | 1 | 35 | 450 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5854 | 5:00
| Highest Generation |  | 9356 | 19:00
| Day Peak Generation |  | 8158 | 12:00
| Evening Peak Generation |  | 9356 | 19:00
| HVDC Max Flow |  | 770 | 18:00
| HVDC EvPeak Flow |  | 770 | 19:00
| Load factor L.F |  | 82.72%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8158 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5888 | MW
Evening Peak Generation : |  | 9356 | MW Hour : | 19:00 | Available Max Generation : |  | 13820 | MW
E.P. Demand (at gen end) : |  | 9356 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 9356 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4420 | MW
Total Gen. (MKWH) : |  | 185.7334 | System Load Factor : | 82.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -231 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-10
Actual : | 94.52 | Ft.(MSL) , | Rule curve : | 95.74 | Ft.( MSL )
Gas Consumed : | Total = | 812.39 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104085005.474
: |  | Coal : | 71196873 | Oil : | 322602644.96 | Total : | 497884523.434
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3360.8602 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1138.6221 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1019.4092 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 920.853 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 832.31 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 671.634 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 381.0219 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 173.0726 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 517.9713 |  |  | 0 | 0%
Total | 0 |  | 9015.7544 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj 225 MW
2) Baghabari-71 &100 MW
3) Ashuganj-4,5
4) Shahjibazar 330 MW GT-2 & STG
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari 132/33 kV T-1 transformer was under shut down from 09:11 to 16:34 for A/M.
b) Savar 132/33 kV T-2 transformers was under shut down from 11:25 to 19:03 for D/W.
c) Savar 132/33 kV T-3 transformers was under shut down from 11:24 to 19:03 for A/M.
d) Ramganj 132/33 kV T-2 transformers was under shut down from 09:27 to 19:41 for A/M.
e) Kodda-Rajendrapur 132 kV Ckt was under shut down from 09:16 to 16:39 for C/M.
f) Fatulla-Haripur132 kV Ckt was under shut down from 09:12 to 12:43 for A/M.
g) Hathazari-Kulshi 132 kV Ckt was under shut down from 09:05 to 15:38 for A/M.
h) Choumohani-Ramganj 132 kV Ckt-1 was under shut down from 09:38 to 20:01 for A/M.
i) Madaripur-Gopalganj 132 kV Ckt-3 was under shut down from 08:42 to 11:07 for A/M.
j) Baghabari-Shahjadpur 132 kV Ckt-1 was under shut down from 08:34 to 17:10 for D/W.
k) Sikalbaha(N)-Sikalbaha(O) 230 kV Ckt-1 was under shut down from 11:52 to 15:27 for D/W.
l) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 09:27 to 16:56 for A/M.
m) Hasnabad-Keraniganj 230 kV Ckt-1 was under shut down from 10:44 to 18:23 for A/M.
n) Halishahar 132/33 kV T-1 transformers was under shut down from 10:11 to 11:58 for A/M.
o) Halishahar 132/33 kV T-2 transformers was under shut down from 12:22 to 15:38 for A/M.
p) Nawabganj 132/33 kV T-1 transformers was under shut down from 12:49 to 15:34 for A/M.
q) Mahastanghor-Bogura 132 kV Ckt-1 was under shut down from 13:23 to 14:19 for A/M.
r) Siddhirganj-Maniknagar 230 kV Ckt-1 & 2 tripped at 12:30 from both end showing Dist. Z1,Z2,Z3 |  |  |  |  | About 145 MW power interruption occurred under Siddhirganj S/S
Diff, relays . |  |  |  |  | areas from 12:30 to 13:02
s) Mahastanghor-Bogura 132 kV Ckt-2 was under shut down from 14:20 to 15:08 for Protection test.
t) Bogura-Naogaon 132 kV Ckt was under shut down from 15:19 to 17:27 for Protection test.
u) Sikalbaha(N)-Sikalbaha(O) 230 kV Ckt-2 was under shut down from 15:43 to 17:29 for A/M.
v) Daudkandi 132/33 kV T-3 transformer tripped at 16:58 showing Diff relay at 33 kV end.
w) Bogura 132/33 kV T-2 transformer was switched on at 17:42.
x) Mirpur-Aminbazar 132 kV Ckt-2 was switched on at 22:41.
y) Tongi 132/33 kV T1 & T2 transformers tripped at 01:41(10/02/2021) showing O/C,E/F, relays & |  |  |  |  | About 32 MW power interruption occurred under Tongi S/S areas
Dokkhinkhan 33 kV feeder fault and were switched on at 01:56(10/02/2021). |  |  |  |  | from 01:41 to 01;56(10/02/2021).
z) Sirajganj unit-4 400 MW GT was synchronized at 00:07(10/02/2021).
aa) Shahjibazar 330 MW GT1 was shut down at 05:38(10/02/2021) due to ST problem.
ab) Ashuganj 225 MW GT was shut down at 06:28(10/02/2021) due maintenance work.
ac) Sikalbaha-TK chemical 132 kV Ckt was shut down at 07:31(10/02/2021) for A/M.
ad) Sylhet-Chattak 132 kV Ckt-2 was shut down at 07:17(10/02/2021) for A/M.
ae) Sirajganj unit-4 400 MW ST was synchronized at 03:24(10/02/2021).
af) Sherpur-UMPL 132 kV Ckt-1 was shut down from 07:27 to 09:31(10/02/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4536000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2388863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8679420 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 268 | 6916000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 60 | 535680 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 245 | 6423273 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1685664
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 950440
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 1244660 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 482256
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1109760 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 396288 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 11 | 51408 | High Voltage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 529920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 446400 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 668121
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 521678 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1284360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 462600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 808100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5171234
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 146 | 1743840
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 35 | 177564 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1581120
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2916000 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 218893
| Dhaka area Total |  |  |  | 5972 | 2644 | 51929542
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 225918 | Reserve.
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 75870
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 446400 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1692000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 160581 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 223301
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 150840 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1806720
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 480768
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 547200
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 83 | 586560 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29760
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 286 | 2443855 | Engine problem
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 960258
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2095680
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 278509 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 842 | 12204220
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 109 | 2333000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6750000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5869000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 228096 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | S/S maint. at Midland end
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | S/S maint. at Midland end
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | S/S maint. at Midland end
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 34208 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 46 | 1206430 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 542880 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 488736
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2100480
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 646800
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 5 | 6173 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 501280
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 887880 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 69840
| Cumilla Area Total |  |  |  | 2980 | 989 | 22139297
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2773720 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502128
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 514560 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4068000 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 65 | 818400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 315440
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 20 | 472320
| Mymensingh Area Total |  |  |  | 709 | 438 | 9479318
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 714000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 524760 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3375981
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2354000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1179000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1187352
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 259000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 55 | 1297920 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 100 | 2410000 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 385216 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7160500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 426 | 9753000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 204120
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0
| Sylhet Area Total |  |  |  | 1988 | 1320 | 30804849
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 770 | 16648000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 672000 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 21 | 142336 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 8158176
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 24000 | Low demand
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 76 | 1133280 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1390 | 26777792
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 96960 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 364000 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 85 | 1298622
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 11668500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 602 | 13428082
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 44304
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 185820 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 8 | 8682 | Low demand
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4064618 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 163 | 4260409 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 67511
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 498480
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223452
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 593760
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 689296
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1861248
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1180416
| Rajshahi Area Total |  |  |  | 2183 | 876 | 13677996
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3684900 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1576320
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31036
| Rangpur Area Total |  |  |  | 605 | 255 | 5292256
| Total |  |  |  | 20929 | 9356 | 185733352
| Eastern Grid Total |  |  |  | 14031 | 6233 | 126557226
| Western Grid Total |  |  |  | 6898 | 3123 | 59176126
| National Grid Total |  |  |  | 20929 | 9356 | 185733352
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-09
(a) ENTIRE EASTERN GRID : |  | 5933 | MW | (b) ENTIRE WESTERN GRID : |  | 3031 | MW
i) Dhaka area |  | 3080 | MW | i) Khulna area |  | 1124 | MW
ii) Chittagong area |  | 961 | MW | ii) Rajshahi area |  | 986 | MW
iii) Comilla area |  | 738 | MW | iii) Barisal area |  | 225 | MW
iv) Mymensingh area |  | 820 | MW | iv) Rangpur area |  | 696 | MW
v) Sylhet area |  | 334 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8964 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 96 | 12:00 | Sherpur | 112 | 18:30 | Jhenida | 86 | 18:30
Munsiganj | 86 | 20:00 | Srimongal | 39 | 18:30 | Bottail | 110 | 19:00
Sonargaon | 69 | 0:00 | Shahjibazar | 78 | 18:00 | G.K Project | 31 | 19:00
Shyampur | 154 | 12:00 | Fenchuganj | 26 | 18:30 | Faridpur | 132 | 19:30
Bhulta | 149 | 19:30 | Kulawara | 29 | 18:30 | Madaripur | 59 | 19:30
Madanganj | 57 | 13:00 | Sylhet | 85 | 18:00 | Sariatpur | 42 | 20:00
Shitalakhya | 105 | 17:00 | Chatak | 20 | 19:00 | Gopalganj | 60 | 19:00
Rahim steel | 20 | 7:00 | Sunamganj | 30 | 19:00 | Bagerhat | 83 | 18:30
Matuail | 90 | 14:00 | Biani Bazar | 40 | 18:30 | Mongla | 40 | 18:30
Ghorasal | 64 | 18:30 | Comilla (S) | 112 | 18:00 | Satkhira | 72 | 19:00
Narsingdi | 128 | 20:00 | Comilla(N) | 85 | 18:30 | Gallamari | 21 | 13:00
Haripur (SBU) | 105 | 18:30 | Chandpur | 46 | 18:30 | Magura | 40 | 18:30
Ullon | 65 | 14:00 | Feni | 76 | 18:30 | Norail | 24 | 18:30
Hasnabad | 101 | 16:00 | Chowmuhani | 98 | 20:00 | Chuadanga | 65 | 18:30
Magbazar | 55 | 19:00 | Ashuganj | 40 | 21:00 | Borguna | 12 | 20:00
Maniknagar | 62 | 12:00 | Daudkandi | 76 | 10:00 | Barisal(N) | 28 | 20:00
Bangabhaban | 15 | 11:00 | B.Baria | 102 | 18:30 | Barisal (S) | 76 | 19:30
Narinda | 68 | 12:00 | Ramganj | 54 | 20:00 | Patuakhali | 70 | 20:00
Dhanmondi | 109 | 14:00 | Chaddagram | 26 | 18:30 | Bhandaria | 36 | 21:00
Lalbag | 65 | 16:00 | PHP | 10 | 13:00 | Borhan Uddin | 25 | 19:30
Madartek | 55 | 18:30 | Kochua | 45 | 18:00 | Ishurdi | 45 | 18:00
Dhaka University |  |  | Madunaghat | 42 | 20:00 | Ruppur Paromanobik | 2 | 1:00
Aftabnagar | 15 | 13:00 | Hathazari | 64 | 19:00 | Natore | 103 | 18:30
Fatullah | 43 | 10:00 | Khulshi | 165 | 19:30 | Bogra | 119 | 19:30
Mirpur | 72 | 18:30 | Halishahar | 89 | 19:00 | Noagaon | 89 | 8:00
Kalyanpur | 72 | 14:00 | Baraulia | 147 | 0:00 | Rajshahi | 96 | 20:00
Gulshan | 78 | 15:00 | Sikalbaha | 20 | 18:30 | Rajshahi New | 13 | 10:00
Uttara | 62 | 13:00 | Dohazari | 62 | 19:00 | C.Nawabganj | 64 | 12:00
Uttara New | 23 | 18:30 | Cox'sbazar | 74 | 19:00 | Amnura | 41 | 18:30
Kamrangirchar | 87 | 18:30 | Chandraghona | 24 | 18:30 | Pabna | 66 | 19:00
Savar | 111 | 20:00 | Kaptai | 0 | 1:00 | Shahjadpur | 85 | 18:30
Bhasantec | 102 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 71 | 7:00
Agargaon | 46 | 13:00 | Bakulia | 74 | 18:30 | Niyamatpur | 72 | 9:00
Satmosjid | 56 | 14:00 | Julda | 18 | 18:00 | Joypurhat | 58 | 13:00
Tongi | 85 | 15:00 | TK chemical | 20.6 | 18:30 | Sherpur(Bogura) | 46 | 8:00
Kabirpur | 191 | 11:00 | Modern Steel | 0 | 1:00 | Mohastangor | 36 | 19:00
Basundhara | 93 | 18:00 | Shahmirpur | 17 | 20:00 | Bangura | 16 | 18:30
Manikganj | 60 | 19:00 | Khagrachhari | 20 | 18:30 | Rangpur | 116 | 19:00
Joydevpur | 118 | 12:00 | Matarbari | 27 | 20:00 | Lalmonirhat | 55 | 19:00
New Tongi | 83 | 10:00 | Baroiar Hat | 26 | 18:30 | Saidpur | 106 | 9:00
Korda | 144 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 98 | 18:30
Dhamrai | 74 | 10:00 | Abul Khair 230 | 151 | 12:00 | Thakurgaon | 68 | 19:00
Rajendrapur | 82 | 12:00 | BSRM | 94 | 23:00 | Palashbari | 108 | 18:30
Valuka | 82 | 10:00 | GPH Ispat | 78 | 3:00 | Barapukuria | 50 | 9:00
Tangail | 164 | 18:30 | Goalpara | 20 | 13:00 | Panchagar | 45 | 19:00
Mymensing | 184 | 18:30 | Central s/s | 84 | 18:30 | Joldhaka | 25 | 8:00
Kishorganj | 100 | 20:00 | Noapara | 47 | 18:30 | Kurigram | 48 | 19:00
Netrokona | 121 | 18:30 | Jessore | 91 | 18:30
Jamalpur | 121 | 8:00 | Benapol | 44 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 20:00 | 406 | 12:00 | Kaliakoir | 410 | 0.20833 | 400 | 0.5
| Bheramara | 406 | 5:00 | 395 | 10:00 | Bhulta | 402 | 0.20833 | 388 | 0.5
| Ashuganj(N) | 405 | 2:00 | 394 | 12:00 | Gopalganj | 412 | 0.625 | 393 | 0.8125
| Payra | 412 | 7:00 | 405 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 234 | 19:00 | 225 | 1:00
| Ishurdi | 243 | 6:00 | 231 | 8:00 | Megnaghat | 244 | 5:00 | 240 | 14:00
| Ashuganj | 245 | 1:00 | 240 | 9:00 | Fenchuganj | 247 | 19:00 | 238 | 12:00
| Serajganj | 236 | 1:00 | 226 | 9:00 | Siddhirganj | 245 | 1:00 | 236 | 12:00
| Baghabari | 240 | 1:00 | 231 | 12:00 | Maniknagar | 239 | 3:00 | 0 | 13:00
| Barapukuria | 237 | 23:00 | 223 | 9:00 | Agargaon | 240 | 5:00 | 234 | 12:00
| Bogra | 236 | 1:00 | 219 | 9:00 | Barisal | 255 | 13:00 | 242 | 3:00
| Rajshahi | 240 | 22:00 | 226 | 8:00 | Bhola 225 MW | 261 | 6:00 | 244 | 20:00
| Khulna South | 245 | 6:00 | 232 | 8:00 | AKSML | 237 | 13:00 | 220 | 12:00
| Rampura | 238 | 7:00 | 231 | 12:00 | BSRM | 236 | 22:00 | 223 | 12:00
| Haripur | 240 | 1:00 | 235 | 12:00 | Bibiyana | 247 | 13:00 | 240 | 17:00
| Hasnabad | 240 | 22:00 | 233 | 11:00 | Bhulta | 242 | 13:00 | 235 | 12:00
| Shyampur | 240 | 7:00 | 220 | 12:00 | Ashuganj (S) | 242 | 5:00 | 236 | 12:00
| Aminbazar | 242 | 22:00 | 236 | 12:00 | Kaliakoir | 240 | 22:00 | 234 | 12:00
| Tongi | 236 | 16:00 | 230 | 11:00 | GPH | 236 | 18:30 | 220 | 6:00
| Comilla (N) | 239 | 18:00 | 233 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 142 | 6:00 | 137 | 12:00 | Madanhat | 142 | 0.77083 | 131 | 0.25
| Munsiganj | 142 | 18:00 | 137 | 1:00 | Hathazari | 139 | 0.79167 | 135 | 0.041667
| Sonargaon | 138 | 8:00 | 135 | 14:00 | Khulshi | 139 | 0.77083 | 131 | 0.25
| Shyampur | 136 | 14:00 | 130 | 12:00 | Halishahar | 139 | 0.54167 | 130 | 0.25
| Bhulta | 138 | 5:00 | 134 | 1:00 | Baraulia | 140 | 0.75 | 130 | 0
| Madanganj | 140 | 20:00 | 135 | 5:00 | Sikalbaha | 141 | 0.77083 | 132 | 0.20833
| Shitalakhya | 141 | 20:00 | 134 | 12:00 | Dohazari | 137 | 0.79167 | 130 | 0.125
| Rahim steal | 140 | 2:00 | 137 | 11:00 | Cox'sbazar | 129 | 0.25 | 123 | 0.5
| Matuail | 142 | 6:00 | 137 | 12:00 | Chandraghona | 139 | 0.77083 | 130 | 0.25
| Ghorasal | 142 | 7:00 | 140 | 1:00 | Kaptai | 0 | 0.041667 | 0 | 0.083333
| Narsinghdi | 139 | 6:00 | 125 | 0:00 | A. Khaer Stl. | 138 | 0.33333 | 132 | 0.5
| Haripur (SBU) | 140 | 7:00 | 137 | 16:00 | Bakulia | 139 | 0.77083 | 129 | 0
| Ullon | 137 | 8:00 | 132 | 11:00 | Julda | 139 | 0.75 | 131 | 0.16667
| Hasnabad | 137 | 1:00 | 133 | 15:00 | TK Chemical | 140 | 0.8125 | 133 | 0.16667
| Magbazar | 137 | 5:00 | 132 | 11:00 | Modern Steel | 139 | 0.75 | 130 | 0.5
| Maniknagar | 140 | 3:00 | 134 | 13:00 | Shahmirpur | 138 | 0.79167 | 128 | 0.20833
| Bangabhaban | 140 | 3:00 | 134 | 13:00 | Khagrachhari | 138 | 0.77083 | 129 | 0.5
| Narinda | 140 | 3:00 | 134 | 13:00 | Matarbari | 133 | 0.29167 | 127 | 0.16667
| Dhanmondi | 137 | 8:00 | 132 | 11:00 | Baroiar Hat | 141 | 0.77083 | 133 | 0.20833
| Lalbag | 139 | 7:00 | 133 | 12:00 | Rangamati | 138 | 13:00 | 130 | 6:00
| Madartek | 136 | 3:00 | 131 | 12:00 | Goalpara S/S | 137 | 4:00 | 134 | 1:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 15:00 | 134 | 0.083333
| Aftabnagar | 137 | 6:00 | 132 | 11:00 | Noapara | 136 | 15:00 | 132 | 0.16667
| Fatullah | 137 | 20:00 | 130 | 12:00 | Jessore | 134 | 3:00 | 124 | 0.29167
| Mirpur | 139 | 19:30 | 135 | 11:00 | Benapol | 135 | 0.16667 | 126 | 0.29167
| Kalyanpur | 140 | 2:00 | 137 | 11:00 | Jhenida | 133 | 1:00 | 126 | 0.5
| Gulshan | 136 | 2:00 | 131 | 12:00 | Bottail | 138 | 0.20833 | 131 | 0.45833
| Uttara | 140 | 14:00 | 135 | 12:00 | G.K Project | 142 | 0.041667 | 137 | 0.375
| Uttara New | 140 | 1:00 | 134 | 15:00 | Faridpur | 140 | 0.16667 | 133 | 0.45833
| Kamrangirchar | 139 | 6:00 | 130 | 12:00 | Madaripur | 143 | 0.125 | 138 | 0.8125
| Savar | 140 | 8:00 | 136 | 6:00 | Shariyatpur S/S | 144 | 4:00 | 137 | 0.8125
| Bhasantec | 139 | 4:00 | 133 | 12:00 | Gopalganj | 146 | 0.25 | 140 | 0.45833
| Agargaon | 139 | 5:00 | 133 | 12:00 | Bagerhat | 136 | 5:00 | 130 | 0.70833
| Satmosjid | 138 | 5:00 | 133 | 11:00 | Mongla | 135 | 18:00 | 130 | 0.5
| Tongi | 141 | 1:00 | 136 | 15:00 | Satkhira | 136 | 4:00 | 130 | 8:00
| Kabirpur | 138 | 3:00 | 130 | 16:00 | Gallamari | 138 | 0.20833 | 132 | 0.33333
| Basundhara | 140 | 6:00 | 135 | 12:00 | Magura | 135 | 2:00 | 126 | 0.375
| Manikganj | 145 | 13:00 | 137 | 17:00 | Narail | 133 | 0.16667 | 125 | 0.77083
| Joydevpur | 141 | 7:00 | 137 | 17:00 | Chuadanga | 133 | 3:00 | 122 | 0.77083
| New Tongi | 141 | 8:00 | 136 | 9:00 | Borguna | 142 | 3:00 | 135 | 0.8125
| Kodda | 137 | 13:00 | 132 | 16:00 | Barisal(N) | 145 | 5:00 | 137 | 20:00
| Dhamrai | 136 | 1:00 | 129 | 11:00 | Barisal (S) | 144 | 0.20833 | 136 | 0.875
| Rajendrapur | 137 | 7:00 | 126 | 16:00 | Patuakhali(S) | 142 | 0.16667 | 134 | 0.8125
| Valuka | 131 | 4:00 | 122 | 16:00 | Bhandaria | 143 | 0.25 | 135 | 0.5
| Tangail | 136 | 5:00 | 128 | 8:00 | Ishurdi | 140 | 3:00 | 134 | 8:00
| Mymensing | 133 | 1:00 | 123 | 18:00 | Ruppur Paromanobik | 139 | 1:00 | 134 | 9:00
| Kishorganj | 134 | 5:00 | 126 | 10:00 | Natore | 138 | 3:00 | 130 | 8:00
| Netrokona | 131 | 18:30 | 121 | 18:30 | Bogra | 139 | 1:00 | 126 | 8:00
| Jamalpur | 139 | 14:00 | 130 | 8:00 | Noagaon | 132 | 1:00 | 116 | 8:00
| Sherpur | 138 | 22:00 | 128 | 8:00 | Rajshahi | 137 | 1:00 | 129 | 9:00
| Srimongal | 142 | 5:00 | 136 | 15:00 | Rajshahi New | 136 | 4:00 | 128 | 8:00
| Shahjibazar | 138 | 1:00 | 133 | 18:00 | C.Nawabganj | 135 | 5:00 | 125 | 8:00
| Fenchuganj | 143 | 5:00 | 137 | 12:00 | Amnura | 136 | 18:00 | 126 | 8:00
| Khulawara | 140 | 1:00 | 136 | 19:00 | Pabna | 141 | 3:00 | 131 | 9:00
| Sylhet | 137 | 1:00 | 131 | 19:00 | Shahjadpur | 144 | 3:00 | 135 | 7:00
| Chatak | 137 | 5:00 | 128 | 19:00 | Serajganj | 138 | 1:00 | 130 | 7:00
| Sunamganj | 136 | 3:00 | 130 | 18:30 | Niyamatpur | 132 | 3:00 | 114 | 9:00
| Biani Bazar | 137 | 4:00 | 130 | 18:00 | Joypurhat | 134 | 1:00 | 113 | 9:00
| Comilla(s) | 132 | 3:00 | 124 | 12:00 | Sherpur(Bogura) | 138 | 1:00 | 126 | 8:00
| Comilla(n) | 145 | 22:00 | 141 | 12:00 | Mohastangor | 136 | 1:00 | 122 | 8:00
| Chandpur | 143 | 14:00 | 142 | 18:30 | Bangura | 140 | 1:00 | 134 | 7:00
| Feni | 140 | 20:00 | 137 | 12:00 | Rangpur | 134 | 1:00 | 119 | 8:00
| Chowmuhani | 140 | 18:30 | 135 | 10:00 | Lalmonirhat | 131 | 1:00 | 120 | 8:00
| Ashuganj | 140 | 2:00 | 136 | 15:00 | Saidpur | 134 | 5:00 | 118 | 9:00
| Daudkandi | 142 | 18:30 | 137 | 12:00 | Purbasadipur | 131 | 2:00 | 111 | 9:00
| B.Baria | 135 | 7:00 | 132 | 16:00 | Thakurgaon | 132 | 1:00 | 111 | 9:00
| Ramganj | 139 | 9:00 | 131 | 18:00 | Palashbari | 134 | 3:00 | 118 | 9:00
| Chaddagram | 142 | 19:00 | 138 | 18:00 | Barapukuria | 136 | 1:00 | 123 | 9:00

## L-Curve
Date | 2021-02-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 191 | 4749 | 2435 | 7184 |  |  |  | QF-LDC-11
0:30 | 96.5 | 4667 | 2231 | 6898 | Date: | 2021-02-09
1:00 | 2 | 4585 | 2027 | 6612
1:30 | 4 | 4416 | 1990.5 | 6406.5
2:00 | 6 | 4247 | 1954 | 6201
2:30 | 34 | 4166 | 1938.5 | 6104.5 | [5 empty] | Gen. at Eve. Peak | 9356 | 9356 MW (19:00 )
3:00 | 62 | 4085 | 1923 | 6008 | [6 empty] | 19:00
3:30 | 81.5 | 4046.5 | 1913.5 | 5960 | [5 empty] | Gen. at Day Peak | 8158 | 8158 MW (12:00 )
4:00 | 101 | 4008 | 1904 | 5912 | [6 empty] | 12:00
4:30 | 74.5 | 3999.5 | 1883.5 | 5883 | [5 empty] | Highest Generation | 9356
5:00 | 48 | 3991 | 1863 | 5854 | [6 empty] | 19:00
5:30 | 44 | 4072 | 1888 | 5960
6:00 | 40 | 4153 | 1913 | 6066
6:30 | 108.5 | 4363.5 | 2010 | 6373.5
7:00 | 177 | 4574 | 2107 | 6681
7:30 | 204 | 4862 | 2240.5 | 7102.5
8:00 | 231 | 5150 | 2374 | 7524
8:30 | 175 | 5288 | 2420 | 7708
9:00 | 119 | 5426 | 2466 | 7892
9:30 | 74.5 | 5452.5 | 2441 | 7893.5
10:00 | 30 | 5479 | 2416 | 7895
10:30 | 33 | 5489.5 | 2448 | 7937.5
11:00 | 36 | 5500 | 2480 | 7980
11:30 | 62 | 5540.5 | 2528.5 | 8069
12:00 | 88 | 5581 | 2577 | 8158
12:30 | 114.5 | 5649 | 2562.5 | 8211.5
13:00 | 141 | 5717 | 2548 | 8265
13:30 | 83 | 5650.5 | 2489 | 8139.5
14:00 | 25 | 5584 | 2430 | 8014
14:30 | 62.5 | 5527.5 | 2397.5 | 7925
15:00 | 100 | 5471 | 2365 | 7836
15:30 | 102 | 5392 | 2342.5 | 7734.5
16:00 | 104 | 5313 | 2320 | 7633
16:30 | 100 | 5272 | 2290.5 | 7562.5
17:00 | 96 | 5231 | 2261 | 7492
17:30 | 95.5 | 5481.5 | 2433.5 | 7915
18:00 | 95 | 5732 | 2606 | 8338
18:30 | 88.5 | 5982.5 | 2864.5 | 8847
19:00 | 82 | 6233 | 3123 | 9356
19:30 | 94 | 6237 | 3059 | 9296
20:00 | 94 | 6186 | 3042 | 9228 |  |  |  | Executive Engineer
20:30 | 87 | 6083.5 | 2980.5 | 9064 |  |  |  | Network Operation Division
21:00 | 80 | 5981 | 2919 | 8900
21:30 | 46.5 | 5828 | 2851.5 | 8679.5
22:00 | 13 | 5675 | 2784 | 8459 |  |  |  |  | Page 6 of 7
22:30 | 120.5 | 5381 | 2734.5 | 8115.5
23:00 | 228 | 5087 | 2685 | 7772
23:30 | 209.5 | 4918 | 2560 | 7478
24:00 | 191 | 4749 | 2435 | 7184
9356 MW (19:00 )
8158 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-09 |  | Energy | 185733352
[11 empty] | 2021-02-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2949 | 770 | 1103 | 1986 | 649 | 70 | 56 | 0 | 88 | 0
0:30 | 2964.5 | 652.5 | 1131.5 | 1572.5 | 639.5 | 70 | 28 | 0 | 83 | 0 | Date: | 2021-02-09
1:00 | 2980 | 535 | 1160 | 1159 | 630 | 70 | 0 | 0 | 78 | 0
1:30 | 2982 | 535 | 1145.5 | 967 | 630 | 70 | 0 | 0 | 77 | 0 | [7 empty] | Total Energy | 185.7334 | Total Energy Gen 185.733 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.733 MKWHr
2:00 | 2984 | 535 | 1131 | 775 | 630 | 70 | 0 | 0 | 76 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2988 | 534.5 | 1138.5 | 673.5 | 625 | 70 | 0 | 0 | 75 | 0 | [7 empty] | Energy Requirement | 185.7334
3:00 | 2992 | 534 | 1146 | 572 | 620 | 70 | 0 | 0 | 74 | 0
3:30 | 2986 | 534 | 1154.5 | 533 | 609.5 | 70 | 0 | 0 | 73 | 0 | [6 empty] | Shortage
4:00 | 2980 | 534 | 1163 | 494 | 599 | 70 | 0 | 0 | 72 | 0
4:30 | 2980 | 531.5 | 1150 | 501 | 579.5 | 70 | 0 | 0 | 71 | 0
5:00 | 2980 | 529 | 1137 | 508 | 560 | 70 | 0 | 0 | 70 | 0
5:30 | 2979 | 570 | 1149 | 579 | 545 | 70 | 0 | 0 | 68 | 0
6:00 | 2978 | 611 | 1161 | 650 | 530 | 70 | 0 | 0 | 66 | 0
6:30 | 2904 | 665 | 1061.5 | 1063.5 | 515 | 70 | 25.5 | 0 | 67 | 2 |  |  |  |  | Coal
7:00 | 2830 | 719 | 962 | 1477 | 500 | 70 | 51 | 0 | 68 | 4
7:30 | 2910 | 718.5 | 1047.5 | 1688.5 | 529.5 | 70 | 51 | 0 | 73 | 14.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2990 | 718 | 1133 | 1900 | 559 | 70 | 51 | 0 | 78 | 25
8:30 | 2972.5 | 718.5 | 1102 | 2100.5 | 589 | 70 | 38 | 0 | 80 | 37.5
9:00 | 2955 | 719 | 1071 | 2301 | 619 | 70 | 25 | 0 | 82 | 50
9:30 | 2932.5 | 719 | 1065 | 2323.5 | 619 | 70 | 20.5 | 0 | 84.5 | 59.5
10:00 | 2910 | 719 | 1059 | 2346 | 619 | 70 | 16 | 0 | 87 | 69
10:30 | 2895.5 | 719 | 1047 | 2399 | 619.5 | 70 | 16 | 0 | 86.5 | 85
11:00 | 2881 | 719 | 1035 | 2452 | 620 | 70 | 16 | 0 | 86 | 101
11:30 | 2903.5 | 719 | 1048 | 2499.5 | 619.5 | 70 | 16 | 0 | 89.5 | 104
12:00 | 2926 | 719 | 1061 | 2547 | 619 | 70 | 16 | 0 | 93 | 107
12:30 | 2903 | 719 | 1060.5 | 2616 | 619.5 | 70 | 24 | 0 | 93 | 106.5
13:00 | 2880 | 719 | 1060 | 2685 | 620 | 70 | 32 | 0 | 93 | 106
13:30 | 2880 | 719 | 1060 | 2685 | 620 | 70 | 32 | 0 | 93 | 106
14:00 | 2880 | 719 | 1060 | 2685 | 620 | 70 | 32 | 0 | 93 | 106
14:30 | 2848 | 719 | 1053 | 2549 | 610 | 70 | 18.5 | 0 | 94 | 89
15:00 | 2816 | 719 | 1046 | 2413 | 600 | 70 | 5 | 0 | 95 | 72
15:30 | 2807 | 718.5 | 1038 | 2343.5 | 600 | 70 | 7 | 0 | 92.5 | 58
16:00 | 2798 | 718 | 1030 | 2274 | 600 | 70 | 9 | 0 | 90 | 44
16:30 | 2788.5 | 718.5 | 1025.5 | 2260.5 | 565 | 70 | 15 | 0 | 89.5 | 30
17:00 | 2779 | 719 | 1021 | 2247 | 530 | 70 | 21 | 0 | 89 | 16
17:30 | 2805 | 744.5 | 1021.5 | 2503.5 | 530 | 70 | 132 | 0 | 100.5 | 8
18:00 | 2831 | 770 | 1022 | 2760 | 530 | 70 | 243 | 0 | 112 | 0
18:30 | 2942 | 770 | 1084 | 2989 | 580 | 70 | 303 | 0 | 109 | 0
19:00 | 3053 | 770 | 1146 | 3218 | 630 | 70 | 363 | 0 | 106 | 0
19:30 | 3072 | 770 | 1169 | 3186 | 650 | 70 | 271 | 0 | 108 | 0
20:00 | 3044 | 770 | 1150 | 3167 | 650 | 70 | 271 | 0 | 106 | 0
20:30 | 3032 | 770 | 1142.5 | 3058.5 | 650 | 70 | 235 | 0 | 106 | 0
21:00 | 3020 | 770 | 1135 | 2950 | 650 | 70 | 199 | 0 | 106 | 0
21:30 | 2986 | 770 | 1109 | 2800.5 | 650 | 70 | 191 | 0 | 103 | 0
22:00 | 2952 | 770 | 1083 | 2651 | 650 | 70 | 183 | 0 | 100 | 0
22:30 | 2955 | 770 | 1089 | 2318.5 | 650 | 70 | 167 | 0 | 96 | 0
23:00 | 2958 | 770 | 1095 | 1986 | 650 | 70 | 151 | 0 | 92 | 0
23:30 | 2953.5 | 770 | 1099 | 1986 | 649.5 | 70 | 103.5 | 0 | 90 | 0 | Max Temp. in Dhaka |  | 29.4° C
24:00 | 2949 | 770 | 1103 | 1986 | 649 | 70 | 56 | 0 | 88 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 185.733 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.733 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 7 | 8 | 8 | 8 | 8 | 8 | 22 | 25 | 25 | 25 | 25 | 25 | [8 empty] | 225918
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  |  |  | 14 | 15 | 15 | 13 | 10 | 6 | 6 | [9 empty] | 75870
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 51 | 51 | 17 |  |  |  | 223301
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 160581
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 38 | [8 empty] | 34208
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 45 | 15 | 15 | 15 | 15 | 60 | 125 | 275 | 281 | 286 | 286 | 286 | 286 | 283 | 290 | 281 | 288 |  | 300 | 300 | 300 | 300 | 300 | 300 | 230 | 5171234
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4536000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 228096
33 | Ashuganj 225 MW CCPP | 90 | 92 | 95 | 101 | 99 | 95 | 87 | 90 | 87 | 87 | 95 | 90 | 76 | 79 | 95 | 101 | 99 | 100 |  | 109 | 102 | 102 | 102 | 107 | 115 | 121 | 2333000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5869000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 6750000
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP | 44 | 48 | 44 | 50 | 50 | 50 | 50 | 45 | 50 | 50 | 51 | 50 | 45 | 50 | 65 | 67 | 45 | 51 |  | 46 | 50 | 46 | 50 | 50 | 50 | 45 | 1206430
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 350 | 354 | 349 | 349 | 378 | 357 | 370 | 356 | 355 | 354 | 367 | 366 | 353 | 359 | 358 | 355 | 339 |  | 350 | 357 | 356 | 351 | 351 | 350 | 350 | 8679420
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 303 | 324 | 334 | 353 | 363 | 363 | 310 | 329 | 290 | 290 | 260 | 251 | 257 | 274 | 272 | 272 | 268 | 268 |  | 268 | 263 | 253 | 254 | 253 | 261 | 269 | 6916000
42 | RPCL 210MW CCPP | 159 | 162 | 160 | 154 | 155 | 163 | 149 | 130 | 111 | 91 | 91 | 90 | 90 | 88 | 104 | 102 | 104 | 104 |  | 107 | 106 | 107 | 108 | 109 | 110 | 108 | 2773720
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 13 | 26 | 37 | 46 | 48 | 47 | 42 | 33 | 19 | 5 | [9 empty] | 315440
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524760
46 | Shajibazar 330 MW CCPP | 100 | 99 | 100 | 101 | 102 | 101 | 101 | 102 | 101 | 101 | 100 | 101 | 100 | 100 | 102 | 100 | 101 | 103 |  | 100 | 100 | 100 | 101 | 101 | 102 | 100 | 2354000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 57 | 57 | 57 | 57 | 57 | 54 | 20 | 52 | 52 | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1297920
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 98 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2410000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 204120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 259000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 14 | 42 | 42 | 42 | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 1179000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 385216
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 275 | 290 | 280 | 275 | 300 | 230 | 300 | 300 | 290 | 310 | 310 | 290 | 280 | 290 | 300 | 290 | 280 |  | 285 | 315 | 300 | 280 | 280 | 280 | 285 | 7160500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 | 28 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 |  | 35 | 35 | 35 | 35 | 17 |  |  | 521678
59 | Tangail Palli Power Gen 22 MW | 24 |  |  |  | 6 | 24 | 24 | 25 | 24 | 24 | 24 | 21 | 23 | 19 | 19 | 24 | 23 | 12 |  | 20 | 23 | 24 | 24 | 24 | 24 | 0 | 472320
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480768
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 482256
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502128
63 | Impoprt (Tripura) | 78 | 76 | 74 | 72 | 70 | 66 | 68 | 78 | 82 | 87 | 86 | 93 | 93 | 98 | 95 | 90 | 89 | 112 |  | 106 | 108 | 106 | 106 | 100 | 92 | 88 | 2100480
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 12 | 3 | 3 | 4 | 4 | 6 | 4 | 3 | 4 | 9 | 13 |  | 25 | 25 | 30 | 30 | 37 | 40 | 40 | 547200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 488736
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257040
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 646800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 22 | 22 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 501280
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 28 | 28 | 28 | 28 | 28 | 23 | 29 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 32 | 32 | 17 |  | 17 | 32 | 32 | 32 | 32 | 32 | 32 | 684360
71 | Maona 33 MW PP(Summit) | 17 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 462600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 808100
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 102 | 99 | 99 | 99 | 99 | 95 | 101 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2388863
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [6 empty] | 20 | 26 | 26 | 26 | 26 | 26 | 46 | 46 | 46 | 46 | 46 | 46 |  | 70 | 74 | 74 | 74 | 74 | 36 |  | 887880
| Manikgonj 162MW PP(MPGL) | 126 | 90 | 72 | 54 | 54 | 54 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2916000
77 | Siddhirganj 100 PP(Dutch Bangla) | [5 empty] | 4 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 64 | 64 | 64 | 64 | 75 |  | 90 | 100 | 100 | 100 | 60 | 7 | 7 | 1109760
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [9 empty] | 16 | 16 | 16 | 32 | 32 |  |  |  | 32 |  | 64 | 64 | 64 | 64 | 64 | 32 |  | 446400
80 | Jamalpur 95 MW PP(Powerpac) | [5 empty] | 7 | 36 | 41 | 64 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 35 | 8 |  | 514560
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 5 | [6 empty] | 6173
| Gazipur 100 MW PP | [6 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 2 |  | 35 | [6 empty] | 177564
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 29760
| Jodiac Power | [6 empty] | 44 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 960258
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 |  |  |  |  | 10 | 18 | 50 | 75 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 100 |  | 100 | 101 | 101 | 80 | 80 | 80 | 80 | 1685664
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | 10 | 10 | 10 | 10 | 21 | 71 | 72 | 72 | 74 | 73 | 70 | 56 | 49 | 50 | 49 | 53 | 51 |  | 50 | 50 | 50 | 50 | 49 | 49 | 67 | 1244660
86 | Meghnaghat CCPP(Summit) | 270 | 285 | 255 | 255 | 255 | 260 | 260 | 255 | 265 | 285 | 285 | 295 | 255 | 240 | 250 | 260 | 270 | 295 |  | 245 | 285 | 240 | 260 | 245 | 275 | 245 | 6423273
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 18 | 16 | 16 | 16 | 16 | 16 | 40 | 18 | 16 | 16 | 16 | 32 |  | 60 | 60 | 65 | 65 | 50 | 16 | 16 | 535680
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 53 | 59 | 104 | 104 | 104 | 104 | 104 | 104 | 54 | 53 | 53 | 80 |  | 104 | 104 | 104 | 104 | 104 | 70 |  | 1581120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | 150840
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1187352
93 | Ashuganj 51 MW PP (Midland) | [26 empty] | 0
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 40 | 40 | 7 | 7 | 16 |  | 64 | 72 | 72 | 16 |  |  |  | 396288
95 | Patenga 50MW PP (Baraka) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 19 | 19 | 14 | 17 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 446400
96 | Chattogram 108 MW PP (ECPV) | [7 empty] | 12 | 18 | 12 | 13 | 48 | 66 | 59 | 51 | 51 | 51 | 59 |  | 83 | 45 | 45 |  |  |  |  | 586560
97 | katpotti 52 MW | [19 empty] | 11 | 12 | 12 | 12 |  |  |  | 51408
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [5 empty] | 13 | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 15 |  | 950440
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 11 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 |  |  | 668121
101 | Kushiara 163 MW CCPP (KP) | 163 | 140 | 140 | 140 | 110 | 110 | 110 | 163 | 130 | 130 | 110 | 110 | 130 | 110 | 110 | 110 | 110 | 110 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3375981
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 54 | 54 | 54 | 35 | 17 |  |  | 529920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 100 | 50 | 50 | 50 | 60 | 150 | 180 | 200 | 193 | 194 | 184 | 193 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4068000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 15 |  |  |  | 1 | 18 | 54 | 80 | 81 | 81 | 81 | 81 | 121 | 132 | 109 | 73 | 66 | 73 |  | 146 | 149 | 149 | 149 | 130 | 55 | 25 | 1743840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 50 | 20 | 20 | 30 | 60 | 90 | 100 | 100 | 100 | 90 | 100 | 50 | 50 | 50 | 50 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1806720
116 | Chandpur 200MW (Desh energy) | 34 | [6 empty] | 7 | 17 | 17 | 17 | 17 | 30 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 542880
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 419 | 421 | 421 | 421 | 421 | 421 | 375 | 421 | 423 | 425 | 427 | 422 | 430 | 400 | 385 | 353 | 352 | 347 |  | 426 | 427 | 420 | 418 | 380 | 381 | 380 | 9753000
| Jamalpur 115 MW PP (United) |  |  |  |  | 2 | 8 | 8 | 9 | 24 | 65 | 103 | 103 | 85 | 85 | 55 | 16 | 16 | 19 |  | 65 | 65 | 65 | 35 | 8 |  |  | 818400
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 248 |  | 286 | 286 | 307 | 307 | 307 | 52 | 52 | 2443855
| Juldah unit-2 (Acorn) | 100 | 70 | 50 | 20 | 20 | 20 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2095680
| Anlima Energy Ltd. | [6 empty] | 8 | 19 | 46 | 53 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 278509
| Bhairob 54.5 MW | [9 empty] | 1 | 13 | 19 | 20 | 4 | 2 | 3 |  | 5 | [8 empty] | 69840
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 9 | 18 | 26 | 30 | 32 | 33 | 29 | 20 | 13 | 4 | [9 empty] | 218893
120 | Eastern Zone Total | 4585 | 4247 | 4085 | 4008 | 3991 | 4153 | 4574 | 5150 | 5426 | 5479 | 5500 | 5581 | 5717 | 5584 | 5471 | 5313 | 5231 | 5732 |  | 6233 | 6237 | 6186 | 5981 | 5675 | 5087 | 4749 | 126557226
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [6 empty] | 16 | 49 | 49 | 49 | 49 | 49 | 83 | 49 | 16 |  |  | 49 |  | 99 | 99 | 99 | 32 | 16 |  |  | 672000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 53 | 70 | 70 | 70 | 76 | 76 | 76 | 76 | 76 | 35 | 35 | 76 |  | 76 | 76 | 76 | 76 | 53 | 17 |  | 1133280
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | [26 empty] | 0
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 |  |  | 96960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 58 | 36 | 35 | 35 | 34 | 34 | 34 | 33 | 53 | 53 | 55 | 77 | 65 | 65 | 61 | 35 | 34 | 35 |  | 85 | 84 | 84 | 88 | 63 | 66 | 63 | 1298622
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 15 | 16 | 14 | 14 | 13 | 11 | 12 | 13 | 15 | 14 | 13 | 12 | 13 | 18 |  | 21 | 20 | 21 | 21 | 21 | 19 | 18 | 364000
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 24 | [6 empty] | 24000
143 | Gopalganj 100 MW Peaking PP | [13 empty] | 2 | 5 | 9 | 14 | 17 |  | 21 | 21 | 21 | 17 | 18 | 18 | 5 | 142336
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 535 | 535 | 534 | 534 | 529 | 611 | 719 | 718 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 718 | 719 | 770 |  | 770 | 770 | 770 | 770 | 770 | 770 | 770 | 16648000
147 | Bheramara 410 MW CCPP | 335 | 335 | 345 | 355 | 365 | 320 | 300 | 375 | 375 | 350 | 340 | 340 | 280 | 250 | 250 | 250 | 250 | 320 |  | 400 | 400 | 390 | 380 | 370 | 370 | 370 | 8158176
148 | Payra 1320 MW | 480 | 480 | 470 | 450 | 410 | 380 | 350 | 410 | 470 | 470 | 470 | 470 | 470 | 470 | 450 | 450 | 380 | 380 |  | 480 | 500 | 500 | 500 | 500 | 500 | 500 | 11668500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3684900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | [6 empty] | 44304
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 150 | 151 | 154 | 151 | 151 | 166 | 152 | 162 | 154 | 154 | 153 | 160 | 158 | 151 | 155 | 154 | 153 | 154 |  | 197 | 196 | 189 | 177 | 172 | 158 | 158 | 4064618
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 186 | 189 | 185 | 174 | 170 | 150 | 158 | 156 | 163 | 162 | 177 | 210 | 159 | 159 | 158 | 157 | 158 |  | 163 | 164 | 164 | 163 | 158 | 152 | 155 | 4260409
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223452
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 |  |  | 185820
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 7 | 8 |  | 8 | [6 empty] | 8682
168 | Santahar 50 MW Peaking PP | [17 empty] | 13 |  | 34 | 34 | 34 |  |  |  |  | 67511
169 | Natore 52 MW PP (Rajlanka) |  |  |  |  | 5 | 8 | 34 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 25 | 8 | 8 | 52 |  | 52 | 52 | 52 | 52 |  |  |  | 593760
170 | Chapainawabganj 100 MW Peaking PP | [6 empty] | 51 | 51 | 25 | [8 empty] | 50 |  | 101 | 101 | 101 | 101 | 101 | 101 | 51 | 689296
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | [6 empty] | 43 | 50 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1861248
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 35 | 40 | 50 | 55 | 55 | 111 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 50 | 1180416
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 15 |  |  |  |  | 28 | 54 | 102 | 94 | 84 | 91 | 93 | 85 | 83 | 70 | 70 | 70 | 70 |  | 105 | 105 | 104 | 105 | 105 | 105 |  | 1576320
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 |  | 5 | 5 | 5 | 5 | 4 | 3 | 1 | [9 empty] | 31036
178
178