## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-12 | Friday
|  |  | Date (day): | 2021-02-12 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12574.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14068 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-11 | 2021-02-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 102 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 349 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 292 | 237 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 86 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 270 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 99 | 100 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 67 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 90 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 80 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 17 | 35 | 35 |  | 20 | 33 kV feeder problem.
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 56 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 22 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 294 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 140 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 26 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 2453 | 2616 | 3545 | 3767 | 318 | 1808
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 22 | 19 | 19 |  | 31 | Engine problem
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 80 | 120 | 120 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 0 | 8 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 35 | 40
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 82 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 200 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 53 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 611 | 862 | 1391 | 1463 | 895 | 146
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 187 | 220 | 220 |  | 1
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 260 | 360 | 360
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 250 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 5 | 26 | 26 | 45 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 38 | 50 | 50 |  | 113 | Gas shortage & ST under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 34 | 51 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 20 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 83 | 106 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 73 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 19 | 8 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1200 | 1076 | 1668 | 1930 | 740 | 120
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 106 | 150 | 150 | 52 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 24 | 82 | 82 |  | 13 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 195 | 195 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 40 | 85 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 25 | 25
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 449 | 455 | 645.6 | 594 | 52 | 13
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22 |  | 68 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 99 | 101 | 100 | 100 |  | 230 | GT-2 & ST under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 69 | 73 | 74 | 74 |  | 12 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 80 | 100 | 100 |  | 131
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 285 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 376 | 340 | 420 | 420
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 15 | 80 | 90
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1149 | 1187 | 1588 | 1598 | 0 | 556
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 775 | 539 | 828
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 85 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 19 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 175 | 300 | 200 | 410
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 95 | 95 |  | 10 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1036 | 1272 | 1224 | 2009 | 0 | 88
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 26 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 35 | 84 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 400 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 496 | 542 | 1001 | 1001 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 18 | 25 | 25 |  | 25 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 8 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | FGMO
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 224 | 159 | 229 | 229 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 154 | 440 | 400 | 400
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 0 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 25 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 101 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 100 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 100 | 35 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 685 | 1033 | 1241 | 1443 | 431 | 25
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 103 | 90 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 258 | 240 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 8337 | 9283 | 12574.6 | 14068 | 2560 | 3167
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8080.1453 | 8997 | 12187.1891 | 13634.5789
| A. |  | 2021-02-11 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 9283 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5993 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9283 | MW
| 3 | Day peak Generation : |  |  | 8337 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8997 | MW
| 4 | Evening peak Generation : |  |  | 9283 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 187.532 | MKWHr | By Solar | 0.54006 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 102.2145 | MKWHr |  | By Oil: | 48.8489 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.5538 | MKWHr |  | By Hydro: | 1.68 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2560 | MW | Dhaka | 3135 | 3135 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3167 | MW | Chittagong | 979 | 979 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5727 | MW | Khulna | 1117 | 1117 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 881.32 | MMCFD |  |  | Rajshahi | 956 | 956 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 111746200.398 | ii) Oil : | Taka | 304992813.47 | Comilla | 757 | 757 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72073848 | Total | Taka | 488812861.868 | Mymensingh | 824 | 824 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.8245 | MKWHr. | Sylhet | 332 | 332 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 1 | MW (E to W) at | 19:00 | hrs | Barisal | 239 | 239 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -356 | MW at | 8:00 | hrs | Rangpur | 658 | 658 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.0° C |  |  | Total | 8997 | 8997 |  | 0
| B. |  | 2021-02-12 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14068 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 5068 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 181.815 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6000 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.7287 | MKWHr. | ii) HVDC Flow at Peak Time |  | 775 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9661 | MKWHr. | iii) Maximum HVDC Flow : |  | 779 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.37 |  | (b) Today: | 94.13 |  | (c) Rule Curve: |  | 95.46
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 351 | 320 |  | 0 | 0 | 270 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 0 | 0 | 0 | 270 | 265 | 35 | 8 | 51 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 76 | 107 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 71 | 0 | 0 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 95 | 0 | 0 | 170 | 0 | 16 | 0 | 100 | 50 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 35 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 144 | 0 | 100 | 0 | 0 |  | 531 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 184 | 0 | 233 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 510 | 0 | 0 | 0 |  | 4707 | 2072 | 6779 | 2730 | 531 | 1481 | 1224 | 659 | 70 | 8 | 76 | 0 | 0 | 94.42
2:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 346 | 333 |  | 0 | 0 | 270 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 125 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 0 | 0 | 0 | 270 | 265 | 36 | 8 | 48 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 70 | 108 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 71 | 0 | 0 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 140 | 0 | 0 | 0 | 100 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 144 | 0 | 100 | 0 | 0 |  | 530 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 184 | 0 | 232 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4525 | 1950 | 6475 | 2748 | 530 | 1472 | 928 | 649 | 70 | 8 | 70 | 0 | 0 | 94.41
3:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 341 | 345 |  | 0 | 0 | 240 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 118 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 0 | 0 | 0 | 270 | 265 | 39 | 8 | 50 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 66 | 108 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 71 | 0 | 0 | 19 | 0 | 9 | 290 | 8 | 11 | 0 | 30 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 125 | 0 | 100 | 0 | 0 |  | 530 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 183 | 0 | 231 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4316 | 1967 | 6283 | 2773 | 530 | 1473 | 714 | 649 | 70 | 8 | 66 | 0 | 0 | 94.4
4:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 350 | 353 |  | 0 | 0 | 260 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 0 | 0 | 0 | 270 | 265 | 40 | 8 | 52 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 62 | 108 | 0 | 22 | 0 | 30 | 22 | 14 | 10 | 163 | 99 | 0 | 40 | 0 | 0 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 373 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 79 | 0 | 100 | 0 | 0 |  | 530 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 184 | 0 | 230 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4058 | 1963 | 6021 | 2780 | 530 | 1380 | 571 | 620 | 70 | 8 | 62 | 0 | 0 | 94.39
5:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 348 | 353 |  | 0 | 0 | 265 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 113 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 0 | 0 | 0 | 280 | 275 | 40 | 8 | 50 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 64 | 109 | 0 | 22 | 0 | 30 | 22 | 14 | 10 | 163 | 99 | 0 | 40 | 0 | 0 | 19 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 374 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 72 | 0 | 100 | 0 | 0 |  | 531 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 194 | 0 | 230 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 0 |  | 4074 | 1919 | 5993 | 2781 | 531 | 1380 | 569 | 590 | 70 | 8 | 64 | 0 | 0 | 94.38
6:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 370 | 354 |  | 0 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 117 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 0 | 0 | 0 | 300 | 290 | 45 | 8 | 50 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 68 | 109 | 0 | 22 | 0 | 30 | 22 | 14 | 10 | 163 | 99 | 0 | 40 | 0 | 0 | 19 | 0 | 9 | 320 | 8 | 11 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 374 | 0 | 0 | 0 | 0 | 16 | 4 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 72 | 0 | 100 | 0 | 0 |  | 719 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 198 | 0 | 231 | 0 | 0 | 41 | 0 | 25 | 0 | 0 | 25 | 440 | 0 | 0 | 0 |  | 4247 | 2156 | 6403 | 2846 | 719 | 1403 | 707 | 590 | 70 | 0 | 68 | 0 | 0 | 94.37
7:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 355 | 323 |  | 0 | 0 | 285 | 6 | 40 | 16 | 0 | 0 | 0 | 1 | 3 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 126 | 0 |  | 8 | 0 | 0 | 0 | 0 | 19 | 20 | 38 | 0 | 0 | 0 | 325 | 320 | 123 | 8 | 51 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 70 | 110 | 5 | 22 | 0 | 30 | 22 | 14 | 10 | 130 | 101 | 0 | 40 | 0 | 0 | 19 | 0 | 9 | 280 | 8 | 8 | 0 | 87 | 0 | 0 | 134 | 0 | 30 | 1 | 50 | 17 | 0 | 351 | 0 | 0 | 2 | 0 | 16 | 44 | 0 | 0 | 0 | 100 | 0 | 17 | 1 | 72 | 11 | 100 | 0 | 1 |  | 719 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 203 | 0 | 200 | 35 | 0 | 55 | 0 | 34 | 0 | 0 | 35 | 410 | 0 | 0 | 0 |  | 4612 | 2116 | 6728 | 2896 | 719 | 1235 | 1175 | 560 | 70 | 0 | 70 | 3 | 0 | 94.36
8:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 362 | 337 |  | 0 | 0 | 250 | 27 | 65 | 35 | 0 | 0 | 0 | 32 | 24 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 28 | 17 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 4 | 0 | 0 | 116 | 0 |  | 18 | 0 | 0 | 10 | 1 | 19 | 20 | 12 | 0 | 0 | 0 | 265 | 250 | 164 | 8 | 50 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 82 | 110 | 40 | 22 | 0 | 30 | 22 | 50 | 28 | 110 | 101 | 0 | 66 | 0 | 0 | 19 | 0 | 9 | 290 | 8 | 8 | 0 | 155 | 0 | 0 | 185 | 0 | 74 | 5 | 100 | 24 | 0 | 420 | 24 | 0 | 8 | 1 | 16 | 54 | 0 | 0 | 12 | 100 | 0 | 82 | 10 | 119 | 34 | 100 | 0 | 6 |  | 718 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 229 | 0 | 154 | 90 | 0 | 55 | 0 | 76 | 0 | 1 | 35 | 440 | 0 | 0 | 0 |  | 5275 | 2309 | 7584 | 2881 | 718 | 1247 | 1957 | 590 | 70 | 16 | 82 | 23 | 0 | 94.35
9:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 348 | 307 |  | 0 | 0 | 270 | 40 | 94 | 55 | 0 | 0 | 0 | 40 | 24 | 16 | 61 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 25 | 29 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 115 | 0 |  | 18 | 0 | 0 | 10 | 25 | 19 | 20 | 4 | 0 | 0 | 0 | 275 | 260 | 195 | 8 | 51 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 84 | 107 | 56 | 22 | 1 | 30 | 22 | 50 | 46 | 110 | 100 | 0 | 67 | 0 | 0 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 263 | 0 | 0 | 191 | 0 | 139 | 10 | 100 | 34 | 0 | 421 | 24 | 0 | 17 | 3 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 20 | 144 | 53 | 0 | 0 | 12 |  | 719 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 230 | 0 | 153 | 90 | 0 | 55 | 0 | 83 | 0 | 3 | 35 | 440 | 0 | 0 | 0 |  | 5653 | 2331 | 7984 | 2789 | 719 | 1236 | 2431 | 590 | 70 | 16 | 84 | 49 | 0 | 94.34
10:00 | 0 | 0 | 0 | 180 | 0 | 99 | 0 | 348 | 305 |  | 0 | 0 | 265 | 40 | 99 | 55 | 0 | 0 | 0 | 40 | 24 | 16 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 32 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 80 | 0 |  | 18 | 0 | 0 | 10 | 31 | 19 | 20 | 3 | 0 | 0 | 0 | 380 | 250 | 230 | 24 | 48 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 81 | 108 | 40 | 22 | 1 | 30 | 22 | 50 | 50 | 110 | 100 | 0 | 67 | 0 | 0 | 18 | 0 | 9 | 290 | 8 | 8 | 0 | 278 | 0 | 0 | 195 | 0 | 149 | 14 | 90 | 34 | 0 | 421 | 24 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 28 | 144 | 53 | 0 | 0 | 18 |  | 718 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 12 | 0 | 0 | 52 | 3 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 229 | 0 | 156 | 90 | 0 | 97 | 0 | 87 | 0 | 3 | 50 | 440 | 0 | 0 | 0 |  | 5771 | 2436 | 8207 | 2862 | 718 | 1240 | 2517 | 590 | 70 | 61 | 81 | 68 | 0 | 94.33
11:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 345 | 292 |  | 0 | 0 | 275 | 40 | 99 | 54 | 0 | 0 | 0 | 40 | 24 | 16 | 62 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 10 | 12 | 19 | 20 | 2 | 0 | 0 | 0 | 295 | 250 | 184 | 26 | 47 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 33 | 15 | 78 | 106 | 24 | 22 | 2 | 30 | 22 | 50 | 50 | 110 | 101 | 0 | 69 | 0 | 0 | 18 | 0 | 9 | 285 | 8 | 8 | 0 | 288 | 0 | 0 | 195 | 0 | 149 | 16 | 90 | 34 | 0 | 375 | 24 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 35 | 144 | 53 | 0 | 12 | 0 |  | 719 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 25 | 23 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 228 | 0 | 155 | 94 | 0 | 113 | 0 | 103 | 0 | 5 | 50 | 440 | 0 | 0 | 0 |  | 5638 | 2474 | 8112 | 2750 | 719 | 1226 | 2528 | 590 | 70 | 89 | 78 | 62 | 0 | 94.32
12:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 353 | 292 |  | 0 | 0 | 275 | 40 | 99 | 55 | 0 | 0 | 0 | 40 | 24 | 16 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 10 | 12 | 19 | 20 | 2 | 0 | 0 | 0 | 355 | 310 | 197 | 26 | 50 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 33 | 15 | 83 | 104 | 24 | 22 | 2 | 30 | 22 | 50 | 50 | 110 | 99 | 0 | 69 | 0 | 0 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 286 | 0 | 0 | 195 | 0 | 149 | 16 | 90 | 34 | 0 | 376 | 40 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 38 | 144 | 53 | 0 | 19 | 26 |  | 719 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 25 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 224 | 0 | 154 | 93 | 0 | 113 | 0 | 103 | 0 | 5 | 50 | 440 | 0 | 0 | 0 |  | 5862 | 2475 | 8337 | 2899 | 719 | 1245 | 2549 | 590 | 70 | 91 | 83 | 91 | 0 | 94.31
13:00 | 0 | 0 | 0 | 180 | 0 | 105 | 0 | 374 | 267 |  | 0 | 0 | 265 | 56 | 96 | 55 | 0 | 0 | 0 | 50 | 32 | 16 | 60 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 120 | 0 |  | 23 | 0 | 0 | 10 | 12 | 19 | 20 | 6 | 0 | 0 | 0 | 320 | 275 | 200 | 26 | 50 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 15 | 85 | 97 | 24 | 22 | 2 | 30 | 22 | 53 | 46 | 163 | 100 | 0 | 69 | 0 | 0 | 18 | 0 | 9 | 315 | 8 | 8 | 0 | 273 | 0 | 0 | 195 | 0 | 149 | 16 | 90 | 43 | 0 | 427 | 45 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 47 | 100 | 0 | 104 | 38 | 144 | 53 | 0 | 0 | 0 |  | 719 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 25 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 221 | 0 | 153 | 93 | 0 | 113 | 0 | 98 | 0 | 5 | 50 | 470 | 0 | 0 | 0 |  | 5958 | 2494 | 8452 | 2906 | 719 | 1292 | 2604 | 620 | 70 | 91 | 85 | 65 | 8452 | 94.3
14:00 | 0 | 0 | 0 | 100 | 0 | 105 | 0 | 345 | 261 |  | 0 | 0 | 250 | 65 | 92 | 40 | 0 | 0 | 0 | 70 | 24 | 16 | 60 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 120 | 0 |  | 23 | 0 | 0 | 10 | 17 | 19 | 20 | 3 | 0 | 0 | 0 | 315 | 270 | 197 | 26 | 51 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 15 | 87 | 92 | 24 | 22 | 2 | 30 | 22 | 53 | 50 | 110 | 101 | 0 | 69 | 0 | 0 | 18 | 0 | 9 | 290 | 8 | 8 | 0 | 285 | 0 | 0 | 183 | 0 | 135 | 0 | 90 | 51 | 0 | 415 | 16 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 55 | 100 | 0 | 104 | 32 | 144 | 45 | 0 | 0 | 19 |  | 719 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 8 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 222 | 0 | 157 | 70 | 0 | 70 | 0 | 68 | 0 | 4 | 35 | 430 | 0 | 0 | 0 |  | 5691 | 2299 | 7990 | 2766 | 719 | 1212 | 2401 | 580 | 70 | 94 | 87 | 61 | 0 | 94.29
15:00 | 0 | 0 | 0 | 100 | 0 | 102 | 0 | 371 | 262 |  | 0 | 0 | 240 | 65 | 99 | 40 | 0 | 0 | 0 | 70 | 0 | 16 | 68 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 19 | 0 | 0 | 8 | 15 | 0 | 20 | 2 | 0 | 0 | 0 | 280 | 255 | 187 | 8 | 48 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 15 | 84 | 101 | 24 | 22 | 1 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 70 | 0 | 60 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 285 | 0 | 0 | 173 | 0 | 115 | 12 | 90 | 51 | 0 | 387 | 16 | 0 | 17 | 3 | 16 | 54 | 0 | 0 | 55 | 100 | 0 | 104 | 22 | 144 | 14 | 0 | 0 | 16 |  | 719 | 0 | 210 | 0 | 7 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 3 | 8 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 208 | 0 | 287 | 70 | 0 | 70 | 0 | 70 | 0 | 3 | 35 | 410 | 0 | 0 | 0 |  | 5508 | 2431 | 7939 | 2753 | 719 | 1332 | 2261 | 560 | 70 | 103 | 84 | 57 | 0 | 94.28
16:00 | 0 | 0 | 0 | 190 | 0 | 99 | 0 | 348 | 262 |  | 0 | 0 | 255 | 35 | 64 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 48 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 0 | 0 | 295 | 270 | 172 | 8 | 40 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 80 | 103 | 24 | 22 | 1 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 70 | 0 | 80 | 18 | 0 | 9 | 290 | 8 | 8 | 0 | 267 | 0 | 0 | 183 | 0 | 106 | 7 | 100 | 51 | 0 | 376 | 16 | 0 | 0 | 2 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 78 | 11 | 144 | 0 | 0 | 0 | 8 |  | 719 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 12 | 0 | 8 | 0 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 193 | 0 | 338 | 35 | 0 | 70 | 0 | 70 | 0 | 2 | 35 | 410 | 0 | 0 | 0 |  | 5258 | 2573 | 7831 | 3008 | 719 | 1369 | 1923 | 560 | 70 | 71 | 80 | 31 | 0 | 94.27
17:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 349 | 252 |  | 0 | 0 | 280 | 24 | 64 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 19 | 0 | 0 | 10 | 1 | 0 | 20 | 7 | 0 | 0 | 0 | 265 | 255 | 158 | 8 | 42 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 103 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 99 | 0 | 70 | 0 | 80 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 255 | 0 | 0 | 183 | 0 | 100 | 2 | 100 | 51 | 0 | 376 | 16 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 26 | 100 | 15 | 53 | 3 | 144 | 0 | 0 | 16 | 2 |  | 779 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 12 | 0 | 8 | 0 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 204 | 0 | 339 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 410 | 0 | 0 | 0 |  | 5121 | 2541 | 7662 | 2937 | 779 | 1376 | 1791 | 560 | 70 | 66 | 76 | 7 | 0 | 94.26
18:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 346 | 240 |  | 0 | 0 | 275 | 25 | 75 | 30 | 0 | 0 | 0 | 30 | 24 | 40 | 42 | 0 | 0 | 0 | 30 | 17 | 17 | 22 | 25 | 20 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 6 | 0 | 0 | 80 | 0 |  | 23 | 0 | 81 | 10 | 52 | 2 | 20 | 19 | 0 | 0 | 0 | 260 | 250 | 180 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 106 | 104 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 102 | 0 | 73 | 0 | 80 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 274 | 0 | 0 | 195 | 0 | 104 | 0 | 100 | 51 | 0 | 353 | 20 | 25 | 0 | 0 | 83 | 54 | 0 | 0 | 33 | 100 | 15 | 58 | 0 | 144 | 12 | 0 | 30 | 0 |  | 775 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 24 | 16 | 0 | 0 | 0 | 50 | 6 | 95 | 18 | 0 | 8 | 25 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 178 | 0 | 421 | 50 | 0 | 43 | 0 | 60 | 0 | 0 | 60 | 350 | 0 | 0 | 0 |  | 5578 | 2836 | 8414 | 2828 | 775 | 1512 | 2302 | 500 | 70 | 321 | 106 | 0 | 0 | 94.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 349 | 237 |  | 0 | 0 | 270 | 86 | 100 | 55 | 0 | 0 | 0 | 90 | 80 | 32 | 67 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 80 | 0 |  | 23 | 0 | 85 | 0 | 82 | 22 | 20 | 24 | 0 | 0 | 0 | 260 | 250 | 187 | 8 | 38 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 106 | 106 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 101 | 0 | 73 | 0 | 80 | 0 | 0 | 9 | 285 | 8 | 11 | 0 | 294 | 0 | 0 | 195 | 0 | 140 | 0 | 100 | 51 | 0 | 340 | 85 | 17 | 0 | 0 | 200 | 54 | 0 | 0 | 73 | 100 | 15 | 104 | 0 | 144 | 0 | 0 | 8 | 0 |  | 775 | 0 | 300 | 0 | 85 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 0 | 101 | 18 | 0 | 8 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 159 | 0 | 440 | 93 | 0 | 100 | 0 | 90 | 0 | 0 | 100 | 400 | 0 | 0 | 0 |  | 6196 | 3087 | 9283 | 2802 | 775 | 1527 | 3158 | 550 | 70 | 295 | 106 | 0 | 0 | 94.22
19:30 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 342 | 233 |  | 0 | 0 | 275 | 80 | 100 | 55 | 0 | 0 | 0 | 100 | 32 | 32 | 75 | 0 | 0 | 0 | 54 | 35 | 17 | 22 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 115 | 0 |  | 23 | 0 | 85 | 0 | 0 | 25 | 20 | 26 | 0 | 0 | 0 | 265 | 260 | 191 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 106 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 73 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 115 | 0 | 100 | 51 | 0 | 371 | 85 | 0 | 0 | 0 | 290 | 17 | 0 | 0 | 55 | 100 | 20 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 775 | 0 | 285 | 0 | 28 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 36 | 0 | 101 | 18 | 0 | 7 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 156 | 0 | 438 | 93 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 480 | 0 | 0 | 0 |  | 6151 | 3079 | 9230 | 2870 | 775 | 1553 | 2946 | 630 | 70 | 280 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 341 | 233 |  | 0 | 0 | 275 | 70 | 100 | 55 | 0 | 0 | 0 | 100 | 7 | 16 | 75 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 114 | 0 |  | 23 | 0 | 85 | 0 | 0 | 29 | 20 | 26 | 0 | 0 | 0 | 260 | 255 | 191 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 104 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 73 | 0 | 80 | 0 | 0 | 9 | 285 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 127 | 0 | 100 | 51 | 0 | 375 | 85 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 26 | 100 | 20 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 775 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 101 | 18 | 0 | 7 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 155 | 0 | 440 | 93 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6094 | 3044 | 9138 | 2852 | 775 | 1587 | 2872 | 650 | 70 | 228 | 104 | 0 | 0 | 94.23
21:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 342 | 231 |  | 0 | 0 | 280 | 24 | 81 | 30 | 0 | 0 | 0 | 70 | 7 | 16 | 75 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 113 | 0 |  | 23 | 0 | 85 | 0 | 0 | 39 | 20 | 32 | 0 | 0 | 0 | 260 | 250 | 195 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 104 | 107 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 100 | 0 | 73 | 0 | 80 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 104 | 0 | 100 | 51 | 0 | 374 | 55 | 0 | 0 | 0 | 301 | 17 | 0 | 0 | 26 | 100 | 30 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 776 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 101 | 18 | 0 | 7 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 156 | 0 | 427 | 94 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 530 | 0 | 0 | 0 |  | 5905 | 3003 | 8908 | 2825 | 776 | 1562 | 2663 | 680 | 70 | 228 | 104 | 0 | 0 | 94.22
22:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 341 | 232 |  | 0 | 0 | 275 | 0 | 81 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 72 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 113 | 0 |  | 23 | 0 | 0 | 0 | 0 | 39 | 20 | 37 | 0 | 0 | 0 | 260 | 250 | 184 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 98 | 108 | 60 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 101 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 102 | 0 | 100 | 51 | 0 | 411 | 0 | 0 | 0 | 0 | 106 | 42 | 0 | 0 | 0 | 100 | 30 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 775 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 7 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 154 | 0 | 398 | 53 | 0 | 113 | 0 | 80 | 0 | 0 | 70 | 530 | 0 | 0 | 0 |  | 5484 | 2814 | 8298 | 2825 | 775 | 1526 | 2203 | 679 | 70 | 122 | 98 | 0 | 0 | 94.21
23:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 346 | 231 |  | 0 | 0 | 285 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 20 | 38 | 0 | 0 | 0 | 290 | 295 | 168 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 92 | 107 | 30 | 22 | 0 | 30 | 22 | 53 | 50 | 130 | 99 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 79 | 0 | 100 | 51 | 0 | 408 | 0 | 0 | 0 | 0 | 106 | 17 | 0 | 0 | 0 | 100 | 64 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 775 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 7 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 158 | 0 | 418 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 35 | 530 | 0 | 0 | 0 |  | 5181 | 2589 | 7770 | 2894 | 775 | 1529 | 1685 | 680 | 70 | 45 | 92 | 0 | 0 | 94.2
24:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 364 | 244 |  | 0 | 0 | 250 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 113 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 20 | 7 | 0 | 0 | 0 | 260 | 270 | 152 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 84 | 107 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 100 | 0 | 0 | 200 | 0 | 53 | 0 | 100 | 51 | 0 | 397 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 100 | 59 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 775 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 170 | 0 | 398 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 4819 | 2409 | 7228 | 2814 | 775 | 1470 | 1335 | 680 | 70 | 0 | 84 | 0 | 0 | 94.19
KWH | 0 | 0 | 0 | 4299750 | 0 | 2438000 | 0 | 8558590 | 6878000 |  | 0 | 0 | 6341644 | 697920 | 1668240 | 682730 | 0 | 0 | 0 | 847680 | 388080 | 240000 | 1267868 | 0 | 0 | 0 | 407520 | 465714 | 430861 | 462672 | 600000 | 695160 | 528500 | 825300 | 0 | 0 | 0 | 1680000 | 0 | 0 | 120391 | 0 | 0 | 2536756 | 0 |  | 332400 | 0 | 337572 | 117240 | 281280 | 493440 | 469104 | 528000 | 0 | 0 | 0 | 7160000 | 6523000 | 3452000 | 301090 | 1077270 | 354888 | 323520 | 0 | 0 | 0 | 0 | 19219 | 404064 | 208260 | 821100 | 494930 | 1966080 | 2482960 | 548160 | 511056 | 11050 | 714000 | 521520 | 1092600 | 1032336 | 3550990 | 2363000 | 0 | 1587840 | 0 | 735970 | 335000 | 0 | 208080 | 7345500 | 191232 | 228048 | 0 | 4960470 | 0 | 0 | 3957600 | 0 | 2051570 | 109890 | 1955520 | 951840 | 0 | 9736000 | 548400 | 73812 | 179818 | 29520 | 1400073 | 922664 | 0 | 0 | 605640 | 2220480 | 245700 | 1462080 | 236480 | 3166560 | 429055 | 0 | 95400 | 124695 |  | 16728727 | 0 | 5742720 | 0 | 457920 | 0 | 0 | 0 | 0 | 145152 | 10875 | 0 | 485800 | 160704 | 0 | 0 | 0 | 401600 | 6588 | 500784 | 203770 | 0 | 97903 | 285120 | 202328 | 496320 | 0 | 242244 | 0 | 0 | 3682200 | 0 | 0 | 0 | 0 | 0 | 0 | 1084229 | 0 | 4884236 | 0 | 6457145 | 1266240 | 0 | 1965216 | 0 | 1356480 | 0 | 28426 | 1119264 | 11871600 | 0 | 0 | 0 |  | 127648442 | 59883591 | 187532033 | 68405030 | 16728727 | 33809450 | 46916958 | 15553800 | 1680000 | 1931927 | 1966080 | 540061 | 0
Fuel Cost | 0 | 0 | 0 | 6320632.5 | 0 | 3218160 | 0 | 8644175.9 | 7084340 |  | 0 | 0 | 7039224.84 | 5297212.8 | 11494173.6 | 5775895.8 | 0 | 0 | 0 | 6383030.4 | 3539289.6 | 2361600 | 11689742.96 | 0 | 0 | 0 | 2974896 | 3599969.22 | 4248289.46 | 347004 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 453600 | 0 | 0 | 1118432.39 | 0 | 0 | 4312485.2 | 0 |  | 0 | 0 | 3274448.4 | 1119642 | 2447136 | 3908044.8 | 591071.04 | 1568160 | 0 | 0 | 0 | 5298400 | 6523000 | 3175840 | 388406.1 | 1238860.5 | 401023.44 | 452928 | 0 | 0 | 0 | 0 | 183541.45 | 513161.28 | 156195 | 1436925 | 371197.5 | 14745600 | 2631937.6 | 4977292.8 | 649041.12 | 176137 | 1170960 | 834432 | 1944828 | 1610444.16 | 4048128.6 | 2457520 | 0 | 3032774.4 | 0 | 1273228.1 | 733650 | 0 | 424483.2 | 7418955 | 143424 | 173316.48 | 0 | 37501153.2 | 0 | 0 | 20579520 | 0 | 20187448.8 | 1284614.1 | 15937488 | 10327464 | 0 | 9054480 | 5001408 | 697523.4 | 1566214.78 | 0 | 10584551.88 | 8036403.44 | 0 | 0 | 5190334.8 | 14788396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96357467.52 | 0 | 6029856 | 0 | 3599251.2 | 0 | 0 | 0 | 0 | 1521192.96 | 113317.5 | 0 | 752990 | 1568471.04 | 0 | 0 | 0 | 3951744 | 66934.08 | 4431938.4 | 1569029 | 0 | 948680.07 | 2762812.8 | 1962581.6 | 952934.4 | 0 | 183378.708 | 0 | 0 | 19957524 | 0 | 0 | 0 | 0 | 0 | 0 | 1626343.5 | 0 | 5714556.12 | 0 | 6392573.55 | 13219545.6 | 0 | 18649899.84 | 0 | 10526284.8 | 0 | 314107.3 | 8271360.96 | 52116324 | 0 | 0 | 0 |  | 338583288.84 | 263561098.948 | 602144387.788 | 70829751.488 | 96357467.52 | 40916448.91 | 286473693.96 | 72073848 | 453600 | 18519119.51 | 14745600 | 1774858.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 353 | 292 |  | 0 | 0 | 275 | 40 | 99 | 55 | 0 | 0 | 0 | 40 | 24 | 16 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 10 | 12 | 19 | 20 | 2 | 0 | 0 | 0 | 355 | 310 | 197 | 26 | 50 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 33 | 15 | 83 | 104 | 24 | 22 | 2 | 30 | 22 | 50 | 50 | 110 | 99 | 0 | 69 | 0 | 0 | 18 | 0 | 9 | 300 | 8 | 8 | 0 | 286 | 0 | 0 | 195 | 0 | 149 | 16 | 90 | 34 | 0 | 376 | 40 | 0 | 17 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 104 | 38 | 144 | 53 | 0 | 19 | 26 |  | 719 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 25 | 25 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 224 | 0 | 154 | 93 | 0 | 113 | 0 | 103 | 0 | 5 | 50 | 440 | 0 | 0 | 0 |  | 8337 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 349 | 237 | 0 | 0 | 0 | 270 | 86 | 100 | 55 | 0 | 0 | 0 | 90 | 80 | 32 | 67 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 80 | 0 | 0 | 23 | 0 | 85 | 0 | 82 | 22 | 20 | 24 | 0 | 0 | 0 | 260 | 250 | 187 | 8 | 38 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 106 | 106 | 24 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 101 | 0 | 73 | 0 | 80 | 0 | 0 | 9 | 285 | 8 | 11 | 0 | 294 | 0 | 0 | 195 | 0 | 140 | 0 | 100 | 51 | 0 | 340 | 85 | 17 | 0 | 0 | 200 | 54 | 0 | 0 | 73 | 100 | 15 | 104 | 0 | 144 | 0 | 0 | 8 | 0 |  | 775 | 0 | 300 | 0 | 85 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 0 | 101 | 18 | 0 | 8 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 159 | 0 | 440 | 93 | 0 | 100 | 0 | 90 | 0 | 0 | 100 | 400 | 0 | 0 | 0 |  | 9283 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 40 | 0 | 0 | 0 | 360 | 300 | 220 | 8 | 50 | 26 | 5 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 150 | 82 | 22 | 0 | 30 | 22 | 51 | 50 | 163 | 100 | 0 | 74 | 0 | 100 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 420 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 90 | 104 | 0 | 144 | 116 | 100 |  |  |  | 828 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 229 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 35 | 0 | 0 | 0 | 360 | 300 | 220 | 8 | 50 | 26 | 5 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 150 | 82 | 22 | 1.6 | 30 | 22 | 51 | 50 | 163 | 100 | 0 | 74 | 0 | 100 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 420 | 115 | 105 | 8 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 80 | 104 | 50 | 144 | 116 | 100 |  | 30 |  | 539 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 229 | 0 | 400 | 95 | 100 | 113 | 100 | 113 | 0 | 8 | 35 | 620 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 368 | 343 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 20 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 20 | 32 | 0 | 0 | 0 | 290 | 280 | 170 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 62 | 140 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 101 | 0 | 69 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 0 | 0 | 44 | 0 | 0 | 134 | 0 | 15 | 5 | 75 | 17 | 0 | 407 | 0 | 0 | 0 | 1 | 248 | 0 | 0 | 0 | 0 | 100 | 90 | 0 | 8 | 144 | 0 | 0 | 0 | 6 | 0 | 530 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 162 | 0 | 417 | 0 | 0 | 27 | 0 | 30 | 0 | 1 | 0 | 470 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5993 | 5:00
| Highest Generation |  | 9283 | 19:00
| Day Peak Generation |  | 8337 | 12:00
| Evening Peak Generation |  | 9283 | 19:00
| HVDC Max Flow |  | 779 | 17:00
| HVDC EvPeak Flow |  | 775 | 19:00
| Load factor L.F |  | 84.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8337 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6000 | MW
Evening Peak Generation : |  | 9283 | MW Hour : | 19:00 | Available Max Generation : |  | 14068 | MW
E.P. Demand (at gen end) : |  | 9283 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 9283 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5068 | MW
Total Gen. (MKWH) : |  | 187.532 | System Load Factor : | 84.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -356 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-12
Actual : | 94.13 | Ft.(MSL) , | Rule curve : | 95.46 | Ft.( MSL )
Gas Consumed : | Total = | 881.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111746200.398
: |  | Coal : | 72073848 | Oil : | 304992813.47 | Total : | 488812861.868
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3255.7067 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1102.1017 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 986.5524 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 891.1158 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 805.4635 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 649.9679 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 369.8884 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 167.5202 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 501.2566 |  |  | 0 | 0%
Total | 0 |  | 8729.5732 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ashuganj-4,5
4) Shahjibazar 330 MW GT-2 & STG
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shahjibazar-B.Baria 132 kV Ckt-2 was under shut down from 08:28 to 09:53 for A/M.
b) Ghorasal-Joydevpur 132 kV Ckt-2 was under shut down from 08:44 to 17:55 for A/M.
c) Feni 132/33 kV T2 transformer tripped at 08:20 showing O/C,E/F relay and was switched on |  |  |  |  | About 30 MW power interruption occurred under Feni S/S
at 08:58. |  |  |  |  | areas from 08:20 to 08:58.
d) Baroierhat 132/33 kV T-2 transformer was under shut down from 09:17 to 18:01 for A/M.
e) Ramganj 132/33 kV T-2 transformers was under shut down from 09:09 to 12:54 for A/M.
f) Ramganj-Chandpur Desh 132 kV Ckt-2 was under shut down from 09:18 to 16:21 for A/M.
g) Mymensing-Bhaluka 132 kV Ckt-1 was under shut down from 09:57 to 10:59 for A/M.
h) Ashuganj-Shahjibazar 132 kV Ckt-3 was under shut down from 10:00 to 10:40 for A/M.
i) Aminbazar 230/132 kV T-2 transformers was under shut down from 10:16 to 13:26 for A/M.
j) Mymensing-Bhaluka 132 kV Ckt-2 was under shut down from 11:30 to 12:12 for A/M.
k) Baghabari-Shahjadpur 132 kV Ckt-1 was under shut down from 08:06 to 17:26 for A/M.
l) Sikalbaha-Bakulia 132 kV Ckt-2 was under shut down from 08:52 to 13:51 for A/M.
m) Cumilla(S)-Tripura 132 kV Ckt-2 was under shut down from 09:15 to 15:56 for A/M.
n) Bhaluka 132/33 kV T1 transformer was under shut down from 09:41 to 10:59 for A/M.
o) Bhaluka 132/33 kV T2 transformer was tripped at 10:41 and was switched on at 10:46. |  |  |  |  | About 78 MW power interruption occurred under Bhaluka S/S
p) Bhaluka 132/33 kV T2 transformer was under shut down from 11:09 to 11:57 for A/M. |  |  |  |  | areas from 10:41 to 10:46.
q) Tongi-Uttara 132 kV Ckt was under shut down from 09:53 to 14:02 for A/M.
r) Baghabari- Paramount 230 kV Ckt was under shut down from 08:45 to 16:45 for A/M.
s) Bogura-Naogaon 132 kV Ckt-2 was under shut down from 11:17 to 13:42 for A/M.
t) Hathazari-Baroierhat 132 kV Ckt-2 was under shut down from 11:51 to 13:37 for A/M.
u) Tongi 132/33 kV T2 transformer was under shut down from 12:16 to 15:10 for A/M.
v) Ramganj 132/33 kV T-1 transformers was under shut down from 12:58 to 15:48 for A/M.
w) Kallyanpur 132/33 kV T-1 transformers was under shut down from 10:51 to 13:28 for A/M.
x) Baroierhat -Feni 132 kV Ckt-1 was under shut down from 13:43 to 14:49 for A/M.
y) Ghorasal-Ashuganj 132 kV Ckt-2 was under shut down from 16:07 to 17:12 due to red hot maint
at Ashuganj end.
z) After maintenance Sylhet 225 MW GT was synchronized at 14:21.
aa) Bheramara HVDC 20DF13 230 kV shunt reactor trip at 15:09 and was switched on at 16:27.
ab) After maintenance Bibiyana South MW GT was synchronized at 16:43.
ac) Haripur-Maniknagar 132 kV Ckt was under shut down from 22:10 to 00:51(12-2-21) due to red |  |  |  |  | About 55 MW power interruption occurred under Bangabhaban,
hot maintenance at B phase LA joint at Maniknagar end. |  |  |  |  | Narinda S/S areas from 22:10 to 00:51.
ad) Halishahar 132/33 kV T1 & T3 transformer tripped at 23:50 from 33 kv side showing O/C,E/F |  |  |  |  | About 24 MW power interruption occurred under Halishahar
relay due to Agrabad 33 kV feeder fault and was switched on at 00:28. |  |  |  |  | S/S areas from 23:50 to 00:28.
ae) Sikalbaha-TK 132 kV Ckt was under shut down since 07:28(12-02-21) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4299750
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2438000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8558590 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 237 | 6878000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 86 | 697920 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6341644 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 1668240
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 682730
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 67 | 1267868 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 462672
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 847680 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 80 | 388080 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 407520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 240000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 465714
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 430861 | High Voltage.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1295160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 528500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 825300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 294 | 4960470
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 140 | 2051570 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 73812 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1462080
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3166560 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 124695
| Dhaka area Total |  |  |  | 5972 | 2616 | 50563416
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 120391
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 109890
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 493440 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1680000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 80 | 2536756
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 179818 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 337572 | High Voltage.
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 117240 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1955520
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 469104
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 528000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 281280 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29520
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 200 | 1400073 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 922664
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2220480
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 429055 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 862 | 13810803
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 3452000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7160000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6523000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 354888 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 323520 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 301090 | S/S maint. at Midland end
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | S/S maint. at Midland end
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | S/S maint. at Midland end
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 38 | 1077270 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 51 | 951840 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 404064
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 208260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 1966080
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821100
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 19219 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 494930
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 605640 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 8 | 95400
| Cumilla Area Total |  |  |  | 2980 | 1076 | 24758301
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2482960 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 511056
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 548160 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11050
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 3957600 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 85 | 548400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 236480
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 332400
| Mymensingh Area Total |  |  |  | 709 | 455 | 8628106
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 714000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 521520 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3550990 | High Voltage.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 2363000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1092600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1032336
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 228048
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1587840 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 735970 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 335000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 191232 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7345500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 340 | 9736000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 208080
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 15 | 245700
| Sylhet Area Total |  |  |  | 1988 | 1187 | 29887816
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 775 | 16728727
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 85 | 457920 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 19 | 145152 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 5742720 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 10875 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1266240 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1272 | 24351634
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 160704 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 485800 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 84 | 1084229
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 11871600
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 542 | 13602333
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 401600
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 6588 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 18 | 203770 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 8 | 97903 | Low demand
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 159 | 4884236 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 440 | 6457145
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 202328 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 496320
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242244
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 285120
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 500784
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 100 | 1965216
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 1119264
| Rajshahi Area Total |  |  |  | 2183 | 1033 | 16862518
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 90 | 1356480 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28426
| Rangpur Area Total |  |  |  | 605 | 240 | 5067106
| Total |  |  |  | 20929 | 9283 | 187532033
| Eastern Grid Total |  |  |  | 14031 | 6196 | 127648442
| Western Grid Total |  |  |  | 6898 | 3087 | 59883591
| National Grid Total |  |  |  | 20929 | 9283 | 187532033
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-11
(a) ENTIRE EASTERN GRID : |  | 6027 | MW | (b) ENTIRE WESTERN GRID : |  | 2970 | MW
i) Dhaka area |  | 3135 | MW | i) Khulna area |  | 1117 | MW
ii) Chittagong area |  | 979 | MW | ii) Rajshahi area |  | 956 | MW
iii) Comilla area |  | 757 | MW | iii) Barisal area |  | 239 | MW
iv) Mymensingh area |  | 824 | MW | iv) Rangpur area |  | 658 | MW
v) Sylhet area |  | 332 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8997 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 94 | 9:00 | Sherpur | 114 | 18:30 | Jhenida | 80 | 18:30
Munsiganj | 82 | 19:30 | Srimongal | 42 | 18:00 | Bottail | 106 | 18:30
Sonargaon | 64 | 12:00 | Shahjibazar | 74 | 18:30 | G.K Project | 31 | 18:30
Shyampur | 154 | 10:00 | Fenchuganj | 25 | 18:00 | Faridpur | 134 | 18:30
Bhulta | 158 | 19:30 | Kulawara | 27 | 18:30 | Madaripur | 62 | 21:00
Madanganj | 45 | 16:00 | Sylhet | 83 | 18:00 | Sariatpur | 42 | 20:00
Shitalakhya | 106 | 11:00 | Chatak | 21 | 19:00 | Gopalganj | 60 | 18:30
Rahim steel | 25 | 13:00 | Sunamganj | 28 | 19:30 | Bagerhat | 81 | 18:30
Matuail | 93 | 12:00 | Biani Bazar | 40 | 18:30 | Mongla | 38 | 12:00
Ghorasal | 65 | 19:00 | Comilla (S) | 106 | 18:00 | Satkhira | 73 | 18:30
Narsingdi | 126 | 19:30 | Comilla(N) | 77 | 20:00 | Gallamari | 21 | 12:00
Haripur (SBU) | 96 | 15:00 | Chandpur | 44 | 18:30 | Magura | 40 | 18:30
Ullon | 58 | 19:00 | Feni | 85 | 18:30 | Norail | 24 | 18:30
Hasnabad | 85 | 15:00 | Chowmuhani | 120 | 19:00 | Chuadanga | 64 | 18:30
Magbazar | 64 | 13:00 | Ashuganj | 41 | 18:30 | Borguna | 12 | 19:30
Maniknagar | 54 | 12:00 | Daudkandi | 82 | 21:00 | Barisal(N) | 27 | 18:30
Bangabhaban | 13 | 10:00 | B.Baria | 107 | 19:00 | Barisal (S) | 78 | 19:00
Narinda | 58 | 19:00 | Ramganj | 52 | 18:30 | Patuakhali | 75 | 20:00
Dhanmondi | 123 | 13:00 | Chaddagram | 21 | 18:00 | Bhandaria | 36 | 19:00
Lalbag | 63 | 18:30 | PHP | 5 | 8:00 | Borhan Uddin | 26 | 21:00
Madartek | 55 | 18:30 | Kochua | 38 | 18:00 | Ishurdi | 47 | 18:30
Dhaka University | 0 | #NUM! | Madunaghat | 54 | 18:30 | Ruppur Paromanobik | 3 | 18:00
Aftabnagar | 7 | 13:00 | Hathazari | 56 | 19:00 | Natore | 96 | 18:30
Fatullah | 47 | 10:00 | Khulshi | 168 | 13:00 | Bogra | 122 | 19:30
Mirpur | 73 | 18:00 | Halishahar | 92 | 18:30 | Noagaon | 88 | 8:00
Kalyanpur | 72 | 18:00 | Baraulia | 146 | 1:00 | Rajshahi | 94 | 20:00
Gulshan | 80 | 18:00 | Sikalbaha | 18 | 18:30 | Rajshahi New | 13 | 18:30
Uttara | 63 | 18:00 | Dohazari | 70 | 19:30 | C.Nawabganj | 72 | 12:00
Uttara New | 24 | 18:00 | Cox'sbazar | 76 | 18:00 | Amnura | 41 | 18:30
Kamrangirchar | 88 | 18:00 | Chandraghona | 24 | 18:00 | Pabna | 66 | 18:30
Savar | 113 | 15:00 | Kaptai | 0 | 1:00 | Shahjadpur | 84 | 19:00
Bhasantec | 104 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 75 | 9:00
Agargaon | 45 | 18:00 | Bakulia | 70 | 18:30 | Niyamatpur | 70 | 9:00
Satmosjid | 55 | 18:00 | Julda | 18 | 8:00 | Joypurhat | 62 | 10:00
Tongi | 79 | 11:00 | TK chemical | 20 | 18:30 | Sherpur(Bogura) | 46 | 8:00
Kabirpur | 184 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 34 | 8:00
Basundhara | 94 | 18:30 | Shahmirpur | 17.7 | 18:00 | Bangura | 14 | 8:00
Manikganj | 56 | 19:00 | Khagrachhari | 18 | 18:30 | Rangpur | 116 | 19:00
Joydevpur | 104 | 17:00 | Matarbari | 27 | 18:30 | Lalmonirhat | 58 | 12:00
New Tongi | 98 | 12:00 | Baroiar Hat | 33 | 18:00 | Saidpur | 106 | 10:00
Korda | 168 | 19:00 | Rangamati | 8 | 12:00 | Purbasadipur | 97 | 13:00
Dhamrai | 72 | 18:30 | Abul Khair 230 | 163 | 22:00 | Thakurgaon | 65 | 19:30
Rajendrapur | 78 | 19:00 | BSRM | 148 | 11:00 | Palashbari | 102 | 8:00
Valuka | 88 | 9:00 | GPH Ispat | 85 | 15:00 | Barapukuria | 51 | 10:00
Tangail | 169 | 18:30 | Goalpara | 11 | 12:00 | Panchagar | 45 | 19:00
Mymensing | 178 | 18:30 | Central s/s | 81 | 18:30 | Joldhaka | 25 | 8:00
Kishorganj | 98 | 18:30 | Noapara | 49 | 19:00 | Kurigram | 45 | 18:30
Netrokona | 100 | 8:00 | Jessore | 88 | 18:30
Jamalpur | 122 | 18:30 | Benapol | 42 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 18:30 | 405 | 12:00 | Kaliakoir | 406 | 0.25 | 398 | 0.66667
| Bheramara | 406 | 4:00 | 395 | 10:00 | Bhulta | 398 | 0.77083 | 387 | 0.5
| Ashuganj(N) | 402 | 1:00 | 391 | 16:00 | Gopalganj | 402 | 0.625 | 388 | 0.54167
| Payra | 409 | 8:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 233 | 21:00 | 215 | 15:00
| Ishurdi | 240 | 18:00 | 226 | 8:00 | Megnaghat | 242 | 1:00 | 232 | 16:00
| Ashuganj | 245 | 18:00 | 237 | 16:00 | Fenchuganj | 242 | 5:00 | 239 | 11:00
| Serajganj | 235 | 18:30 | 223 | 9:00 | Siddhirganj | 240 | 1:00 | 233 | 16:00
| Baghabari | 238 | 5:00 | 226 | 12:00 | Maniknagar | 0 | 8:00 | 0 | 1:00
| Barapukuria | 235 | 1:00 | 223 | 8:00 | Agargaon | 240 | 5:00 | 231 | 16:00
| Bogra | 233 | 4:00 | 218 | 8:00 | Barisal | 253 | 9:00 | 239 | 13:00
| Rajshahi | 238 | 4:00 | 219 | 8:00 | Bhola 225 MW | 255 | 19:00 | 242 | 13:00
| Khulna South | 241 | 18:00 | 224 | 7:00 | AKSML | 232 | 9:00 | 219 | 12:00
| Rampura | 235 | 5:00 | 230 | 17:00 | BSRM | 236 | 18:30 | 219 | 16:00
| Haripur | 239 | 7:00 | 232 | 16:00 | Bibiyana | 246 | 8:00 | 237 | 17:00
| Hasnabad | 236 | 7:00 | 231 | 16:00 | Bhulta | 242 | 20:00 | 234 | 16:00
| Shyampur | 239 | 8:00 | 220 | 16:00 | Ashuganj (S) | 240 | 1:00 | 235 | 12:00
| Aminbazar | 241 | 20:00 | 235 | 12:00 | Kaliakoir | 238 | 18:00 | 232 | 16:00
| Tongi | 236 | 13:00 | 230 | 15:00 | GPH | 233 | 21:00 | 215 | 22:00
| Comilla (N) | 237 | 8:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 8:00 | 135 | 16:00 | Madanhat | 141 | 0.77083 | 130 | 0.66667
| Munsiganj | 142 | 18:00 | 135 | 16:00 | Hathazari | 137 | 0.33333 | 130 | 0.625
| Sonargaon | 139 | 19:00 | 135 | 1:00 | Khulshi | 138 | 0.77083 | 128 | 0.66667
| Shyampur | 136 | 19:30 | 130 | 16:00 | Halishahar | 139 | 0.77083 | 128 | 0.66667
| Bhulta | 136 | 4:00 | 129 | 12:00 | Baraulia | 136 | 0.8125 | 127 | 0.66667
| Madanganj | 141 | 19:00 | 135 | 16:00 | Sikalbaha | 140 | 0.77083 | 131 | 0.20833
| Shitalakhya | 141 | 18:30 | 129 | 16:00 | Dohazari | 135 | 0.79167 | 126 | 0.66667
| Rahim steal | 139 | 7:00 | 134 | 16:00 | Cox'sbazar | 130 | 0.29167 | 123 | 0.20833
| Matuail | 140 | 8:00 | 135 | 16:00 | Chandraghona | 138 | 0.77083 | 128 | 0.66667
| Ghorasal | 142 | 1:00 | 140 | 16:00 | Kaptai
| Narsinghdi | 136 | 18:00 | 132 | 16:00 | A. Khaer Stl. | 135 | 0.83333 | 130 | 0.5
| Haripur (SBU) | 139 | 18:30 | 135 | 19:00 | Bakulia | 137 | 0.77083 | 128 | 0.66667
| Ullon | 135 | 7:00 | 130 | 15:00 | Julda | 138 | 0.77083 | 131 | 0.5
| Hasnabad | 137 | 19:30 | 129 | 16:00 | TK Chemical | 138 | 0.77083 | 130 | 0.625
| Magbazar | 136 | 3:00 | 130 | 12:00 | Modern Steel | 135 | 0.041667 | 132 | 0.20833
| Maniknagar | 138 | 4:00 | 132 | 16:00 | Shahmirpur | 139 | 0.77083 | 131 | 0.5
| Bangabhaban | 138 | 4:00 | 132 | 16:00 | Khagrachhari | 138 | 0.77083 | 129 | 0.5
| Narinda | 138 | 4:00 | 132 | 16:00 | Matarbari | 131 | 0.875 | 125 | 0.5
| Dhanmondi | 135 | 7:00 | 130 | 15:00 | Baroiar Hat | 138 | 0.29167 | 133 | 0.58333
| Lalbag | 139 | 8:00 | 130 | 16:00 | Rangamati | 138 | 18:30 | 128 | 16:00
| Madartek | 135 | 4:00 | 129 | 16:00 | Goalpara S/S | 138 | 18:30 | 127 | 20:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 18:00 | 128 | 0.83333
| Aftabnagar | 135 | 1:00 | 131 | 12:00 | Noapara | 136 | 18:00 | 126 | 0.54167
| Fatullah | 136 | 18:00 | 131 | 16:00 | Jessore | 133 | 18:00 | 120 | 0.29167
| Mirpur | 138 | 6:00 | 133 | 12:00 | Benapol | 134 | 0.75 | 124 | 0.54167
| Kalyanpur | 139 | 6:00 | 136 | 12:00 | Jhenida | 133 | 3:00 | 120 | 0.54167
| Gulshan | 135 | 6:00 | 130 | 12:00 | Bottail | 137 | 0.16667 | 125 | 0.54167
| Uttara | 137 | 6:00 | 136 | 12:00 | G.K Project | 141 | 0.20833 | 132 | 0.5
| Uttara New | 138 | 6:00 | 136 | 12:00 | Faridpur | 138 | 0.75 | 132 | 0.5
| Kamrangirchar | 134 | 6:00 | 130 | 12:00 | Madaripur | 144 | 0.16667 | 136 | 0.875
| Savar | 139 | 6:00 | 136 | 12:00 | Shariyatpur S/S | 142 | 7:00 | 135 | 0.54167
| Bhasantec | 138 | 6:00 | 133 | 12:00 | Gopalganj | 145 | 0.75 | 137 | 0.54167
| Agargaon | 136 | 6:00 | 132 | 12:00 | Bagerhat | 135 | 18:30 | 125 | 0.8125
| Satmosjid | 137 | 6:00 | 133 | 12:00 | Mongla | 135 | 18:30 | 125 | 0.8125
| Tongi | 140 | 21:00 | 137 | 15:00 | Satkhira | 136 | 18:30 | 126 | 7:00
| Kabirpur | 135 | 1:00 | 129 | 12:00 | Gallamari | 138 | 0.77083 | 128 | 0.29167
| Basundhara | 141 | 13:00 | 134 | 16:00 | Magura | 133 | 4:00 | 120 | 0.54167
| Manikganj | 144 | 18:30 | 136 | 16:00 | Narail | 133 | 0.16667 | 120 | 0.54167
| Joydevpur | 140 | 0:00 | 134 | 13:00 | Chuadanga | 132 | 4:00 | 117 | 0.54167
| New Tongi | 140 | 18:00 | 135 | 15:00 | Borguna | 142 | 6:00 | 134 | 0.5
| Kodda | 139 | 18:30 | 132 | 2:00 | Barisal(N) | 143 | 5:00 | 134 | 13:00
| Dhamrai | 135 | 1:00 | 129 | 12:00 | Barisal (S) | 144 | 0.16667 | 134 | 0.54167
| Rajendrapur | 138 | 18:30 | 131 | 17:00 | Patuakhali(S) | 139 | 0.625 | 131 | 0.54167
| Valuka | 131 | 1:00 | 119 | 12:00 | Bhandaria | 140 | 0.20833 | 135 | 0.5
| Tangail | 132 | 1:00 | 127 | 8:00 | Ishurdi | 139 | 2:00 | 131 | 11:00
| Mymensing | 132 | 1:00 | 123 | 14:00 | Ruppur Paromanobik | 139 | 4:00 | 130 | 7:00
| Kishorganj | 132 | 1:00 | 127 | 8:00 | Natore | 137 | 2:00 | 128 | 8:00
| Netrokona | 130 | 1:00 | 121 | 9:00 | Bogra | 138 | 2:00 | 125 | 9:00
| Jamalpur | 139 | 22:00 | 129 | 5:00 | Noagaon | 133 | 4:00 | 114 | 13:00
| Sherpur | 137 | 20:00 | 126 | 7:00 | Rajshahi | 137 | 18:00 | 126 | 13:00
| Srimongal | 140 | 3:00 | 137 | 12:00 | Rajshahi New | 137 | 3:00 | 126 | 8:00
| Shahjibazar | 137 | 1:00 | 134 | 12:00 | C.Nawabganj | 136 | 18:00 | 121 | 8:00
| Fenchuganj | 140 | 10:00 | 137 | 12:00 | Amnura | 138 | 18:30 | 124 | 12:00
| Khulawara | 139 | 5:00 | 135 | 13:00 | Pabna | 138 | 5:00 | 129 | 9:00
| Sylhet | 137 | 1:00 | 133 | 11:00 | Shahjadpur | 141 | 4:00 | 132 | 9:00
| Chatak | 136 | 1:00 | 132 | 10:00 | Serajganj | 137 | 3:00 | 125 | 9:00
| Sunamganj | 136 | 2:00 | 131 | 12:00 | Niyamatpur | 131 | 3:00 | 112 | 8:00
| Biani Bazar | 137 | 1:00 | 132 | 12:00 | Joypurhat | 135 | 3:00 | 112 | 13:00
| Comilla(s) | 131 | 2:00 | 121 | 12:00 | Sherpur(Bogura) | 138 | 3:00 | 124 | 8:00
| Comilla(n) | 143 | 19:00 | 139 | 16:00 | Mohastangor | 136 | 2:00 | 123 | 8:00
| Chandpur | 143 | 8:00 | 141 | 17:00 | Bangura | 140 | 4:00 | 132 | 8:00
| Feni | 140 | 20:00 | 135 | 17:00 | Rangpur | 133 | 4:00 | 120 | 8:00
| Chowmuhani | 139 | 19:00 | 135 | 16:00 | Lalmonirhat | 132 | 4:00 | 116 | 8:00
| Ashuganj | 139 | 1:00 | 136 | 9:00 | Saidpur | 132 | 5:00 | 118 | 9:00
| Daudkandi | 141 | 7:00 | 136 | 17:00 | Purbasadipur | 132 | 3:00 | 112 | 9:00
| B.Baria | 134 | 18:00 | 132 | 10:00 | Thakurgaon | 132 | 4:00 | 114 | 8:00
| Ramganj | 138 | 9:00 | 133 | 12:00 | Palashbari | 133 | 3:00 | 119 | 9:00
| Chaddagram | 141 | 8:00 | 136 | 16:00 | Barapukuria | 135 | 1:00 | 123 | 8:00

## L-Curve
Date | 2021-02-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 186 | 4819 | 2409 | 7228 |  |  |  | QF-LDC-11
0:30 | 96.5 | 4763 | 2240.5 | 7003.5 | Date: | 2021-02-11
1:00 | 7 | 4707 | 2072 | 6779
1:30 | 48 | 4616 | 2011 | 6627
2:00 | 89 | 4525 | 1950 | 6475
2:30 | 92 | 4420.5 | 1958.5 | 6379 | [5 empty] | Gen. at Eve. Peak | 9283 | 9283 MW (19:00 )
3:00 | 95 | 4316 | 1967 | 6283 | [6 empty] | 19:00
3:30 | 102.5 | 4187 | 1965 | 6152 | [5 empty] | Gen. at Day Peak | 8337 | 8337 MW (12:00 )
4:00 | 110 | 4058 | 1963 | 6021 | [6 empty] | 12:00
4:30 | 117.5 | 4066 | 1941 | 6007 | [5 empty] | Highest Generation | 9283
5:00 | 125 | 4074 | 1919 | 5993 | [6 empty] | 19:00
5:30 | 128 | 4160.5 | 2037.5 | 6198
6:00 | 131 | 4247 | 2156 | 6403
6:30 | 155.5 | 4429.5 | 2136 | 6565.5
7:00 | 180 | 4612 | 2116 | 6728
7:30 | 268 | 4943.5 | 2212.5 | 7156
8:00 | 356 | 5275 | 2309 | 7584
8:30 | 309.5 | 5464 | 2320 | 7784
9:00 | 263 | 5653 | 2331 | 7984
9:30 | 170.5 | 5712 | 2383.5 | 8095.5
10:00 | 78 | 5771 | 2436 | 8207
10:30 | 54.5 | 5704.5 | 2455 | 8159.5
11:00 | 31 | 5638 | 2474 | 8112
11:30 | 43 | 5750 | 2474.5 | 8224.5
12:00 | 55 | 5862 | 2475 | 8337
12:30 | 87.5 | 5910 | 2484.5 | 8394.5
13:00 | 120 | 5958 | 2494 | 8452
13:30 | 104 | 5824.5 | 2396.5 | 8221
14:00 | 88 | 5691 | 2299 | 7990
14:30 | 129.5 | 5599.5 | 2365 | 7964.5
15:00 | 171 | 5508 | 2431 | 7939
15:30 | 287 | 5383 | 2502 | 7885
16:00 | 403 | 5258 | 2573 | 7831
16:30 | 364.5 | 5189.5 | 2557 | 7746.5
17:00 | 326 | 5121 | 2541 | 7662
17:30 | 225 | 5349.5 | 2688.5 | 8038
18:00 | 124 | 5578 | 2836 | 8414
18:30 | 62.5 | 5887 | 2961.5 | 8848.5
19:00 | 1 | 6196 | 3087 | 9283
19:30 | 0 | 6151 | 3079 | 9230
20:00 | 0 | 6094 | 3044 | 9138 |  |  |  | Executive Engineer
20:30 | 21.5 | 5999.5 | 3023.5 | 9023 |  |  |  | Network Operation Division
21:00 | 43 | 5905 | 3003 | 8908
21:30 | 81 | 5694.5 | 2908.5 | 8603
22:00 | 119 | 5484 | 2814 | 8298 |  |  |  |  | Page 6 of 7
22:30 | 127 | 5332.5 | 2701.5 | 8034
23:00 | 135 | 5181 | 2589 | 7770
23:30 | 160.5 | 5000 | 2499 | 7499
24:00 | 186 | 4819 | 2409 | 7228
9283 MW (19:00 )
8337 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-11 |  | Energy | 187532033
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 2814 | 775 | 1470 | 1685 | 680 | 70 | 0 | 0 | 84 | 0
0:30 | 2772 | 653 | 1475.5 | 1454.5 | 669.5 | 70 | 4 | 0 | 80 | 0 | Date: | 2021-02-11
1:00 | 2730 | 531 | 1481 | 1224 | 659 | 70 | 8 | 0 | 76 | 0
1:30 | 2739 | 530.5 | 1476.5 | 1076 | 654 | 70 | 8 | 0 | 73 | 0 | [7 empty] | Total Energy | 187.532 | Total Energy Gen 187.532 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.532 MKWHr
2:00 | 2748 | 530 | 1472 | 928 | 649 | 70 | 8 | 0 | 70 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2760.5 | 530 | 1472.5 | 821 | 649 | 70 | 8 | 0 | 68 | 0 | [7 empty] | Energy Requirement | 187.532
3:00 | 2773 | 530 | 1473 | 714 | 649 | 70 | 8 | 0 | 66 | 0
3:30 | 2776.5 | 530 | 1426.5 | 642.5 | 634.5 | 70 | 8 | 0 | 64 | 0 | [6 empty] | Shortage
4:00 | 2780 | 530 | 1380 | 571 | 620 | 70 | 8 | 0 | 62 | 0
4:30 | 2780.5 | 530.5 | 1380 | 570 | 605 | 70 | 8 | 0 | 63 | 0
5:00 | 2781 | 531 | 1380 | 569 | 590 | 70 | 8 | 0 | 64 | 0
5:30 | 2813.5 | 625 | 1391.5 | 638 | 590 | 70 | 4 | 0 | 66 | 0
6:00 | 2846 | 719 | 1403 | 707 | 590 | 70 | 0 | 0 | 68 | 0
6:30 | 2871 | 719 | 1319 | 941 | 575 | 70 | 0 | 0 | 69 | 1.5 |  |  |  |  | Coal
7:00 | 2896 | 719 | 1235 | 1175 | 560 | 70 | 0 | 0 | 70 | 3
7:30 | 2888.5 | 718.5 | 1241 | 1566 | 575 | 70 | 8 | 0 | 76 | 13 |  |  |  | Oil |  |  |  | ,
8:00 | 2881 | 718 | 1247 | 1957 | 590 | 70 | 16 | 0 | 82 | 23
8:30 | 2835 | 718.5 | 1241.5 | 2194 | 590 | 70 | 16 | 0 | 83 | 36
9:00 | 2789 | 719 | 1236 | 2431 | 590 | 70 | 16 | 0 | 84 | 49
9:30 | 2825.5 | 718.5 | 1238 | 2474 | 590 | 70 | 38.5 | 0 | 82.5 | 58.5
10:00 | 2862 | 718 | 1240 | 2517 | 590 | 70 | 61 | 0 | 81 | 68
10:30 | 2806 | 718.5 | 1233 | 2522.5 | 590 | 70 | 75 | 0 | 79.5 | 65
11:00 | 2750 | 719 | 1226 | 2528 | 590 | 70 | 89 | 0 | 78 | 62
11:30 | 2824.5 | 719 | 1235.5 | 2538.5 | 590 | 70 | 90 | 0 | 80.5 | 76.5
12:00 | 2899 | 719 | 1245 | 2549 | 590 | 70 | 91 | 0 | 83 | 91
12:30 | 2902.5 | 719 | 1268.5 | 2576.5 | 605 | 70 | 91 | 0 | 84 | 78
13:00 | 2906 | 719 | 1292 | 2604 | 620 | 70 | 91 | 0 | 85 | 65
13:30 | 2906 | 719 | 1292 | 2604 | 620 | 70 | 91 | 0 | 85 | 65
14:00 | 2906 | 719 | 1292 | 2604 | 620 | 70 | 91 | 0 | 85 | 65
14:30 | 2829.5 | 719 | 1312 | 2432.5 | 590 | 70 | 97 | 0 | 84.5 | 61
15:00 | 2753 | 719 | 1332 | 2261 | 560 | 70 | 103 | 0 | 84 | 57
15:30 | 2880.5 | 719 | 1350.5 | 2092 | 560 | 70 | 87 | 0 | 82 | 44
16:00 | 3008 | 719 | 1369 | 1923 | 560 | 70 | 71 | 0 | 80 | 31
16:30 | 2972.5 | 749 | 1372.5 | 1857 | 560 | 70 | 68.5 | 0 | 78 | 19
17:00 | 2937 | 779 | 1376 | 1791 | 560 | 70 | 66 | 0 | 76 | 7
17:30 | 2882.5 | 777 | 1444 | 2046.5 | 530 | 70 | 193.5 | 0 | 91 | 3.5
18:00 | 2828 | 775 | 1512 | 2302 | 500 | 70 | 321 | 0 | 106 | 0
18:30 | 2815 | 775 | 1519.5 | 2730 | 525 | 70 | 308 | 0 | 106 | 0
19:00 | 2802 | 775 | 1527 | 3158 | 550 | 70 | 295 | 0 | 106 | 0
19:30 | 2870 | 775 | 1553 | 2946 | 630 | 70 | 280 | 0 | 106 | 0
20:00 | 2852 | 775 | 1587 | 2872 | 650 | 70 | 228 | 0 | 104 | 0
20:30 | 2838.5 | 775.5 | 1574.5 | 2767.5 | 665 | 70 | 228 | 0 | 104 | 0
21:00 | 2825 | 776 | 1562 | 2663 | 680 | 70 | 228 | 0 | 104 | 0
21:30 | 2825 | 775.5 | 1544 | 2433 | 679.5 | 70 | 175 | 0 | 101 | 0
22:00 | 2825 | 775 | 1526 | 2203 | 679 | 70 | 122 | 0 | 98 | 0
22:30 | 2859.5 | 775 | 1527.5 | 1944 | 679.5 | 70 | 83.5 | 0 | 95 | 0
23:00 | 2894 | 775 | 1529 | 1685 | 680 | 70 | 45 | 0 | 92 | 0
23:30 | 2854 | 775 | 1499.5 | 1685 | 680 | 70 | 22.5 | 0 | 88 | 0 | Max Temp. in Dhaka |  | 29.0° C
24:00 | 2814 | 775 | 1470 | 1685 | 680 | 70 | 0 | 0 | 84 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.532 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.532 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1680000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 6 |  | 25 | 8 | 8 | 8 |  |  |  | 120391
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 16 | 16 |  | 12 | 7 | 2 | [9 empty] | 109890
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 116 | 125 | 118 | 115 | 113 | 117 | 126 | 116 | 115 | 80 | 120 | 120 | 120 | 120 | 80 | 80 | 80 | 80 |  | 80 | 115 | 114 | 113 | 113 | 114 | 113 | 2536756
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 81 |  | 85 | 85 | 85 | 85 |  |  |  | 337572
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 2 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 179818
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 30 | 30 | 30 | 30 | 40 | 87 | 155 | 263 | 278 | 288 | 286 | 273 | 285 | 285 | 267 | 255 | 274 |  | 294 | 300 | 300 | 300 | 300 | 200 | 100 | 4960470
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 301090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 100 | 100 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4299750
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 23 | 23 | 23 | 23 | 10 | 10 | 10 | 10 | 26 | 26 | 23 | 20 | 20 | 26 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 354888
33 | Ashuganj 225 MW CCPP | 35 | 36 | 39 | 40 | 40 | 45 | 123 | 164 | 195 | 230 | 184 | 197 | 200 | 197 | 187 | 172 | 158 | 180 |  | 187 | 191 | 191 | 195 | 184 | 168 | 152 | 3452000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 275 | 290 | 320 | 250 | 260 | 250 | 250 | 310 | 275 | 270 | 255 | 270 | 255 | 250 |  | 250 | 260 | 255 | 250 | 250 | 295 | 270 | 6523000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 280 | 300 | 325 | 265 | 275 | 380 | 295 | 355 | 320 | 315 | 280 | 295 | 265 | 260 |  | 260 | 265 | 260 | 260 | 260 | 290 | 260 | 7160000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 323520
36 | Chandpur 150 MW CCPP | 51 | 48 | 50 | 52 | 50 | 50 | 51 | 50 | 51 | 48 | 47 | 50 | 50 | 51 | 48 | 40 | 42 | 40 |  | 38 | 40 | 36 | 40 | 40 | 40 | 40 | 1077270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 346 | 341 | 350 | 348 | 370 | 355 | 362 | 348 | 348 | 345 | 353 | 374 | 345 | 371 | 348 | 349 | 346 |  | 349 | 342 | 341 | 342 | 341 | 346 | 364 | 8558590
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 320 | 333 | 345 | 353 | 353 | 354 | 323 | 337 | 307 | 305 | 292 | 292 | 267 | 261 | 262 | 262 | 252 | 240 |  | 237 | 233 | 233 | 231 | 232 | 231 | 244 | 6878000
42 | RPCL 210MW CCPP | 107 | 108 | 108 | 108 | 109 | 109 | 110 | 110 | 107 | 108 | 106 | 104 | 97 | 92 | 101 | 103 | 103 | 104 |  | 106 | 107 | 107 | 107 | 108 | 107 | 107 | 2482960
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 10 | 20 | 28 | 35 | 38 | 38 | 32 | 22 | 11 | 3 | [9 empty] | 236480
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 521520
46 | Shajibazar 330 MW CCPP | 100 | 100 | 100 | 99 | 99 | 99 | 101 | 101 | 100 | 100 | 101 | 99 | 100 | 101 | 100 | 100 | 99 | 102 |  | 101 | 100 | 100 | 100 | 101 | 99 | 100 | 2363000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 71 | 71 | 71 | 40 | 40 | 40 | 40 | 66 | 67 | 67 | 69 | 69 | 69 | 69 | 70 | 70 | 70 | 73 |  | 73 | 73 | 73 | 73 | 74 | 74 | 74 | 1587840
| Shahjibazar 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [14 empty] | 60 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 735970
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [8 empty] | 335000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 208080
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228048
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 14 | 14 | 14 | 14 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1092600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191232
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 290 | 300 | 300 | 320 | 280 | 290 | 300 | 290 | 285 | 300 | 315 | 290 | 300 | 290 | 300 | 300 |  | 285 | 310 | 285 | 290 | 280 | 300 | 310 | 7345500
| Bibiyana South 400 MW | [16 empty] | 15 | 15 |  | 15 | 20 | 20 | 30 | 30 | 64 | 59 | 245700
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 430861
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 8 | 18 | 18 | 18 | 22 | 24 | 23 | 23 | 19 | 20 | 19 | 23 |  | 23 | 23 | 23 | 23 | 23 |  |  | 332400
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 469104
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 462672
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511056
63 | Impoprt (Tripura) | 76 | 70 | 66 | 62 | 64 | 68 | 70 | 82 | 84 | 81 | 78 | 83 | 85 | 87 | 84 | 80 | 76 | 106 |  | 106 | 106 | 104 | 104 | 98 | 92 | 84 | 1966080
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 41 | 41 | 41 | 41 | 38 | 12 | 4 | 3 | 2 | 2 | 6 | 3 | 2 | 3 | 7 | 19 |  | 24 | 26 | 26 | 32 | 37 | 38 | 7 | 528000
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 |  |  | 14 | 16 | 16 | 15 | 18 | 19 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 404064
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 208260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 32 | 32 | 20 | 28 | 28 | 28 | 31 | 31 | 20 |  | 31 | 32 | 32 | 32 | 32 | 32 | 33 | 695160
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 825300
73 | Ghorashal 108MW PP (Regent) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 103 | 103 | 99 | 101 | 101 | 105 | 105 | 102 | 99 | 102 | 102 |  | 102 | 104 | 105 | 105 | 105 | 105 | 105 | 2438000
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [7 empty] | 12 | 26 | 26 | 26 | 26 | 47 | 55 | 55 | 26 | 26 | 33 |  | 73 | 55 | 26 | 26 |  |  |  | 605640
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 125 | 79 | 72 | 72 | 72 | 119 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3166560
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 1 | 32 | 40 | 40 | 40 | 40 | 50 | 70 | 70 | 30 | 15 | 30 |  | 90 | 100 | 100 | 70 | 40 |  |  | 847680
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 40 |  | 32 | 32 | 16 | 16 |  |  |  | 240000
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 5 | 40 | 56 | 40 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 60 | 30 |  | 548160
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 8 | [8 empty] | 19219
| Gazipur 100 MW PP | [17 empty] | 25 |  | 17 | [6 empty] | 73812
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 29520
| Jodiac Power | 35 | 17 | 17 |  |  | 4 | 44 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 17 | 17 | 17 | 42 | 17 |  | 922664
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 15 | 15 | 15 | 15 | 16 | 40 | 65 | 94 | 99 | 99 | 99 | 96 | 92 | 99 | 64 | 64 | 75 |  | 100 | 100 | 100 | 81 | 81 | 64 | 30 | 1668240
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | 25 | 10 | 10 | 10 | 12 | 53 | 64 | 61 | 60 | 62 | 60 | 60 | 60 | 68 | 48 | 40 | 42 |  | 67 | 75 | 75 | 75 | 72 | 71 | 50 | 1267868
86 | Meghnaghat CCPP(Summit) | 270 | 270 | 240 | 260 | 265 | 270 | 285 | 250 | 270 | 265 | 275 | 275 | 265 | 250 | 240 | 255 | 280 | 275 |  | 270 | 275 | 275 | 280 | 275 | 285 | 250 | 6341644
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 6 | 27 | 40 | 40 | 40 | 40 | 56 | 65 | 65 | 35 | 24 | 25 |  | 86 | 80 | 70 | 24 |  |  |  | 697920
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 17 | 82 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 78 | 53 | 58 |  | 104 | 104 | 104 | 70 | 70 |  |  | 1462080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 |  | 10 | 10 | [8 empty] | 117240
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 28 | 46 | 50 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1032336
93 | Ashuganj 51 MW PP (Midland) | [26 empty] | 0
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 3 | 24 | 24 | 24 | 24 | 24 | 32 | 24 |  |  |  | 24 |  | 80 | 32 | 7 | 7 |  |  |  | 388080
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 2 |  | 22 | 25 | 29 | 39 | 39 | 39 | 39 | 493440
96 | Chattogram 108 MW PP (ECPV) | [7 empty] | 1 | 25 | 31 | 12 | 12 | 12 | 17 | 15 |  | 1 | 52 |  | 82 | [6 empty] | 281280
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 16 | 35 | 55 | 55 | 54 | 55 | 55 | 40 | 40 | 15 | 15 | 30 |  | 55 | 55 | 55 | 30 | 15 |  |  | 682730
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 17 | 17 | 17 |  | 55 | 35 | 17 | 17 |  |  |  | 465714
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 110 | 110 | 110 | 110 | 163 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 163 | 163 | 163 | 130 | 110 | 3550990
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 11050
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 54 | 35 | 17 | 17 | 17 | 30 |  | 54 | 54 | 54 | 35 | 35 |  |  | 407520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 140 | 70 | 50 | 50 | 50 | 134 | 185 | 191 | 195 | 195 | 195 | 195 | 183 | 173 | 183 | 183 | 195 |  | 195 | 195 | 195 | 195 | 200 | 200 | 200 | 3957600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 16 | [5 empty] | 30 | 74 | 139 | 149 | 149 | 149 | 149 | 135 | 115 | 106 | 100 | 104 |  | 140 | 115 | 127 | 104 | 102 | 79 | 53 | 2051570
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 50 | 10 | 10 | 10 | 50 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1955520
116 | Chandpur 200MW (Desh energy) | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 34 | 34 | 34 | 34 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 951840
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 373 | 374 | 374 | 351 | 420 | 421 | 421 | 375 | 376 | 427 | 415 | 387 | 376 | 376 | 353 |  | 340 | 371 | 375 | 374 | 411 | 408 | 397 | 9736000
| Jamalpur 115 MW PP (United) | [7 empty] | 24 | 24 | 24 | 24 | 40 | 45 | 16 | 16 | 16 | 16 | 20 |  | 85 | 85 | 85 | 55 |  |  |  | 548400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 83 |  | 200 | 290 | 300 | 301 | 106 | 106 | 105 | 1400073
| Juldah unit-2 (Acorn) | 100 | 100 | 70 | 30 | 30 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2220480
| Anlima Energy Ltd. | [6 empty] | 11 | 34 | 53 | 53 | 53 | 53 | 53 | 45 | 14 |  |  | 12 | [8 empty] | 429055
| Bhairob 54.5 MW | [10 empty] | 12 | 19 |  |  |  |  | 16 | 30 |  | 8 | [6 empty] | 95400
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 12 | 18 |  | 26 |  | 19 | 16 | 8 | 2 | [9 empty] | 124695
120 | Eastern Zone Total | 4707 | 4525 | 4316 | 4058 | 4074 | 4247 | 4612 | 5275 | 5653 | 5771 | 5638 | 5862 | 5958 | 5691 | 5508 | 5258 | 5121 | 5578 |  | 6196 | 6151 | 6094 | 5905 | 5484 | 5181 | 4819 | 127648442
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 49 | 49 | 49 | 49 | 49 | 49 | 16 | 7 |  |  | 49 |  | 85 | 28 | [5 empty] | 457920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 35 | 90 | 90 | 90 | 94 | 93 | 93 | 70 | 70 | 35 | 35 | 50 |  | 93 | 93 | 93 | 94 | 53 | 35 |  | 1266240
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 32 | 32 | 32 | 32 | 32 | 16 |  | 160704
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 55 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 35 | 33 | 33 | 34 | 33 | 34 | 77 |  | 84 | 87 | 89 | 68 | 64 | 62 | 52 | 1084229
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 21 | 21 | 22 | 18 | 19 | 18 | 16 | 17 | 21 | 21 | 20 | 19 | 18 | 16 | 24 |  | 26 | 26 | 26 | 26 | 26 | 24 | 23 | 485800
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 | [8 empty] | 10875
143 | Gopalganj 100 MW Peaking PP | [13 empty] | 3 | 9 | 15 | 15 | 15 |  | 19 | 19 | 19 | 19 | 19 | 17 |  | 145152
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 531 | 530 | 530 | 530 | 531 | 719 | 719 | 718 | 719 | 718 | 719 | 719 | 719 | 719 | 719 | 719 | 779 | 775 |  | 775 | 775 | 775 | 776 | 775 | 775 | 775 | 16728727
147 | Bheramara 410 MW CCPP | 210 | 225 | 245 | 270 | 245 | 240 | 190 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 210 | 385 | 360 | 300 |  | 300 | 285 | 280 | 240 | 215 | 195 | 165 | 5742720
148 | Payra 1320 MW | 510 | 500 | 500 | 470 | 440 | 440 | 410 | 440 | 440 | 440 | 440 | 440 | 470 | 430 | 410 | 410 | 410 | 350 |  | 400 | 480 | 500 | 530 | 530 | 530 | 530 | 11871600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [9 empty] | 42 | 50 | 50 | 50 | 50 | 50 | 23 | 17 | 50 |  | 50 | 36 | [5 empty] | 401600
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 184 | 183 | 184 | 194 | 198 | 203 | 229 | 230 | 229 | 228 | 224 | 221 | 222 | 208 | 193 | 204 | 178 |  | 159 | 156 | 155 | 156 | 154 | 158 | 170 | 4884236
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 233 | 232 | 231 | 230 | 230 | 231 | 200 | 154 | 153 | 156 | 155 | 154 | 153 | 157 | 287 | 338 | 339 | 421 |  | 440 | 438 | 440 | 427 | 398 | 418 | 398 | 6457145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 6 | [8 empty] | 6588
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 496320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242244
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 |  | 18 | 18 | 18 | 18 |  |  |  | 203770
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 8 | 8 | 8 | 8 | 8 | [9 empty] | 3 | 8 | 8 | 8 |  | 8 | 7 | 7 | 7 | 7 | 7 |  | 97903
168 | Santahar 50 MW Peaking PP | [9 empty] | 3 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | [8 empty] | 202328
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 51 | 52 | 52 | 25 | 25 | 25 | 8 | 8 |  |  | 25 |  | 25 | [6 empty] | 285120
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 1 | 95 |  | 101 | 101 | 101 | 101 | 96 | 21 |  | 500784
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | 35 | 35 | 35 | 41 | 55 | 55 | 55 | 97 | 113 | 113 | 113 | 70 | 70 | 70 | 35 | 43 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1965216
172 | Confidence Power Bogura Unit-1 113 MW | 35 |  |  |  |  | 25 | 35 | 35 | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 60 |  | 100 | 113 | 113 | 113 | 70 | 35 |  | 1119264
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 |  |  |  |  | 25 | 34 | 76 | 83 | 87 | 103 | 103 | 98 | 68 | 70 | 70 | 34 | 60 |  | 90 | 90 | 100 | 100 | 80 |  |  | 1356480
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 3 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 28426
178
178