## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-13 | Saturday
|  |  | Date (day): | 2021-02-13 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12678.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14091 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-12 | 2021-02-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 103 | 107 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 341 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 360 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 24 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 245 | 270 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 64 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 62 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 50 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | 33 kV feeder problem.
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 51 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 20 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 110 | 215 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 7 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 22 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 14 | 70 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 22 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 1749 | 2274 | 3545 | 3767 | 318 | 1808
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 19 | 19 |  | 31 | Engine problem
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 124 | 110 | 120 | 120 | 30 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 8 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 50 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 42 | 25 | 30
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 197 | 251 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 641 | 780 | 1381 | 1453 | 775 | 146
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 146 | 213 | 220 | 220
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 260 | 360 | 360
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 250 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 0 | 26 | 26 | 19 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 2 | 5 | 5 | 50 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | CB problem.
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 76 | 51 | 80 | 80 |  | 83 | Gas shortage & ST under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 17 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 94 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 16 | 0 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 952 | 1006 | 1698 | 1960 | 714 | 89
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 128 | 150 | 150 | 52 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 40 | 82 | 82 |  | 13 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 150 | 0 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 25 | 25
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 431 | 363 | 445.6 | 594 | 52 | 13
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Engine problem
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 30 | 30 |  | 60 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 101 | 101 | 100 | 100 |  | 230 | GT-2 & ST under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 22 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 20 | 50 | 50
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 71 | 74 | 74 |  | 12 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 70 | 100 | 100 |  | 131
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 300 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 411 | 304 | 420 | 420
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 55 | 130 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1288 | 1228 | 1516 | 1516 | 0 | 548
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 530 | 811 | 826 | 922
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 12 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 135 | 180 | 200 | 410
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 95 | 95 |  | 10 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 665 | 1056 | 1511 | 2103 | 0 | 88
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 32 | 76 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 450 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 500 | 568 | 1001 | 1001 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 8 | 25 | 25 |  | 25 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | FGMO
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 151 | 220 | 220 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 384 | 222 | 400 | 400
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 21 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 87 | 70 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 70 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 689 | 655 | 1310 | 1434 | 431 | 25
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 70 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 224 | 220 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 7139 | 8150 | 12678.6 | 14091 | 2414 | 3128
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6832.4172 | 7800 | 12134.1202 | 13485.865
| A. |  | 2021-02-12 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 8150 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 6000 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8150 | MW
| 3 | Day peak Generation : |  |  | 7139 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7800 | MW
| 4 | Evening peak Generation : |  |  | 8150 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 169.0914 | MKWHr | By Solar | 0.56921 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.2097 | MKWHr |  | By Oil: | 32.4018 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.5858 | MKWHr |  | By Hydro: | 1.644 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2414 | MW | Dhaka | 2490 | 2490 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3128 | MW | Chittagong | 797 | 797 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5542 | MW | Khulna | 999 | 999 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 861.32 | MMCFD |  |  | Rajshahi | 878 | 878 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 111090552.94 | ii) Oil : | Taka | 179950257.65 | Comilla | 727 | 727 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72187342 | Total | Taka | 363228152.59 | Mymensingh | 761 | 761 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.3285 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -355 | MW (E to W) at | 19:30 | hrs | Barisal | 228 | 228 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -435 | MW at | 18:30 | hrs | Rangpur | 604 | 604 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 28.2° C |  |  | Total | 7800 | 7800 |  | 0
| B. |  | 2021-02-13 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 28.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14091 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
| 4 | Reserve(Generation end) |  |  |  | 4791 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 192.9509 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5581 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.9222 | MKWHr. | ii) HVDC Flow at Peak Time |  | 811 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7587 | MKWHr. | iii) Maximum HVDC Flow : |  | 812 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.13 |  | (b) Today: | 93.93 |  | (c) Rule Curve: |  | 95.32
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 353 | 273 |  | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 16 | 0 | 0 | 0 | 285 | 295 | 162 | 8 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 78 | 107 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 20 | 0 | 100 | 51 | 0 | 410 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 161 | 0 | 405 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 |  | 4617 | 2090 | 6707 | 2857 | 483 | 1515 | 1044 | 660 | 70 | 0 | 78 | 0 | 0 | 94.18
2:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 352 | 302 |  | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 27 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 113 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 0 | 0 | 0 | 260 | 275 | 170 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 74 | 107 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 99 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 50 | 51 | 0 | 411 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 80 | 60 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 165 | 0 | 411 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 |  | 4397 | 2016 | 6413 | 2816 | 483 | 1545 | 765 | 660 | 70 | 0 | 74 | 0 | 0 | 94.17
3:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 361 | 314 |  | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 27 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 0 | 0 | 0 | 260 | 275 | 166 | 8 | 41 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 70 | 117 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 51 | 0 | 410 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 164 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 |  | 4289 | 1969 | 6258 | 2834 | 483 | 1556 | 585 | 660 | 70 | 0 | 70 | 0 | 0 | 94.16
4:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 347 | 331 |  | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 27 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 255 | 270 | 176 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 70 | 141 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 101 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 84 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4157 | 1956 | 6113 | 2837 | 483 | 1578 | 425 | 650 | 70 | 0 | 70 | 0 | 0 | 94.15
5:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 346 | 333 |  | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 27 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 255 | 265 | 180 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 68 | 146 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 74 | 0 | 80 | 0 | 0 | 9 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 160 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4085 | 1915 | 6000 | 2837 | 483 | 1561 | 361 | 620 | 70 | 0 | 68 | 0 | 0 | 94.14
6:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 363 | 354 |  | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 27 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 126 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 27 | 0 | 0 | 0 | 305 | 320 | 182 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 68 | 146 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 71 | 0 | 80 | 0 | 0 | 9 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 165 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4279 | 1894 | 6173 | 2988 | 483 | 1548 | 396 | 620 | 70 | 0 | 68 | 0 | 0 | 94.13
7:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 363 | 353 |  | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 18 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 265 | 270 | 190 | 8 | 35 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 64 | 146 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 110 | 100 | 0 | 69 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 8 | 0 | 5 | 0 | 0 | 40 | 0 | 5 | 1 | 30 | 8 | 0 | 410 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 80 | 90 | 0 | 1 | 104 | 0 | 0 | 0 | 1 |  | 483 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 173 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 4486 | 1893 | 6379 | 2895 | 483 | 1551 | 693 | 620 | 70 | 0 | 64 | 3 | 0 | 0
8:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 368 | 343 |  | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 112 | 0 |  | 7 | 0 | 0 | 0 | 0 | 2 | 20 | 32 | 0 | 0 | 0 | 290 | 280 | 170 | 8 | 36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 62 | 140 | 0 | 22 | 0 | 30 | 22 | 53 | 50 | 163 | 101 | 0 | 69 | 0 | 80 | 0 | 0 | 9 | 310 | 8 | 0 | 0 | 44 | 0 | 0 | 134 | 0 | 15 | 5 | 75 | 17 | 0 | 407 | 0 | 0 | 0 | 1 | 248 | 0 | 0 | 0 | 0 | 100 | 90 | 0 | 8 | 144 | 0 | 0 | 0 | 6 |  | 530 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 162 | 0 | 417 | 0 | 0 | 27 | 0 | 30 | 0 | 1 | 0 | 470 | 0 | 0 | 0 |  | 4925 | 2031 | 6956 | 2889 | 530 | 1638 | 1126 | 620 | 70 | 0 | 62 | 21 | 0 | 0
9:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 341 | 336 |  | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 25 | 24 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 116 | 0 |  | 11 | 0 | 0 | 0 | 0 | 24 | 20 | 32 | 0 | 0 | 0 | 275 | 265 | 175 | 8 | 33 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 58 | 127 | 2 | 22 | 1 | 30 | 22 | 31 | 50 | 163 | 101 | 0 | 69 | 0 | 60 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 0 | 10 | 80 | 17 | 0 | 409 | 0 | 0 | 0 | 3 | 251 | 0 | 0 | 0 | 0 | 100 | 60 | 0 | 20 | 144 | 0 | 0 | 0 | 12 |  | 530 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 151 | 0 | 414 | 0 | 0 | 70 | 0 | 60 | 0 | 1 | 0 | 470 | 0 | 0 | 0 |  | 4975 | 2080 | 7055 | 2766 | 530 | 1581 | 1383 | 620 | 70 | 0 | 58 | 47 | 0 | 0
10:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 345 | 330 |  | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 24 | 22 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 22 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 0 | 0 | 0 | 280 | 285 | 175 | 8 | 42 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 60 | 110 | 30 | 22 | 1 | 30 | 22 | 22 | 50 | 130 | 100 | 0 | 69 | 0 | 25 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 95 | 0 | 0 | 180 | 0 | 0 | 14 | 50 | 17 | 0 | 411 | 0 | 0 | 0 | 4 | 197 | 0 | 0 | 0 | 0 | 100 | 61 | 0 | 23 | 144 | 0 | 0 | 1 | 15 |  | 530 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 150 | 0 | 414 | 0 | 0 | 70 | 0 | 70 | 0 | 3 | 0 | 450 | 0 | 0 | 0 |  | 4846 | 2057 | 6903 | 2741 | 530 | 1532 | 1345 | 600 | 35 | 0 | 60 | 60 | 0 | 0
11:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 343 | 330 |  | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 25 | 0 | 0 | 0 | 25 | 12 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 0 | 0 | 0 | 265 | 265 | 172 | 8 | 44 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 64 | 109 | 40 | 22 | 2 | 30 | 22 | 22 | 50 | 130 | 102 | 0 | 72 | 0 | 25 | 0 | 0 | 9 | 285 | 8 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 0 | 16 | 50 | 17 | 0 | 411 | 0 | 0 | 0 | 4 | 197 | 0 | 0 | 0 | 0 | 100 | 60 | 0 | 37 | 144 | 0 | 0 | 10 | 22 |  | 530 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 135 | 0 | 418 | 0 | 0 | 70 | 0 | 70 | 0 | 4 | 0 | 450 | 0 | 0 | 0 |  | 4900 | 2047 | 6947 | 2678 | 530 | 1534 | 1386 | 600 | 70 | 0 | 64 | 85 | 0 | 0
12:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 357 | 326 |  | 0 | 0 | 245 | 0 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 60 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 12 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 124 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 0 | 0 | 0 | 265 | 265 | 146 | 8 | 76 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 70 | 109 | 32 | 22 | 2 | 30 | 22 | 22 | 50 | 130 | 101 | 0 | 72 | 0 | 100 | 0 | 0 | 9 | 270 | 8 | 8 | 0 | 110 | 0 | 0 | 200 | 0 | 7 | 18 | 50 | 17 | 0 | 411 | 0 | 22 | 0 | 4 | 197 | 0 | 0 | 0 | 0 | 100 | 55 | 14 | 42 | 144 | 0 | 0 | 16 | 22 |  | 530 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 130 | 0 | 384 | 0 | 0 | 87 | 0 | 70 | 0 | 4 | 55 | 450 | 0 | 0 | 0 |  | 5061 | 2078 | 7139 | 2761 | 530 | 1484 | 1532 | 600 | 70 | 0 | 70 | 92 | 0 | 0
13:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 373 | 320 |  | 0 | 0 | 240 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 8 | 22 | 33 | 12 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 114 | 0 |  | 19 | 0 | 0 | 0 | 0 | 25 | 20 | 30 | 0 | 0 | 0 | 270 | 260 | 132 | 8 | 47 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 16 | 76 | 107 | 32 | 22 | 2 | 5 | 22 | 22 | 50 | 163 | 99 | 0 | 71 | 0 | 100 | 0 | 0 | 9 | 310 | 8 | 8 | 0 | 160 | 0 | 0 | 200 | 0 | 50 | 16 | 82 | 20 | 0 | 414 | 0 | 68 | 0 | 4 | 230 | 0 | 0 | 0 | 0 | 100 | 45 | 34 | 42 | 144 | 0 | 0 | 0 | 21 |  | 530 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 125 | 0 | 353 | 0 | 0 | 113 | 0 | 80 | 0 | 4 | 90 | 460 | 0 | 0 | 0 |  | 5300 | 2114 | 7414 | 2650 | 530 | 1537 | 1852 | 610 | 70 | 0 | 76 | 89 | 7414 | 0
14:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 295 | 260 |  | 0 | 0 | 250 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 8 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 18 | 0 | 0 | 0 | 0 | 25 | 20 | 30 | 0 | 0 | 0 | 270 | 250 | 136 | 8 | 45 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 16 | 68 | 106 | 24 | 22 | 1 | 5 | 22 | 22 | 20 | 100 | 100 | 0 | 50 | 0 | 70 | 0 | 0 | 9 | 270 | 8 | 8 | 0 | 80 | 0 | 0 | 200 | 0 | 80 | 15 | 100 | 34 | 0 | 306 | 0 | 70 | 0 | 3 | 179 | 0 | 0 | 0 | 0 | 100 | 55 | 34 | 34 | 144 | 0 | 0 | 0 | 20 |  | 530 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 123 | 0 | 270 | 0 | 0 | 50 | 0 | 65 | 0 | 5 | 50 | 400 | 0 | 0 | 0 |  | 4743 | 1841 | 6584 | 2395 | 530 | 1237 | 1656 | 550 | 70 | 0 | 68 | 78 | 0 | 0
15:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 253 | 290 |  | 0 | 0 | 240 | 0 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 62 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 20 | 0 | 0 | 0 | 0 | 25 | 19 | 30 | 0 | 0 | 0 | 250 | 250 | 141 | 8 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 21 | 60 | 112 | 8 | 22 | 1 | 30 | 22 | 22 | 20 | 100 | 100 | 0 | 50 | 0 | 70 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 45 | 0 | 0 | 150 | 0 | 96 | 11 | 50 | 34 | 0 | 316 | 0 | 35 | 0 | 2 | 179 | 0 | 0 | 0 | 0 | 100 | 54 | 25 | 17 | 144 | 0 | 0 | 0 | 14 |  | 530 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 125 | 0 | 270 | 0 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 400 | 0 | 0 | 0 |  | 4496 | 1765 | 6261 | 2384 | 530 | 1263 | 1357 | 550 | 70 | 0 | 60 | 47 | 0 | 0
16:00 | 0 | 0 | 0 | 190 | 0 | 105 | 0 | 363 | 288 |  | 0 | 0 | 260 | 0 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 23 | 0 | 0 | 0 | 0 | 25 | 19 | 26 | 0 | 0 | 0 | 250 | 250 | 140 | 8 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 12 | 56 | 130 | 8 | 22 | 1 | 30 | 20 | 22 | 20 | 163 | 100 | 0 | 50 | 0 | 70 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 30 | 0 | 0 | 100 | 0 | 100 | 7 | 20 | 34 | 0 | 340 | 0 | 35 | 0 | 1 | 144 | 0 | 0 | 0 | 0 | 60 | 52 | 17 | 13 | 108 | 0 | 0 | 0 | 7 |  | 528 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 124 | 0 | 276 | 0 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 390 | 0 | 0 | 0 |  | 4457 | 1751 | 6208 | 2511 | 528 | 1325 | 1148 | 540 | 70 | 0 | 56 | 30 | 0 | 0
17:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 350 | 290 |  | 0 | 0 | 270 | 0 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 0 |  | 23 | 0 | 0 | 0 | 2 | 25 | 19 | 36 | 0 | 0 | 0 | 250 | 250 | 198 | 8 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 21 | 60 | 129 | 8 | 22 | 0 | 30 | 20 | 25 | 20 | 163 | 100 | 0 | 50 | 0 | 70 | 0 | 0 | 9 | 300 | 8 | 8 | 0 | 30 | 0 | 0 | 100 | 0 | 100 | 2 | 20 | 34 | 0 | 340 | 0 | 35 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 60 | 101 | 17 | 2 | 72 | 0 | 0 | 0 | 4 |  | 528 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 125 | 0 | 273 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 390 | 0 | 0 | 0 |  | 4531 | 1756 | 6287 | 2614 | 528 | 1350 | 1095 | 540 | 70 | 22 | 60 | 8 | 0 | 0
18:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 353 | 320 |  | 0 | 0 | 275 | 12 | 8 | 15 | 0 | 0 | 0 | 16 | 7 | 16 | 15 | 0 | 0 | 0 | 30 | 10 | 7 | 16 | 25 | 8 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 111 | 0 |  | 24 | 0 | 85 | 10 | 13 | 25 | 19 | 42 | 0 | 0 | 0 | 280 | 250 | 206 | 8 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 21 | 78 | 145 | 10 | 22 | 0 | 30 | 20 | 28 | 20 | 163 | 102 | 0 | 60 | 0 | 70 | 0 | 0 | 9 | 290 | 8 | 8 | 0 | 30 | 0 | 0 | 110 | 0 | 100 | 0 | 32 | 41 | 0 | 338 | 8 | 35 | 0 | 0 | 194 | 12 | 0 | 0 | 10 | 100 | 110 | 17 | 0 | 80 | 0 | 0 | 0 | 0 |  | 718 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 143 | 0 | 222 | 53 | 0 | 38 | 0 | 55 | 0 | 0 | 60 | 380 | 0 | 0 | 0 |  | 5034 | 2179 | 7213 | 2765 | 718 | 1343 | 1504 | 530 | 70 | 205 | 78 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 342 | 360 |  | 0 | 0 | 260 | 24 | 48 | 36 | 0 | 0 | 0 | 50 | 16 | 16 | 54 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 21 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 11 | 0 | 0 | 111 | 0 |  | 23 | 0 | 68 | 0 | 0 | 43 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 213 | 8 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 94 | 145 | 40 | 22 | 0 | 30 | 20 | 28 | 20 | 130 | 100 | 0 | 71 | 0 | 70 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 179 | 0 | 0 | 150 | 0 | 139 | 0 | 50 | 51 | 0 | 304 | 16 | 0 | 0 | 0 | 251 | 48 | 0 | 0 | 26 | 100 | 123 | 56 | 0 | 144 | 0 | 0 | 0 | 0 |  | 811 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 152 | 0 | 223 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 400 | 0 | 0 | 0 |  | 5668 | 2473 | 8141 | 2804 | 811 | 1386 | 2226 | 550 | 70 | 200 | 94 | 0 | 0 | 94.22
19:30 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 341 | 360 |  | 0 | 0 | 270 | 24 | 64 | 40 | 0 | 0 | 0 | 50 | 7 | 0 | 62 | 0 | 0 | 0 | 54 | 17 | 0 | 22 | 25 | 26 | 20 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 110 | 0 |  | 23 | 0 | 34 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 213 | 8 | 51 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 94 | 128 | 40 | 22 | 0 | 30 | 22 | 22 | 20 | 130 | 101 | 0 | 71 | 0 | 70 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 215 | 0 | 0 | 150 | 0 | 149 | 0 | 50 | 17 | 0 | 304 | 0 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 26 | 100 | 130 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 811 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 102 | 8 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 151 | 0 | 222 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 450 | 0 | 0 | 0 |  | 5651 | 2499 | 8150 | 2797 | 811 | 1416 | 2214 | 600 | 70 | 148 | 94 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 341 | 356 |  | 0 | 0 | 270 | 24 | 63 | 40 | 0 | 0 | 0 | 50 | 7 | 0 | 62 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 20 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 23 | 0 | 9 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 217 | 8 | 49 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 96 | 131 | 16 | 22 | 0 | 30 | 22 | 22 | 20 | 130 | 101 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 218 | 0 | 0 | 150 | 0 | 149 | 0 | 50 | 17 | 0 | 304 | 0 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 26 | 100 | 133 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 811 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 151 | 0 | 231 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 450 | 0 | 0 | 0 |  | 5630 | 2518 | 8148 | 2856 | 811 | 1426 | 2167 | 600 | 70 | 122 | 96 | 0 | 0 | 94.23
21:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 354 | 356 |  | 0 | 0 | 275 | 24 | 63 | 40 | 0 | 0 | 0 | 50 | 7 | 0 | 61 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 183 | 8 | 72 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 96 | 130 | 0 | 22 | 0 | 30 | 26 | 22 | 20 | 163 | 100 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 310 | 8 | 11 | 0 | 218 | 0 | 0 | 150 | 0 | 122 | 0 | 50 | 17 | 0 | 304 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 149 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 811 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 151 | 0 | 220 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 490 | 0 | 0 | 0 |  | 5581 | 2547 | 8128 | 2892 | 811 | 1459 | 2048 | 640 | 70 | 112 | 96 | 0 | 0 | 94.22
22:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 340 | 355 |  | 0 | 0 | 255 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 130 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 182 | 8 | 75 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 92 | 131 | 0 | 22 | 0 | 30 | 32 | 2 | 0 | 110 | 95 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 275 | 8 | 11 | 0 | 180 | 0 | 0 | 150 | 0 | 70 | 0 | 50 | 17 | 0 | 276 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 48 | 0 | 144 | 0 | 0 | 0 | 0 |  | 812 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 151 | 0 | 230 | 17 | 0 | 70 | 0 | 38 | 0 | 0 | 35 | 470 | 0 | 0 | 0 |  | 5202 | 2420 | 7622 | 3070 | 812 | 1346 | 1575 | 620 | 70 | 37 | 92 | 0 | 0 | 94
23:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 341 | 310 |  | 0 | 0 | 265 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 131 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 184 | 8 | 76 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 86 | 131 | 0 | 22 | 0 | 30 | 32 | 2 | 0 | 110 | 96 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 110 | 0 | 0 | 150 | 0 | 31 | 0 | 50 | 17 | 0 | 279 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 100 | 400 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 641 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 150 | 0 | 231 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 470 | 0 | 0 | 0 |  | 5079 | 2167 | 7246 | 3183 | 641 | 1275 | 1334 | 620 | 70 | 37 | 86 | 0 | 0 | 93.99
24:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 340 | 310 |  | 0 | 0 | 220 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 183 | 8 | 72 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 76 | 133 | 0 | 20 | 0 | 30 | 32 | 2 | 0 | 110 | 95 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 275 | 8 | 11 | 0 | 15 | 0 | 0 | 75 | 0 | 30 | 0 | 30 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 80 | 400 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 529 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 150 | 0 | 228 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 0 |  | 4695 | 2002 | 6697 | 3216 | 529 | 1267 | 937 | 590 | 70 | 12 | 76 | 0 | 0 | 93.99
KWH | 0 | 0 | 0 | 4488750 | 0 | 2456818 | 0 | 8412160 | 7646000 |  | 0 | 0 | 6235258 | 99840 | 316176 | 248046 | 0 | 0 | 0 | 300480 | 41328 | 36960 | 800614 | 0 | 0 | 102000 | 442800 | 33424 | 31208 | 246852 | 600000 | 521460 | 574000 | 794600 | 11280 | 0 | 0 | 1644000 | 0 | 0 | 16655 | 0 | 0 | 2673548 | 0 |  | 327120 | 0 | 152882 | 6600 | 28800 | 594720 | 461424 | 815040 | 0 | 0 | 0 | 6681900 | 6498000 | 4226000 | 200727 | 1101330 | 99648 | 108960 | 0 | 0 | 0 | 0 | 0 | 432036 | 246420 | 821100 | 507430 | 1758720 | 2929080 | 279360 | 502308 | 9650 | 663000 | 561240 | 774000 | 875736 | 3266836 | 2338000 | 0 | 1626240 | 0 | 1737760 | 0 | 0 | 207720 | 7243000 | 195072 | 208096 | 0 | 2067490 | 0 | 0 | 3134400 | 0 | 1155460 | 115155 | 1133760 | 621120 | 0 | 8770000 | 39600 | 355464 | 0 | 27602 | 4305600 | 127324 | 0 | 0 | 89040 | 1881600 | 2565000 | 447360 | 243500 | 3045600 | 0 | 0 | 26640 | 143809 |  | 13922181 | 0 | 4046112 | 0 | 33600 | 0 | 0 | 0 | 0 | 58752 | 0 | 0 | 462000 | 70368 | 0 | 0 | 0 | 0 | 0 | 463024 | 28800 | 0 | 0 | 29760 | 0 | 488880 | 0 | 253800 | 0 | 0 | 3656000 | 0 | 0 | 0 | 0 | 0 | 0 | 1078818 | 0 | 3805100 | 0 | 7997727 | 237600 | 0 | 1376928 | 0 | 872640 | 0 | 29497 | 694272 | 11929800 | 0 | 0 | 0 |  | 117555736 | 51535659 | 169091395 | 67961226 | 13922181 | 35248502 | 31690135 | 15585800 | 1644000 | 711618 | 1758720 | 569213 | 0
Fuel Cost | 0 | 0 | 0 | 6598462.5 | 0 | 3242999.76 | 0 | 8496281.6 | 7875380 |  | 0 | 0 | 6921136.38 | 757785.6 | 2178452.64 | 2098469.16 | 0 | 0 | 0 | 2262614.4 | 376911.36 | 363686.4 | 7381661.08 | 0 | 0 | 927180 | 3232440 | 258367.52 | 307710.88 | 185139 | 450000 | 0 | 0 | 0 | 109077.6 | 0 | 0 | 443880 | 0 | 0 | 154724.95 | 0 | 0 | 4545031.6 | 0 |  | 0 | 0 | 1482955.4 | 63030 | 250560 | 4710182.4 | 581394.24 | 2420668.8 | 0 | 0 | 0 | 4944606 | 6498000 | 3887920 | 258937.83 | 1266529.5 | 112602.24 | 152544 | 0 | 0 | 0 | 0 | 0 | 548685.72 | 184815 | 1436925 | 380572.5 | 13190400 | 3104824.8 | 2536588.8 | 637931.16 | 153821 | 1087320 | 897984 | 1377720 | 1366148.16 | 3724193.04 | 2431520 | 0 | 3106118.4 | 0 | 3006324.8 | 0 | 0 | 423748.8 | 7315430 | 146304 | 158152.96 | 0 | 15630224.4 | 0 | 0 | 16298880 | 0 | 11369726.4 | 1346161.95 | 9240144 | 6739152 | 0 | 8156100 | 361152 | 3359134.8 | 0 | 0 | 32550336 | 1108992.04 | 0 | 0 | 763072.8 | 12531456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80191762.56 | 0 | 4248417.6 | 0 | 264096 | 0 | 0 | 0 | 0 | 615720.96 | 0 | 0 | 716100 | 686791.68 | 0 | 0 | 0 | 0 | 0 | 4097762.4 | 221760 | 0 | 0 | 288374.4 | 0 | 938649.6 | 0 | 192126.6 | 0 | 0 | 19815520 | 0 | 0 | 0 | 0 | 0 | 0 | 1618227 | 0 | 4451967 | 0 | 7917749.73 | 2480544 | 0 | 13067046.72 | 0 | 6771686.4 | 0 | 325941.85 | 5130670.08 | 52371822 | 0 | 0 | 0 |  | 252467383.37 | 206412736.58 | 458880119.95 | 68635937.82 | 80191762.56 | 42454615.12 | 173390132.49 | 72187342 | 443880 | 6560125.16 | 13190400 | 1825924.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 357 | 326 |  | 0 | 0 | 245 | 0 | 0 | 15 | 0 | 0 | 0 | 7 | 0 | 0 | 60 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 12 | 22 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 124 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 0 | 0 | 0 | 265 | 265 | 146 | 8 | 76 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 70 | 109 | 32 | 22 | 2 | 30 | 22 | 22 | 50 | 130 | 101 | 0 | 72 | 0 | 100 | 0 | 0 | 9 | 270 | 8 | 8 | 0 | 110 | 0 | 0 | 200 | 0 | 7 | 18 | 50 | 17 | 0 | 411 | 0 | 22 | 0 | 4 | 197 | 0 | 0 | 0 | 0 | 100 | 55 | 14 | 42 | 144 | 0 | 0 | 16 | 22 |  | 530 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 130 | 0 | 384 | 0 | 0 | 87 | 0 | 70 | 0 | 4 | 55 | 450 | 0 | 0 | 0 |  | 7139 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 341 | 360 | 0 | 0 | 0 | 270 | 24 | 64 | 40 | 0 | 0 | 0 | 50 | 7 | 0 | 62 | 0 | 0 | 0 | 54 | 17 | 0 | 22 | 25 | 26 | 20 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 23 | 0 | 34 | 0 | 0 | 50 | 19 | 42 | 0 | 0 | 0 | 260 | 250 | 213 | 8 | 51 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 94 | 128 | 40 | 22 | 0 | 30 | 22 | 22 | 20 | 130 | 101 | 0 | 71 | 0 | 70 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 215 | 0 | 0 | 150 | 0 | 149 | 0 | 50 | 17 | 0 | 304 | 0 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 26 | 100 | 130 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 811 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 102 | 8 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 151 | 0 | 222 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 450 | 0 | 0 | 0 |  | 8150 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 30 | 0 | 0 | 0 | 360 | 300 | 220 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 150 | 82 | 22 | 0 | 30 | 30 | 51 | 50 | 163 | 100 | 0 | 74 | 0 | 100 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 420 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 104 | 0 | 144 | 116 | 100 |  |  |  | 922 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 25 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 25 |  | 85 | 100 | 102 | 19 | 22 | 25 | 0 | 0 | 0 | 360 | 300 | 220 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 150 | 82 | 22 | 1.6 | 30 | 30 | 51 | 50 | 163 | 100 | 0 | 74 | 0 | 100 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 0 | 100 | 149 | 20 | 100 | 200 | 0 | 420 | 115 | 105 | 8 | 5 | 300 | 54 | 110 | 114 | 113 | 100 |  | 104 | 50 | 144 | 116 | 100 |  | 30 |  | 826 | 0 | 200 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 25 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 220 | 0 | 400 | 95 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 92 | 0 | 354 | 321 | 0 | 0 | 0 | 250 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 19 | 19 | 17 | 0 | 0 | 0 | 265 | 265 | 184 | 8 | 82 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 66 | 161 | 11 | 22 | 0 | 15 | 32 | 2 | 0 | 163 | 81 | 0 | 72 | 0 | 70 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 24 | 0 | 0 | 132 | 0 | 35 | 5 | 10 | 17 | 0 | 301 | 8 | 0 | 0 | 1 | 117 | 0 | 0 | 0 | 0 | 40 | 400 | 0 | 9 | 54 | 0 | 0 | 0 | 6 | 0 | 810 | 0 | 370 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 165 | 0 | 338 | 53 | 0 | 31 | 0 | 30 | 0 | 1 | 25 | 380 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6000 | 5:00
| Highest Generation |  | 8150 | 19:30
| Day Peak Generation |  | 7139 | 12:00
| Evening Peak Generation |  | 8150 | 19:30
| HVDC Max Flow |  | 812 | 22:00
| HVDC EvPeak Flow |  | 811 | 19:30
| Load factor L.F |  | 86.45%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-13
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7139 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5581 | MW
Evening Peak Generation : |  | 8150 | MW Hour : | 19:30 | Available Max Generation : |  | 14091 | MW
E.P. Demand (at gen end) : |  | 8150 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 8150 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4791 | MW
Total Gen. (MKWH) : |  | 169.0914 | System Load Factor : | 86.45% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -435 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-13
Actual : | 93.93 | Ft.(MSL) , | Rule curve : | 95.32 | Ft.( MSL )
Gas Consumed : | Total = | 861.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111090552.94
: |  | Coal : | 72187342 | Oil : | 179950257.65 | Total : | 363228152.59
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3322.1799 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1125.1882 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1007.3229 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 909.9142 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 822.4346 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 663.6642 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 376.9265 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 171.0302 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 511.8228 |  |  | 0 | 0%
Total | 0 |  | 8910.4836 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ashuganj-4,5
4) Shahjibazar 330 MW GT-2 & STG
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Gopalganj 132/33 kV T-2 transformer was under shut down from 08:17 to 17:13 for A/M & D/W.
b) Kaliakoir-Tangail 132 kV Ckt-1 was under shut down from 09:12 to 16:56 for A/M.
c) Khulshi-BSRM 132 kV Ckt is under shut down since 08:20 for A/M.
d) Sreemangal-Fenchuganj 132 kV Ckt-2 was under shut down from 09:12 to 16:13 for C/M.
e) Madanganj S/S-Madanganj P.S. 132 kV Ckt was under shut down from 09:02 to 16:20 for C/M.
f) Madanganj 132 kV main Bus was under shut down from 08:59 to 15:50 for C/M.
g) Meghnaghat-Shyampur 230 kV Ckt-1 was under shut down from 09:55 to 16:46 for C/M.
h) Ishwardi 33 kV Bus-1 along with 132/33 kV T-1 transformer was under shut down from 10:10 to
14:02 for D/W.
i) Barguna 132/33 kV T-2 transformer was under shut down from 08:46 to 18:34 for A/M.
j) Bhola 230/33 kV transformer was under shut down from 08:32 to 11:58 for C/M.
k) Bhaluka 132/33 kV T1 transformer was under shut down from 10:58 to 17:10 for D/W.
l) Baghabari-Ishwardi 132 kV Ckt was under shut down from 08:56 to 17:51 for A/M.
m) Kabirpur 132 kV main Bus was under shut down from 13:23 to 15:14 due to R/H at Kabirpur-Kodda
132 kV Ckt-1 Isolator at Kabirpur end.
n) Baghabari-Shahjadpur 132 kV Ckt-1 was under shut down from 08:35 to 17:25 for D/W.
o) Naogaon 132/33 kV T2 transformer tripped at 08:47 from both sides showing DEF, Tcs at 132 kV
side & DEF at 33 kV side and was switched on at 10:38.
p) Bibiyana South ST was synchronized at 16:16.
q) Kodda 132/33 kV T3, T4,T5 transformers & 33 kV Bus-1 were under shutdown from 22:02 to |  |  |  |  | About 90 MW power interruption occurred under Kodda S/S
22:33 due to emergency maintenance work at DS by PBS. |  |  |  |  | area from 22:02 to 22:33.
r) Sikalbaha-TK. Chemical 132 kV Ckt is under shut down since 07:36 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4488750
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 2456818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 8412160 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 360 | 7646000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 24 | 99840 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6235258 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 316176 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 248046 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 62 | 800614 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 246852
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 300480 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 41328 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 102000 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 442800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 36960 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 33424 | High Voltage.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 31208 | High Voltage.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1121460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 574000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 794600 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 11280 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 215 | 2067490 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1155460
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 355464 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 447360 | High Voltage.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3045600 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 143809
| Dhaka area Total |  |  |  | 5972 | 2274 | 41655237
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 16655
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115155
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 594720
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1644000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2673548
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 152882 | High Voltage.
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 6600 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 1133760 | High Voltage.
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 461424
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 815040
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 28800 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27602
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 251 | 4305600 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 127324
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1881600
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 780 | 13984710
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4226000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6681900 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6498000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 99648 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 2 | 108960 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | S/S maint. at Midland end
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | S/S maint. at Midland end
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | S/S maint. at Midland end
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1101330 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 621120 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 432036
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246420
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 94 | 1758720
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821100
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 507430
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 89040 | High Voltage.
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 26640
| Cumilla Area Total |  |  |  | 2980 | 1006 | 23419071
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 128 | 2929080 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502308
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 40 | 279360 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9650
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 3134400 | Reserve.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 39600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 243500
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 327120
| Mymensingh Area Total |  |  |  | 709 | 363 | 7465018
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 663000 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 561240 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3266836 | Low demand
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 2338000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 774000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 20 | 875736
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 208096
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1626240 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 70 | 1737760 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 195072 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7243000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 304 | 8770000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 207720
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 130 | 2565000
| Sylhet Area Total |  |  |  | 1988 | 1228 | 31031700
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 811 | 13922181
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 33600 | Reserve.
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 12 | 58752 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 4046112 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 237600 | Low demand
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1056 | 18298245
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 70368 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 462000 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1078818 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 450 | 11929800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 568 | 13540986
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 8 | 28800 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shoetage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 151 | 3805100 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 222 | 7997727 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 488880
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 253800
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 29760 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 463024
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 1376928 | Low demand
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 694272 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 655 | 15138291
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3656000 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 872640 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29497
| Rangpur Area Total |  |  |  | 605 | 220 | 4558137
| Total |  |  |  | 20929 | 8150 | 169091395
| Eastern Grid Total |  |  |  | 14031 | 5651 | 117555736
| Western Grid Total |  |  |  | 6898 | 2499 | 51535659
| National Grid Total |  |  |  | 20929 | 8150 | 169091395
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-12
(a) ENTIRE EASTERN GRID : |  | 5091 | MW | (b) ENTIRE WESTERN GRID : |  | 2709 | MW
i) Dhaka area |  | 2490 | MW | i) Khulna area |  | 999 | MW
ii) Chittagong area |  | 797 | MW | ii) Rajshahi area |  | 878 | MW
iii) Comilla area |  | 727 | MW | iii) Barisal area |  | 228 | MW
iv) Mymensingh area |  | 761 | MW | iv) Rangpur area |  | 604 | MW
v) Sylhet area |  | 316 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7800 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 76 | 13:00 | Sherpur | 100 | 18:30 | Jhenida | 82 | 19:00
Munsiganj | 82 | 20:00 | Srimongal | 39 | 19:30 | Bottail | 84 | 18:30
Sonargaon | 64 | 21:00 | Shahjibazar | 72 | 19:00 | G.K Project | 30 | 19:00
Shyampur | 146 | 4:00 | Fenchuganj | 25 | 18:00 | Faridpur | 120 | 19:00
Bhulta | 148 | 1:00 | Kulawara | 26 | 20:00 | Madaripur | 82 | 21:00
Madanganj | 39 | 20:00 | Sylhet | 74 | 20:00 | Sariatpur | 40 | 19:30
Shitalakhya | 71 | 1:00 | Chatak | 19 | 18:30 | Gopalganj | 59 | 19:00
Rahim steel | 4 | 1:00 | Sunamganj | 29 | 20:00 | Bagerhat | 70 | 20:00
Matuail | 66 | 12:00 | Biani Bazar | 38 | 18:00 | Mongla | 32 | 18:30
Ghorasal | 51 | 1:00 | Comilla (S) | 96 | 20:00 | Satkhira | 71 | 19:00
Narsingdi | 117 | 20:00 | Comilla(N) | 85 | 18:00 | Gallamari | 20 | 13:00
Haripur (SBU) | 70 | 1:00 | Chandpur | 43 | 19:00 | Magura | 38 | 18:30
Ullon | 54 | 20:00 | Feni | 81 | 19:00 | Norail | 22 | 19:00
Hasnabad | 60 | 1:00 | Chowmuhani | 116 | 18:30 | Chuadanga | 58 | 18:30
Magbazar | 55 | 13:00 | Ashuganj | 38 | 18:30 | Borguna | 8 | 24:00
Maniknagar | 38 | 12:00 | Daudkandi | 70 | 19:00 | Barisal(N) | 27 | 20:00
Bangabhaban | 6 | 11:00 | B.Baria | 102 | 19:30 | Barisal (S) | 70 | 21:00
Narinda | 48 | 1:00 | Ramganj | 52 | 19:30 | Patuakhali | 77 | 20:00
Dhanmondi | 89 | 19:00 | Chaddagram | 20 | 18:30 | Bhandaria | 40 | 20:00
Lalbag | 42 | 1:00 | PHP | 4 | 12:00 | Borhan Uddin | 25 | 22:00
Madartek | 53 | 13:00 | Kochua | 38 | 18:30 | Ishurdi | 40 | 19:30
Dhaka University |  |  | Madunaghat | 45 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Aftabnagar | 6 | 11:00 | Hathazari | 58 | 19:00 | Natore | 86 | 18:30
Fatullah | 40 | 1:00 | Khulshi | 114 | 1:00 | Bogra | 117 | 19:30
Mirpur | 68 | 13:00 | Halishahar | 85 | 21:00 | Noagaon | 80 | 19:00
Kalyanpur | 72 | 13:00 | Baraulia | 132 | 2:00 | Rajshahi | 84 | 20:00
Gulshan | 64 | 13:00 | Sikalbaha | 18 | 19:00 | Rajshahi New | 13 | 9:00
Uttara | 56 | 13:00 | Dohazari | 60 | 19:00 | C.Nawabganj | 64 | 12:00
Uttara New | 16 | 9:00 | Cox'sbazar | 75 | 19:00 | Amnura | 40 | 10:00
Kamrangirchar | 64 | 12:00 | Chandraghona | 22 | 18:30 | Pabna | 56 | 19:00
Savar | 80 | 18:30 | Kaptai | 0 | 1:00 | Shahjadpur | 73 | 8:00
Bhasantec | 94 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 51 | 19:00
Agargaon | 41 | 13:00 | Bakulia | 57 | 15:00 | Niyamatpur | 70 | 9:00
Satmosjid | 57 | 13:00 | Julda | 16 | 11:00 | Joypurhat | 57 | 8:00
Tongi | 72 | 21:00 | TK chemical | 20 | 18:30 | Sherpur(Bogura) | 40 | 18:30
Kabirpur | 122 | 10:00 | Modern Steel | 0 | 1:00 | Mohastangor | 34 | 8:00
Basundhara | 83 | 18:00 | Shahmirpur | 13 | 1:00 | Bangura | 16 | 19:30
Manikganj | 40 | 22:00 | Khagrachhari | 20 | 18:30 | Rangpur | 106 | 18:30
Joydevpur | 76 | 10:00 | Matarbari | 27 | 18:30 | Lalmonirhat | 48 | 19:00
New Tongi | 64 | 12:00 | Baroiar Hat | 24 | 18:30 | Saidpur | 92 | 9:00
Korda | 130 | 21:00 | Rangamati | 8 | 12:00 | Purbasadipur | 94 | 12:00
Dhamrai | 66 | 19:00 | Abul Khair 230 | 137 | 10:00 | Thakurgaon | 63 | 19:00
Rajendrapur | 60 | 19:30 | BSRM | 142 | 23:00 | Palashbari | 101 | 19:00
Valuka | 66 | 12:00 | GPH Ispat | 79 | 8:00 | Barapukuria | 45 | 10:00
Tangail | 160 | 18:30 | Goalpara | 17 | 13:00 | Panchagar | 43 | 18:30
Mymensing | 172 | 13:00 | Central s/s | 66 | 19:00 | Joldhaka | 23 | 9:00
Kishorganj | 96 | 18:30 | Noapara | 41 | 19:00 | Kurigram | 43 | 19:00
Netrokona | 95 | 18:00 | Jessore | 81 | 20:00
Jamalpur | 123 | 8:00 | Benapol | 40 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 18:30 | 406 | 11:00 | Kaliakoir | 411 | 0.25 | 401 | 0.29167
| Bheramara | 409 | 14:00 | 395 | 19:00 | Bhulta | 401 | 0.58333 | 392 | 0.20833
| Ashuganj(N) | 405 | 18:00 | 397 | 8:00 | Gopalganj | 407 | 0.625 | 393 | 0.54167
| Payra | 411 | 14:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 238 | 7:00 | Hathazari | 234 | 14:00 | 226 | 17:00
| Ishurdi | 242 | 5:00 | 234 | 7:00 | Megnaghat | 242 | 14:00 | 238 | 1:00
| Ashuganj | 245 | 14:00 | 241 | 10:00 | Fenchuganj | 244 | 19:00 | 239 | 22:00
| Serajganj | 235 | 1:00 | 227 | 8:00 | Siddhirganj | 242 | 1:00 | 237 | 10:00
| Baghabari | 239 | 14:00 | 232 | 8:00 | Maniknagar | 0 | 14:00 | 0 | 1:00
| Barapukuria | 236 | 14:00 | 228 | 10:00 | Agargaon | 241 | 5:00 | 235 | 4:00
| Bogra | 236 | 14:00 | 222 | 8:00 | Barisal | 255 | 20:00 | 242 | 18:30
| Rajshahi | 239 | 18:00 | 224 | 8:00 | Bhola 225 MW | 257 | 16:00 | 244 | 18:30
| Khulna South | 241 | 14:00 | 228 | 18:30 | AKSML | 235 | 20:00 | 224 | 3:00
| Rampura | 238 | 19:00 | 231 | 22:00 | BSRM | 236 | 14:00 | 225 | 6:00
| Haripur | 240 | 18:00 | 236 | 7:00 | Bibiyana | 246 | 14:00 | 239 | 20:00
| Hasnabad | 242 | 18:00 | 235 | 1:00 | Bhulta | 243 | 15:00 | 237 | 4:00
| Shyampur | 240 | 14:00 | 220 | 1:00 | Ashuganj (S) | 243 | 13:00 | 238 | 4:00
| Aminbazar | 243 | 18:00 | 238 | 1:00 | Kaliakoir | 237 | 12:00 | 231 | 23:00
| Tongi | 237 | 13:00 | 231 | 9:00 | GPH | 234 | 20:00 | 225 | 7:00
| Comilla (N) | 240 | 14:00 | 232 | 5:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 14:00 | 137 | 1:00 | Madanhat | 140 | 0.375 | 136 | 0.041667
| Munsiganj | 142 | 18:30 | 136 | 1:00 | Hathazari | 139 | 0.75 | 135 | 0.70833
| Sonargaon | 140 | 18:30 | 135 | 1:00 | Khulshi | 137 | 0.33333 | 130 | 0.25
| Shyampur | 136 | 14:00 | 132 | 6:00 | Halishahar | 139 | 0.375 | 132 | 0.125
| Bhulta | 137 | 14:00 | 132 | 23:00 | Baraulia | 137 | 0.79167 | 134 | 0.041667
| Madanganj | 139 | 18:30 | 133 | 15:00 | Sikalbaha | 139 | 0.375 | 131 | 0.125
| Shitalakhya | 141 | 18:00 | 133 | 1:00 | Dohazari | 136 | 0.375 | 130 | 0.041667
| Rahim steal | 140 | 18:00 | 137 | 1:00 | Cox'sbazar | 130 | 0.41667 | 126 | 0.041667
| Matuail | 140 | 14:00 | 137 | 1:00 | Chandraghona | 139 | 0.75 | 130 | 0.25
| Ghorasal | 142 | 1:00 | 142 | 1:00 | Kaptai
| Narsinghdi | 138 | 14:00 | 134 | 23:00 | A. Khaer Stl. | 137 | 0.8125 | 134 | 0.041667
| Haripur (SBU) | 140 | 18:30 | 136 | 7:00 | Bakulia | 138 | 0.54167 | 130 | 0.25
| Ullon | 135 | 14:00 | 133 | 1:00 | Julda | 139 | 0.29167 | 130 | 0.16667
| Hasnabad | 137 | 19:30 | 134 | 15:00 | TK Chemical | 139 | 0.75 | 133 | 0.041667
| Magbazar | 136 | 3:00 | 133 | 10:00 | Modern Steel | 138 | 0.33333 | 132 | 0.20833
| Maniknagar | 138 | 4:00 | 135 | 15:00 | Shahmirpur | 139 | 0.375 | 132 | 0.20833
| Bangabhaban | 138 | 4:00 | 135 | 15:00 | Khagrachhari | 138 | 0.77083 | 131 | 0.25
| Narinda | 138 | 4:00 | 135 | 15:00 | Matarbari | 132 | 0.29167 | 128 | 0.083333
| Dhanmondi | 135 | 14:00 | 133 | 1:00 | Baroiar Hat | 139 | 0.77083 | 134 | 0.16667
| Lalbag | 139 | 18:30 | 133 | 1:00 | Rangamati | 137 | 9:00 | 131 | 6:00
| Madartek | 135 | 14:00 | 132 | 17:00 | Goalpara S/S | 136 | 14:00 | 130 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 135 | 1:00 | 127 | 0.77083
| Aftabnagar | 135 | 13:00 | 133 | 11:00 | Noapara | 135 | 14:00 | 128 | 0.29167
| Fatullah | 137 | 14:00 | 134 | 1:00 | Jessore | 133 | 4:00 | 125 | 0.29167
| Mirpur | 140 | 21:00 | 137 | 17:00 | Benapol | 134 | 0.16667 | 127 | 0.83333
| Kalyanpur | 140 | 18:30 | 137 | 5;00 | Jhenida | 133 | 1:00 | 125 | 0.33333
| Gulshan | 135 | 14:00 | 133 | 1:00 | Bottail | 136 | 0.625 | 130 | 0.375
| Uttara | 139 | 13:00 | 136 | 2:00 | G.K Project | 142 | 0 | 138 | 0.33333
| Uttara New | 140 | 18:00 | 135 | 11:00 | Faridpur | 139 | 0.16667 | 135 | 0.375
| Kamrangirchar | 137 | 18:00 | 132 | 1:00 | Madaripur | 143 | 0.375 | 138 | 0.041667
| Savar | 140 | 9:00 | 137 | 2:00 | Shariyatpur S/S | 144 | 15:00 | 138 | 0.91667
| Bhasantec | 137 | 9:00 | 135 | 4:00 | Gopalganj | 146 | 0.66667 | 140 | 0.041667
| Agargaon | 138 | 14:00 | 135 | 6:00 | Bagerhat | 134 | 14:00 | 126 | 0.77083
| Satmosjid | 137 | 9:00 | 135 | 17:00 | Mongla | 132 | 14:00 | 125 | 0.77083
| Tongi | 141 | 13:00 | 138 | 9:00 | Satkhira | 137 | 14:00 | 125 | 8:00
| Kabirpur | 137 | 14:00 | 131 | 8:00 | Gallamari | 138 | 0.625 | 128 | 0.77083
| Basundhara | 142 | 18:00 | 136 | 8:00 | Magura | 135 | 2:00 | 122 | 0.77083
| Manikganj | 143 | 21:00 | 136 | 18:30 | Narail | 133 | 0.16667 | 122 | 0.77083
| Joydevpur | 141 | 19:00 | 138 | 15:00 | Chuadanga | 130 | 3:00 | 119 | 0.77083
| New Tongi | 141 | 21:00 | 137 | 11:00 | Borguna | 140 | 4:00 | 138 | 0.041667
| Kodda | 141 | 18:30 | 131 | 11:00 | Barisal(N) | 144 | 5:00 | 139 | 20:00
| Dhamrai | 136 | 14:00 | 131 | 8:00 | Barisal (S) | 142 | 0.66667 | 136 | 0.77083
| Rajendrapur | 141 | 14:00 | 130 | 10:00 | Patuakhali(S) | 140 | 0.70833 | 135 | 0.54167
| Valuka | 130 | 23:00 | 124 | 8:00 | Bhandaria | 140 | 0.16667 | 135 | 0.77083
| Tangail | 134 | 23:00 | 126 | 8:00 | Ishurdi | 140 | 14:00 | 127 | 13:00
| Mymensing | 131 | 14:00 | 123 | 7:00 | Ruppur Paromanobik | 140 | 4:00 | 134 | 8:00
| Kishorganj | 133 | 14:00 | 128 | 7:00 | Natore | 138 | 18:00 | 130 | 8:00
| Netrokona | 130 | 1:00 | 121 | 7:00 | Bogra | 137 | 13:00 | 127 | 8:00
| Jamalpur | 137 | 14:00 | 122 | 6:00 | Noagaon | 133 | 14:00 | 120 | 8:00
| Sherpur | 135 | 14:00 | 119 | 7:00 | Rajshahi | 137 | 18:00 | 129 | 8:00
| Srimongal | 139 | 9:00 | 136 | 19:30 | Rajshahi New | 137 | 18:00 | 128 | 8:00
| Shahjibazar | 136 | 3:00 | 135 | 1:00 | C.Nawabganj | 137 | 18:00 | 125 | 8:00
| Fenchuganj | 140 | 24:00 | 137 | 20:00 | Amnura | 138 | 18:00 | 125 | 8:00
| Khulawara | 139 | 1:00 | 138 | 8:00 | Pabna | 139 | 3:00 | 134 | 8:00
| Sylhet | 137 | 7:00 | 135 | 11:00 | Shahjadpur | 142 | 1:00 | 135 | 7:00
| Chatak | 135 | 1:00 | 134 | 10:00 | Serajganj | 136 | 1:00 | 132 | 9:00
| Sunamganj | 136 | 2:00 | 133 | 13:00 | Niyamatpur | 132 | 14:00 | 117 | 8:00
| Biani Bazar | 136 | 1:00 | 134 | 18:00 | Joypurhat | 134 | 14:00 | 118 | 8:00
| Comilla(s) | 131 | 16:00 | 128 | 11:00 | Sherpur(Bogura) | 138 | 1:00 | 128 | 8:00
| Comilla(n) | 145 | 14:00 | 141 | 9:00 | Mohastangor | 137 | 14:00 | 125 | 8:00
| Chandpur | 143 | 17:00 | 140 | 18:00 | Bangura | 140 | 1:00 | 138 | 7:00
| Feni | 140 | 20:00 | 138 | 7:00 | Rangpur | 132 | 2:00 | 121 | 8:00
| Chowmuhani | 139 | 18:00 | 136 | 21:00 | Lalmonirhat | 131 | 5:00 | 118 | 8:00
| Ashuganj | 138 | 18:00 | 137 | 12:00 | Saidpur | 132 | 14:00 | 120 | 8:00
| Daudkandi | 141 | 18:00 | 137 | 7:00 | Purbasadipur | 130 | 5:00 | 115 | 9:00
| B.Baria | 135 | 14:00 | 132 | 20:00 | Thakurgaon | 132 | 14:00 | 117 | 8:00
| Ramganj | 138 | 7:00 | 136 | 22:00 | Palashbari | 134 | 14:00 | 120 | 7:00
| Chaddagram | 141 | 18:00 | 138 | 7:00 | Barapukuria | 136 | 14:00 | 128 | 10:00

## L-Curve
Date | 2021-02-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 140 | 4695 | 2002 | 6697 |  |  |  | QF-LDC-11
0:30 | 85.5 | 4656 | 2046 | 6702 | Date: | 2021-02-12
1:00 | 31 | 4617 | 2090 | 6707
1:30 | 42 | 4507 | 2053 | 6560
2:00 | 53 | 4397 | 2016 | 6413
2:30 | 75.5 | 4343 | 1992.5 | 6335.5 | [5 empty] | Gen. at Eve. Peak | 8150 | 8150 MW (19:30 )
3:00 | 98 | 4289 | 1969 | 6258 | [6 empty] | 19:30
3:30 | 49.5 | 4223 | 1962.5 | 6185.5 | [5 empty] | Gen. at Day Peak | 7139 | 7139 MW (12:00 )
4:00 | 1 | 4157 | 1956 | 6113 | [6 empty] | 12:00
4:30 | 2 | 4121 | 1935.5 | 6056.5 | [5 empty] | Highest Generation | 8150
5:00 | 3 | 4085 | 1915 | 6000 | [6 empty] | 19:30
5:30 | 10 | 4182 | 1904.5 | 6086.5
6:00 | 17 | 4279 | 1894 | 6173
6:30 | 126.5 | 4382.5 | 1893.5 | 6276
7:00 | 236 | 4486 | 1893 | 6379
7:30 | 321.5 | 4705.5 | 1962 | 6667.5
8:00 | 407 | 4925 | 2031 | 6956
8:30 | 391 | 4950 | 2055.5 | 7005.5
9:00 | 375 | 4975 | 2080 | 7055
9:30 | 262 | 4910.5 | 2068.5 | 6979
10:00 | 149 | 4846 | 2057 | 6903
10:30 | 162 | 4873 | 2052 | 6925
11:00 | 175 | 4900 | 2047 | 6947
11:30 | 188 | 4980.5 | 2062.5 | 7043
12:00 | 201 | 5061 | 2078 | 7139
12:30 | 192 | 5180.5 | 2096 | 7276.5
13:00 | 183 | 5300 | 2114 | 7414
13:30 | 160.5 | 5021.5 | 1977.5 | 6999
14:00 | 138 | 4743 | 1841 | 6584
14:30 | 106.5 | 4619.5 | 1803 | 6422.5
15:00 | 75 | 4496 | 1765 | 6261
15:30 | 68 | 4476.5 | 1758 | 6234.5
16:00 | 61 | 4457 | 1751 | 6208
16:30 | 90.5 | 4494 | 1753.5 | 6247.5
17:00 | 120 | 4531 | 1756 | 6287
17:30 | 136.5 | 4782.5 | 1967.5 | 6750
18:00 | 153 | 5034 | 2179 | 7213
18:30 | 277.5 | 5351 | 2326 | 7677
19:00 | 402 | 5668 | 2473 | 8141
19:30 | 355 | 5651 | 2499 | 8150
20:00 | 322 | 5630 | 2518 | 8148 |  |  |  | Executive Engineer
20:30 | 262.5 | 5605.5 | 2532.5 | 8138 |  |  |  | Network Operation Division
21:00 | 203 | 5581 | 2547 | 8128
21:30 | 173 | 5391.5 | 2483.5 | 7875
22:00 | 143 | 5202 | 2420 | 7622 |  |  |  |  | Page 6 of 7
22:30 | 140.5 | 5140.5 | 2293.5 | 7434
23:00 | 138 | 5079 | 2167 | 7246
23:30 | 139 | 4887 | 2084.5 | 6971.5
24:00 | 140 | 4695 | 2002 | 6697
8150 MW (19:30 )
7139 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-12 |  | Energy | 169091395
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3216 | 529 | 1267 | 1334 | 590 | 70 | 12 | 0 | 76 | 0
0:30 | 3036.5 | 506 | 1391 | 1189 | 625 | 70 | 6 | 0 | 77 | 0 | Date: | 2021-02-12
1:00 | 2857 | 483 | 1515 | 1044 | 660 | 70 | 0 | 0 | 78 | 0
1:30 | 2836.5 | 483 | 1530 | 904.5 | 660 | 70 | 0 | 0 | 76 | 0 | [7 empty] | Total Energy | 169.0914 | Total Energy Gen 169.091 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.091 MKWHr
2:00 | 2816 | 483 | 1545 | 765 | 660 | 70 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2825 | 483 | 1550.5 | 675 | 660 | 70 | 0 | 0 | 72 | 0 | [7 empty] | Energy Requirement | 169.0914
3:00 | 2834 | 483 | 1556 | 585 | 660 | 70 | 0 | 0 | 70 | 0
3:30 | 2835.5 | 483 | 1567 | 505 | 655 | 70 | 0 | 0 | 70 | 0 | [6 empty] | Shortage
4:00 | 2837 | 483 | 1578 | 425 | 650 | 70 | 0 | 0 | 70 | 0
4:30 | 2837 | 483 | 1569.5 | 393 | 635 | 70 | 0 | 0 | 69 | 0
5:00 | 2837 | 483 | 1561 | 361 | 620 | 70 | 0 | 0 | 68 | 0
5:30 | 2912.5 | 483 | 1554.5 | 378.5 | 620 | 70 | 0 | 0 | 68 | 0
6:00 | 2988 | 483 | 1548 | 396 | 620 | 70 | 0 | 0 | 68 | 0
6:30 | 2941.5 | 483 | 1549.5 | 544.5 | 620 | 70 | 0 | 0 | 66 | 1.5 |  |  |  |  | Coal
7:00 | 2895 | 483 | 1551 | 693 | 620 | 70 | 0 | 0 | 64 | 3
7:30 | 2892 | 506.5 | 1594.5 | 909.5 | 620 | 70 | 0 | 0 | 63 | 12 |  |  |  | Oil |  |  |  | ,
8:00 | 2889 | 530 | 1638 | 1126 | 620 | 70 | 0 | 0 | 62 | 21
8:30 | 2827.5 | 530 | 1609.5 | 1254.5 | 620 | 70 | 0 | 0 | 60 | 34
9:00 | 2766 | 530 | 1581 | 1383 | 620 | 70 | 0 | 0 | 58 | 47
9:30 | 2753.5 | 530 | 1556.5 | 1364 | 610 | 52.5 | 0 | 0 | 59 | 53.5
10:00 | 2741 | 530 | 1532 | 1345 | 600 | 35 | 0 | 0 | 60 | 60
10:30 | 2709.5 | 530 | 1533 | 1365.5 | 600 | 52.5 | 0 | 0 | 62 | 72.5
11:00 | 2678 | 530 | 1534 | 1386 | 600 | 70 | 0 | 0 | 64 | 85
11:30 | 2719.5 | 530 | 1509 | 1459 | 600 | 70 | 0 | 0 | 67 | 88.5
12:00 | 2761 | 530 | 1484 | 1532 | 600 | 70 | 0 | 0 | 70 | 92
12:30 | 2705.5 | 530 | 1510.5 | 1692 | 605 | 70 | 0 | 0 | 73 | 90.5
13:00 | 2650 | 530 | 1537 | 1852 | 610 | 70 | 0 | 0 | 76 | 89
13:30 | 2650 | 530 | 1537 | 1852 | 610 | 70 | 0 | 0 | 76 | 89
14:00 | 2650 | 530 | 1537 | 1852 | 610 | 70 | 0 | 0 | 76 | 89
14:30 | 2517 | 530 | 1400 | 1604.5 | 580 | 70 | 0 | 0 | 68 | 68
15:00 | 2384 | 530 | 1263 | 1357 | 550 | 70 | 0 | 0 | 60 | 47
15:30 | 2447.5 | 529 | 1294 | 1252.5 | 545 | 70 | 0 | 0 | 58 | 38.5
16:00 | 2511 | 528 | 1325 | 1148 | 540 | 70 | 0 | 0 | 56 | 30
16:30 | 2562.5 | 528 | 1337.5 | 1121.5 | 540 | 70 | 11 | 0 | 58 | 19
17:00 | 2614 | 528 | 1350 | 1095 | 540 | 70 | 22 | 0 | 60 | 8
17:30 | 2689.5 | 623 | 1346.5 | 1299.5 | 535 | 70 | 113.5 | 0 | 69 | 4
18:00 | 2765 | 718 | 1343 | 1504 | 530 | 70 | 205 | 0 | 78 | 0
18:30 | 2784.5 | 764.5 | 1364.5 | 1865 | 540 | 70 | 202.5 | 0 | 86 | 0
19:00 | 2804 | 811 | 1386 | 2226 | 550 | 70 | 200 | 0 | 94 | 0
19:30 | 2797 | 811 | 1416 | 2214 | 600 | 70 | 148 | 0 | 94 | 0
20:00 | 2856 | 811 | 1426 | 2167 | 600 | 70 | 122 | 0 | 96 | 0
20:30 | 2874 | 811 | 1442.5 | 2107.5 | 620 | 70 | 117 | 0 | 96 | 0
21:00 | 2892 | 811 | 1459 | 2048 | 640 | 70 | 112 | 0 | 96 | 0
21:30 | 2981 | 811.5 | 1402.5 | 1811.5 | 630 | 70 | 74.5 | 0 | 94 | 0
22:00 | 3070 | 812 | 1346 | 1575 | 620 | 70 | 37 | 0 | 92 | 0
22:30 | 3126.5 | 726.5 | 1310.5 | 1454.5 | 620 | 70 | 37 | 0 | 89 | 0
23:00 | 3183 | 641 | 1275 | 1334 | 620 | 70 | 37 | 0 | 86 | 0
23:30 | 3199.5 | 585 | 1271 | 1334 | 605 | 70 | 24.5 | 0 | 81 | 0 | Max Temp. in Dhaka |  | 28.2° C
24:00 | 3216 | 529 | 1267 | 1334 | 590 | 70 | 12 | 0 | 76 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 169.091 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.091 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1644000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 11 | [5 empty] | 0 | 16655
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 18 | 16 | 15 | 11 | 7 | 2 | [9 empty] | 115155
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 114 | 113 | 114 | 114 | 115 | 126 | 114 | 112 | 116 | 114 | 114 | 124 | 114 | 80 | 80 | 80 | 80 | 111 |  | 111 | 110 | 140 | 140 | 130 | 131 | 130 | 2673548
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 68 | 34 | 9 |  |  |  | 0 | 152882
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 5 | 44 | 95 | 95 | 95 | 110 | 160 | 80 | 45 | 30 | 30 | 30 |  | 179 | 215 | 218 | 218 | 180 | 110 | 15 | 2067490
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4488750
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [9 empty] | 5 | 5 | 5 | 99648
33 | Ashuganj 225 MW CCPP | 162 | 170 | 166 | 176 | 180 | 182 | 190 | 170 | 175 | 175 | 172 | 146 | 132 | 136 | 141 | 140 | 198 | 206 |  | 213 | 213 | 217 | 183 | 182 | 184 | 183 | 4226000
34 | Ashuganj 450 MW CCPP(South) | 295 | 275 | 275 | 270 | 265 | 320 | 270 | 280 | 265 | 285 | 265 | 265 | 260 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6498000
| Ashuganj 450 MW CCPP(North) | 285 | 260 | 260 | 255 | 255 | 305 | 265 | 290 | 275 | 280 | 265 | 265 | 270 | 270 | 250 | 250 | 250 | 280 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6681900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 108960
36 | Chandpur 150 MW CCPP | 40 | 36 | 41 | 36 | 36 | 36 | 35 | 36 | 33 | 42 | 44 | 76 | 47 | 45 | 50 | 45 | 45 | 45 |  | 47 | 51 | 49 | 72 | 75 | 76 | 72 | 1101330
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 353 | 352 | 361 | 347 | 346 | 363 | 363 | 368 | 341 | 345 | 343 | 357 | 373 | 295 | 253 | 363 | 350 | 353 |  | 342 | 341 | 341 | 354 | 340 | 341 | 340 | 8412160
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 273 | 302 | 314 | 331 | 333 | 354 | 353 | 343 | 336 | 330 | 330 | 326 | 320 | 260 | 290 | 288 | 290 | 320 |  | 360 | 360 | 356 | 356 | 355 | 310 | 310 | 7646000
42 | RPCL 210MW CCPP | 107 | 107 | 117 | 141 | 146 | 146 | 146 | 140 | 127 | 110 | 109 | 109 | 107 | 106 | 112 | 130 | 129 | 145 |  | 145 | 128 | 131 | 130 | 131 | 131 | 133 | 2929080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 20 | 23 | 37 | 42 | 42 | 34 | 17 | 13 | 2 | [9 empty] | 243500
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 5 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 663000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 |  | 20 | 22 | 22 | 26 | 32 | 32 | 32 | 561240
46 | Shajibazar 330 MW CCPP | 100 | 99 | 100 | 101 | 100 | 100 | 100 | 101 | 101 | 100 | 102 | 101 | 99 | 100 | 100 | 100 | 100 | 102 |  | 100 | 101 | 101 | 100 | 95 | 96 | 95 | 2338000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 74 | 74 | 71 | 69 | 69 | 69 | 69 | 72 | 72 | 71 | 50 | 50 | 50 | 50 | 60 |  | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 1626240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 60 | 25 | 25 | 100 | 100 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1737760
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 207720
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 208096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 31 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 28 |  | 28 | 22 | 22 | 22 | 2 | 2 | 2 | 774000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195072
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 310 | 310 | 300 | 300 | 310 | 310 | 290 | 290 | 285 | 270 | 310 | 270 | 290 | 290 | 300 | 290 |  | 270 | 300 | 300 | 310 | 275 | 280 | 275 | 7243000
| Bibiyana South 400 MW | 60 | 60 | 61 | 60 | 60 | 70 | 90 | 90 | 60 | 61 | 60 | 55 | 45 | 55 | 54 | 52 | 101 | 110 |  | 123 | 130 | 133 | 149 | 300 | 400 | 400 | 2565000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 7 |  | 17 | [5 empty] | 0 | 31208
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 7 | 11 | 22 | 24 | 24 | 19 | 18 | 20 | 23 | 23 | 24 |  | 23 | 23 | 23 | 23 | 23 |  | 0 | 327120
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 461424
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | [11 empty] | 16 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 246852
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 502308
63 | Impoprt (Tripura) | 78 | 74 | 70 | 70 | 68 | 68 | 64 | 62 | 58 | 60 | 64 | 70 | 76 | 68 | 60 | 56 | 60 | 78 |  | 94 | 94 | 96 | 96 | 92 | 86 | 76 | 1758720
64 | Malancha, Ctg. EPZ (United) | 16 | 26 | 26 | 32 | 32 | 27 | 32 | 32 | 32 | 33 | 33 | 33 | 30 | 30 | 30 | 26 | 36 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 815040
65 | Feni 22MW PP (Doreen) | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 432036
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 16 | 16 | 21 | 12 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 507430
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 12 | 12 | 8 | 8 | 8 | 8 | 8 | 8 |  | 21 | 26 | 32 | 32 | 32 | 32 | 32 | 521460
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 574000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 17 | 17 | 33 | 33 | 33 | 33 | 794600
73 | Ghorashal 108MW PP (Regent) | 105 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 103 | 103 | 103 | 103 | 106 | 105 | 105 | 106 | 106 |  | 106 | 107 | 107 | 107 | 107 | 107 | 107 | 2456818
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [17 empty] | 10 |  | 26 | 26 | 26 |  |  |  | 0 | 89040
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 84 | 35 | 35 | 104 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 108 | 72 | 80 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3045600
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 7 | 24 | 24 | 7 | 7 | 7 | 16 |  | 50 | 50 | 50 | 50 |  |  | 0 | 300480
78 | Gazipur 52 MW PP | [12 empty] | 12 | [13 empty] | 11280
79 | Kodda 150MW PP | [16 empty] | 16 | 16 |  | 16 | [5 empty] | 0 | 36960
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 2 | 30 | 40 | 32 | 32 | 24 | 8 | 8 | 8 | 10 |  | 40 | 40 | 16 |  |  |  | 0 | 279360
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [11 empty] | 22 | 68 | 70 | 35 | 35 | 35 | 35 | [7 empty] | 0 | 355464
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 27602
| Jodiac Power | [17 empty] | 12 |  | 48 | 54 | 54 |  |  |  | 0 | 127324
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 8 |  | 48 | 64 | 63 | 63 | 30 | 30 | 15 | 316176
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 18 | 50 | 50 | 50 | 60 | 60 | 60 | 62 | 40 | 11 | 15 |  | 54 | 62 | 62 | 61 | 30 | 30 | 0 | 800614
86 | Meghnaghat CCPP(Summit) | 265 | 270 | 260 | 265 | 250 | 280 | 260 | 265 | 260 | 270 | 250 | 245 | 240 | 250 | 240 | 260 | 270 | 275 |  | 260 | 270 | 270 | 275 | 255 | 265 | 220 | 6235258
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 12 |  | 24 | 24 | 24 | 24 |  |  | 0 | 99840
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 14 | 34 | 34 | 25 | 17 | 17 | 17 |  | 56 | 70 | 70 | 70 | 48 |  | 0 | 447360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 | [7 empty] | 0 | 6600
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 0 |  | 0 | 875736
93 | Ashuganj 51 MW PP (Midland) | [25 empty] | 0 | 0
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 7 |  | 16 | 7 | 7 | 7 |  |  | 0 | 41328
95 | Patenga 50MW PP (Baraka) | 25 | [6 empty] | 2 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 43 | 50 | 50 | 50 | 50 | 50 | 25 | 594720
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 2 | 13 | [7 empty] | 0 | 28800
97 | katpotti 52 MW | [8 empty] | 19 | 24 | 24 | [14 empty] | 0 | 102000
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 36 | 40 | 40 | 40 |  |  | 0 | 248046
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 10 |  | 17 | 17 |  |  |  |  | 0 | 33424
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 130 | 130 | 130 | 163 | 100 | 100 | 163 | 163 | 163 |  | 130 | 130 | 130 | 163 | 110 | 110 | 110 | 3266836
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 9650
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 25 | 35 | 54 | 54 | 17 | 17 | 17 | 30 |  | 54 | 54 | 54 | 54 | 17 |  | 0 | 442800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 120 | 30 | 25 | 8 | 8 | 8 | 40 | 134 | 200 | 180 | 193 | 200 | 200 | 200 | 150 | 100 | 100 | 110 |  | 150 | 150 | 150 | 150 | 150 | 150 | 75 | 3134400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 20 | [5 empty] | 5 | 15 |  |  |  | 7 | 50 | 80 | 96 | 100 | 100 | 100 |  | 139 | 149 | 149 | 122 | 70 | 31 | 30 | 1155460
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 50 |  |  |  |  | 30 | 75 | 80 | 50 | 50 | 50 | 82 | 100 | 50 | 20 | 20 | 32 |  | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 1133760
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 |  |  |  | 8 | 17 | 17 | 17 | 17 | 17 | 20 | 34 | 34 | 34 | 34 | 41 |  | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 621120
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 410 | 411 | 410 | 410 | 409 | 410 | 410 | 407 | 409 | 411 | 411 | 411 | 414 | 306 | 316 | 340 | 340 | 338 |  | 304 | 304 | 304 | 304 | 276 | 279 | 280 | 8770000
| Jamalpur 115 MW PP (United) | [17 empty] | 8 |  | 16 | [6 empty] | 39600
| Anwara 300 MW PP (United) | 106 | 105 | 105 | 68 | 68 | 68 | 161 | 248 | 251 | 197 | 197 | 197 | 230 | 179 | 179 | 144 | 144 | 194 |  | 251 | 251 | 251 | 251 | 251 | 252 | 216 | 4305600
| Juldah unit-2 (Acorn) | 100 | 80 |  |  |  | 5 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 1881600
| Anlima Energy Ltd. | [25 empty] | 0 | 0
| Bhairob 54.5 MW | [9 empty] | 1 | 10 | 16 | [14 empty] | 26640
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 12 | 15 | 22 | 22 | 21 | 20 | 14 | 7 | 4 | [9 empty] | 143809
120 | Eastern Zone Total | 4617 | 4397 | 4289 | 4157 | 4085 | 4279 | 4486 | 4925 | 4975 | 4846 | 4900 | 5061 | 5300 | 4743 | 4496 | 4457 | 4531 | 5034 |  | 5668 | 5651 | 5630 | 5581 | 5202 | 5079 | 4695 | 117555736
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 16 | [5 empty] | 0 | 33600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 53 |  | 53 | 53 | 53 | 53 | 17 |  | 0 | 237600
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 70368
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 54 | 49 | 35 | 35 | 35 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 52 | 52 | 33 | 33 | 33 | 33 |  | 71 | 76 | 80 | 81 | 87 | 56 | 55 | 1078818
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 19 | 20 | 20 | 19 | 18 | 13 | 15 | 15 | 18 | 21 | 15 | 14 | 13 | 14 | 19 |  | 25 | 26 | 26 | 26 | 26 | 25 | 25 | 462000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 6 | 2 |  | 14 | 12 | 13 | 12 | 12 | 12 | 12 | 58752
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 483 | 483 | 483 | 483 | 483 | 483 | 483 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 528 | 528 | 718 |  | 811 | 811 | 811 | 811 | 812 | 641 | 529 | 13922181
147 | Bheramara 410 MW CCPP | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 155 | 140 | 140 | 135 | 105 | 100 | 105 | 100 | 100 | 120 |  | 170 | 180 | 195 | 195 | 265 | 270 | 310 | 4046112
148 | Payra 1320 MW | 510 | 510 | 510 | 500 | 470 | 470 | 470 | 470 | 470 | 450 | 450 | 450 | 460 | 400 | 400 | 390 | 390 | 380 |  | 400 | 450 | 450 | 490 | 470 | 470 | 440 | 11929800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3656000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 161 | 165 | 164 | 162 | 160 | 165 | 173 | 162 | 151 | 150 | 135 | 130 | 125 | 123 | 125 | 124 | 125 | 143 |  | 152 | 151 | 151 | 151 | 151 | 150 | 150 | 3805100
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 405 | 411 | 414 | 414 | 404 | 380 | 372 | 417 | 414 | 414 | 418 | 384 | 353 | 270 | 270 | 276 | 273 | 222 |  | 223 | 222 | 231 | 220 | 230 | 231 | 228 | 7997727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 488880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253800
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 8 | [5 empty] | 28800
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 16 | [5 empty] | 0 | 29760
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 102 |  | 102 | 102 | 100 | 100 | 25 | 25 | 0 | 463024
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 35 | [5 empty] | 27 | 70 | 70 | 70 | 87 | 113 | 50 | 35 | 35 | 35 | 38 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1376928
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 55 | 90 | 50 | 35 | 35 | 35 | 60 |  | 70 | 70 | 70 | 70 | 35 | 35 | 0 | 694272
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 30 | 60 | 70 | 70 | 70 | 80 | 65 | 35 | 35 | 35 | 55 |  | 70 | 70 | 70 | 70 | 38 |  | 0 | 872640
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 3 | 4 | 4 | 4 | 5 | 2 | 1 | 0 | [9 empty] | 29497
178
178