## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-17 | Wednesday
|  |  | Date (day): | 2021-02-17 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13174.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14144 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-16 | 2021-02-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 103 | 12 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 337 | 339 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 210 | 225 | 225 |  | 225 | GT-1 Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 42 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 240 | 300 | 300
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 85 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 51 | 60 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 115 | 115 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 70 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 72 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 132 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 50 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 55 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 8 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 260 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 147 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 101 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 28 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 1926 | 2563 | 3585 | 3807 | 108 | 1963
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 41 | 46 | 46
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 19 | 12 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 306 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 46 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 647 | 866 | 1317 | 1355 | 895 | 115
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 166 | 167 | 220 | 220
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 280 | 280 | 80 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 255 | 260 | 280 | 280 | 80 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 20 | 20 | 25 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 2 | 2 | 40 | 40 | 15 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under fround cable fault
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under fround cable fault
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 74 | 80 | 80 |  | 83 | Gas shortage & ST under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 60 | 85 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 110 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 20 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 52 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 2 | 8 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 994 | 1144 | 1627 | 1889 | 785 | 89
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 118 | 145 | 145 | 57 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 30 | 80 | 80 |  | 15 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 194 | 195 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 95 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 17 | 14 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 425 | 474 | 635.6 | 584 | 57 | 15
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 32 | 32 | 32 | 32 |  | 58 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 126 | 114 | 135 | 135 |  | 195 | GT-2 under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 38 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 72 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 100 | 100
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 138 | 138 | 136 | 136 |  | 95
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 304 | 340 | 350 | 350
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 4 | 5 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 422 | 205 | 400 | 400 |  |  | On Test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1555 | 1383 | 1837 | 1837 | 0 | 507
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 823 | 843 | 836 | 933
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 83 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 6 | 7 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 320 | 250 | 250
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 80 | 90 | 90 |  | 15 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1202 | 1343 | 1566 | 1949 | 0 | 93
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 25 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 34 | 87 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 430 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 37 | 36 | 38 | 38 |  |  | On Test
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 505 | 610 | 1039 | 1039 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 12 | 12 |  | 38 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 161 | 220 | 220 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 379 | 297 | 400 | 400 |  |  | FGMO
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 101 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 112 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 805 | 905 | 1297 | 1421 | 651 | 38
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 99 | 107 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 254 | 257 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 8313 | 9545 | 13174.6 | 14144 | 2620 | 3231
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7936.7595 | 9113 | 12578.3269 | 13503.8525
| A. |  | 2021-02-16 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9545 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6129 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9545 | MW
| 3 | Day peak Generation : |  |  | 8313 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9113 | MW
| 4 | Evening peak Generation : |  |  | 9545 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 190.9914 | MKWHr | By Solar | 0.59674 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 108.2102 | MKWHr |  | By Oil: | 44.956 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.9558 | MKWHr |  | By Hydro: | 1.684 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2620 | MW | Dhaka | 3260 | 3260 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3231 | MW | Chittagong | 922 | 922 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5851 | MW | Khulna | 1144 | 1144 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 874.96 | MMCFD |  |  | Rajshahi | 996 | 996 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 110148757.43 | ii) Oil : | Taka | 281350036.4 | Comilla | 774 | 774 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69447495 | Total | Taka | 460946288.83 | Mymensingh | 774 | 774 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.023 | MKWHr. | Sylhet | 346 | 346 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -64 | MW (E to W) at | 19:00 | hrs | Barisal | 227 | 227 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -64 | MW at | 19:00 | hrs | Rangpur | 670 | 670 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.0° C |  |  | Total | 9113 | 9113 |  | 0
| B. |  | 2021-02-17 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14144 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4444 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 194.0928 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6195 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.4516 | MKWHr. | ii) HVDC Flow at Peak Time |  | 843 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.137 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.54 |  | (b) Today: | 93.39 |  | (c) Rule Curve: |  | 94.76
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 337 | 0 |  | 0 | 0 | 125 | 0 | 30 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 0 | 275 | 255 | 201 | 8 | 48 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 78 | 131 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 130 | 125 | 0 | 75 | 0 | 136 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 27 | 0 | 50 | 85 | 0 | 417 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 50 | 396 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 538 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 160 | 0 | 350 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 500 | 18 | 0 | 0 |  | 4586 | 2196 | 6782 | 3414 | 538 | 1092 | 928 | 650 | 70 | 12 | 78 | 0 | 0 | 93.57
2:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 333 | 0 |  | 0 | 0 | 125 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 38 | 0 | 0 | 0 | 275 | 255 | 204 | 8 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 72 | 131 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 130 | 127 | 0 | 75 | 0 | 136 | 0 | 0 | 5 | 270 | 8 | 11 | 0 | 0 | 0 | 0 | 85 | 0 | 16 | 0 | 30 | 51 | 0 | 380 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 30 | 400 | 0 | 0 | 108 | 0 | 0 | 0 | 0 |  | 539 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 156 | 0 | 345 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 4293 | 2158 | 6451 | 3382 | 539 | 1055 | 671 | 650 | 70 | 12 | 72 | 0 | 0 | 93.56
3:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 336 | 0 |  | 0 | 0 | 120 | 0 | 15 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 38 | 0 | 0 | 0 | 275 | 255 | 199 | 8 | 51 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 68 | 144 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 127 | 0 | 40 | 0 | 135 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 0 | 10 | 20 | 0 | 357 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 30 | 400 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 538 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 158 | 0 | 386 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 4076 | 2146 | 6222 | 3370 | 538 | 1065 | 507 | 600 | 70 | 4 | 68 | 0 | 0 | 93.56
4:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 333 | 0 |  | 0 | 0 | 130 | 0 | 15 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 10 | 0 | 0 | 0 | 275 | 255 | 199 | 8 | 51 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 66 | 154 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 126 | 0 | 40 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 65 | 0 | 16 | 0 | 10 | 17 | 0 | 357 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 30 | 400 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 538 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 157 | 0 | 356 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 |  | 4062 | 2094 | 6156 | 3381 | 538 | 1016 | 511 | 570 | 70 | 4 | 66 | 0 | 0 | 93.55
5:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 339 | 0 |  | 0 | 0 | 170 | 0 | 15 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 8 | 0 | 0 | 0 | 275 | 255 | 190 | 8 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 68 | 154 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 127 | 0 | 40 | 0 | 136 | 0 | 0 | 5 | 305 | 8 | 8 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 10 | 17 | 0 | 316 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 30 | 400 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 538 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 161 | 0 | 335 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 |  | 4073 | 2056 | 6129 | 3383 | 538 | 992 | 534 | 540 | 70 | 4 | 68 | 0 | 0 | 93.55
6:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 342 | 0 |  | 0 | 0 | 230 | 0 | 15 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 8 | 0 | 0 | 0 | 300 | 275 | 186 | 8 | 51 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 72 | 155 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 127 | 0 | 40 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 10 | 17 | 0 | 316 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 30 | 400 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 715 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 163 | 0 | 338 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 15 | 390 | 0 | 0 | 0 |  | 4183 | 2254 | 6437 | 3431 | 715 | 991 | 614 | 540 | 70 | 4 | 72 | 0 | 0 | 93.54
7:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 352 | 0 |  | 0 | 0 | 280 | 0 | 15 | 3 | 0 | 0 | 120 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 6 | 19 | 15 | 0 | 0 | 0 | 295 | 275 | 166 | 8 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 72 | 155 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 126 | 0 | 69 | 0 | 136 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 8 | 0 | 0 | 103 | 0 | 3 | 1 | 50 | 32 | 0 | 303 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 60 | 400 | 2 | 1 | 85 | 0 | 0 | 0 | 1 |  | 822 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 169 | 0 | 365 | 6 | 0 | 43 | 0 | 0 | 0 | 0 | 35 | 390 | 0 | 0 | 0 |  | 4564 | 2426 | 6990 | 3404 | 822 | 1062 | 1013 | 540 | 70 | 4 | 72 | 3 | 0 | 93.54
8:00 | 0 | 0 | 0 | 190 | 0 | 106 | 0 | 356 | 0 |  | 0 | 0 | 280 | 0 | 32 | 15 | 0 | 0 | 162 | 7 | 0 | 0 | 33 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 33 | 17 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 18 | 19 | 4 | 0 | 0 | 0 | 295 | 275 | 165 | 0 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 82 | 155 | 0 | 22 | 1 | 0 | 32 | 8 | 0 | 130 | 127 | 0 | 69 | 0 | 136 | 0 | 0 | 5 | 315 | 8 | 8 | 0 | 105 | 0 | 0 | 175 | 0 | 50 | 5 | 50 | 50 | 0 | 398 | 0 | 0 | 0 | 1 | 288 | 0 | 0 | 0 | 0 | 100 | 201 | 17 | 10 | 126 | 0 | 0 | 0 | 6 |  | 823 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 188 | 0 | 361 | 53 | 0 | 96 | 0 | 90 | 0 | 1 | 90 | 410 | 0 | 0 | 0 |  | 4993 | 2713 | 7706 | 3370 | 823 | 1069 | 1704 | 560 | 70 | 4 | 82 | 24 | 0 | 93.53
9:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 346 | 0 |  | 0 | 0 | 250 | 0 | 64 | 15 | 0 | 0 | 155 | 7 | 0 | 0 | 38 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 33 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 34 | 19 | 2 | 0 | 0 | 0 | 275 | 255 | 165 | 0 | 49 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 88 | 124 | 24 | 22 | 1 | 0 | 32 | 8 | 0 | 130 | 127 | 0 | 69 | 0 | 137 | 0 | 0 | 4 | 290 | 8 | 8 | 0 | 210 | 0 | 0 | 194 | 0 | 71 | 9 | 100 | 50 | 0 | 422 | 18 | 0 | 0 | 2 | 305 | 0 | 0 | 0 | 0 | 100 | 420 | 39 | 20 | 144 | 0 | 0 | 0 | 13 |  | 822 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 194 | 0 | 321 | 53 | 0 | 113 | 0 | 98 | 0 | 2 | 113 | 440 | 17 | 0 | 0 |  | 5467 | 2800 | 8267 | 3534 | 822 | 1041 | 2071 | 590 | 70 | 4 | 88 | 47 | 0 | 93.53
10:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 334 | 0 |  | 0 | 0 | 270 | 0 | 64 | 15 | 0 | 0 | 70 | 7 | 0 | 0 | 37 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 26 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 37 | 19 | 2 | 0 | 0 | 0 | 275 | 255 | 172 | 0 | 50 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 90 | 126 | 41 | 22 | 2 | 0 | 32 | 8 | 0 | 130 | 127 | 0 | 69 | 0 | 137 | 0 | 0 | 4 | 280 | 8 | 8 | 0 | 220 | 0 | 0 | 194 | 0 | 100 | 14 | 70 | 50 | 0 | 361 | 8 | 0 | 0 | 3 | 253 | 0 | 0 | 0 | 0 | 100 | 421 | 104 | 29 | 144 | 0 | 0 | 10 | 20 |  | 824 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 185 | 0 | 335 | 53 | 0 | 113 | 0 | 99 | 0 | 3 | 113 | 390 | 38 | 0 | 0 |  | 5390 | 2710 | 8100 | 3321 | 824 | 1043 | 2137 | 540 | 70 | 4 | 90 | 71 | 0 | 93.52
11:00 | 0 | 0 | 0 | 190 | 0 | 97 | 0 | 337 | 0 |  | 0 | 0 | 270 | 0 | 64 | 15 | 0 | 0 | 115 | 7 | 0 | 16 | 41 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 39 | 19 | 2 | 0 | 0 | 0 | 275 | 255 | 177 | 0 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 92 | 103 | 41 | 22 | 2 | 0 | 32 | 8 | 0 | 130 | 126 | 0 | 72 | 0 | 137 | 0 | 0 | 4 | 300 | 8 | 8 | 0 | 220 | 0 | 0 | 194 | 0 | 100 | 17 | 70 | 50 | 0 | 304 | 8 | 0 | 0 | 4 | 253 | 0 | 0 | 0 | 0 | 100 | 421 | 104 | 33 | 144 | 0 | 0 | 32 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 188 | 0 | 330 | 53 | 0 | 113 | 0 | 99 | 0 | 4 | 113 | 390 | 37 | 0 | 0 |  | 5448 | 2705 | 8153 | 3331 | 823 | 1050 | 2165 | 540 | 70 | 22 | 92 | 60 | 0 | 93.52
12:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 337 | 0 |  | 0 | 0 | 280 | 0 | 64 | 15 | 0 | 0 | 115 | 7 | 0 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 10 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 39 | 19 | 3 | 0 | 0 | 0 | 275 | 255 | 166 | 0 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33 | 21 | 90 | 104 | 40 | 22 | 2 | 0 | 32 | 11 | 0 | 130 | 126 | 0 | 72 | 0 | 138 | 0 | 0 | 4 | 300 | 8 | 8 | 0 | 260 | 0 | 0 | 194 | 0 | 100 | 18 | 90 | 60 | 0 | 304 | 8 | 0 | 0 | 4 | 304 | 0 | 0 | 0 | 0 | 100 | 422 | 104 | 38 | 144 | 0 | 0 | 2 | 28 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 187 | 0 | 379 | 53 | 0 | 113 | 0 | 99 | 0 | 5 | 95 | 420 | 37 | 0 | 0 |  | 5547 | 2766 | 8313 | 3279 | 823 | 1109 | 2255 | 570 | 70 | 22 | 90 | 95 | 0 | 93.51
13:00 | 0 | 0 | 0 | 190 | 0 | 107 | 0 | 340 | 0 |  | 0 | 0 | 250 | 0 | 66 | 30 | 0 | 0 | 145 | 7 | 0 | 16 | 51 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 10 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 39 | 19 | 9 | 0 | 0 | 0 | 275 | 255 | 166 | 0 | 79 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 98 | 102 | 24 | 22 | 2 | 0 | 32 | 8 | 0 | 163 | 126 | 0 | 69 | 0 | 137 | 0 | 0 | 5 | 285 | 8 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 100 | 17 | 100 | 74 | 0 | 304 | 8 | 0 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 100 | 317 | 104 | 39 | 144 | 0 | 0 | 22 | 28 |  | 822 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 203 | 0 | 386 | 53 | 0 | 113 | 0 | 99 | 0 | 5 | 95 | 450 | 37 | 0 | 0 |  | 5600 | 2812 | 8412 | 3235 | 822 | 1138 | 2331 | 600 | 70 | 23 | 98 | 95 | 8412 | 93.51
14:00 | 0 | 0 | 0 | 190 | 0 | 72 | 0 | 337 | 0 |  | 0 | 0 | 280 | 0 | 99 | 45 | 0 | 0 | 80 | 7 | 7 | 16 | 50 | 0 | 0 | 0 | 35 | 0 | 15 | 16 | 25 | 26 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 39 | 19 | 3 | 0 | 0 | 0 | 275 | 255 | 175 | 0 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 102 | 102 | 24 | 22 | 2 | 0 | 32 | 8 | 0 | 110 | 127 | 0 | 69 | 0 | 137 | 0 | 0 | 4 | 270 | 8 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 85 | 15 | 100 | 85 | 0 | 304 | 35 | 0 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 100 | 318 | 104 | 34 | 144 | 0 | 0 | 29 | 24 |  | 823 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 149 | 0 | 321 | 35 | 0 | 113 | 0 | 99 | 0 | 4 | 113 | 390 | 37 | 0 | 0 |  | 5571 | 2607 | 8178 | 3114 | 823 | 964 | 2459 | 540 | 70 | 23 | 102 | 83 | 0 | 93.5
15:00 | 0 | 0 | 0 | 190 | 0 | 72 | 0 | 339 | 0 |  | 0 | 0 | 280 | 0 | 99 | 55 | 0 | 0 | 62 | 7 | 7 | 16 | 50 | 0 | 0 | 0 | 35 | 0 | 17 | 16 | 25 | 30 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 39 | 19 | 3 | 0 | 0 | 0 | 280 | 260 | 171 | 8 | 78 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 98 | 101 | 24 | 22 | 2 | 0 | 32 | 8 | 0 | 110 | 120 | 0 | 69 | 0 | 122 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 245 | 0 | 0 | 194 | 0 | 75 | 11 | 100 | 85 | 0 | 315 | 35 | 0 | 0 | 3 | 307 | 0 | 0 | 0 | 0 | 100 | 317 | 102 | 22 | 144 | 0 | 0 | 21 | 18 |  | 823 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 144 | 0 | 322 | 17 | 0 | 113 | 0 | 99 | 0 | 3 | 70 | 370 | 37 | 0 | 0 |  | 5501 | 2524 | 8025 | 3091 | 823 | 1004 | 2337 | 520 | 70 | 23 | 98 | 59 | 0 | 93.5
16:00 | 0 | 0 | 0 | 190 | 0 | 72 | 0 | 338 | 0 |  | 0 | 30 | 285 | 0 | 80 | 40 | 0 | 0 | 70 | 7 | 7 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 30 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 39 | 19 | 5 | 0 | 0 | 0 | 275 | 260 | 171 | 8 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 33 | 20 | 88 | 101 | 24 | 22 | 1 | 0 | 32 | 8 | 0 | 110 | 114 | 0 | 69 | 0 | 123 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 195 | 0 | 0 | 193 | 0 | 75 | 6 | 70 | 85 | 0 | 315 | 35 | 0 | 0 | 2 | 253 | 0 | 0 | 0 | 0 | 70 | 318 | 44 | 11 | 144 | 0 | 0 | 32 | 10 |  | 822 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 160 | 0 | 327 | 17 | 0 | 70 | 0 | 71 | 0 | 2 | 35 | 370 | 37 | 0 | 0 |  | 5235 | 2466 | 7701 | 3107 | 822 | 1040 | 1969 | 520 | 70 | 53 | 88 | 32 | 0 | 93.49
17:00 | 0 | 0 | 0 | 190 | 0 | 72 | 0 | 353 | 0 |  | 0 | 30 | 285 | 1 | 80 | 40 | 0 | 0 | 70 | 7 | 7 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 30 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 4 | 39 | 19 | 4 | 0 | 0 | 0 | 305 | 290 | 144 | 8 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 90 | 104 | 24 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 114 | 0 | 69 | 0 | 123 | 0 | 0 | 5 | 320 | 8 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 75 | 2 | 70 | 85 | 0 | 316 | 35 | 0 | 0 | 0 | 252 | 2 | 0 | 0 | 4 | 96 | 182 | 34 | 4 | 144 | 0 | 0 | 25 | 3 |  | 822 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 0 | 0 | 16 | 4 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 170 | 0 | 348 | 17 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 370 | 37 | 0 | 0 |  | 5168 | 2512 | 7680 | 3034 | 822 | 1085 | 1988 | 520 | 70 | 62 | 90 | 9 | 0 | 93.49
18:00 | 0 | 0 | 0 | 190 | 0 | 72 | 0 | 344 | 0 |  | 0 | 120 | 295 | 21 | 80 | 50 | 0 | 0 | 70 | 24 | 50 | 82 | 50 | 0 | 0 | 0 | 17 | 17 | 22 | 16 | 25 | 18 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 12 | 0 | 85 | 7 | 25 | 39 | 19 | 10 | 0 | 0 | 0 | 285 | 270 | 159 | 8 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 4 | 18 | 11 | 33 | 20 | 108 | 123 | 24 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 114 | 0 | 72 | 0 | 123 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 237 | 0 | 0 | 194 | 0 | 116 | 0 | 95 | 85 | 0 | 317 | 38 | 0 | 0 | 0 | 252 | 17 | 0 | 0 | 17 | 100 | 175 | 50 | 0 | 144 | 0 | 0 | 24 | 0 |  | 823 | 0 | 290 | 0 | 45 | 0 | 0 | 0 | 7 | 10 | 8 | 0 | 25 | 16 | 0 | 0 | 0 | 15 | 0 | 100 | 12 | 0 | 0 | 8 | 9 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 165 | 0 | 348 | 53 | 0 | 70 | 0 | 81 | 0 | 0 | 50 | 370 | 37 | 0 | 0 |  | 5705 | 2802 | 8507 | 2999 | 823 | 1226 | 2453 | 520 | 70 | 308 | 108 | 0 | 0 | 93.48
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 339 | 0 |  | 0 | 210 | 240 | 42 | 85 | 55 | 0 | 0 | 115 | 70 | 72 | 132 | 51 | 0 | 0 | 0 | 54 | 55 | 50 | 16 | 25 | 30 | 20 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 85 | 10 | 45 | 41 | 19 | 19 | 0 | 0 | 0 | 275 | 260 | 167 | 8 | 74 | 5 | 2 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 110 | 118 | 30 | 22 | 0 | 0 | 32 | 38 | 0 | 130 | 114 | 0 | 72 | 0 | 138 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 147 | 0 | 100 | 85 | 0 | 340 | 95 | 0 | 0 | 0 | 306 | 46 | 0 | 0 | 52 | 100 | 205 | 101 | 0 | 144 | 0 | 0 | 8 | 0 |  | 843 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 101 | 12 | 0 | 0 | 8 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 161 | 0 | 297 | 80 | 0 | 112 | 0 | 107 | 0 | 0 | 113 | 430 | 36 | 0 | 0 |  | 6430 | 3115 | 9545 | 3105 | 843 | 1252 | 3181 | 580 | 70 | 404 | 110 | 0 | 0 | 93.47
19:30 | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 339 | 0 |  | 0 | 220 | 275 | 16 | 100 | 40 | 0 | 0 | 115 | 50 | 16 | 132 | 50 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 32 | 20 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 16 | 0 | 85 | 0 | 12 | 39 | 19 | 27 | 0 | 0 | 0 | 275 | 260 | 176 | 8 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 110 | 117 | 77 | 22 | 0 | 0 | 32 | 48 | 0 | 163 | 112 | 0 | 72 | 0 | 138 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 132 | 0 | 100 | 85 | 0 | 339 | 65 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 26 | 100 | 205 | 70 | 0 | 144 | 0 | 0 | 0 | 0 |  | 842 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 102 | 12 | 0 | 0 | 8 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 159 | 0 | 326 | 80 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 37 | 0 | 0 |  | 6234 | 3112 | 9346 | 3116 | 842 | 1362 | 2831 | 610 | 70 | 405 | 110 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 339 | 0 |  | 0 | 225 | 265 | 25 | 100 | 40 | 0 | 0 | 115 | 50 | 16 | 132 | 55 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 85 | 0 | 0 | 39 | 19 | 32 | 0 | 0 | 0 | 250 | 220 | 181 | 8 | 74 | 20 | 2 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 106 | 117 | 82 | 22 | 0 | 0 | 32 | 48 | 0 | 163 | 112 | 0 | 72 | 0 | 138 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 85 | 0 | 339 | 45 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 26 | 100 | 206 | 81 | 0 | 144 | 0 | 0 | 0 | 0 |  | 843 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 102 | 12 | 0 | 0 | 8 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 161 | 0 | 374 | 73 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 37 | 0 | 0 |  | 6138 | 3178 | 9316 | 3085 | 843 | 1402 | 2775 | 630 | 70 | 405 | 106 | 0 | 0 | 93.47
21:00 | 0 | 0 | 0 | 190 | 0 | 25 | 0 | 340 | 0 |  | 0 | 225 | 270 | 16 | 100 | 15 | 0 | 0 | 115 | 40 | 0 | 132 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 17 | 0 | 0 | 39 | 19 | 33 | 0 | 0 | 0 | 250 | 220 | 196 | 8 | 78 | 26 | 15 | 0 | 0 | 0 | 0 | 8 | 18 | 11 | 33 | 20 | 108 | 117 | 64 | 22 | 0 | 0 | 32 | 53 | 0 | 163 | 113 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 117 | 0 | 100 | 85 | 0 | 339 | 8 | 0 | 0 | 0 | 306 | 17 | 0 | 0 | 8 | 100 | 325 | 62 | 0 | 144 | 0 | 0 | 0 | 0 |  | 843 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 167 | 0 | 392 | 73 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 38 | 0 | 0 |  | 6036 | 3099 | 9135 | 3216 | 843 | 1466 | 2516 | 650 | 70 | 266 | 108 | 0 | 0 | 93.47
22:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 338 | 0 |  | 0 | 225 | 275 | 0 | 64 | 15 | 0 | 0 | 115 | 0 | 0 | 115 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 36 | 0 | 0 | 0 | 250 | 220 | 218 | 8 | 80 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 98 | 117 | 40 | 22 | 0 | 0 | 32 | 53 | 0 | 163 | 112 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 145 | 0 | 0 | 195 | 0 | 92 | 0 | 100 | 85 | 0 | 339 | 8 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 8 | 100 | 350 | 20 | 0 | 144 | 0 | 0 | 0 | 0 |  | 843 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 168 | 0 | 409 | 17 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 510 | 38 | 0 | 0 |  | 5663 | 2849 | 8512 | 3253 | 843 | 1502 | 1912 | 660 | 70 | 174 | 98 | 0 | 0 | 93.46
23:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 345 | 0 |  | 0 | 225 | 285 | 0 | 30 | 15 | 0 | 0 | 80 | 0 | 0 | 64 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 208 | 8 | 75 | 26 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 92 | 118 | 40 | 22 | 0 | 0 | 32 | 53 | 0 | 110 | 119 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 45 | 0 | 0 | 195 | 0 | 68 | 0 | 100 | 85 | 0 | 339 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 325 | 16 | 0 | 144 | 0 | 0 | 0 | 0 |  | 840 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 164 | 0 | 427 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 470 | 37 | 0 | 0 |  | 5336 | 2568 | 7904 | 3194 | 840 | 1469 | 1543 | 620 | 70 | 76 | 92 | 0 | 0 | 93.46
24:00 | 0 | 0 | 0 | 190 | 0 | 55 | 0 | 348 | 0 |  | 0 | 225 | 290 | 0 | 15 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 184 | 8 | 75 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 86 | 119 | 24 | 22 | 0 | 0 | 32 | 8 | 0 | 130 | 116 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 280 | 8 | 11 | 0 | 15 | 0 | 0 | 195 | 0 | 32 | 0 | 40 | 85 | 0 | 340 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 325 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 840 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 163 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 35 | 0 | 0 |  | 4960 | 2457 | 7417 | 3151 | 840 | 1397 | 1246 | 620 | 70 | 7 | 86 | 0 | 0 | 93.45
KWH | 0 | 0 | 0 | 4520250 | 0 | 1943500 | 0 | 8330240 | 0 |  | 0 | 1305000 | 5784960 | 110400 | 1393464 | 522477 | 0 | 0 | 2765000 | 292800 | 167184 | 792000 | 921130 | 0 | 0 | 0 | 357480 | 100514 | 187608 | 414720 | 600000 | 639540 | 565600 | 588400 | 0 | 0 | 0 | 1684000 | 0 | 0 | 41569 | 0 | 0 | 0 | 0 |  | 222240 | 0 | 232756 | 10320 | 93120 | 672960 | 462096 | 430560 | 0 | 0 | 0 | 6973700 | 6196000 | 4372000 | 150545 | 1563590 | 207360 | 135360 | 0 | 0 | 0 | 0 | 53227 | 379008 | 250200 | 820700 | 520610 | 2136960 | 2894320 | 589440 | 511236 | 12200 | 0 | 765480 | 401400 | 0 | 3274363 | 2795000 | 0 | 1613760 | 0 | 3890950 | 0 | 0 | 114480 | 7391500 | 192000 | 211000 | 0 | 3919199 | 0 | 0 | 3873600 | 0 | 1650096 | 112995 | 1676160 | 1564800 | 0 | 8185000 | 420000 | 0 | 0 | 28682 | 6104618 | 110358 | 0 | 0 | 171360 | 1937280 | 7809900 | 1124160 | 246720 | 2972160 | 0 | 0 | 214920 | 168769 |  | 18451636 | 0 | 8318016 | 0 | 147840 | 0 | 0 | 0 | 121440 | 58752 | 9000 | 0 | 432600 | 11990 | 0 | 0 | 0 | 87824 | 0 | 474144 | 33700 | 0 | 0 | 22560 | 47794 | 494640 | 0 | 210780 | 0 | 0 | 3681100 | 0 | 0 | 0 | 0 | 0 | 0 | 1106835 | 0 | 4296636 | 0 | 8566036 | 775680 | 0 | 1965600 | 0 | 1495680 | 0 | 27379 | 1419648 | 11274700 | 600300 | 0 | 0 |  | 126859054 | 64132310 | 190991364 | 80249332 | 18451636 | 27960879 | 43141302 | 14955800 | 1684000 | 1814710 | 2136960 | 596745 | 0
Fuel Cost | 0 | 0 | 0 | 6644767.5 | 0 | 2565420 | 0 | 8413542.4 | 0 |  | 0 | 1422450 | 6421305.6 | 837936 | 9600966.96 | 4420155.42 | 0 | 0 | 4783450 | 2204784 | 1524718.08 | 7793280 | 8492818.6 | 0 | 0 | 0 | 2609604 | 776973.22 | 1849814.88 | 311040 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 454680 | 0 | 0 | 386176.01 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2257733.2 | 98556 | 810144 | 5329843.2 | 582240.96 | 1278763.2 | 0 | 0 | 0 | 5160538 | 6196000 | 4022240 | 194203.05 | 1798128.5 | 234316.8 | 189504 | 0 | 0 | 0 | 0 | 508317.85 | 481340.16 | 187650 | 1436225 | 390457.5 | 16027200 | 3067979.2 | 5352115.2 | 649269.72 | 194468 | 0 | 1224768 | 714492 | 0 | 3732773.82 | 2906800 | 0 | 3082281.6 | 0 | 6731343.5 | 0 | 0 | 233539.2 | 7465415 | 144000 | 160360 | 0 | 29629144.44 | 0 | 0 | 20142720 | 0 | 16236944.64 | 1320911.55 | 13660704 | 16978080 | 0 | 7612050 | 3830400 | 0 | 0 | 0 | 46150912.08 | 961218.18 | 0 | 0 | 1468555.2 | 12902284.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 106281423.36 | 0 | 8733916.8 | 0 | 1162022.4 | 0 | 0 | 0 | 1273905.6 | 615720.96 | 93780 | 0 | 670530 | 117022.4 | 0 | 0 | 0 | 864188.16 | 0 | 4196174.4 | 259490 | 0 | 0 | 218606.4 | 463601.8 | 949708.8 | 0 | 159560.46 | 0 | 0 | 19951562 | 0 | 0 | 0 | 0 | 0 | 0 | 1660252.5 | 0 | 5027064.12 | 0 | 8480375.64 | 8098099.2 | 0 | 18653544 | 0 | 11606476.8 | 0 | 302537.95 | 10491198.72 | 49495933 | 0 | 0 | 0 |  | 325700814.22 | 259826695.47 | 585527509.69 | 77509048.62 | 106281423.36 | 32639708.81 | 263885432.28 | 69447495 | 454680 | 17464604.12 | 16027200 | 1817917.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 337 | 0 |  | 0 | 0 | 280 | 0 | 64 | 15 | 0 | 0 | 115 | 7 | 0 | 16 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 10 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 39 | 19 | 3 | 0 | 0 | 0 | 275 | 255 | 166 | 0 | 80 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33 | 21 | 90 | 104 | 40 | 22 | 2 | 0 | 32 | 11 | 0 | 130 | 126 | 0 | 72 | 0 | 138 | 0 | 0 | 4 | 300 | 8 | 8 | 0 | 260 | 0 | 0 | 194 | 0 | 100 | 18 | 90 | 60 | 0 | 304 | 8 | 0 | 0 | 4 | 304 | 0 | 0 | 0 | 0 | 100 | 422 | 104 | 38 | 144 | 0 | 0 | 2 | 28 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 187 | 0 | 379 | 53 | 0 | 113 | 0 | 99 | 0 | 5 | 95 | 420 | 37 | 0 | 0 |  | 8313 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 339 | 0 | 0 | 0 | 210 | 240 | 42 | 85 | 55 | 0 | 0 | 115 | 70 | 72 | 132 | 51 | 0 | 0 | 0 | 54 | 55 | 50 | 16 | 25 | 30 | 20 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 85 | 10 | 45 | 41 | 19 | 19 | 0 | 0 | 0 | 275 | 260 | 167 | 8 | 74 | 5 | 2 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 110 | 118 | 30 | 22 | 0 | 0 | 32 | 38 | 0 | 130 | 114 | 0 | 72 | 0 | 138 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 147 | 0 | 100 | 85 | 0 | 340 | 95 | 0 | 0 | 0 | 306 | 46 | 0 | 0 | 52 | 100 | 205 | 101 | 0 | 144 | 0 | 0 | 8 | 0 |  | 843 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 101 | 12 | 0 | 0 | 8 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 161 | 0 | 297 | 80 | 0 | 112 | 0 | 107 | 0 | 0 | 113 | 430 | 36 | 0 | 0 |  | 9545 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 102 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 25 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 80 | 20 | 40 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 145 | 80 | 22 | 0 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 136 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 100 |  |  |  | 933 | 16 | 250 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 38 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 12 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 80 | 20 | 40 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 145 | 80 | 22 | 1.6 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 136 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 100 |  | 30 |  | 836 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 38 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 343 | 0 | 0 | 0 | 225 | 270 | 0 | 26 | 15 | 0 | 0 | 115 | 14 | 0 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 24 | 19 | 10 | 0 | 0 | 0 | 260 | 220 | 197 | 8 | 80 | 19 | 40 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 33 | 21 | 84 | 146 | 15 | 22 | 1 | 0 | 32 | 8 | 0 | 163 | 122 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 80 | 0 | 0 | 186 | 0 | 36 | 0 | 30 | 0 | 0 | 340 | 0 | 0 | 0 | 1 | 305 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 11 | 144 | 0 | 0 | 0 | 6 | 0 | 821 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 162 | 0 | 379 | 0 | 0 | 99 | 0 | 35 | 0 | 1 | 35 | 390 | 38 | 0 | 0 | 0
199
| Minimum Generation |  | 6129 | 5:00
| Highest Generation |  | 9545 | 19:00
| Day Peak Generation |  | 8313 | 12:00
| Evening Peak Generation |  | 9545 | 19:00
| HVDC Max Flow |  | 843 | 19:00
| HVDC EvPeak Flow |  | 843 | 19:00
| Load factor L.F |  | 83.37%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-17
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8313 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6195 | MW
Evening Peak Generation : |  | 9545 | MW Hour : | 19:00 | Available Max Generation : |  | 14144 | MW
E.P. Demand (at gen end) : |  | 9545 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9700 | MW
Maximum Generation : |  | 9545 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4444 | MW
Total Gen. (MKWH) : |  | 190.9914 | System Load Factor : | 83.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -64 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-17
Actual : | 93.39 | Ft.(MSL) , | Rule curve : | 94.76 | Ft.( MSL )
Gas Consumed : | Total = | 874.96 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 110148757.43
: |  | Coal : | 69447495 | Oil : | 281350036.4 | Total : | 460946288.83
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3454.7929 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1171.2454 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1048.76 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 947.4169 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 856.2917 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 690.9881 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 390.9675 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 178.0326 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 532.9023 |  |  | 0 | 0%
Total | 0 |  | 9271.3974 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Haripur 360 MW
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW Gt-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down from 08:17 to 10:07 for A/M.
b) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 08:44 to 16:32 for A/M.
c) Baroirhat-PHP 132 kV Ckt was under shut down from 09:21 to 18:28 for D/W.
d) Comilla(N)-Shahjibazar 230 kV Ckt-1 was under shut down from 09:54 to 16:49 for A/M.
e) Hathazari-Baroirhat 132 kV Ckt-2 was under shut down from 09:52 to 18:45 for A/M.
f) Kaliakoir-Tangail 132 kV Ckt-1 was under shut down from 08:53 to 17:14 for D/W.
g) Halishahar-(Rampur)-Khulshi 132 kV Ckt-2 was under shut down from 08:51 to 11:32 for C/M.
h) Kulaura 132/33 kV T-1 transformer was under shut down from 08:40 to 15:09 for 33 kV cable change.
i) Sikalbaha-Juldah 132 kV Ckt was under shut down from 08:59 to 14:48 for A/M.
j) Sikalbaha-TK Chemical 132 kV Ckt was under shut down from 08:21 to 17:09 for D/W.
k) Mymensingh-Jamalpur 132 kV Ckt-1 was under shut down from 10:30 to 12:44 for C/M.
l) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 10:10 to 11:38 for A/M.
m) Ashuganj 230/132 kV OAT-12 transformer was under shut down from 12:05 to 12:55 for A/M.
n) Hathazari 230/132 kV MT-3 transformer was under shut down from 09:12 to 18:36 for A/M.
o) Meghnaghat-Shyampur 230 kV Ckt-2 was under shut down from 12:58 to 16:14 for OPGW work.
p) Haripur 230/132 kV T-1 transformer was under shut down from 10:58 to12:21 for meter replacement .
r) Haripur 230/132 kV T-2 transformer was under shut down from 13:03 to 13:54 for meter replacement .
s) Bibiyana 400/230 kV ICT-2 transformer was under shut down from 08:46 to 13:27 for A/M.
t) Ghorashal 230/132 kV AT-1 transformer, Ghorashal 132 kV Bus-2, Ghorashal-Joydevpur 132 kV Ckt-2, |  |  |  |  | About 20 MW power interruption occurred under Ghorashal S/S area
Ghorashal-Narshingdi 132 kV Ckt-2, Ghorashal-Ashuganj 132 kV Ckt-2 tripped at 13:40 due to problem |  |  |  |  | from 13:40 15:16.
at 230 kV side CB air system at Ghorashal end. And were switched on at 14:43,15:00,15:03,14:59 respectively.
u) Meghnaghat 450 MW GT-2 was synchronized at 15:49 and STG was synchronized at 18:00.
v) Polashbari-Rangpur Confidence 132 kV Ckt-2 was shut down at 15:53 for gas leakage at CB at
Rangpur Confidence end.
w) Khulna(C) 132/33 kV T-1 transformer and 33 kV Bus section-1 were under shut down from 15:03 to
15:45 for 33 kV Bus Y-phase, isolator flashing at Pikgasa feeder.
x) After maintenance Ashuganj Network-Ashuganj(S) 230 kV Ckt-2 was switched on at 18:08.
y) Madaripur 132/33 kV T-1 & T-2 transformers tripped at 18:14 showing E/F relay at 33 kV side and were |  |  |  |  | About 52 MW power interruption occurred under Madaripur S/S area
switched on at 18:46. |  |  |  |  | from 18:14 to 18:46.
z) After maintenance Madaripur 132/33 kV T-3 transformer was switched on at 20:35.
aa) Aminbazar-Bosila-Lalbag tripped at 00:05(17/02/2021) showing Dist. Z1,A,B-phase
at Aminbazar end and E/F relay at Bosila end.
ab) Sikalbaha-TK Chemical 132 kV Ckt was shut down at 07:29(17/02/2021) for D/W.
ac) Kaliakoir-Tangail 132 kV Ckt-1 was shut down at 07:40(17/02/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4520250
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 1943500 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8330240 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 210 | 1305000 | GT-1 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 42 | 110400 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 5784960 | GT-1 under maint,FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 85 | 1393464 | High Voltage.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 522477
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 51 | 921130 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 414720
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 115 | 2765000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 292800 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 167184 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 357480
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 792000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 100514
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 50 | 187608
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1239540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 565600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 588400 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3919199
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 147 | 1650096
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 101 | 1124160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2972160 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 168769
| Dhaka area Total |  |  |  | 5972 | 2563 | 42136651
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 41569
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 112995
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 41 | 672960
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1684000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 232756 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 10320 | High Voltage.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1676160
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 462096 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 19 | 430560
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 93120 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28682
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 6104618
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 46 | 110358 | High Voltage.
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1937280
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 866 | 13597474
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 167 | 4372000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6973700 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6196000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 207360 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 2 | 135360 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 150545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Engine problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 74 | 1563590 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 1564800 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 379008
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2136960
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820700
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 53227 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 520610
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 52 | 171360 | High Voltage.
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 8 | 214920
| Cumilla Area Total |  |  |  | 2980 | 1144 | 25710340
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 118 | 2894320 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 511236
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 30 | 589440 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12200
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 3873600 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 420000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 246720
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 14 | 222240 | Engine problem
| Mymensingh Area Total |  |  |  | 709 | 474 | 8769756
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 765480 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3274363
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 114 | 2795000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 38 | 401400 | Gass shortage
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Gas shortage
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 211000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1613760 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 138 | 3890950 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 192000 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7391500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 340 | 8185000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 5 | 114480 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 205 | 7809900 | On test.
| Sylhet Area Total |  |  |  | 1988 | 1383 | 36644833
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 843 | 18451636
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 147840 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 7 | 121440 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 58752 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8318016 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 9000 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 80 | 775680 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1343 | 27882364
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 11990 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 432600 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 87 | 1106835 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 11274700 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 600300
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 610 | 13426425
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 87824 | Low demand
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 33700 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 161 | 4296636 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 297 | 8566036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 47794 | Low demand
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 494640
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210780
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 22560 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 474144
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 1965600
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1419648
| Rajshahi Area Total |  |  |  | 2183 | 905 | 17619362
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3681100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1495680
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27379
| Rangpur Area Total |  |  |  | 605 | 257 | 5204159
| Total |  |  |  | 20929 | 9545 | 190991364
| Eastern Grid Total |  |  |  | 14031 | 6430 | 126859054
| Western Grid Total |  |  |  | 6898 | 3115 | 64132310
| National Grid Total |  |  |  | 20929 | 9545 | 190991364
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-16
(a) ENTIRE EASTERN GRID : |  | 6076 | MW | (b) ENTIRE WESTERN GRID : |  | 3037 | MW
i) Dhaka area |  | 3260 | MW | i) Khulna area |  | 1144 | MW
ii) Chittagong area |  | 922 | MW | ii) Rajshahi area |  | 996 | MW
iii) Comilla area |  | 774 | MW | iii) Barisal area |  | 227 | MW
iv) Mymensingh area |  | 774 | MW | iv) Rangpur area |  | 670 | MW
v) Sylhet area |  | 346 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9113 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 107 | 12:00 | Sherpur | 106 | 19:30 | Jhenida | 84 | 18:30
Munsiganj | 84 | 21:00 | Srimongal | 40 | 19:30 | Bottail | 110 | 19:00
Sonargaon | 70 | 18:30 | Shahjibazar | 80 | 19:00 | G.K Project | 29 | 19:00
Shyampur | 180 | 11:00 | Fenchuganj | 27 | 18:30 | Faridpur | 134 | 19:00
Bhulta | 177 | 19:30 | Kulawara | 29 | 18:30 | Madaripur | 66 | 19:00
Madanganj | 52 | 14:00 | Sylhet | 85 | 19:00 | Sariatpur | 42 | 20:00
Shitalakhya | 105 | 18:00 | Chatak | 20 | 18:00 | Gopalganj | 60 | 19:00
Rahim steel | 22 | 11:00 | Sunamganj | 31 | 20:00 | Bagerhat | 82 | 19:00
Matuail | 90 | 10:00 | Biani Bazar | 40 | 18:30 | Mongla | 34 | 12:00
Ghorasal | 65 | 12:00 | Comilla (S) | 112 | 18:30 | Satkhira | 76 | 19:00
Narsingdi | 130 | 20:00 | Comilla(N) | 79 | 20:00 | Gallamari | 20 | 13:00
Haripur (SBU) | 86 | 12:00 | Chandpur | 46 | 20:00 | Magura | 40 | 18:30
Ullon | 65 | 19:00 | Feni | 86 | 20:00 | Norail | 24 | 19:00
Hasnabad | 78 | 18:30 | Chowmuhani | 122 | 19:00 | Chuadanga | 64 | 19:00
Magbazar | 63 | 13:00 | Ashuganj | 41 | 20:00 | Borguna | 6 | 1:00
Maniknagar | 54 | 18:30 | Daudkandi | 78 | 18:30 | Barisal(N) | 27 | 19:00
Bangabhaban | 16 | 12:00 | B.Baria | 102 | 19:00 | Barisal (S) | 72 | 18:30
Narinda | 59 | 14:00 | Ramganj | 56 | 20:00 | Patuakhali | 78 | 21:00
Dhanmondi | 115 | 14:00 | Chaddagram | 21 | 19:30 | Bhandaria | 38 | 19:00
Lalbag | 80 | 18:30 | PHP | 7 | 3:00 | Borhan Uddin | 25 | 19:00
Madartek | 49 | 18:30 | Kochua | 40 | 18:30 | Ishurdi | 45 | 19:00
Dhaka University |  |  | Madunaghat | 49 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Aftabnagar | 7 | 13:00 | Hathazari | 70 | 19:00 | Natore | 100 | 19:00
Fatullah | 47 | 10:00 | Khulshi | 169 | 14:00 | Bogra | 123 | 19:30
Mirpur | 77 | 18:30 | Halishahar | 94 | 19:30 | Noagaon | 94 | 9:00
Kalyanpur | 72 | 18:30 | Baraulia | 138 | 12:00 | Rajshahi | 88 | 19:30
Gulshan | 86 | 13:00 | Sikalbaha | 20 | 18:30 | Rajshahi New | 13 | 9:00
Uttara | 62 | 18:30 | Dohazari | 58 | 18:30 | C.Nawabganj | 65 | 9:00
Uttara New | 16 | 15:00 | Cox'sbazar | 79 | 22:00 | Amnura | 38 | 20:00
Kamrangirchar | 74 | 13:00 | Chandraghona | 24 | 18:30 | Pabna | 70 | 19:00
Savar | 126 | 18:30 | Kaptai | 0 | #N/A | Shahjadpur | 90 | 19:00
Bhasantec | 109 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 85 | 10:00
Agargaon | 50 | 13:00 | Bakulia | 79 | 18:30 | Niyamatpur | 71 | 9:00
Satmosjid | 64 | 13:00 | Julda | 20 | 9:00 | Joypurhat | 56 | 9:00
Tongi | 74 | 11:00 | TK chemical | 20.1 | 19:00 | Sherpur(Bogura) | 44 | 18:30
Kabirpur | 201 | 20:00 | Modern Steel | 0 | #N/A | Mohastangor | 46 | 11:00
Basundhara | 100 | 18:30 | Shahmirpur | 19.1 | 9:00 | Bangura | 18 | 18:30
Manikganj | 30 | 18:00 | Khagrachhari | 20 | 18:30 | Rangpur | 123 | 19:00
Joydevpur | 97 | 12:00 | Matarbari | 28 | 18:00 | Lalmonirhat | 50 | 18:30
New Tongi | 99 | 12:00 | Baroiar Hat | 30 | 18:00 | Saidpur | 106 | 10:00
Korda | 188 | 15:00 | Rangamati | 9 | 18:30 | Purbasadipur | 96 | 9:00
Dhamrai | 84 | 10:00 | Abul Khair 230 | 144 | 10:00 | Thakurgaon | 64 | 19:00
Rajendrapur | 78 | 19:00 | BSRM | 146 | 5:00 | Palashbari | 106 | 8:00
Valuka | 82 | 18:30 | GPH Ispat | 15 | 1:00 | Barapukuria | 48 | 9:00
Tangail | 175 | 18:30 | Goalpara | 19 | 13:00 | Panchagar | 44 | 19:00
Mymensing | 174 | 19:00 | Central s/s | 81 | 19:00 | Joldhaka | 26 | 8:00
Kishorganj | 100 | 19:30 | Noapara | 58 | 18:30 | Kurigram | 51 | 18:30
Netrokona | 91 | 20:00 | Jessore | 87 | 18:30
Jamalpur | 111 | 8:00 | Benapol | 44 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 19:00 | 404 | 9:00 | Kaliakoir | 409 | 0.20833 | 391 | 0.5
| Bheramara | 411 | 19:00 | 394 | 10:00 | Bhulta | 399 | 0.79167 | 381 | 0.5
| Ashuganj(N) | 402 | 19:00 | 384 | 12:00 | Gopalganj | 412 | 0.625 | 390 | 0.91667
| Payra | 410 | 19:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 245 | 18:00 | 240 | 1:00 | Hathazari | 236 | 19:30 | 217 | 16:00
| Ishurdi | 241 | 4:00 | 232 | 9:00 | Megnaghat | 242 | 21:00 | 236 | 9:00
| Ashuganj | 245 | 18:00 | 236 | 11:00 | Fenchuganj | 242 | 19:00 | 238 | 9:00
| Serajganj | 235 | 1:00 | 230 | 7:00 | Siddhirganj | 242 | 1:00 | 230 | 11:00
| Baghabari | 238 | 1:00 | 230 | 11:00 | Maniknagar | 0 | 1:00 | 0 | 1:00
| Barapukuria | 236 | 19:00 | 229 | 9:00 | Agargaon | 241 | 5:00 | 229 | 12:00
| Bogra | 233 | 14:00 | 224 | 9:00 | Barisal | 254 | 19:00 | 242 | 21:00
| Rajshahi | 238 | 4:00 | 224 | 13:00 | Bhola 225 MW | 253 | 5:00 | 245 | 1:00
| Khulna South | 242 | 5:00 | 224 | 13:00 | AKSML | 237 | 19:00 | 216 | 6:00
| Rampura | 235 | 19:30 | 229 | 12:00 | BSRM | 237 | 19:00 | 220 | 6:00
| Haripur | 240 | 19:00 | 228 | 11:00 | Bibiyana | 243 | 20:00 | 235 | 12:00
| Hasnabad | 236 | 22:00 | 227 | 11:00 | Bhulta | 242 | 20:00 | 230 | 12:00
| Shyampur | 240 | 19:00 | 220 | 11:00 | Ashuganj (S) | 241 | 18:00 | 232 | 12:00
| Aminbazar | 241 | 18:30 | 231 | 10:00 | Kaliakoir | 241 | 20:00 | 230 | 11:00
| Tongi | 236 | 18:00 | 226 | 11:00 | GPH | 236 | 19:00 | 217 | 6:00
| Comilla (N) | 239 | 18:30 | 227 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 18:30 | 133 | 12:00 | Madanhat | 141 | 0.77083 | 131 | 0.41667
| Munsiganj | 142 | 19:00 | 133 | 4:00 | Hathazari | 139 | 0.79167 | 131 | 0.41667
| Sonargaon | 138 | 19:00 | 133 | 1:00 | Khulshi | 137 | 0.77083 | 128 | 0.41667
| Shyampur | 136 | 19:00 | 128 | 12:00 | Halishahar | 140 | 0.79167 | 128 | 0.25
| Bhulta | 136 | 5:00 | 127 | 11:00 | Baraulia | 139 | 0.125 | 127 | 0.41667
| Madanganj | 140 | 19:30 | 132 | 4:00 | Sikalbaha | 140 | 0.77083 | 128 | 0.16667
| Shitalakhya | 140 | 18:00 | 127 | 12:00 | Dohazari | 138 | 0.79167 | 126 | 0.41667
| Rahim steal | 140 | 18:30 | 133 | 12:00 | Cox'sbazar | 128 | 0.75 | 119 | 0.25
| Matuail | 141 | 18:30 | 133 | 12:00 | Chandraghona | 140 | 0.79167 | 129 | 0.20833
| Ghorasal | 142 | 1:00 | 138 | 17:00 | Kaptai
| Narsinghdi | 136 | 18:00 | 130 | 12:00 | A. Khaer Stl. | 136 | 0.77083 | 127 | 0.5
| Haripur (SBU) | 140 | 19:00 | 133 | 12:00 | Bakulia | 140 | 0.79167 | 129 | 0.66667
| Ullon | 136 | 18:30 | 129 | 10:00 | Julda | 139 | 0.79167 | 129 | 0.70833
| Hasnabad | 137 | 18:30 | 128 | 10:00 | TK Chemical | 140 | 0.8125 | 130 | 0.625
| Magbazar | 135 | 4:00 | 129 | 11:00 | Modern Steel
| Maniknagar | 137 | 18:30 | 130 | 13:00 | Shahmirpur | 139 | 0.77083 | 129 | 0.41667
| Bangabhaban | 137 | 18:30 | 130 | 13:00 | Khagrachhari | 138 | 0.77083 | 128 | 0.25
| Narinda | 137 | 18:30 | 130 | 13:00 | Matarbari | 132 | 0.75 | 123 | 0.41667
| Dhanmondi | 136 | 18:30 | 129 | 10:00 | Baroiar Hat | 140 | 0.79167 | 130 | 0.66667
| Lalbag | 136 | 19:00 | 127 | 12:00 | Rangamati | 138 | 18:30 | 130 | 5:00
| Madartek | 136 | 19:00 | 128 | 12:00 | Goalpara S/S | 138 | 5:00 | 126 | 13:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 2:00 | 127 | 0.5
| Aftabnagar | 137 | 4:00 | 130 | 10:00 | Noapara | 137 | 4:00 | 126 | 0.5
| Fatullah | 137 | 19:00 | 129 | 12:00 | Jessore | 134 | 2:00 | 124 | 0.5
| Mirpur | 138 | 18:30 | 133 | 12:00 | Benapol | 136 | 0.125 | 124 | 0.5
| Kalyanpur | 140 | 18:30 | 133 | 12:00 | Jhenida | 135 | 1:00 | 123 | 0.54167
| Gulshan | 136 | 19:00 | 129 | 12:00 | Bottail | 137 | 0.083333 | 130 | 0.29167
| Uttara | 141 | 19:00 | 131 | 11:00 | G.K Project | 142 | 0.16667 | 137 | 0.375
| Uttara New | 140 | 19:00 | 132 | 11:00 | Faridpur | 139 | 0.25 | 134 | 0.83333
| Kamrangirchar | 135 | 19:00 | 124 | 12:00 | Madaripur | 143 | 0.083333 | 136 | 0.91667
| Savar | 140 | 19:00 | 134 | 11:00 | Shariyatpur S/S | 143 | 5:00 | 137 | 0.91667
| Bhasantec | 137 | 19:00 | 129 | 12:00 | Gopalganj | 145 | 0.16667 | 139 | 0.875
| Agargaon | 137 | 19:00 | 130 | 12:00 | Bagerhat | 135 | 2:00 | 124 | 0.54167
| Satmosjid | 137 | 19:00 | 130 | 12:00 | Mongla | 133 | 19:00 | 124 | 0.54167
| Tongi | 141 | 19:00 | 134 | 11:00 | Satkhira | 136 | 4:00 | 124 | 8:00
| Kabirpur | 133 | 18:00 | 126 | 12:00 | Gallamari | 137 | 0.16667 | 127 | 0.54167
| Basundhara | 141 | 20:00 | 132 | 12:00 | Magura | 135 | 2:00 | 121 | 0.54167
| Manikganj | 142 | 18:00 | 136 | 144:00 | Narail | 134 | 0.16667 | 123 | 0.5
| Joydevpur | 140 | 18:00 | 135 | 17:00 | Chuadanga | 132 | 1:00 | 120 | 0.54167
| New Tongi | 141 | 19:00 | 133 | 12:00 | Borguna | 141 | 7:00 | 137 | 0.041667
| Kodda | 137 | 18:30 | 128 | 15:00 | Barisal(N) | 143 | 5:00 | 137 | 21:00
| Dhamrai | 133 | 19:00 | 125 | 12:00 | Barisal (S) | 141 | 0.20833 | 135 | 0.91667
| Rajendrapur | 136 | 18:30 | 127 | 168:00 | Patuakhali(S) | 139 | 0.20833 | 133 | 0.91667
| Valuka | 130 | 1:00 | 118 | 8:00 | Bhandaria | 139 | 0.45833 | 135 | 0.20833
| Tangail | 131 | 12:00 | 122 | 12:00 | Ishurdi | 140 | 5:00 | 134 | 9:00
| Mymensing | 132 | 1:00 | 121 | 12:00 | Ruppur Paromanobik | 140 | 1:00 | 135 | 7:00
| Kishorganj | 133 | 1:00 | 126 | 11:00 | Natore | 138 | 4:00 | 130 | 13:00
| Netrokona | 133 | 24:00 | 117 | 8:00 | Bogra | 137 | 3:00 | 130 | 9:00
| Jamalpur | 141 | 19:30 | 126 | 7:00 | Noagaon | 133 | 1:00 | 124 | 8:00
| Sherpur | 140 | 20:00 | 121 | 8:00 | Rajshahi | 136 | 1:00 | 128 | 8:00
| Srimongal | 139 | 23:00 | 136 | 11:00 | Rajshahi New | 136 | 2:00 | 128 | 12:00
| Shahjibazar | 137 | 2:00 | 133 | 11:00 | C.Nawabganj | 134 | 18:00 | 124 | 8:00
| Fenchuganj | 138 | 11:00 | 136 | 13:00 | Amnura | 136 | 19:00 | 124 | 8:00
| Khulawara | 138 | 1:00 | 137 | 9:00 | Pabna | 139 | 1:00 | 133 | 12:00
| Sylhet | 136 | 1:00 | 134 | 12:00 | Shahjadpur | 142 | 1:00 | 135 | 12:00
| Chatak | 135 | 1:00 | 134 | 10:00 | Serajganj | 136 | 1:00 | 130 | 8:00
| Sunamganj | 136 | 4:00 | 133 | 11:00 | Niyamatpur | 131 | 3:00 | 121 | 7:00
| Biani Bazar | 136 | 4:00 | 134 | 11:00 | Joypurhat | 135 | 3:00 | 120 | 8:00
| Comilla(s) | 130 | 1:00 | 126 | 9:00 | Sherpur(Bogura) | 137 | 1:00 | 129 | 7:00
| Comilla(n) | 144 | 18:30 | 138 | 10:00 | Mohastangor | 135 | 1:00 | 127 | 7:00
| Chandpur | 144 | 23:00 | 140 | 17:00 | Bangura | 140 | 1:00 | 134 | 8:00
| Feni | 139 | 19:00 | 132 | 10:00 | Rangpur | 132 | 1:00 | 122 | 7:00
| Chowmuhani | 136 | 19:30 | 132 | 12:00 | Lalmonirhat | 131 | 3:00 | 122 | 7:00
| Ashuganj | 139 | 20:00 | 136 | 13:00 | Saidpur | 133 | 1:00 | 122 | 8:00
| Daudkandi | 141 | 18:30 | 133 | 12:00 | Purbasadipur | 132 | 3:00 | 116 | 7:00
| B.Baria | 134 | 6:00 | 130 | 14:00 | Thakurgaon | 132 | 2:00 | 119 | 8:00
| Ramganj | 139 | 19:00 | 133 | 10:00 | Palashbari | 134 | 3:00 | 123 | 7:00
| Chaddagram | 141 | 18:00 | 134 | 10:00 | Barapukuria | 134 | 1:00 | 129 | 9:00

## L-Curve
Date | 2021-02-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 215 | 4960 | 2457 | 7417 |  |  |  | QF-LDC-11
0:30 | 161.5 | 4773 | 2326.5 | 7099.5 | Date: | 2021-02-16
1:00 | 108 | 4586 | 2196 | 6782
1:30 | 133 | 4439.5 | 2177 | 6616.5
2:00 | 158 | 4293 | 2158 | 6451
2:30 | 195 | 4184.5 | 2152 | 6336.5 | [5 empty] | Gen. at Eve. Peak | 9545 | 9201 MW (19:30 )
3:00 | 232 | 4076 | 2146 | 6222 | [6 empty] | 19:00
3:30 | 241 | 4069 | 2120 | 6189 | [5 empty] | Gen. at Day Peak | 8313 | 8127 MW (12:00 )
4:00 | 250 | 4062 | 2094 | 6156 | [6 empty] | 12:00
4:30 | 250 | 4067.5 | 2075 | 6142.5 | [5 empty] | Highest Generation | 9545
5:00 | 250 | 4073 | 2056 | 6129 | [6 empty] | 19:00
5:30 | 287 | 4128 | 2155 | 6283
6:00 | 324 | 4183 | 2254 | 6437
6:30 | 235.5 | 4373.5 | 2340 | 6713.5
7:00 | 147 | 4564 | 2426 | 6990
7:30 | 106.5 | 4778.5 | 2569.5 | 7348
8:00 | 66 | 4993 | 2713 | 7706
8:30 | 74 | 5230 | 2756.5 | 7986.5
9:00 | 82 | 5467 | 2800 | 8267
9:30 | 149 | 5428.5 | 2755 | 8183.5
10:00 | 216 | 5390 | 2710 | 8100
10:30 | 229 | 5419 | 2707.5 | 8126.5
11:00 | 242 | 5448 | 2705 | 8153
11:30 | 258 | 5497.5 | 2735.5 | 8233
12:00 | 274 | 5547 | 2766 | 8313
12:30 | 238.5 | 5573.5 | 2789 | 8362.5
13:00 | 203 | 5600 | 2812 | 8412
13:30 | 214 | 5585.5 | 2709.5 | 8295
14:00 | 225 | 5571 | 2607 | 8178
14:30 | 295.5 | 5536 | 2565.5 | 8101.5
15:00 | 366 | 5501 | 2524 | 8025
15:30 | 356.5 | 5368 | 2495 | 7863
16:00 | 347 | 5235 | 2466 | 7701
16:30 | 371 | 5201.5 | 2489 | 7690.5
17:00 | 395 | 5168 | 2512 | 7680
17:30 | 333.5 | 5436.5 | 2657 | 8093.5
18:00 | 272 | 5705 | 2802 | 8507
18:30 | 168 | 6067.5 | 2958.5 | 9026
19:00 | 64 | 6430 | 3115 | 9545
19:30 | 17 | 6234 | 3112 | 9346
20:00 | 88 | 6138 | 3178 | 9316 |  |  |  | Executive Engineer
20:30 | 98.5 | 6087 | 3138.5 | 9225.5 |  |  |  | Network Operation Division
21:00 | 109 | 6036 | 3099 | 9135
21:30 | 128 | 5849.5 | 2974 | 8823.5
22:00 | 147 | 5663 | 2849 | 8512 |  |  |  |  | Page 6 of 7
22:30 | 156.5 | 5499.5 | 2708.5 | 8208
23:00 | 166 | 5336 | 2568 | 7904
23:30 | 190.5 | 5148 | 2512.5 | 7660.5
24:00 | 215 | 4960 | 2457 | 7417
9201 MW (19:30 )
8127 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-16 |  | Energy | 190991364
[11 empty] | 2021-02-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3151 | 840 | 1397 | 1543 | 620 | 70 | 7 | 0 | 86 | 0
0:30 | 3282.5 | 689 | 1244.5 | 1235.5 | 635 | 70 | 9.5 | 0 | 82 | 0 | Date: | 2021-02-16
1:00 | 3414 | 538 | 1092 | 928 | 650 | 70 | 12 | 0 | 78 | 0
1:30 | 3398 | 538.5 | 1073.5 | 799.5 | 650 | 70 | 12 | 0 | 75 | 0 | [7 empty] | Total Energy | 190.9914 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 3382 | 539 | 1055 | 671 | 650 | 70 | 12 | 0 | 72 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3376 | 538.5 | 1060 | 589 | 625 | 70 | 8 | 0 | 70 | 0 | [7 empty] | Energy Requirement | 190.9914
3:00 | 3370 | 538 | 1065 | 507 | 600 | 70 | 4 | 0 | 68 | 0
3:30 | 3375.5 | 538 | 1040.5 | 509 | 585 | 70 | 4 | 0 | 67 | 0 | [6 empty] | Shortage
4:00 | 3381 | 538 | 1016 | 511 | 570 | 70 | 4 | 0 | 66 | 0
4:30 | 3382 | 538 | 1004 | 522.5 | 555 | 70 | 4 | 0 | 67 | 0
5:00 | 3383 | 538 | 992 | 534 | 540 | 70 | 4 | 0 | 68 | 0
5:30 | 3407 | 626.5 | 991.5 | 574 | 540 | 70 | 4 | 0 | 70 | 0
6:00 | 3431 | 715 | 991 | 614 | 540 | 70 | 4 | 0 | 72 | 0
6:30 | 3417.5 | 768.5 | 1026.5 | 813.5 | 540 | 70 | 4 | 0 | 72 | 1.5 |  |  |  |  | Coal
7:00 | 3404 | 822 | 1062 | 1013 | 540 | 70 | 4 | 0 | 72 | 3
7:30 | 3387 | 822.5 | 1065.5 | 1358.5 | 550 | 70 | 4 | 0 | 77 | 13.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3370 | 823 | 1069 | 1704 | 560 | 70 | 4 | 0 | 82 | 24
8:30 | 3452 | 822.5 | 1055 | 1887.5 | 575 | 70 | 4 | 0 | 85 | 35.5
9:00 | 3534 | 822 | 1041 | 2071 | 590 | 70 | 4 | 0 | 88 | 47
9:30 | 3427.5 | 823 | 1042 | 2104 | 565 | 70 | 4 | 0 | 89 | 59
10:00 | 3321 | 824 | 1043 | 2137 | 540 | 70 | 4 | 0 | 90 | 71
10:30 | 3326 | 823.5 | 1046.5 | 2151 | 540 | 70 | 13 | 0 | 91 | 65.5
11:00 | 3331 | 823 | 1050 | 2165 | 540 | 70 | 22 | 0 | 92 | 60
11:30 | 3305 | 823 | 1079.5 | 2210 | 555 | 70 | 22 | 0 | 91 | 77.5
12:00 | 3279 | 823 | 1109 | 2255 | 570 | 70 | 22 | 0 | 90 | 95
12:30 | 3257 | 822.5 | 1123.5 | 2293 | 585 | 70 | 22.5 | 0 | 94 | 95
13:00 | 3235 | 822 | 1138 | 2331 | 600 | 70 | 23 | 0 | 98 | 95
13:30 | 3235 | 822 | 1138 | 2331 | 600 | 70 | 23 | 0 | 98 | 95
14:00 | 3235 | 822 | 1138 | 2331 | 600 | 70 | 23 | 0 | 98 | 95
14:30 | 3163 | 822.5 | 1071 | 2334 | 560 | 70 | 23 | 0 | 98 | 77
15:00 | 3091 | 823 | 1004 | 2337 | 520 | 70 | 23 | 0 | 98 | 59
15:30 | 3099 | 822.5 | 1022 | 2153 | 520 | 70 | 38 | 0 | 93 | 45.5
16:00 | 3107 | 822 | 1040 | 1969 | 520 | 70 | 53 | 0 | 88 | 32
16:30 | 3070.5 | 822 | 1062.5 | 1978.5 | 520 | 70 | 57.5 | 0 | 89 | 20.5
17:00 | 3034 | 822 | 1085 | 1988 | 520 | 70 | 62 | 0 | 90 | 9
17:30 | 3016.5 | 822.5 | 1155.5 | 2220.5 | 520 | 70 | 185 | 0 | 99 | 4.5
18:00 | 2999 | 823 | 1226 | 2453 | 520 | 70 | 308 | 0 | 108 | 0
18:30 | 3052 | 833 | 1239 | 2817 | 550 | 70 | 356 | 0 | 109 | 0
19:00 | 3105 | 843 | 1252 | 3181 | 580 | 70 | 404 | 0 | 110 | 0
19:30 | 3116 | 842 | 1362 | 2831 | 610 | 70 | 405 | 0 | 110 | 0
20:00 | 3085 | 843 | 1402 | 2775 | 630 | 70 | 405 | 0 | 106 | 0
20:30 | 3150.5 | 843 | 1434 | 2645.5 | 640 | 70 | 335.5 | 0 | 107 | 0
21:00 | 3216 | 843 | 1466 | 2516 | 650 | 70 | 266 | 0 | 108 | 0
21:30 | 3234.5 | 843 | 1484 | 2214 | 655 | 70 | 220 | 0 | 103 | 0
22:00 | 3253 | 843 | 1502 | 1912 | 660 | 70 | 174 | 0 | 98 | 0
22:30 | 3223.5 | 841.5 | 1485.5 | 1727.5 | 640 | 70 | 125 | 0 | 95 | 0
23:00 | 3194 | 840 | 1469 | 1543 | 620 | 70 | 76 | 0 | 92 | 0
23:30 | 3172.5 | 840 | 1433 | 1543 | 620 | 70 | 41.5 | 0 | 89 | 0 | Max Temp. in Dhaka |  | 30.0° C
24:00 | 3151 | 840 | 1397 | 1543 | 620 | 70 | 7 | 0 | 86 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1684000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 4 |  | 25 | 8 | 8 |  |  |  |  | 41569
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 9 | 14 | 17 | 18 | 17 | 15 | 11 | 6 | 2 | [9 empty] | 112995
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 85 | 85 | 17 |  |  |  | 232756
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 90 | 95 | 95 | 93 | 120 | 120 | 120 | 162 | 155 | 70 | 115 | 115 | 145 | 80 | 62 | 70 | 70 | 70 |  | 115 | 115 | 115 | 115 | 115 | 80 | 75 | 2765000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | [5 empty] | 8 | 105 | 210 | 220 | 220 | 260 | 300 | 300 | 245 | 195 | 195 | 237 |  | 300 | 300 | 300 | 300 | 145 | 45 | 15 | 3919199
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 150545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4520250
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 20 | 26 | 26 | 26 | 26 | 207360
33 | Ashuganj 225 MW CCPP | 201 | 204 | 199 | 199 | 190 | 186 | 166 | 165 | 165 | 172 | 177 | 166 | 166 | 175 | 171 | 171 | 144 | 159 |  | 167 | 176 | 181 | 196 | 218 | 208 | 184 | 4372000
34 | Ashuganj 450 MW CCPP(South) | 255 | 255 | 255 | 255 | 255 | 275 | 275 | 275 | 255 | 255 | 255 | 255 | 255 | 255 | 260 | 260 | 290 | 270 |  | 260 | 260 | 220 | 220 | 220 | 220 | 220 | 6196000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 300 | 295 | 295 | 275 | 275 | 275 | 275 | 275 | 275 | 280 | 275 | 305 | 285 |  | 275 | 275 | 250 | 250 | 250 | 260 | 260 | 6973700
35 | Ashuganj 55 MW PP (Precision) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 15 | 15 | 15 | 30 | 135360
36 | Chandpur 150 MW CCPP | 48 | 50 | 51 | 51 | 50 | 51 | 50 | 50 | 49 | 50 | 80 | 80 | 79 | 80 | 78 | 80 | 80 | 80 |  | 74 | 80 | 74 | 78 | 80 | 75 | 75 | 1563590
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 333 | 336 | 333 | 339 | 342 | 352 | 356 | 346 | 334 | 337 | 337 | 340 | 337 | 339 | 338 | 353 | 344 |  | 339 | 339 | 339 | 340 | 338 | 345 | 348 | 8330240
40 | Meghnaghat 450 MW CCPP(MPL) | [15 empty] | 30 | 30 | 120 |  | 210 | 220 | 225 | 225 | 225 | 225 | 225 | 1305000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 131 | 131 | 144 | 154 | 154 | 155 | 155 | 155 | 124 | 126 | 103 | 104 | 102 | 102 | 101 | 101 | 104 | 123 |  | 118 | 117 | 117 | 117 | 117 | 118 | 119 | 2894320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 10 | 20 | 29 | 33 | 38 | 39 | 34 | 22 | 11 | 4 | 0 | [8 empty] | 246720
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 765480
46 | Shajibazar 330 MW CCPP | 125 | 127 | 127 | 126 | 127 | 127 | 126 | 127 | 127 | 127 | 126 | 126 | 126 | 127 | 120 | 114 | 114 | 114 |  | 114 | 112 | 112 | 113 | 112 | 119 | 116 | 2795000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 40 | 40 | 40 | 40 | 69 | 69 | 69 | 69 | 72 | 72 | 69 | 69 | 69 | 69 | 69 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1613760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 135 | 136 | 136 | 136 | 136 | 136 | 137 | 137 | 137 | 138 | 137 | 137 | 122 | 123 | 123 | 123 |  | 138 | 138 | 138 | 137 | 137 | 137 | 137 | 3890950
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 114480
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 211000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 38 | 48 | 48 | 53 | 53 | 53 | 8 | 401400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192000
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 290 | 300 | 305 | 300 | 310 | 315 | 290 | 280 | 300 | 300 | 285 | 270 | 300 | 300 | 320 | 310 |  | 290 | 310 | 290 | 300 | 290 | 290 | 280 | 7391500
| Bibiyana South 400 MW | 396 | 400 | 400 | 400 | 400 | 400 | 400 | 201 | 420 | 421 | 421 | 422 | 317 | 318 | 317 | 318 | 182 | 175 |  | 205 | 205 | 206 | 325 | 350 | 325 | 325 | 7809900
58 | Nababganj 55 MW PP (Southern power ) | [13 empty] | 15 | 17 | 17 | 17 | 22 |  | 50 | 17 | 17 |  |  |  |  | 187608
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 1 | 12 | 14 | 18 | 18 | 17 | 17 | 16 | 17 | 14 | 10 | 12 |  | 14 | 16 | 17 | 17 |  |  |  | 222240
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 462096
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 414720
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511236
63 | Impoprt (Tripura) | 78 | 72 | 68 | 66 | 68 | 72 | 72 | 82 | 88 | 90 | 92 | 90 | 98 | 102 | 98 | 88 | 90 | 108 |  | 110 | 110 | 106 | 108 | 98 | 92 | 86 | 2136960
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 10 | 8 | 8 | 15 | 4 | 2 | 2 | 2 | 3 | 9 | 3 | 3 | 5 | 4 | 10 |  | 19 | 27 | 32 | 33 | 36 | 38 | 38 | 430560
65 | Feni 22MW PP (Doreen) | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 379008
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250200
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 520610
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 26 | 28 | 10 | 10 | 26 | 30 | 30 | 30 | 18 |  | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 639540
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 565600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 588400
73 | Ghorashal 108MW PP (Regent) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 103 | 100 | 97 | 103 | 107 | 72 | 72 | 72 | 72 | 72 |  | 12 | 12 | 12 | 25 | 52 | 52 | 55 | 1943500
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [16 empty] | 4 | 17 |  | 52 | 26 | 26 | 8 | 8 |  |  | 171360
| Manikgonj 162MW PP(MPGL) | 144 | 108 | 35 | 35 | 35 | 35 | 85 | 126 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2972160
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 |  | 70 | 50 | 50 | 40 |  |  |  | 292800
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [10 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 82 |  | 132 | 132 | 132 | 132 | 115 | 64 |  | 792000
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 24 | 41 | 41 | 40 | 24 | 24 | 24 | 24 | 24 | 24 |  | 30 | 77 | 82 | 64 | 40 | 40 | 24 | 589440
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 4 |  | 16 | 16 | 16 | 8 |  |  |  | 53227
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 28682
| Jodiac Power | [16 empty] | 2 | 17 |  | 46 | 17 | 17 | 17 |  |  |  | 110358
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 64 | 64 | 64 | 64 | 66 | 99 | 99 | 80 | 80 | 80 |  | 85 | 100 | 100 | 100 | 64 | 30 | 15 | 1393464
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 33 | 38 | 37 | 41 | 50 | 51 | 50 | 50 | 50 | 50 | 50 |  | 51 | 50 | 55 | 61 | 61 | 59 |  | 921130
86 | Meghnaghat CCPP(Summit) | 125 | 125 | 120 | 130 | 170 | 230 | 280 | 280 | 250 | 270 | 270 | 280 | 250 | 280 | 280 | 285 | 285 | 295 |  | 240 | 275 | 265 | 270 | 275 | 285 | 290 | 5784960
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 21 |  | 42 | 16 | 25 | 16 |  |  |  | 110400
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 2 | 17 | 39 | 104 | 104 | 104 | 104 | 104 | 102 | 44 | 34 | 50 |  | 101 | 70 | 81 | 62 | 20 | 16 |  | 1124160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 7 |  | 10 | [6 empty] | 10320
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | [26 empty] | 0
94 | Gagnagar 102 MW PP (Digital Power) | [13 empty] | 7 | 7 | 7 | 7 | 50 |  | 72 | 16 | 16 |  |  |  |  | 167184
95 | Patenga 50MW PP (Baraka) | 25 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 34 | 37 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 41 | 39 | 39 | 39 | 19 | 19 | 0 | 672960
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 4 | 25 |  | 45 | 12 | [5 empty] | 93120
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 3 | 15 | 15 | 15 | 15 | 15 | 30 | 45 | 55 | 40 | 40 | 50 |  | 55 | 40 | 40 | 15 | 15 | 15 |  | 522477
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 55 | 17 | 17 |  |  |  |  | 100514
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 163 | 110 | 110 | 110 | 110 | 110 |  | 130 | 163 | 163 | 163 | 163 | 110 | 130 | 3274363
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 12200
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 17 | 17 | 17 |  | 54 | 54 | 17 |  |  |  |  | 357480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 120 | 85 | 65 | 65 | 65 | 70 | 103 | 175 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 193 | 194 | 194 |  | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 3873600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 27 | 16 | 15 | 16 |  |  | 3 | 50 | 71 | 100 | 100 | 100 | 100 | 85 | 75 | 75 | 75 | 116 |  | 147 | 132 | 131 | 117 | 92 | 68 | 32 | 1650096
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 30 | 10 | 10 | 10 | 10 | 50 | 50 | 100 | 70 | 70 | 90 | 100 | 100 | 100 | 70 | 70 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 1676160
116 | Chandpur 200MW (Desh energy) | 85 | 51 | 20 | 17 | 17 | 17 | 32 | 50 | 50 | 50 | 50 | 60 | 74 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1564800
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 417 | 380 | 357 | 357 | 316 | 316 | 303 | 398 | 422 | 361 | 304 | 304 | 304 | 304 | 315 | 315 | 316 | 317 |  | 340 | 339 | 339 | 339 | 339 | 339 | 340 | 8185000
| Jamalpur 115 MW PP (United) | [8 empty] | 18 | 8 | 8 | 8 | 8 | 35 | 35 | 35 | 35 | 38 |  | 95 | 65 | 45 | 8 | 8 |  |  | 420000
| Anwara 300 MW PP (United) | 197 | 160 | 146 | 142 | 141 | 141 | 250 | 288 | 305 | 253 | 253 | 304 | 306 | 306 | 307 | 253 | 252 | 252 |  | 306 | 307 | 307 | 306 | 306 | 307 | 306 | 6104618
| Juldah unit-2 (Acorn) | 50 | 30 | 30 | 30 | 30 | 30 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 96 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1937280
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | [9 empty] | 10 | 32 | 2 | 22 | 29 | 21 | 32 | 25 | 24 |  | 8 | [6 empty] | 214920
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 13 | 20 |  | 28 | 28 | 24 | 18 | 10 | 3 | [9 empty] | 168769
120 | Eastern Zone Total | 4586 | 4293 | 4076 | 4062 | 4073 | 4183 | 4564 | 4993 | 5467 | 5390 | 5448 | 5547 | 5600 | 5571 | 5501 | 5235 | 5168 | 5705 |  | 6430 | 6234 | 6138 | 6036 | 5663 | 5336 | 4960 | 126859054
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 45 |  | 83 | 16 | 16 |  |  |  |  | 147840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 121440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 6 | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 17 | 17 | 17 | 53 |  | 80 | 80 | 73 | 73 | 17 |  |  | 775680
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 18 | [7 empty] | 17 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 36 | 37 | 37 | 38 | 38 | 37 | 35 | 600300
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 4 | 16 |  | 32 | 32 | 32 | 32 |  |  |  | 11990
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 26 | 30 | 27 | 27 | 27 | 27 | 27 | 32 | 54 | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 36 | 78 |  | 87 | 86 | 88 | 90 | 90 | 91 | 91 | 1106835
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 14 | 16 | 23 | 22 | 16 | 17 | 15 | 15 | 19 | 19 | 12 | 14 | 13 | 14 | 14 | 13 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 432600
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 | [8 empty] | 9000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 10 |  | 10 | 10 | 10 | 10 | 10 | 5 |  | 58752
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 538 | 539 | 538 | 538 | 538 | 715 | 822 | 823 | 822 | 824 | 823 | 823 | 822 | 823 | 823 | 822 | 822 | 823 |  | 843 | 842 | 843 | 843 | 843 | 840 | 840 | 18451636
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 355 | 370 | 370 | 370 | 370 | 370 | 320 | 320 | 320 | 320 | 290 | 290 | 290 | 290 | 290 |  | 320 | 320 | 320 | 300 | 290 | 285 | 270 | 8318016
148 | Payra 1320 MW | 500 | 500 | 450 | 420 | 390 | 390 | 390 | 410 | 440 | 390 | 390 | 420 | 450 | 390 | 370 | 370 | 370 | 370 |  | 430 | 460 | 480 | 500 | 510 | 470 | 470 | 11274700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3681100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 15 |  | 43 | 43 | 43 |  |  |  |  | 87824
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 156 | 158 | 157 | 161 | 163 | 169 | 188 | 194 | 185 | 188 | 187 | 203 | 149 | 144 | 160 | 170 | 165 |  | 161 | 159 | 161 | 167 | 168 | 164 | 163 | 4296636
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 345 | 386 | 356 | 335 | 338 | 365 | 361 | 321 | 335 | 330 | 379 | 386 | 321 | 322 | 327 | 348 | 348 |  | 297 | 326 | 374 | 392 | 409 | 427 | 374 | 8566036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 22 | 21 | 22 | 21 | 494640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 5 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210780
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 12 | 12 |  |  |  |  | 33700
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 8 | 8
168 | Santahar 50 MW Peaking PP | [17 empty] | 9 |  | 26 | 26 | 26 |  |  |  |  | 47794
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 | 8 |  |  |  |  | 22560
170 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 30 | 34 | 100 |  | 101 | 102 | 102 | 100 | 42 |  |  | 474144
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 35 | 35 | 35 | 35 | 35 | 43 | 96 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 |  | 112 | 113 | 113 | 113 | 70 | 35 |  | 1965600
172 | Confidence Power Bogura Unit-1 113 MW | [5 empty] | 15 | 35 | 90 | 113 | 113 | 113 | 95 | 95 | 113 | 70 | 35 | 35 | 50 |  | 113 | 113 | 113 | 113 | 35 |  |  | 1419648
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 90 | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 71 | 70 | 81 |  | 107 | 113 | 113 | 113 | 113 |  |  | 1495680
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 27379
178
178