## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-18 | Thursday
|  |  | Date (day): | 2021-02-18 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13136.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14125 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-17 | 2021-02-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 180 | 180 |  | 185 | ST Under maint
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 52 | 52 | 52
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 341 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-1 Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 5 | 50 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 250 | 300 | 300
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 60 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 62 | 60 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 130 | 150 | 130 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 45 | 60 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 40 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 12 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 115 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 50 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 32 | 117 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 90 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 138 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 12 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 2080 | 2602 | 3639 | 3881 | 108 | 1783
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 41 | 46 | 46
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 23 | 12 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 306 | 306 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 650 | 849 | 1317 | 1355 | 895 | 115
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 227 | 225 | 225
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 280 | 280 | 80 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 220 | 220 | 280 | 280 | 80 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 20 | 20 | 25 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 40 | 40 | 40 | 40 | 15 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 74 | 80 | 80 |  | 83 | Gas shortage & ST under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 70 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 110 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 8 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 20 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 46 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 9 | 0 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 976 | 1187 | 1632 | 1894 | 785 | 89
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 106 | 109 | 145 | 145 | 57 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 74 | 80 | 80 |  | 15 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 194 | 200 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 22 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 374 | 450 | 635.6 | 584 | 57 | 15
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 42 | 32 | 32 |  | 58 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 120 | 112 | 135 | 135 |  | 195 | GT-2 under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 52 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint |  | 20/04/2021
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 136 | 120 | 136 | 136 |  | 95
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 340 | 340 | 350 | 350
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 5 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 419 | 215 | 400 | 400 |  |  | On Test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1559 | 1443 | 1737 | 1737 | 0 | 507
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 821 | 841 | 839 | 935
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 6 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 205 | 250 | 250
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 94 | 90 | 90 |  | 15 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1053 | 1195 | 1569 | 1951 | 0 | 93
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 25 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 62 | 87 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 390 | 450 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 37 | 0 | 38 | 38 |  |  | On Test
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 506 | 610 | 1039 | 1039 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 12 | 12 |  | 38 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 162 | 220 | 220 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 353 | 334 | 400 | 400 |  |  | FGMO
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 95 | 105 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 90 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 742 | 933 | 1297 | 1421 | 651 | 38
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 107 | 100 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 261 | 250 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 8201 | 9519 | 13136.6 | 14125 | 2620 | 3051
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7817.6147 | 9074 | 12522.4822 | 13464.6759
| A. |  | 2021-02-17 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 9519 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6195 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9519 | MW
| 3 | Day peak Generation : |  |  | 8201 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9074 | MW
| 4 | Evening peak Generation : |  |  | 9519 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 195.8681 | MKWHr | By Solar | 0.45939 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 115.5712 | MKWHr |  | By Oil: | 42.8491 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.599 | MKWHr |  | By Hydro: | 1.696 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2620 | MW | Dhaka | 3343 | 3343 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3051 | MW | Chittagong | 863 | 863 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5671 | MW | Khulna | 1114 | 1114 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 895.09 | MMCFD |  |  | Rajshahi | 939 | 939 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 111748886.24 | ii) Oil : | Taka | 261146578.99 | Comilla | 770 | 770 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 67882276 | Total | Taka | 440777741.23 | Mymensingh | 813 | 813 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.219 | MKWHr. | Sylhet | 341 | 341 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -98 | MW (E to W) at | 19:00 | hrs | Barisal | 235 | 235 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -203 | MW at | 8:00 | hrs | Rangpur | 656 | 656 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.4° C |  |  | Total | 9074 | 9074 |  | 0
| B. |  | 2021-02-18 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14125 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4425 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 199.5925 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6093 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.448 | MKWHr. | ii) HVDC Flow at Peak Time |  | 841 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2454 | MKWHr. | iii) Maximum HVDC Flow : |  | 841 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.39 |  | (b) Today: | 93.15 |  | (c) Rule Curve: |  | 94.62
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 |  | 0 | 225 | 280 | 0 | 15 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 191 | 8 | 80 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 84 | 121 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 118 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 85 | 0 | 340 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 20 | 325 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 539 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 162 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 38 | 0 | 0 |  | 4739 | 2179 | 6918 | 3152 | 539 | 1456 | 1010 | 600 | 70 | 7 | 84 | 0 | 0 | 93.44
2:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 340 | 0 |  | 0 | 225 | 275 | 0 | 15 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 184 | 8 | 77 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 82 | 120 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 119 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 539 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 162 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 38 | 0 | 0 |  | 4461 | 2071 | 6532 | 3137 | 539 | 1368 | 749 | 580 | 70 | 7 | 82 | 0 | 0 | 93.43
3:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 342 | 0 |  | 0 | 225 | 285 | 0 | 15 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 190 | 8 | 80 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 80 | 120 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 119 | 0 | 72 | 0 | 137 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 340 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 0 | 0 | 0 | 0 |  | 538 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 162 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 38 | 0 | 0 |  | 4286 | 2078 | 6364 | 3145 | 538 | 1406 | 558 | 560 | 70 | 7 | 80 | 0 | 0 | 93.42
4:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 343 | 0 |  | 0 | 225 | 290 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 192 | 8 | 80 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 80 | 142 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 119 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 305 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 539 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 162 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 38 | 0 | 0 |  | 4153 | 2057 | 6210 | 3145 | 539 | 1399 | 430 | 540 | 70 | 7 | 80 | 0 | 0 | 93.41
5:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 340 | 0 |  | 0 | 225 | 295 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 32 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 39 | 0 | 0 | 0 | 260 | 220 | 185 | 8 | 81 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 78 | 142 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 119 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 538 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 163 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 38 | 0 | 0 |  | 4143 | 2052 | 6195 | 3132 | 538 | 1395 | 435 | 540 | 70 | 7 | 78 | 0 | 0 | 93.4
6:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 349 | 0 |  | 0 | 225 | 270 | 0 | 1 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 183 | 8 | 79 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 78 | 144 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 787 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 160 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 38 | 0 | 0 |  | 4215 | 2294 | 6509 | 3128 | 787 | 1405 | 494 | 540 | 70 | 7 | 78 | 0 | 0 | 93.39
7:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 344 | 0 |  | 0 | 225 | 300 | 0 | 15 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 20 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 38 | 0 | 0 | 0 | 260 | 220 | 186 | 8 | 80 | 19 | 40 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 78 | 146 | 0 | 22 | 0 | 0 | 32 | 8 | 0 | 110 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 14 | 0 | 0 | 96 | 0 | 16 | 1 | 30 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 2 | 144 | 0 | 0 | 0 | 1 |  | 821 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 162 | 0 | 424 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 10 | 390 | 38 | 0 | 0 |  | 4680 | 2355 | 7035 | 3121 | 821 | 1397 | 1004 | 540 | 70 | 0 | 78 | 4 | 0 | 93.38
8:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 343 | 0 |  | 0 | 225 | 270 | 0 | 26 | 15 | 0 | 0 | 115 | 14 | 0 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 24 | 19 | 10 | 0 | 0 | 0 | 260 | 220 | 197 | 8 | 80 | 19 | 40 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 33 | 21 | 84 | 146 | 15 | 22 | 1 | 0 | 32 | 8 | 0 | 163 | 122 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 80 | 0 | 0 | 186 | 0 | 36 | 0 | 30 | 0 | 0 | 340 | 0 | 0 | 0 | 1 | 305 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 11 | 144 | 0 | 0 | 0 | 6 |  | 821 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 162 | 0 | 379 | 0 | 0 | 99 | 0 | 35 | 0 | 1 | 35 | 390 | 38 | 0 | 0 |  | 5135 | 2426 | 7561 | 3149 | 821 | 1375 | 1486 | 540 | 70 | 16 | 84 | 20 | 0 | 93.37
9:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 347 | 0 |  | 0 | 225 | 280 | 0 | 48 | 55 | 0 | 0 | 118 | 24 | 0 | 48 | 50 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 25 | 19 | 3 | 0 | 0 | 0 | 260 | 220 | 196 | 8 | 80 | 23 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 21 | 90 | 122 | 40 | 22 | 1 | 0 | 32 | 8 | 0 | 163 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 145 | 0 | 0 | 193 | 0 | 85 | 10 | 30 | 0 | 0 | 340 | 0 | 0 | 0 | 3 | 306 | 0 | 0 | 0 | 0 | 100 | 420 | 7 | 22 | 144 | 0 | 0 | 0 | 13 |  | 821 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 159 | 0 | 388 | 0 | 0 | 113 | 0 | 91 | 0 | 2 | 100 | 390 | 38 | 0 | 0 |  | 5586 | 2594 | 8180 | 3200 | 821 | 1418 | 1942 | 540 | 70 | 48 | 90 | 51 | 0 | 93.36
10:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 338 | 0 |  | 0 | 225 | 280 | 0 | 48 | 55 | 0 | 0 | 119 | 24 | 0 | 48 | 50 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 25 | 19 | 3 | 0 | 0 | 0 | 260 | 220 | 193 | 8 | 48 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 21 | 94 | 123 | 24 | 22 | 1 | 0 | 32 | 8 | 0 | 130 | 122 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 290 | 8 | 8 | 0 | 145 | 0 | 0 | 194 | 0 | 85 | 14 | 30 | 0 | 0 | 340 | 0 | 0 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 100 | 421 | 17 | 32 | 144 | 0 | 0 | 9 | 20 |  | 822 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 155 | 0 | 359 | 0 | 0 | 113 | 0 | 98 | 0 | 3 | 113 | 390 | 37 | 0 | 0 |  | 5526 | 2574 | 8100 | 3155 | 822 | 1332 | 1965 | 540 | 70 | 48 | 94 | 74 | 0 | 93.35
11:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 344 | 0 |  | 0 | 225 | 285 | 0 | 48 | 30 | 0 | 0 | 160 | 24 | 0 | 48 | 52 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 25 | 20 | 3 | 0 | 0 | 0 | 260 | 220 | 181 | 8 | 51 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 21 | 96 | 109 | 24 | 20 | 1 | 0 | 43 | 8 | 0 | 130 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 145 | 0 | 0 | 194 | 0 | 32 | 16 | 72 | 0 | 0 | 340 | 0 | 0 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 100 | 414 | 18 | 24 | 144 | 0 | 0 | 20 | 22 |  | 822 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 149 | 0 | 373 | 4 | 0 | 95 | 0 | 99 | 0 | 4 | 113 | 390 | 37 | 0 | 0 |  | 5534 | 2565 | 8099 | 3165 | 822 | 1356 | 1931 | 540 | 70 | 48 | 96 | 71 | 0 | 93.34
12:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 |  | 0 | 225 | 290 | 5 | 60 | 30 | 0 | 0 | 130 | 45 | 0 | 48 | 60 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 25 | 20 | 6 | 0 | 0 | 0 | 260 | 220 | 187 | 8 | 51 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 21 | 102 | 106 | 8 | 22 | 2 | 0 | 43 | 8 | 0 | 110 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 290 | 8 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 32 | 18 | 100 | 0 | 0 | 340 | 0 | 0 | 0 | 5 | 306 | 0 | 0 | 0 | 0 | 100 | 419 | 53 | 24 | 138 | 0 | 0 | 9 | 12 |  | 821 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 150 | 0 | 353 | 17 | 0 | 95 | 0 | 107 | 0 | 4 | 113 | 390 | 37 | 0 | 0 |  | 5639 | 2562 | 8201 | 3146 | 821 | 1305 | 2104 | 540 | 70 | 48 | 102 | 65 | 0 | 93.33
13:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 361 | 0 |  | 0 | 225 | 280 | 7 | 72 | 30 | 0 | 0 | 175 | 50 | 0 | 48 | 60 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 25 | 20 | 6 | 0 | 0 | 0 | 260 | 220 | 192 | 8 | 47 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 20 | 106 | 81 | 8 | 22 | 1 | 0 | 43 | 8 | 0 | 163 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 220 | 0 | 0 | 194 | 0 | 55 | 16 | 100 | 0 | 0 | 340 | 0 | 0 | 0 | 5 | 306 | 0 | 0 | 0 | 0 | 100 | 420 | 53 | 35 | 144 | 0 | 0 | 11 | 15 |  | 822 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 150 | 0 | 365 | 17 | 0 | 113 | 0 | 98 | 0 | 3 | 113 | 390 | 37 | 0 | 0 |  | 5830 | 2642 | 8472 | 3173 | 822 | 1408 | 2179 | 540 | 70 | 99 | 106 | 75 | 8472 | 93.32
14:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 340 | 0 |  | 0 | 225 | 275 | 7 | 64 | 30 | 0 | 0 | 140 | 40 | 0 | 48 | 61 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 25 | 20 | 6 | 0 | 0 | 0 | 260 | 220 | 195 | 8 | 51 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 20 | 104 | 88 | 8 | 22 | 1 | 0 | 43 | 8 | 0 | 110 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 280 | 8 | 0 | 0 | 220 | 0 | 0 | 194 | 0 | 65 | 15 | 100 | 0 | 0 | 340 | 0 | 0 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 100 | 419 | 35 | 15 | 144 | 0 | 0 | 15 | 10 |  | 821 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 150 | 0 | 295 | 17 | 0 | 113 | 0 | 35 | 0 | 3 | 113 | 390 | 36 | 0 | 0 |  | 5623 | 2505 | 8128 | 3117 | 821 | 1257 | 2072 | 540 | 70 | 99 | 104 | 48 | 0 | 93.31
15:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 340 | 0 |  | 0 | 225 | 265 | 7 | 64 | 30 | 0 | 0 | 140 | 20 | 0 | 48 | 61 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0 | 0 | 0 | 260 | 220 | 196 | 8 | 47 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 20 | 102 | 90 | 8 | 22 | 1 | 0 | 43 | 8 | 0 | 110 | 112 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 290 | 8 | 8 | 0 | 220 | 0 | 0 | 200 | 0 | 65 | 11 | 70 | 0 | 0 | 340 | 0 | 0 | 0 | 3 | 306 | 0 | 0 | 0 | 0 | 100 | 424 | 17 | 7 | 144 | 0 | 0 | 5 | 4 |  | 821 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 150 | 0 | 295 | 17 | 0 | 113 | 0 | 35 | 0 | 3 | 70 | 390 | 37 | 0 | 0 |  | 5505 | 2454 | 7959 | 3110 | 821 | 1266 | 1922 | 540 | 70 | 99 | 102 | 29 | 0 | 93.3
16:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 340 | 0 |  | 0 | 225 | 280 | 7 | 48 | 18 | 0 | 0 | 140 | 7 | 0 | 32 | 40 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 8 | 20 | 5 | 0 | 0 | 0 | 275 | 220 | 198 | 8 | 80 | 26 | 40 | 0 | 0 | 0 | 0 | 8 | 15 | 11 | 8 | 20 | 90 | 89 | 8 | 22 | 0 | 0 | 43 | 8 | 0 | 130 | 113 | 0 | 72 | 0 | 135 | 0 | 0 | 5 | 285 | 8 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 62 | 0 | 50 | 9 | 0 | 340 | 0 | 0 | 0 | 2 | 218 | 0 | 0 | 0 | 0 | 50 | 422 | 17 | 5 | 108 | 0 | 0 | 15 | 3 |  | 822 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 152 | 0 | 322 | 17 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 390 | 37 | 0 | 0 |  | 5278 | 2355 | 7633 | 3214 | 822 | 1275 | 1527 | 540 | 70 | 83 | 90 | 12 | 0 | 93.29
17:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 |  | 0 | 225 | 285 | 7 | 48 | 25 | 0 | 0 | 140 | 7 | 0 | 32 | 40 | 0 | 0 | 0 | 17 | 9 | 17 | 19 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 25 | 20 | 8 | 0 | 0 | 0 | 275 | 220 | 221 | 8 | 80 | 26 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 11 | 8 | 20 | 92 | 107 | 8 | 22 | 0 | 0 | 42 | 8 | 0 | 130 | 114 | 0 | 75 | 0 | 136 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 48 | 1 | 50 | 17 | 0 | 340 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 10 | 50 | 410 | 17 | 2 | 108 | 0 | 0 | 7 | 2 |  | 822 | 0 | 215 | 0 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 153 | 0 | 305 | 35 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 390 | 37 | 0 | 0 |  | 5354 | 2366 | 7720 | 3252 | 822 | 1278 | 1573 | 540 | 70 | 88 | 92 | 5 | 0 | 93.28
18:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 334 | 0 |  | 0 | 225 | 280 | 31 | 51 | 35 | 0 | 0 | 79 | 30 | 16 | 64 | 45 | 0 | 0 | 2 | 35 | 35 | 25 | 22 | 25 | 20 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 23 | 0 | 82 | 0 | 18 | 27 | 20 | 12 | 0 | 0 | 0 | 275 | 220 | 225 | 8 | 80 | 26 | 40 | 0 | 0 | 0 | 0 | 6 | 19 | 11 | 33 | 20 | 112 | 107 | 30 | 22 | 0 | 0 | 42 | 8 | 0 | 130 | 113 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 285 | 8 | 11 | 0 | 240 | 0 | 0 | 200 | 0 | 70 | 0 | 66 | 52 | 0 | 340 | 6 | 4 | 0 | 0 | 216 | 29 | 0 | 0 | 35 | 64 | 180 | 42 | 0 | 126 | 0 | 0 | 8 | 0 |  | 821 | 0 | 215 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 14 | 0 | 102 | 0 | 0 | 0 | 8 | 8 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 158 | 0 | 345 | 70 | 0 | 54 | 0 | 97 | 0 | 0 | 70 | 380 | 0 | 0 | 0 |  | 5610 | 2661 | 8271 | 2977 | 821 | 1275 | 2212 | 530 | 70 | 274 | 112 | 0 | 0 | 93.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 |  | 0 | 225 | 250 | 50 | 97 | 55 | 0 | 0 | 150 | 60 | 40 | 115 | 62 | 0 | 0 | 12 | 35 | 35 | 50 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 0 | 25 | 41 | 20 | 23 | 0 | 0 | 0 | 275 | 220 | 227 | 8 | 74 | 26 | 40 | 0 | 0 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 110 | 109 | 74 | 22 | 0 | 0 | 42 | 52 | 0 | 163 | 112 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 117 | 0 | 100 | 70 | 0 | 340 | 22 | 17 | 0 | 0 | 306 | 54 | 0 | 0 | 46 | 100 | 215 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 205 | 0 | 49 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 50 | 0 | 102 | 12 | 0 | 0 | 25 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 162 | 0 | 334 | 94 | 0 | 105 | 0 | 100 | 0 | 0 | 90 | 450 | 0 | 0 | 0 |  | 6531 | 2988 | 9519 | 3092 | 841 | 1411 | 3000 | 600 | 70 | 395 | 110 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 339 | 0 |  | 0 | 225 | 275 | 24 | 101 | 55 | 0 | 0 | 150 | 30 | 7 | 115 | 62 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 0 | 0 | 43 | 20 | 25 | 0 | 0 | 0 | 275 | 220 | 227 | 8 | 78 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 110 | 109 | 74 | 22 | 0 | 0 | 43 | 53 | 0 | 163 | 112 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 70 | 0 | 340 | 8 | 0 | 0 | 0 | 306 | 35 | 0 | 0 | 46 | 100 | 280 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 840 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 50 | 0 | 102 | 12 | 0 | 0 | 8 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 165 | 0 | 350 | 94 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6388 | 3034 | 9422 | 3159 | 840 | 1420 | 2829 | 650 | 70 | 344 | 110 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 338 | 0 |  | 0 | 225 | 255 | 31 | 101 | 55 | 0 | 0 | 150 | 30 | 7 | 115 | 62 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 0 | 0 | 44 | 20 | 28 | 0 | 0 | 0 | 275 | 240 | 230 | 8 | 74 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 110 | 109 | 74 | 22 | 0 | 0 | 43 | 53 | 0 | 163 | 119 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 275 | 8 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 70 | 0 | 340 | 8 | 0 | 0 | 0 | 306 | 35 | 0 | 0 | 46 | 100 | 290 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 200 | 0 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 0 | 102 | 12 | 0 | 6 | 8 | 20 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 166 | 0 | 332 | 94 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6381 | 3027 | 9408 | 3195 | 841 | 1391 | 2798 | 651 | 70 | 352 | 110 | 0 | 0 | 93.25
21:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 338 | 0 |  | 0 | 225 | 255 | 0 | 101 | 30 | 0 | 0 | 150 | 0 | 0 | 115 | 61 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 0 | 0 | 50 | 20 | 34 | 0 | 0 | 0 | 275 | 260 | 230 | 8 | 74 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 110 | 109 | 74 | 22 | 0 | 0 | 43 | 53 | 0 | 163 | 119 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 285 | 8 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 122 | 0 | 100 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 306 | 17 | 0 | 0 | 46 | 100 | 294 | 96 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 50 | 0 | 102 | 12 | 0 | 8 | 0 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 164 | 0 | 335 | 75 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6240 | 2942 | 9182 | 3207 | 841 | 1410 | 2548 | 650 | 70 | 346 | 110 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 338 | 0 |  | 0 | 225 | 235 | 0 | 64 | 15 | 0 | 0 | 150 | 0 | 0 | 100 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 3 | 0 | 0 | 50 | 20 | 35 | 0 | 0 | 0 | 260 | 260 | 229 | 8 | 72 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 104 | 109 | 50 | 22 | 0 | 0 | 43 | 53 | 0 | 163 | 120 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 275 | 8 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 72 | 0 | 90 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 0 | 16 | 100 | 297 | 77 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 152 | 0 | 329 | 70 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 5909 | 2806 | 8715 | 3166 | 841 | 1397 | 2276 | 650 | 70 | 211 | 104 | 0 | 0 | 93.24
23:00 | 0 | 0 | 0 | 190 | 0 | 51 | 0 | 338 | 0 |  | 0 | 225 | 275 | 0 | 48 | 0 | 0 | 0 | 150 | 0 | 0 | 84 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 19 | 20 | 36 | 0 | 0 | 0 | 260 | 260 | 224 | 8 | 80 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 108 | 24 | 22 | 0 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 275 | 8 | 11 | 0 | 145 | 0 | 0 | 195 | 0 | 45 | 0 | 70 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 155 | 0 | 350 | 0 | 0 | 70 | 0 | 35 | 0 | 0 | 35 | 500 | 0 | 0 | 0 |  | 5470 | 2516 | 7986 | 3144 | 841 | 1384 | 1655 | 650 | 70 | 142 | 100 | 0 | 0 | 93.22
24:00 | 0 | 0 | 0 | 190 | 0 | 51 | 0 | 339 | 0 |  | 0 | 225 | 270 | 0 | 30 | 0 | 0 | 0 | 150 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 0 | 260 | 260 | 223 | 8 | 72 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 88 | 111 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 295 | 8 | 11 | 0 | 95 | 0 | 0 | 195 | 0 | 45 | 0 | 70 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 70 | 270 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 161 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 5200 | 2317 | 7517 | 3145 | 841 | 1372 | 1295 | 650 | 70 | 56 | 88 | 0 | 0 | 93.21
KWH | 0 | 0 | 0 | 4583250 | 0 | 1234681 | 0 | 8330240 | 0 |  | 0 | 4745000 | 6659462 | 163200 | 1206768 | 554870 | 0 | 0 | 3174000 | 430080 | 72576 | 1067520 | 918391 | 0 | 0 | 24336 | 363600 | 92839 | 253773 | 420300 | 600000 | 684360 | 610900 | 616900 | 0 | 0 | 0 | 1696000 | 0 | 0 | 19971 | 0 | 0 | 0 | 0 |  | 325680 | 0 | 266101 | 0 | 49920 | 509760 | 468624 | 528000 | 0 | 0 | 0 | 6681400 | 5555000 | 4878000 | 200727 | 1704450 | 558936 | 988800 | 0 | 0 | 0 | 0 | 424358 | 309744 | 181260 | 537500 | 522770 | 2245440 | 2662440 | 553920 | 508752 | 7900 | 0 | 887040 | 442800 | 0 | 3366573 | 2646000 | 0 | 1749120 | 0 | 3271160 | 0 | 0 | 122940 | 7304000 | 366168 | 206000 | 0 | 3510216 | 0 | 0 | 3849600 | 0 | 1246608 | 103140 | 1280640 | 726240 | 0 | 8172000 | 52800 | 21420 | 0 | 30719 | 6275236 | 163939 | 0 | 0 | 318360 | 1609920 | 7989000 | 658560 | 190940 | 2831040 | 0 | 0 | 100080 | 102056 |  | 18448000 | 0 | 5426208 | 0 | 112320 | 0 | 0 | 0 | 41760 | 19072 | 0 | 0 | 509600 | 120960 | 0 | 0 | 0 | 154588 | 0 | 797072 | 37550 | 0 | 30200 | 39840 | 55723 | 502560 | 0 | 210420 | 0 | 0 | 3682200 | 0 | 0 | 0 | 0 | 0 | 0 | 1475312 | 0 | 4035755 | 0 | 8915636 | 533760 | 0 | 1644480 | 0 | 1233600 | 0 | 24638 | 1426368 | 10916800 | 6686864 | 0 | 0 |  | 128786814 | 67081286 | 195868100 | 76798577 | 18448000 | 38772613 | 40417041 | 14599000 | 1696000 | 2432036 | 2245440 | 459393 | 0
Fuel Cost | 0 | 0 | 0 | 6737377.5 | 0 | 1629778.92 | 0 | 8413542.4 | 0 |  | 0 | 5172050 | 7392002.82 | 1238688 | 8314631.52 | 4694200.2 | 0 | 0 | 5491020 | 3238502.4 | 661893.12 | 10504396.8 | 8467565.02 | 0 | 0 | 221214.24 | 2654280 | 717645.47 | 2502201.78 | 315225 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 457920 | 0 | 0 | 185530.59 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2581179.7 | 0 | 434304 | 4037299.2 | 590466.24 | 1568160 | 0 | 0 | 0 | 4944236 | 5555000 | 4487760 | 258937.83 | 1960117.5 | 631597.68 | 1384320 | 0 | 0 | 0 | 0 | 4052618.9 | 393374.88 | 135945 | 940625 | 392077.5 | 16840800 | 2822186.4 | 5029593.6 | 646115.04 | 125926 | 0 | 1419264 | 788184 | 0 | 3837893.22 | 2751840 | 0 | 3340819.2 | 0 | 5659106.8 | 0 | 0 | 250797.6 | 7377040 | 274626 | 156560 | 0 | 26537232.96 | 0 | 0 | 20017920 | 0 | 12266622.72 | 1205706.6 | 10437216 | 7879704 | 0 | 7599960 | 481536 | 202419 | 0 | 0 | 47440784.16 | 1427908.69 | 0 | 0 | 2728345.2 | 10722067.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 106260480 | 0 | 5697518.4 | 0 | 882835.2 | 0 | 0 | 0 | 438062.4 | 199874.56 | 0 | 0 | 789880 | 1180569.6 | 0 | 0 | 0 | 1521145.92 | 0 | 7054087.2 | 289135 | 0 | 292638 | 386049.6 | 540513.1 | 964915.2 | 0 | 159287.94 | 0 | 0 | 19957524 | 0 | 0 | 0 | 0 | 0 | 0 | 2212968 | 0 | 4721833.35 | 0 | 8826479.64 | 5572454.4 | 0 | 15606115.2 | 0 | 9572736 | 0 | 272249.9 | 10540859.52 | 47924752 | 0 | 0 | 0 |  | 314075859.6 | 251864964.13 | 565940823.73 | 73346662.63 | 106260480 | 38402223.61 | 238014681.31 | 67882276 | 457920 | 23131897.68 | 16840800 | 1603882.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 |  | 0 | 225 | 290 | 5 | 60 | 30 | 0 | 0 | 130 | 45 | 0 | 48 | 60 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 25 | 20 | 6 | 0 | 0 | 0 | 260 | 220 | 187 | 8 | 51 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 21 | 102 | 106 | 8 | 22 | 2 | 0 | 43 | 8 | 0 | 110 | 120 | 0 | 72 | 0 | 136 | 0 | 0 | 5 | 290 | 8 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 32 | 18 | 100 | 0 | 0 | 340 | 0 | 0 | 0 | 5 | 306 | 0 | 0 | 0 | 0 | 100 | 419 | 53 | 24 | 138 | 0 | 0 | 9 | 12 |  | 821 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 150 | 0 | 353 | 17 | 0 | 95 | 0 | 107 | 0 | 4 | 113 | 390 | 37 | 0 | 0 |  | 8201 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 341 | 0 | 0 | 0 | 225 | 250 | 50 | 97 | 55 | 0 | 0 | 150 | 60 | 40 | 115 | 62 | 0 | 0 | 12 | 35 | 35 | 50 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 0 | 25 | 41 | 20 | 23 | 0 | 0 | 0 | 275 | 220 | 227 | 8 | 74 | 26 | 40 | 0 | 0 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 110 | 109 | 74 | 22 | 0 | 0 | 42 | 52 | 0 | 163 | 112 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 117 | 0 | 100 | 70 | 0 | 340 | 22 | 17 | 0 | 0 | 306 | 54 | 0 | 0 | 46 | 100 | 215 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 841 | 0 | 205 | 0 | 49 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 50 | 0 | 102 | 12 | 0 | 0 | 25 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 162 | 0 | 334 | 94 | 0 | 105 | 0 | 100 | 0 | 0 | 90 | 450 | 0 | 0 | 0 |  | 9519 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 180 | 52 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 150 | 100 | 102 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 25 | 0 | 0 | 0 | 280 | 280 | 225 | 8 | 80 | 20 | 40 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 145 | 80 | 22 | 0 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 136 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 |  |  |  | 935 | 16 | 250 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 38 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 180 | 52 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 130 | 100 | 100 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 12 | 0 | 0 | 0 | 280 | 280 | 225 | 8 | 80 | 20 | 40 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 145 | 80 | 22 | 1.6 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 136 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 |  | 30 |  | 839 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 38 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 360 | 0 | 0 | 0 | 225 | 285 | 0 | 65 | 10 | 0 | 0 | 122 | 4 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 34 | 20 | 8 | 0 | 0 | 0 | 250 | 230 | 228 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 88 | 131 | 0 | 22 | 1 | 0 | 43 | 53 | 0 | 130 | 118 | 0 | 69 | 0 | 120 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 82 | 0 | 0 | 166 | 0 | 35 | 6 | 100 | 68 | 0 | 340 | 0 | 0 | 0 | 1 | 251 | 0 | 0 | 0 | 0 | 100 | 100 | 24 | 9 | 144 | 0 | 0 | 0 | 7 | 0 | 824 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 172 | 0 | 361 | 17 | 0 | 90 | 0 | 70 | 0 | 1 | 80 | 390 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6195 | 5:00
| Highest Generation |  | 9519 | 19:00
| Day Peak Generation |  | 8201 | 12:00
| Evening Peak Generation |  | 9519 | 19:00
| HVDC Max Flow |  | 841 | 19:00
| HVDC EvPeak Flow |  | 841 | 19:00
| Load factor L.F |  | 85.74%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8201 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6093 | MW
Evening Peak Generation : |  | 9519 | MW Hour : | 19:00 | Available Max Generation : |  | 14125 | MW
E.P. Demand (at gen end) : |  | 9519 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9700 | MW
Maximum Generation : |  | 9519 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4425 | MW
Total Gen. (MKWH) : |  | 195.8681 | System Load Factor : | 85.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -203 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-18
Actual : | 93.15 | Ft.(MSL) , | Rule curve : | 94.62 | Ft.( MSL )
Gas Consumed : | Total = | 895.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111748886.24
: |  | Coal : | 67882276 | Oil : | 261146578.99 | Total : | 440777741.23
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3449.6221 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1169.4496 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1047.1443 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 945.9546 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 854.9716 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 689.9227 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 390.42 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 177.7596 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 532.0804 |  |  | 0 | 0%
Total | 0 |  | 9257.3248 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Haripur 360 MW
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW GT-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 08:41 to 19:34 for A/M.
b) Bagabari-Bangura 132 kV Ckt-1 was under shut down from 09:10 to 14:51 for D/W.
c) Baghabari-Ishwardi 132 kV Ckt was under shut down from 09:18 to 15:58 for D/W.
d) Baghabari-Shajadpur 132 kV Ckt-1 was under shut down from 09:15 to 15:38 for D/W.
e) Barishal 132/33 kV T-1 transformer was under shut down from 10:26 to 11:03 for C/M.
f) Baroiarhat 132/33 kV T-2 transformer was under shut down from 10:02 to 19:40 for D/W.
g) Baroiarhat-Hathazari 132 kV Ckt-2 was under shut down from 09:27 to 16:30 for D/W.
h) Bhaluka 132/33 kV T-2 transformer was under shut down from 09:43 to 17:44 for A/M.
i) Bibiyana 400/230 kV ICT-02 transformer was under shut down from 08:42 to 16:15 for A/M.
j) Cumilla(N)-Shahjibazar 230 kV Ckt-1 was under shut down from 08:37 to 16:48 for A/M.
k) Julda-Halishahar 132 kV Ckt was under shut down from 08:36 to 13:41 for A/M.
l) Ghorashal-Joydevpur 132 kV Ckt-1 was under shut down from 09:20 to 12:43 for A/M.
m) Kaliakoir-Tangail 132 kV Ckt-1 was under shut down from 07:40 to 16:33 for A/M.
n) Keraniganj 132/33 kV T-2 transformer was under shut down from 10:27 to 14:30 for D/W.
o) Kodda 33 kV Bus under T3, T4 & T5 transformers were under shut down from 10:06 to 12:01 |  |  |  |  | About 120 MW power interruption occurred under Kodda S/S area
for maintenance work by PBS. |  |  |  |  | since 10:06 to 12:01.
p) Manikganj-Kabirpur 132 kV Ckt-1 was shut down at 09:10 for A/M and was charged at 20:10 from
Kabirpur end.
q) Patuakhali Peaking P.P-Rajshahi S/S 132 kV Ckt was under shut down from 09:24 to 15:03 for
P.P side work.
r) Rangpur 132/33 kV T-3 transformer was under shut down from 09:15 to 15:25 for C/M.
s) Sherpur 132/33 kV T-3 transformer was under shut down from 11:17 to 14:37 for C/M.
t) Sikalbhaha-Tk. Chemical 132 kV Ckt was under shut down from 07:29 to 16:55 for D/W.
u) Sirajganj 132/33 kV T-3 transformer was under shut down from 12:28 to 13:38 due to R/H. |  |  |  |  | About 24 MW power interruption occurred under Sirajganj S/S area
since 12:28 to 13:38.
v) Joydevpur-Kodda 132 kV Ckt-1 was under shut down from 12:52 to 14:33 for C/M.
w) Baroiarhat 132 kV Bus-A is under shutdown since 15:41 for T-2 Bus isolator R/H.
x) Manikganj 132/33 kV T-2 transformer tripped at 17:36 showing O/C and was switched on at 17:57. |  |  |  |  | About 24 MW power interruption occurred under Manikganj S/S area
since 17:36 to 17:57.
y) Baroiarhat 132/33 kV T-1 transformer was under shut down from 19:52 to 20:56 due to R/H at 33 kV.
incoming isolator.
z) Rangpur Confidence-Polashbari 132 kV Ckt-2 was switched on at 15:32.
aa) Meghnaghat-Cumilla(N) 230 kV Ckt-1 tripped at 21:40 from Meghnaghat end showing lock out
and was switched on at 22;44.
ab) After maintenance Ghorashal unit-7 CCPP GT was synchronized at 01:41(18/02/2021).
ac) Thakurgaon-Ponchagarh 132 kV Ckt tripped at 02:32(18/02/2021) from Thakurgaon end showing |  |  |  |  | About 25 MW power interruption occurred under Ponchagarh S/S area
Dist. B,C-phase, Z2 as 33 kV incomer U/C of T-3 got burst and was switched on at 03:33(18/02/2021). |  |  |  |  | since 02:32(18/02/2021) to 03:33(18/02/2021).
ad) Ashuganj-Ghorashal 132 kV Ckt-1 & 2 were shut down at 07:31(18/02/2021) for D/W.
ae) Khulna(C)-Goalpara 132 kV Ckt-1 was shut down at 06:58(18/02/2021) for C/M.
af) Ghorashal-Narshingdi 132 kV Ckt-1 & 2 were shut down at 07:36(18/02/2021) for D/W.
ag) Sikalbaha-TK Chemical 132 kV Ckt was shut down at 07:07(18/02/2021) for D/W.
ah) Kaliakoir-Tangail 132 kV Ckt-1 was shut down at 07:44(18/02/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4583250
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 52 | 1234681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 8330240 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4745000 | GT-1 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 163200 | High Voltage.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 6659462 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1206768
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 554870
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 62 | 918391 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 420300
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3174000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 60 | 430080 | High Voltage.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 72576 | High Voltage.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 12 | 24336 | High Voltage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 363600 | High Voltage.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1067520 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 92839 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 50 | 253773
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1284360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 610900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 616900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 3510216
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 117 | 1246608 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 21420 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 658560 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2831040 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 102056
| Dhaka area Total |  |  |  | 5972 | 2602 | 45176946
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 19971 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 103140
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 41 | 509760
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1696000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 266101
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | High Voltage.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1280640
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 468624 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 528000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 49920 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30719
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 6275236
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 163939
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1609920
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 849 | 13001970
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 227 | 4878000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6681400 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 5555000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 558936 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 40 | 988800 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Engine problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 74 | 1704450 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 70 | 726240 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 309744
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 181260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2245440
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 537500
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 424358 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 522770
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 318360 | High Voltage.
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 100080
| Cumilla Area Total |  |  |  | 2980 | 1187 | 25933065
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 109 | 2662440 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508752
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 553920 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7900
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3849600 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 22 | 52800 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 190940
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 325680 | Engine problem
| Mymensingh Area Total |  |  |  | 709 | 450 | 8152032
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 887040 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3366573
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 112 | 2646000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 442800 | Gass shortage
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Gas shortage
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 206000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1749120 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 3271160 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 366168 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7304000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 340 | 8172000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 5 | 122940 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 215 | 7989000 | On test.
| Sylhet Area Total |  |  |  | 1988 | 1443 | 36522801
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 841 | 18448000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 112320 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 41760 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 6 | 19072 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 205 | 5426208 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 533760 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1195 | 24581120
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 120960 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 509600 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 87 | 1475312 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 450 | 10916800 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 6686864
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 610 | 19709536
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 154588 | Low demand
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 37550 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 30200 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 4035755 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 334 | 8915636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 55723 | Low demand
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 502560
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210420
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 39840 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 797072
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 105 | 1644480
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1426368
| Rajshahi Area Total |  |  |  | 2183 | 933 | 17850192
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 100 | 1233600
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24638
| Rangpur Area Total |  |  |  | 605 | 250 | 4940438
| Total |  |  |  | 20929 | 9519 | 195868100
| Eastern Grid Total |  |  |  | 14031 | 6531 | 128786814
| Western Grid Total |  |  |  | 6898 | 2988 | 67081286
| National Grid Total |  |  |  | 20929 | 9519 | 195868100
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-17
(a) ENTIRE EASTERN GRID : |  | 6130 | MW | (b) ENTIRE WESTERN GRID : |  | 2944 | MW
i) Dhaka area |  | 3343 | MW | i) Khulna area |  | 1114 | MW
ii) Chittagong area |  | 863 | MW | ii) Rajshahi area |  | 939 | MW
iii) Comilla area |  | 770 | MW | iii) Barisal area |  | 235 | MW
iv) Mymensingh area |  | 813 | MW | iv) Rangpur area |  | 656 | MW
v) Sylhet area |  | 341 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9074 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 10:00 | Sherpur | 104 | 18:30 | Jhenida | 78 | 18:30
Munsiganj | 86 | 21:00 | Srimongal | 40 | 18:30 | Bottail | 100 | 8:00
Sonargaon | 67 | 18:30 | Shahjibazar | 78 | 19:00 | G.K Project | 36 | 18:30
Shyampur | 174 | 0:00 | Fenchuganj | 25 | 18:00 | Faridpur | 134 | 19:00
Bhulta | 165 | 19:00 | Kulawara | 27 | 18:30 | Madaripur | 63 | 20:00
Madanganj | 53 | 19:30 | Sylhet | 84 | 19:00 | Sariatpur | 42 | 20:00
Shitalakhya | 107 | 11:00 | Chatak | 20 | 19:00 | Gopalganj | 60 | 19:00
Rahim steel | 20 | 9:00 | Sunamganj | 30 | 18:30 | Bagerhat | 82 | 19:00
Matuail | 88 | 11:00 | Biani Bazar | 37 | 18:30 | Mongla | 34 | 19:00
Ghorasal | 68 | 18:00 | Comilla (S) | 120 | 18:30 | Satkhira | 72 | 18:30
Narsingdi | 125 | 19:30 | Comilla(N) | 77 | 18:30 | Gallamari | 19 | 19:00
Haripur (SBU) | 95 | 18:00 | Chandpur | 46 | 19:00 | Magura | 40 | 18:30
Ullon | 62 | 19:00 | Feni | 84 | 18:30 | Norail | 23 | 19:00
Hasnabad | 114 | 19:00 | Chowmuhani | 122 | 19:00 | Chuadanga | 62 | 18:30
Magbazar | 69 | 13:00 | Ashuganj | 41 | 18:30 | Borguna | 8 | 18:00
Maniknagar | 54 | 18:30 | Daudkandi | 80 | 21:00 | Barisal(N) | 27 | 19:00
Bangabhaban | 55 | 24:00 | B.Baria | 104 | 20:00 | Barisal (S) | 72 | 18:30
Narinda | 56 | 13:00 | Ramganj | 54 | 19:30 | Patuakhali | 75 | 20:00
Dhanmondi | 127 | 14:00 | Chaddagram | 25 | 19:30 | Bhandaria | 40 | 20:00
Lalbag | 82 | 18:30 | PHP | 9 | 20:00 | Borhan Uddin | 25 | 19:00
Madartek | 48 | 19:00 | Kochua | 40 | 20:00 | Ishurdi | 42 | 19:00
Dhaka University |  |  | Madunaghat | 52 | 19:30 | Ruppur Paromanobik | 2 | 18:00
Aftabnagar | 7 | 13:00 | Hathazari | 65 | 18:00 | Natore | 90 | 19:00
Fatullah | 46 | 10:00 | Khulshi | 149 | 12:00 | Bogra | 122 | 20:00
Mirpur | 76 | 18:00 | Halishahar | 96 | 19:00 | Noagaon | 90 | 13:00
Kalyanpur | 66 | 18:00 | Baraulia | 142 | 23:00 | Rajshahi | 95 | 20:00
Gulshan | 82 | 18:00 | Sikalbaha | 22 | 18:30 | Rajshahi New | 12 | 18:30
Uttara | 51 | 18:00 | Dohazari | 58 | 18:30 | C.Nawabganj | 59 | 20:00
Uttara New | 26 | 18:00 | Cox'sbazar | 78 | 21:00 | Amnura | 38 | 9:00
Kamrangirchar | 73 | 18:00 | Chandraghona | 24 | 18:30 | Pabna | 78 | 18:30
Savar | 124 | 18:00 | Kaptai |  |  | Shahjadpur | 87 | 9:00
Bhasantec | 108 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 78 | 19:00
Agargaon | 51 | 18:00 | Bakulia | 76 | 18:00 | Niyamatpur | 69 | 10:00
Satmosjid | 66 | 18:00 | Julda | 21 | 11:00 | Joypurhat | 55 | 8:00
Tongi | 79 | 18:00 | TK chemical | 15.8 | 12:00 | Sherpur(Bogura) | 47 | 18:30
Kabirpur | 203 | 18:00 | Modern Steel | 0 | #N/A | Mohastangor | 36 | 18:00
Basundhara | 99 | 18:30 | Shahmirpur | 17.5 | 16:00 | Bangura | 18 | 19:30
Manikganj | 30 | 21:00 | Khagrachhari | 14 | 22:00 | Rangpur | 112 | 18:30
Joydevpur | 111 | 19:00 | Matarbari | 26.5 | 19:30 | Lalmonirhat | 49 | 8:00
New Tongi | 100 | 12:00 | Baroiar Hat | 31 | 18:30 | Saidpur | 106 | 9:00
Korda | 170 | 9:00 | Rangamati | 10 | 18:30 | Purbasadipur | 94 | 9:00
Dhamrai | 82 | 20:00 | Abul Khair 230 | 141 | 1:00 | Thakurgaon | 64 | 19:00
Rajendrapur | 236 | 21:00 | BSRM | 148 | 1:00 | Palashbari | 102 | 8:00
Valuka | 82 | 9:00 | GPH Ispat | 16 | 18:30 | Barapukuria | 46 | 13:00
Tangail | 169 | 8:00 | Goalpara | 20 | 13:00 | Panchagar | 43 | 18:30
Mymensing | 170 | 19:30 | Central s/s | 78 | 19:30 | Joldhaka | 24 | 8:00
Kishorganj | 100 | 20:00 | Noapara | 52 | 19:00 | Kurigram | 49 | 18:30
Netrokona | 98 | 18:30 | Jessore | 84 | 19:00
Jamalpur | 122 | 8:00 | Benapol | 44 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 19:00 | 403 | 15:00 | Kaliakoir | 406 | 0.16667 | 394 | 0.45833
| Bheramara | 406 | 22:00 | 393 | 19:00 | Bhulta | 403 | 0.79167 | 385 | 0.66667
| Ashuganj(N) | 402 | 18:00 | 387 | 16:00 | Gopalganj | 411 | 0.625 | 392 | 0.875
| Payra | 409 | 19:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 235 | 19:00 | 218 | 16:00
| Ishurdi | 240 | 18:00 | 227 | 8:00 | Megnaghat | 243 | 22:00 | 236 | 15:00
| Ashuganj | 246 | 21:00 | 238 | 11:00 | Fenchuganj | 244 | 18:00 | 240 | 3:00
| Serajganj | 235 | 18:00 | 225 | 8:00 | Siddhirganj | 241 | 1:00 | 232 | 15:00
| Baghabari | 239 | 22:00 | 230 | 8:00 | Maniknagar | 0 | 1:00 | 0 | 1:00
| Barapukuria | 235 | 20:00 | 230 | 7:00 | Agargaon | 240 | 4:00 | 230 | 16:00
| Bogra | 235 | 22:00 | 220 | 8:00 | Barisal | 251 | 19:00 | 240 | 21:00
| Rajshahi | 238 | 19:00 | 224 | 8:00 | Bhola 225 MW | 252 | 18:30 | 242 | 22:00
| Khulna South | 241 | 18:00 | 216 | 8:00 | AKSML | 235 | 19:00 | 218 | 16:00
| Rampura | 234 | 7:00 | 230 | 15:00 | BSRM | 237 | 19:00 | 220 | 16:00
| Haripur | 239 | 19:30 | 230 | 16:00 | Bibiyana | 244 | 22:00 | 239 | 8:00
| Hasnabad | 238 | 22:00 | 231 | 19:00 | Bhulta | 241 | 18:00 | 232 | 16:00
| Shyampur | 240 | 19:00 | 220 | 16:00 | Ashuganj (S) | 243 | 19:00 | 234 | 15:00
| Aminbazar | 240 | 18:00 | 230 | 16:00 | Kaliakoir | 237 | 21:00 | 231 | 11:00
| Tongi | 236 | 18:00 | 227 | 17:00 | GPH | 233 | 20:00 | 218 | 17:00
| Comilla (N) | 238 | 18:30 | 227 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 18:00 | 134 | 16:00 | Madanhat | 141 | 0.79167 | 130 | 0.66667
| Munsiganj | 141 | 18:30 | 133 | 16:00 | Hathazari | 139 | 0.875 | 130 | 0.66667
| Sonargaon | 140 | 18:00 | 132 | 15:00 | Khulshi | 138 | 0.79167 | 127 | 0.16667
| Shyampur | 136 | 19:00 | 130 | 16:00 | Halishahar | 139 | 0.79167 | 129 | 0.5
| Bhulta | 135 | 4:00 | 130 | 7:00 | Baraulia | 138 | 0.79167 | 128 | 0.66667
| Madanganj | 139 | 12:00 | 134 | 2:00 | Sikalbaha | 136 | 0.54167 | 129 | 0.041667
| Shitalakhya | 139 | 18:30 | 129 | 16:00 | Dohazari | 138 | 0.79167 | 128 | 0.041667
| Rahim steal | 139 | 18:00 | 133 | 16:00 | Cox'sbazar | 128 | 0.375 | 121 | 0.625
| Matuail | 140 | 18:00 | 134 | 16:00 | Chandraghona | 139 | 0.79167 | 129 | 0.16667
| Ghorasal | 140 | 1:00 | 138 | 16:00 | Kaptai
| Narsinghdi | 137 | 18:00 | 130 | 16:00 | A. Khaer Stl. | 136 | 0.8125 | 130 | 0.5
| Haripur (SBU) | 140 | 19:00 | 134 | 2:00 | Bakulia | 139 | 0.79167 | 128 | 0.66667
| Ullon | 136 | 21:00 | 130 | 17:00 | Julda | 137 | 0.29167 | 128 | 0.66667
| Hasnabad | 136 | 18:00 | 130 | 10:00 | TK Chemical | 138 | 0.041667 | 130 | 0.70833
| Magbazar | 135 | 1:00 | 130 | 12:00 | Modern Steel
| Maniknagar | 136 | 8:00 | 132 | 16:00 | Shahmirpur | 136 | 0.54167 | 128 | 0.66667
| Bangabhaban | 136 | 8:00 | 132 | 16:00 | Khagrachhari | 137 | 0.91667 | 129 | 0.70833
| Narinda | 136 | 8:00 | 132 | 16:00 | Matarbari | 130 | 0.58333 | 122 | 0.041667
| Dhanmondi | 136 | 21:00 | 130 | 17:00 | Baroiar Hat | 139 | 0.875 | 132 | 0.41667
| Lalbag | 136 | 8:00 | 129 | 11:00 | Rangamati | 138 | 19:00 | 127 | 16:00
| Madartek | 136 | 19:00 | 131 | 11:00 | Goalpara S/S | 137 | 18:00 | 122 | 8:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 136 | 18:00 | 120 | 0.33333
| Aftabnagar | 137 | 19:00 | 130 | 16:00 | Noapara | 134 | 18:00 | 126 | 0.5
| Fatullah | 136 | 18:00 | 131 | 11:00 | Jessore | 133 | 2:00 | 125 | 0.5
| Mirpur | 138 | 5:00 | 134 | 18:00 | Benapol | 131 | 0.083333 | 125 | 0.5
| Kalyanpur | 139 | 8;00 | 133 | 18:00 | Jhenida | 132 | 16:00 | 124 | 0.45833
| Gulshan | 135 | 5:00 | 131 | 18:00 | Bottail | 136 | 0.20833 | 130 | 0.33333
| Uttara | 135 | 5:00 | 134 | 18:00 | G.K Project | 140 | 0.083333 | 136 | 0.41667
| Uttara New | 136 | 5:00 | 132 | 18:00 | Faridpur | 137 | 0.16667 | 135 | 0.41667
| Kamrangirchar | 134 | 5:00 | 128 | 18:00 | Madaripur | 141 | 0.20833 | 137 | 0.20833
| Savar | 139 | 5:00 | 134 | 18:00 | Shariyatpur S/S | 143 | 5:00 | 135 | 0.875
| Bhasantec | 136 | 8:00 | 132 | 18:00 | Gopalganj | 144 | 0.16667 | 138 | 0.875
| Agargaon | 136 | 6:00 | 132 | 18:00 | Bagerhat | 135 | 18:00 | 121 | 0.33333
| Satmosjid | 136 | 8;00 | 132 | 18:00 | Mongla | 132 | 20:00 | 120 | 0.33333
| Tongi | 238 | 4:00 | 135 | 13:00 | Satkhira | 135 | 15:00 | 122 | 8:00
| Kabirpur | 134 | 23:00 | 127 | 16:00 | Gallamari | 137 | 0.75 | 123 | 0.33333
| Basundhara | 140 | 22:00 | 132 | 16:00 | Magura | 132 | 3:00 | 124 | 0.33333
| Manikganj | 145 | 19:00 | 135 | 16:00 | Narail | 131 | 0.125 | 120 | 0.33333
| Joydevpur | 140 | 1:00 | 134 | 16:00 | Chuadanga | 131 | 4:00 | 118 | 0.33333
| New Tongi | 142 | 19:00 | 134 | 16:00 | Borguna | 141 | 4:00 | 138 | 0.75
| Kodda | 140 | 9:00 | 127 | 17:00 | Barisal(N) | 143 | 4:00 | 135 | 21:00
| Dhamrai | 133 | 22:00 | 127 | 13:00 | Barisal (S) | 140 | 0.125 | 134 | 0.875
| Rajendrapur | 138 | 19:30 | 126 | 13:00 | Patuakhali(S) | 139 | 0.625 | 131 | 0.95833
| Valuka | 130 | 21:00 | 118 | 14:00 | Bhandaria | 140 | 0.25 | 133 | 0.875
| Tangail | 134 | 1:00 | 123 | 11:00 | Ishurdi | 139 | 18:0 | 131 | 8:00
| Mymensing | 133 | 1:00 | 121 | 13:00 | Ruppur Paromanobik | 139 | 2:00 | 132 | 7:00
| Kishorganj | 133 | 1:00 | 126 | 8:00 | Natore | 138 | 18:00 | 127 | 8:00
| Netrokona | 130 | 1:00 | 118 | 9:00 | Bogra | 138 | 18:00 | 127 | 8:00
| Jamalpur | 140 | 18:00 | 125 | 4:00 | Noagaon | 133 | 3:00 | 120 | 8:00
| Sherpur | 138 | 19:00 | 124 | 6:00 | Rajshahi | 137 | 18:00 | 126 | 8:00
| Srimongal | 140 | 23:00 | 136 | 13:00 | Rajshahi New | 137 | 19:00 | 127 | 9:00
| Shahjibazar | 137 | 23:00 | 133 | 14:00 | C.Nawabganj | 135 | 18:00 | 126 | 7:00
| Fenchuganj | 140 | 24:00 | 137 | 9:00 | Amnura | 137 | 19:00 | 122 | 8:00
| Khulawara | 138 | 1:00 | 137 | 11:00 | Pabna | 139 | 4:00 | 132 | 9:00
| Sylhet | 136 | 1:00 | 135 | 11:00 | Shahjadpur | 141 | 18:00 | 133 | 9:00
| Chatak | 136 | 2:00 | 133 | 18:30 | Serajganj | 137 | 18:00 | 128 | 8:00
| Sunamganj | 135 | 1:00 | 133 | 13:00 | Niyamatpur | 131 | 3:00 | 117 | 8:00
| Biani Bazar | 136 | 1:00 | 134 | 11:00 | Joypurhat | 135 | 18:00 | 115 | 8:00
| Comilla(s) | 131 | 1:00 | 126 | 18:00 | Sherpur(Bogura) | 137 | 18:00 | 130 | 9:00
| Comilla(n) | 143 | 19:00 | 137 | 16:00 | Mohastangor | 138 | 3:00 | 125 | 8:00
| Chandpur | 144 | 19:00 | 135 | 15:00 | Bangura | 140 | 4:00 | 134 | 9:00
| Feni | 137 | 22:00 | 132 | 11:00 | Rangpur | 133 | 20:00 | 120 | 8:00
| Chowmuhani | 137 | 18:00 | 131 | 16:00 | Lalmonirhat | 132 | 4:00 | 116 | 8:00
| Ashuganj | 138 | 20:00 | 136 | 13:00 | Saidpur | 133 | 4:00 | 120 | 8:00
| Daudkandi | 140 | 8:00 | 134 | 11:00 | Purbasadipur | 131 | 5:00 | 113 | 8:00
| B.Baria | 135 | 22:00 | 131 | 16:00 | Thakurgaon | 131 | 4:00 | 114 | 8:00
| Ramganj | 138 | 18:00 | 132 | 11:00 | Palashbari | 135 | 20:00 | 123 | 8:00
| Chaddagram | 139 | 7:00 | 135 | 16:00 | Barapukuria | 135 | 20:00 | 130 | 7:00

## L-Curve
Date | 2021-02-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 102 | 5200 | 2317 | 7517 |  |  |  | QF-LDC-11
0:30 | 113.5 | 4969.5 | 2248 | 7217.5 | Date: | 2021-02-17
1:00 | 125 | 4739 | 2179 | 6918
1:30 | 123 | 4600 | 2125 | 6725
2:00 | 121 | 4461 | 2071 | 6532
2:30 | 174.5 | 4373.5 | 2074.5 | 6448 | [5 empty] | Gen. at Eve. Peak | 9519 | 9519 MW (19:00 )
3:00 | 228 | 4286 | 2078 | 6364 | [6 empty] | 19:00
3:30 | 227 | 4219.5 | 2067.5 | 6287 | [5 empty] | Gen. at Day Peak | 8201 | 8201 MW (12:00 )
4:00 | 226 | 4153 | 2057 | 6210 | [6 empty] | 12:00
4:30 | 224.5 | 4148 | 2054.5 | 6202.5 | [5 empty] | Highest Generation | 9519
5:00 | 223 | 4143 | 2052 | 6195 | [6 empty] | 19:00
5:30 | 245 | 4179 | 2173 | 6352
6:00 | 267 | 4215 | 2294 | 6509
6:30 | 156 | 4447.5 | 2324.5 | 6772
7:00 | 45 | 4680 | 2355 | 7035
7:30 | 124 | 4907.5 | 2390.5 | 7298
8:00 | 203 | 5135 | 2426 | 7561
8:30 | 122.5 | 5360.5 | 2510 | 7870.5
9:00 | 42 | 5586 | 2594 | 8180
9:30 | 42 | 5556 | 2584 | 8140
10:00 | 42 | 5526 | 2574 | 8100
10:30 | 62.5 | 5530 | 2569.5 | 8099.5
11:00 | 83 | 5534 | 2565 | 8099
11:30 | 47 | 5586.5 | 2563.5 | 8150
12:00 | 11 | 5639 | 2562 | 8201
12:30 | 26.5 | 5734.5 | 2602 | 8336.5
13:00 | 42 | 5830 | 2642 | 8472
13:30 | 82 | 5726.5 | 2573.5 | 8300
14:00 | 122 | 5623 | 2505 | 8128
14:30 | 156.5 | 5564 | 2479.5 | 8043.5
15:00 | 191 | 5505 | 2454 | 7959
15:30 | 203.5 | 5391.5 | 2404.5 | 7796
16:00 | 216 | 5278 | 2355 | 7633
16:30 | 217 | 5316 | 2360.5 | 7676.5
17:00 | 218 | 5354 | 2366 | 7720
17:30 | 172.5 | 5482 | 2513.5 | 7995.5
18:00 | 127 | 5610 | 2661 | 8271
18:30 | 112.5 | 6070.5 | 2824.5 | 8895
19:00 | 98 | 6531 | 2988 | 9519
19:30 | 68 | 6388 | 3034 | 9422
20:00 | 67 | 6381 | 3027 | 9408 |  |  |  | Executive Engineer
20:30 | 60.5 | 6310.5 | 2984.5 | 9295 |  |  |  | Network Operation Division
21:00 | 54 | 6240 | 2942 | 9182
21:30 | 64 | 6074.5 | 2874 | 8948.5
22:00 | 74 | 5909 | 2806 | 8715 |  |  |  |  | Page 6 of 7
22:30 | 74 | 5689.5 | 2661 | 8350.5
23:00 | 74 | 5470 | 2516 | 7986
23:30 | 88 | 5335 | 2416.5 | 7751.5
24:00 | 102 | 5200 | 2317 | 7517
9519 MW (19:00 )
8201 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-17 |  | Energy | 195868100
[11 empty] | 2021-02-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3145 | 841 | 1372 | 1655 | 650 | 70 | 56 | 0 | 88 | 0
0:30 | 3148.5 | 690 | 1414 | 1332.5 | 625 | 70 | 31.5 | 0 | 86 | 0 | Date: | 2021-02-17
1:00 | 3152 | 539 | 1456 | 1010 | 600 | 70 | 7 | 0 | 84 | 0
1:30 | 3144.5 | 539 | 1412 | 879.5 | 590 | 70 | 7 | 0 | 83 | 0 | [7 empty] | Total Energy | 195.8681 | Total Energy Gen 195.868 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.868 MKWHr
2:00 | 3137 | 539 | 1368 | 749 | 580 | 70 | 7 | 0 | 82 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3141 | 538.5 | 1387 | 653.5 | 570 | 70 | 7 | 0 | 81 | 0 | [7 empty] | Energy Requirement | 195.8681
3:00 | 3145 | 538 | 1406 | 558 | 560 | 70 | 7 | 0 | 80 | 0
3:30 | 3145 | 538.5 | 1402.5 | 494 | 550 | 70 | 7 | 0 | 80 | 0 | [6 empty] | Shortage
4:00 | 3145 | 539 | 1399 | 430 | 540 | 70 | 7 | 0 | 80 | 0
4:30 | 3138.5 | 538.5 | 1397 | 432.5 | 540 | 70 | 7 | 0 | 79 | 0
5:00 | 3132 | 538 | 1395 | 435 | 540 | 70 | 7 | 0 | 78 | 0
5:30 | 3130 | 662.5 | 1400 | 464.5 | 540 | 70 | 7 | 0 | 78 | 0
6:00 | 3128 | 787 | 1405 | 494 | 540 | 70 | 7 | 0 | 78 | 0
6:30 | 3124.5 | 804 | 1401 | 749 | 540 | 70 | 3.5 | 0 | 78 | 2 |  |  |  |  | Coal
7:00 | 3121 | 821 | 1397 | 1004 | 540 | 70 | 0 | 0 | 78 | 4
7:30 | 3135 | 821 | 1386 | 1245 | 540 | 70 | 8 | 0 | 81 | 12 |  |  |  | Oil |  |  |  | ,
8:00 | 3149 | 821 | 1375 | 1486 | 540 | 70 | 16 | 0 | 84 | 20
8:30 | 3174.5 | 821 | 1396.5 | 1714 | 540 | 70 | 32 | 0 | 87 | 35.5
9:00 | 3200 | 821 | 1418 | 1942 | 540 | 70 | 48 | 0 | 90 | 51
9:30 | 3177.5 | 821.5 | 1375 | 1953.5 | 540 | 70 | 48 | 0 | 92 | 62.5
10:00 | 3155 | 822 | 1332 | 1965 | 540 | 70 | 48 | 0 | 94 | 74
10:30 | 3160 | 822 | 1344 | 1948 | 540 | 70 | 48 | 0 | 95 | 72.5
11:00 | 3165 | 822 | 1356 | 1931 | 540 | 70 | 48 | 0 | 96 | 71
11:30 | 3155.5 | 821.5 | 1330.5 | 2017.5 | 540 | 70 | 48 | 0 | 99 | 68
12:00 | 3146 | 821 | 1305 | 2104 | 540 | 70 | 48 | 0 | 102 | 65
12:30 | 3159.5 | 821.5 | 1356.5 | 2141.5 | 540 | 70 | 73.5 | 0 | 104 | 70
13:00 | 3173 | 822 | 1408 | 2179 | 540 | 70 | 99 | 0 | 106 | 75
13:30 | 3173 | 822 | 1408 | 2179 | 540 | 70 | 99 | 0 | 106 | 75
14:00 | 3173 | 822 | 1408 | 2179 | 540 | 70 | 99 | 0 | 106 | 75
14:30 | 3141.5 | 821.5 | 1337 | 2050.5 | 540 | 70 | 99 | 0 | 104 | 52
15:00 | 3110 | 821 | 1266 | 1922 | 540 | 70 | 99 | 0 | 102 | 29
15:30 | 3162 | 821.5 | 1270.5 | 1724.5 | 540 | 70 | 91 | 0 | 96 | 20.5
16:00 | 3214 | 822 | 1275 | 1527 | 540 | 70 | 83 | 0 | 90 | 12
16:30 | 3233 | 822 | 1276.5 | 1550 | 540 | 70 | 85.5 | 0 | 91 | 8.5
17:00 | 3252 | 822 | 1278 | 1573 | 540 | 70 | 88 | 0 | 92 | 5
17:30 | 3114.5 | 821.5 | 1276.5 | 1892.5 | 535 | 70 | 181 | 0 | 102 | 2.5
18:00 | 2977 | 821 | 1275 | 2212 | 530 | 70 | 274 | 0 | 112 | 0
18:30 | 3034.5 | 831 | 1343 | 2606 | 565 | 70 | 334.5 | 0 | 111 | 0
19:00 | 3092 | 841 | 1411 | 3000 | 600 | 70 | 395 | 0 | 110 | 0
19:30 | 3159 | 840 | 1420 | 2829 | 650 | 70 | 344 | 0 | 110 | 0
20:00 | 3195 | 841 | 1391 | 2798 | 651 | 70 | 352 | 0 | 110 | 0
20:30 | 3201 | 841 | 1400.5 | 2673 | 650.5 | 70 | 349 | 0 | 110 | 0
21:00 | 3207 | 841 | 1410 | 2548 | 650 | 70 | 346 | 0 | 110 | 0
21:30 | 3186.5 | 841 | 1403.5 | 2412 | 650 | 70 | 278.5 | 0 | 107 | 0
22:00 | 3166 | 841 | 1397 | 2276 | 650 | 70 | 211 | 0 | 104 | 0
22:30 | 3155 | 841 | 1390.5 | 1965.5 | 650 | 70 | 176.5 | 0 | 102 | 0
23:00 | 3144 | 841 | 1384 | 1655 | 650 | 70 | 142 | 0 | 100 | 0
23:30 | 3144.5 | 841 | 1378 | 1655 | 650 | 70 | 99 | 0 | 94 | 0 | Max Temp. in Dhaka |  | 29.4° C
24:00 | 3145 | 841 | 1372 | 1655 | 650 | 70 | 56 | 0 | 88 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 195.868 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.868 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 2 |  | 8 | 8 | 8 |  |  |  | 0 | 19971
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  | 10 | 14 | 16 | 18 | 16 | 15 | 11 |  | 1 | [9 empty] | 103140
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 82 |  | 102 | 51 | 51 | 51 | 3 |  | 0 | 266101
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 79 | 75 | 75 | 75 | 75 | 75 | 75 | 115 | 118 | 119 | 160 | 130 | 175 | 140 | 140 | 140 | 140 | 79 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3174000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 14 | 80 | 145 | 145 | 145 | 195 | 220 | 220 | 220 | 195 | 195 | 240 |  | 286 | 286 | 286 | 283 | 283 | 145 | 95 | 3510216
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4583250
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 19 | 19 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 558936
33 | Ashuganj 225 MW CCPP | 191 | 184 | 190 | 192 | 185 | 183 | 186 | 197 | 196 | 193 | 181 | 187 | 192 | 195 | 196 | 198 | 221 | 225 |  | 227 | 227 | 230 | 230 | 229 | 224 | 223 | 4878000
34 | Ashuganj 450 MW CCPP(South) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 240 | 260 | 260 | 260 | 260 | 5555000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 260 | 260 | 260 | 6681400
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 988800
36 | Chandpur 150 MW CCPP | 80 | 77 | 80 | 80 | 81 | 79 | 80 | 80 | 80 | 48 | 51 | 51 | 47 | 51 | 47 | 80 | 80 | 80 |  | 74 | 78 | 74 | 74 | 72 | 80 | 72 | 1704450
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 340 | 342 | 343 | 340 | 349 | 344 | 343 | 347 | 338 | 344 | 341 | 361 | 340 | 340 | 340 | 341 | 334 |  | 341 | 339 | 338 | 338 | 338 | 338 | 339 | 8330240
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4745000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 121 | 120 | 120 | 142 | 142 | 144 | 146 | 146 | 122 | 123 | 109 | 106 | 81 | 88 | 90 | 89 | 107 | 107 |  | 109 | 109 | 109 | 109 | 109 | 108 | 111 | 2662440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 11 | 22 | 32 | 24 | 24 | 35 | 15 | 7 | 5 | 2 | 0 | [8 empty] | 190940
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 887040
46 | Shajibazar 330 MW CCPP | 118 | 119 | 119 | 119 | 119 | 120 | 120 | 122 | 120 | 122 | 120 | 120 | 120 | 120 | 112 | 113 | 114 | 113 |  | 112 | 112 | 119 | 119 | 120 | 120 | 120 | 2646000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1749120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 135 | 136 | 121 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3271160
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 122940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 206000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 442800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 366168
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 310 | 305 | 300 | 310 | 300 | 300 | 310 | 290 | 300 | 290 | 310 | 280 | 290 | 285 | 300 | 285 |  | 300 | 290 | 275 | 285 | 275 | 275 | 295 | 7304000
| Bibiyana South 400 MW | 325 | 325 | 325 | 300 | 300 | 300 | 300 | 300 | 420 | 421 | 414 | 419 | 420 | 419 | 424 | 422 | 410 | 180 |  | 215 | 280 | 290 | 294 | 297 | 270 | 270 | 7989000
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 50 | 35 | 35 | 17 |  |  | 0 | 253773
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 10 | 19 | 18 | 14 | 18 | 19 | 19 | 19 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 325680
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 468624
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 420300
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508752
63 | Impoprt (Tripura) | 84 | 82 | 80 | 80 | 78 | 78 | 78 | 84 | 90 | 94 | 96 | 102 | 106 | 104 | 102 | 90 | 92 | 112 |  | 110 | 110 | 110 | 110 | 104 | 100 | 88 | 2245440
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 39 | 38 | 38 | 10 | 3 | 3 | 3 | 6 | 6 | 6 | 2 | 5 | 8 | 12 |  | 23 | 25 | 28 | 34 | 35 | 36 | 39 | 528000
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 19 | 19 | 19 | 16 | 16 | [7 empty] | 15 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 309744
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [8 empty] | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 181260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | [6 empty] | 8 | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 537500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 522770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 32 | 32 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 684360
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 610900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 616900
73 | Ghorashal 108MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 1234681
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [16 empty] | 10 | 35 |  | 46 | 46 | 46 | 46 | 16 |  | 0 | 318360
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 54 |  |  |  | 144 | 144 | 144 | 144 | 144 | 138 | 144 | 144 | 144 | 108 | 108 | 126 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2831040
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 14 | 24 | 24 | 24 | 45 | 50 | 40 | 20 | 7 | 7 | 30 |  | 60 | 30 | 30 |  |  |  | 0 | 430080
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [7 empty] | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 32 | 64 |  | 115 | 115 | 115 | 115 | 100 | 84 | 48 | 1067520
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 15 | 40 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 30 |  | 74 | 74 | 74 | 74 | 50 | 24 | 0 | 553920
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 16 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 7 | 6 |  | 8 | [6 empty] | 424358
| Gazipur 100 MW PP | [17 empty] | 4 |  | 17 | [5 empty] | 0 | 21420
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 30719
| Jodiac Power | [17 empty] | 29 |  | 54 | 35 | 35 | 17 | 17 |  | 0 | 163939
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 |  |  | 1 | 15 | 26 | 48 | 48 | 48 | 60 | 72 | 64 | 64 | 48 | 48 | 51 |  | 97 | 101 | 101 | 101 | 64 | 48 | 30 | 1206768
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 2 | 46 | 50 | 50 | 52 | 60 | 60 | 61 | 61 | 40 | 40 | 45 |  | 62 | 62 | 62 | 61 | 60 | 50 | 0 | 918391
86 | Meghnaghat CCPP(Summit) | 280 | 275 | 285 | 290 | 295 | 270 | 300 | 270 | 280 | 280 | 285 | 290 | 280 | 275 | 265 | 280 | 285 | 280 |  | 250 | 275 | 255 | 255 | 235 | 275 | 270 | 6659462
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 5 | 7 | 7 | 7 | 7 | 7 | 31 |  | 50 | 24 | 31 |  |  |  | 0 | 163200
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 7 | 17 | 18 | 53 | 53 | 35 | 17 | 17 | 17 | 42 |  | 90 | 90 | 90 | 96 | 77 |  | 0 | 658560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | [25 empty] | 0 | 0
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 16 |  | 40 | 7 | 7 |  |  |  | 0 | 72576
95 | Patenga 50MW PP (Baraka) | [6 empty] | 3 | 24 | 25 | 25 | 25 | 25 | 25 | 25 |  | 8 | 25 | 27 |  | 41 | 43 | 44 | 50 | 50 | 19 |  | 509760
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 18 |  | 25 | [5 empty] | 0 | 49920
97 | katpotti 52 MW | [17 empty] | 2 |  | 12 | [5 empty] | 0 | 24336
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 15 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 18 | 25 | 35 |  | 55 | 55 | 55 | 30 | 15 |  | 0 | 554870
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 9 | 35 |  | 35 | 35 | 17 |  |  |  | 0 | 92839
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 130 | 130 | 110 | 163 | 110 | 110 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 3366573
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 7900
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 17 | 17 |  |  | 0 | 363600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 160 | 65 | 45 | 16 | 16 | 21 | 96 | 186 | 193 | 194 | 194 | 194 | 194 | 194 | 200 | 200 | 194 | 200 |  | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 3849600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 5 | 16 | 36 | 85 | 85 | 32 | 32 | 55 | 65 | 65 | 62 | 48 | 70 |  | 117 | 131 | 149 | 122 | 72 | 45 | 45 | 1246608
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 30 | 30 | 30 | 30 | 72 | 100 | 100 | 100 | 70 | 50 | 50 | 66 |  | 100 | 100 | 100 | 100 | 90 | 70 | 70 | 1280640
116 | Chandpur 200MW (Desh energy) | 85 | 70 | 17 | [12 empty] | 9 | 17 | 52 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 726240
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8172000
| Jamalpur 115 MW PP (United) | [17 empty] | 6 |  | 22 | 8 | 8 |  |  |  | 0 | 52800
| Anwara 300 MW PP (United) | 306 | 180 | 142 | 124 | 124 | 197 | 300 | 305 | 306 | 306 | 306 | 306 | 306 | 306 | 306 | 218 | 217 | 216 |  | 306 | 306 | 306 | 306 | 307 | 307 | 306 | 6275236
| Juldah unit-2 (Acorn) | 20 | [5 empty] | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 64 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1609920
| Anlima Energy Ltd. | [25 empty] | 0 | 0
| Bhairob 54.5 MW | [8 empty] | 0 | 9 | 20 | 9 | 11 | 15 | 5 | 15 | 7 | 8 | [8 empty] | 100080
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 13 | 20 | 22 | 12 | 15 | 10 | 4 | 3 | 2 | [9 empty] | 102056
120 | Eastern Zone Total | 4739 | 4461 | 4286 | 4153 | 4143 | 4215 | 4680 | 5135 | 5586 | 5526 | 5534 | 5639 | 5830 | 5623 | 5505 | 5278 | 5354 | 5610 |  | 6531 | 6388 | 6381 | 6240 | 5909 | 5470 | 5200 | 128786814
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 2 | 32 |  | 49 | 32 | 26 |  |  |  | 0 | 112320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 7 | 7 | 7 | 7 | 7 | 7 | [20 empty] | 41760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [10 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 35 | 70 |  | 94 | 94 | 94 | 75 | 70 |  | 0 | 533760
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 37 | 36 | 37 | 37 | 37 | [9 empty] | 6686864
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 32 |  | 48 | 32 | 32 | 16 |  |  | 0 | 120960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 90 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 68 | 63 | 65 | 62 | 77 | 79 | 81 | 46 | 46 | 43 |  | 87 | 87 | 87 | 88 | 89 | 88 | 88 | 1475312
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 24 | 23 | 23 | 22 | 22 | 23 | 21 | 20 | 16 | 18 | 17 | 17 | 19 | 20 | 20 | 19 | 18 | 25 |  | 25 | 25 | 26 | 25 | 26 | 26 | 26 | 509600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 4 |  | 6 | 6 | 8 |  |  |  |  | 19072
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 539 | 539 | 538 | 539 | 538 | 787 | 821 | 821 | 821 | 822 | 822 | 821 | 822 | 821 | 821 | 822 | 822 | 821 |  | 841 | 840 | 841 | 841 | 841 | 841 | 841 | 18448000
147 | Bheramara 410 MW CCPP | 265 | 265 | 265 | 265 | 260 | 255 | 248 | 230 | 225 | 220 | 215 | 215 | 205 | 200 | 200 | 210 | 215 | 215 |  | 205 | 200 | 200 | 190 | 175 | 175 | 175 | 5426208
148 | Payra 1320 MW | 450 | 430 | 410 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 380 |  | 450 | 500 | 500 | 500 | 500 | 500 | 500 | 10916800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 14 |  | 50 | 50 | 50 | 50 |  |  |  | 154588
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 162 | 162 | 162 | 163 | 160 | 162 | 162 | 159 | 155 | 149 | 150 | 150 | 150 | 150 | 152 | 153 | 158 |  | 162 | 165 | 166 | 164 | 152 | 155 | 161 | 4035755
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 424 | 393 | 421 | 420 | 420 | 420 | 424 | 379 | 388 | 359 | 373 | 353 | 365 | 295 | 295 | 322 | 305 | 345 |  | 334 | 350 | 332 | 335 | 329 | 350 | 335 | 8915636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210420
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 12 | 12 | 12 | 12 |  |  |  | 37550
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [21 empty] | 6 | 8 | 8 | 8 | 8 | 30200
168 | Santahar 50 MW Peaking PP | [17 empty] | 8 |  | 20 | 20 | 20 | 20 |  |  | 0 | 55723
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 25 | 8 | 8 |  |  |  | 0 | 39840
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 51 | 51 | 51 | 51 | 51 | 102 |  | 102 | 102 | 102 | 102 | 100 | 50 | 0 | 797072
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 24 | 99 | 113 | 113 | 95 | 95 | 113 | 113 | 113 | 35 | 35 | 54 |  | 105 | 113 | 113 | 113 | 113 | 70 | 0 | 1644480
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 70 |  | 90 | 113 | 113 | 113 | 113 | 35 | 0 | 1426368
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 35 | 91 | 98 | 99 | 107 | 98 | 35 | 35 | 35 | 35 | 97 |  | 100 | 102 | 107 | 107 | 107 | 35 | 0 | 1233600
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 3 | 2 | 0 | [9 empty] | 24638
178
178