## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | January 2021 |  | December 2020 |  | January 2020
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9380 | 19-01-2021 | 9098 | 05-12-2020 | 9223 | 29/01/20 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 5153 | 02/01/21 | 4945 | 19/12/20 | 4592 | 04/01/20 | - | -
|  |  | 4:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9380 | 19-01-2021 | 9098 | 05-12-2020 | 9223 | 29/01/20 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 8147 | 20-01-2021 | 7608 | 01-12-2020 | 7826.5 | 30/01/20 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9380 | 19-01-2021 | 9098 | 05/12/20 | 9223 | 29/01/20 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9006.2258 |  | 8691.1613 |  | 8654.0323 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 7478.5484 |  | 6979.6774 |  | 6812.4677 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 916 | 25/25/2021 | 821 | 31/12/2020 | 744 | 26/01/2020 | 956 | 27/3/2019
|  |  | 20:00 |  | 19:00 |  | 21:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 118 | 30/01/2021 | 120 | 03/12/2020 | 114 | 28/01/2020 | 194 | 12/06/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2455.6397 |  | 2669.4632 |  | 3270.3498 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 60.8695 |  | 69.6277 |  | 109.7554
22 | Net Generation of BPDB (MKWH) | 2394.7701 |  | 2599.8354 |  | 3160.5944
23 | Net Generation of IPP & RPCL (MKWH) | 1839.415 |  | 1680.4416 |  | 1203.4622
24 | Net Generation of REB (MKWH) | 130.737 |  | 124.3119 |  | 122.5711
24 | Net Generation of Rental Power Plant (MKWH) | 490.6295 |  | 305.4926 |  | 192.4291
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4855.5516 |  | 4710.0814 |  | 4679.0569 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 3124.5982 |  | 3403.3482 |  | 4188.1368 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 195.6927 |  | 102.7579 |  | 18.1418 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1194.4037 |  | 857.005 |  | 309.3084 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 34.537 |  | 39.3592 |  | 29.2644 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 8.8809 |  | 4.6748 |  | 4.9089 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 358.3085 |  | 372.5639 |  | 239.052 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 528.0244 |  | 430.7191 |  | 286.1577 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 80.6155 |  | 79.5417 |  | 73.9585 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:January' 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9380 | 19-01-2021 | 19:00
Generation Period
| Dhaka | MW | 3078
| Chattogram | MW | 1032
| Cumilla | MW | 746
| Mymensingh | MW | 810
| Sylhet | MW | 329
a) | Total supply in East zone | MW | 5995
| Khulna | MW | 1102
| Barisal | MW | 233
| Rajshahi | MW | 960
| Rangpur | MW | 664
b) | Total supply in West zone | MW | 2959
c) | Total supply in both zone ( a+b) | MW | 8954
Ref: | 27.21.0000.603.16.087.20.373 | Date: 18/02/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January' 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 490 | 26/01/21 | 13:00
| b) Ishurdi end | MW | 240 | 09/01/21 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 590 | 09/01/21 | 15:00
| b) Ishurdi end | MW | 191 | 26/01/21 | 13:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 11.0214
| b) Ishurdi end | MKWH | 47.6309
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 46.205
| b) Ishurdi end | MKWH | 10.7004
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 525 | 26/01/21 | 13:00
| b)Serajganj end | MW | 480 | 10/01/21 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 10/01/21 | 15:00
| b)Sirajganj end | MW | 510 | 26/01/21 | 13:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.718 | 26/01/21
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 6.69 | 26/01/21
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 40.5
| b)Sirajganj end | MKWH | 65.688
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 64.21
| b)Sirajganj end | MKWH | 40.388
30 | Transmission loss of EWI /NO-2 | % | 1.288

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda | 132/33 kV Transformers-T1 | 2021-01-01 09:28 | 2021-01-01 12:20 | 2:52 | E/O | Due to 33 kV bus sectionalizes insulator got cracked | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2021-01-01 09:28 | 2021-01-01 12:27 | 2:59 | E/O
| 132/33 kV Transformers-T3 | 2021-01-01 09:28 | 2021-01-01 11:56 | 2:28 | E/O
| 132/33 kV Transformers-T4 | 2021-01-01 09:28 | 2021-01-01 11:22 | 1:54 | E/O
| 132/33 kV Transformers-T5 | 2021-01-01 09:28 | 2021-01-01 09:50 | 0:22 | E/O |  | 160 | 58.6667 | Power interruption 09:28 to 09:50
Kishoreganj | 132/33 kV Transformer-T3 | 2021-01-14 23:56 | 2021-01-15 08:34 | 8:38 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Kodda | 33 kV Bus | 2021-01-17 11:50 | 2021-01-17 13:56 | 2:06 | E/O | Due to Emergency maintenance work | 120 | 252 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 | 2021-01-21 01:24 | 2021-01-21 01:44 | 0:20 | T | Tripped showing all Transformer 33 kV feeder fault | 70 | 23.3333 | Power interruption 01:24 to 01:44
| 132/33 kV Transformers-T2 | 2021-01-21 01:24 | 2021-01-21 06:23 | 4:59 | T
Tangail | 132/33 kV Transformers-T1 & T2 | 2021-01-22 04:50 | 2021-01-22 05:16 | 0:26 | T | Tripped showing O/C & E/F relay | 80 | 34.6667 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-01-25 16:20 | 2021-01-25 17:50 | 1:30 | E/O | Due to Oil leakage | 90 | 138 | Power interruption 16:20 to 17:52
| 132/33 kV Transformer-T2 | 2021-01-25 16:18 | 2021-01-25 17:52 | 1:34 | E/O |  | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2021-01-28 16:15 | 2021-01-28 16:30 | 0:15 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-01-28 16:15 | 2021-01-28 21:40 | 5:25 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1 | 2021-01-31 07:50 | 2021-01-31 08:20 | 0:30 | E/O | Due to bursting of Y-phase CT at 33 kV feeder fault | 80 | 40 | Power interruption 07:50 to 08:20
| 132/33 kV Transformers-T2 | 2021-01-31 07:50 | 2021-01-31 08:56 | 1:06 | E/O
|  |  | Total : | 37:24 |  | Unserved Energy: |  | 546.6667
Dhaka (South) Grid Circle :
Bhulta | 132/33 kV Transformers-T1& T2 | 2021-01-12 05:51 | 2021-01-12 06:27 | 0:36 | E/O | Due to 33 kV PBS(R-phase) CT burst | 58 | 34.8 | Power interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2021-01-15 00:42 | 2021-01-15 00:58 | 0:16 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-15 06:10 | 2021-01-15 10:35 | 4:25 | T |  | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T03 | 2021-01-20 12:16 | 2021-01-20 12:16 | 0:00 | E/O | Due to Oil filling | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T03 | 2021-01-21 14:38 | 2021-01-21 17:34 | 2:56 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T2 | 2021-01-28 06:23 | 2021-01-28 07:03 | 0:40 | T | Tripped showing diff. relay | 20 | 13.3333 | Power interruption
|  |  | Total : | 8:53 |  | Unserved Energy: |  | 48.1333
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T2 | 2021-01-02 15:45 | 2021-01-02 16:48 | 1:03 | E/O | Due to red-hot maintenance | 22 | 23.1 | Power interruption
|  |  | Total : | 1:03 |  | Unserved Energy: |  | 23.1
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T2 | 2021-01-02 11:02 | 2021-01-02 12:45 | 1:43 | E/O | Due to Ol leakage | 0 | 0 | No interruption
Coumilla(N) | 132/33 kV Transformers-T3 & T4 | 2021-01-03 09:09 | 2021-01-03 09:37 | 0:28 | T | Tripped showing O/C relay at 33 kV side | 37 | 17.2667 | Power interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-01-03 11:30 | 2021-01-03 13:26 | 1:56 | E/O | Due to cable burst (B-phase) | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2021-01-06 20:33 | 2021-01-06 20:57 | 0:24 | E/O | Due to red-hot maintenance at 33 kV side | 9 | 3.6 | Power interruption
Coumilla(N) | 132/33 kV Transformers-T3 | 2021-01-11 12:26 | 2021-01-11 14:21 | 1:55 | T | Tripped showing O/C relay at 33 kV side | 60 | 22 | Power interruption 12:26 to 12:35 & 13:42 to 13:55
| 132/33 kV Transformers-T4 | 2021-01-11 12:26 | 2021-01-11 12:35 | 0:09 | T
| 132/33 kV Transformers-T4 | 2021-01-11 13:42 | 2021-01-11 13:55 | 0:13 | T
| 132/33 kV Transformers-T3 | 2021-01-18 18:55 | 2021-01-18 19:10 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-01-19 03:21 | 2021-01-19 07:59 | 4:38 | E/O | Due to cable burst | 20 | 92.6667 | Power interruption
Kulaura | 132/33 kV auxiliary Transformer-T1 | 2021-01-20 23:07 | 2021-01-20 23:55 | 0:48 | E/O | Due to cable burst | 13 | 10.4 | Power interruption
Coumilla(N) | 132/33 kV Transformers-T3 | 2021-01-21 04:34 | 2021-01-21 05:12 | 0:38 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2021-01-25 00:14 | 2021-01-25 00:38 | 0:24 | T |  | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T1 | 2021-01-29 05:33 | 2021-01-29 21:26 | 15:53 | T | Tripped showing lockout relay | 8 | 127.0667 | Power interruption
|  |  | Total : | 29:24 |  |  |  | 273
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barishal(S) | 132/33 kV Transformer-T1 | 2021-01-04 10:05 | 2021-01-04 10:32 | 0:27 | E/O | Due to gas leakage | 0 | 0 | No interruption
Noapara | 132/33 kV Transformers-T1 | 2021-01-14 08:36 | 2021-01-14 08:39 | 0:03 | T | Tripped showing differential & E/F relay | 25 | 1.25 | Power interruption 08:36 to 8:39
| 132/33 kV Transformers-T2 | 2021-01-14 08:36 | 2021-01-14 08:56 | 0:20 | T
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2021-01-15 07:55 | 2021-01-15 07:59 | 0:04 | T | Tripped showing O/C at 33 kV side | 12 | 0.8 | Power interruption
Faridpur | 132/33 kV Transformers-T1 & T2 | 2021-01-17 18:57 | 2021-01-17 19:07 | 0:10 | T | Due to 33 kV feeder fault | 120 | 20 | Power interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2021-01-24 18:01 | 2021-01-24 18:18 | 0:17 | T | Tripped showing E/F relay | 36 | 10.2 | Power interruption
Khulna© | 132/33 kV Transformer-T3 | 2021-01-25 13:41 | 2021-01-25 13:53 | 0:12 | T | Tripped showing inst.E/F relay | 20 | 4 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 | 2021-01-26 06:41 | 2021-01-26 16:52 | 10:11 | T | Tripped showing ins. E/F relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2021-01-26 06:41 | 2021-01-26 06:53 | 0:12 | T |  | 0 | 0 | No interruption
|  |  | Total : | 11:56 |  | Unserved Energy: |  | 36.25
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T2 | 2021-01-01 18:14 | 2021-01-01 18:26 | 0:12 | T | Tripped showing O/C & E/F relay | 25 | 5 | Power interruption
Pabna | 132/33 kV Transformer-T-1 | 2021-01-06 16:29 | 2021-01-07 10:06 | 17:37 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC pole-2 | 2021-01-28 14:58 | 2021-01-28 14:58 | 0:00 | T | Due to external protection fault | 0 | 0 | No interruption
|  |  | Total : | 17:49 |  |  |  | 5
Bogura Grid Circle:
Rajshahi | 230/132 kV Transformers-T-02 | 2020-12-04 16:56 | 2020-12-04 19:13 | 2:17 | T | Tripped showing O/V relay at 33 kV side | 0 | 0 | No interruption
Rajshahi(N) | 230/132 kV Transformers-T-1 & T2 | 2021-01-07 04:11 | 2021-01-07 04:58 | 0:47 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-1 | 2021-01-12 06:56 | 2021-01-12 07:28 | 0:32 | T | Tripped showing O/C & E/F relay | 39 | 20.8 | Power interruption
Panchugar | 132/33 kV Transformer-T-3 | 2021-01-13 11:45 | 2021-01-13 23:00 | 11:15 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-4 | 2021-01-15 11:01 | 2021-01-15 12:12 | 1:11 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T-4 & 33 kV Bus | 2021-01-15 15:25 | 2021-01-15 17:01 | 1:36 | E/O | Due to red-hot maintenance at 33 kV side | 15 | 24 | Power interruption
Mohasthagarth | 132/33 kV Transformer-T-2 & 33 kV Bus | 2021-01-22 18:39 | 2021-01-22 18:39 | 0:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 17:38 |  |  |  | 44.8
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 124:07 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2021-01-03 18:35 | 2021-01-03 21:11 | 2:36 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-01-16 10:25 | 2021-01-16 10:37 | 0:12 | T | Tripped showing dist. relay | 110 | 22 | Power interruption 10:25 to 10:37
| Aminbazar-Mirpur 132 kV line-2 | 2021-01-16 10:25 | 2021-01-16 20:20 | 9:55 | T
| Aminbazar-Meghnaghat 230 kV line-1 | 2021-01-16 10:25 | 2021-01-17 13:59 | 27:34 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-2 | 2021-01-18 06:53 | 2021-01-18 07:30 | 0:37 | T | Tripped showing Gen.trip | 0 | 0 | No interruption
Kodda | Kodda Summit -Kaliakoir 230 kV line | 2021-01-23 13:52 | 2021-01-23 15:01 | 1:09 | E/O | Due to gas filling | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV line-2 | 2021-01-24 19:57 | 2021-01-25 15:11 | 19:14 | T | Due to bursting of L/A | 0 | 0 | No interruption
| Aminbazar-Maniganj P/P 132 kV line-1& 2 | 2021-01-25 05:42 | 2021-01-25 05:58 | 0:16 | T | Tripped showing dist. relay | 65 | 17.3333 | No interruption
|  |  | Total : | 61:33 |  | Unserved Energy: |  | 39.3333
Dhaka (South) Grid Circle :
Haripur | Haripur-Haripur 360 MW 132 kV line-2 | 2020-12-01 08:58 | 2020-12-01 10:45 | 1:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Matuail 132 kV line | 2021-01-07 10:12 | 2021-01-07 10:36 | 0:24 | T | Tripped showing dist.& O/C relay | 55 | 22 | Power interruption
Ghorashal | Ghorashal-Ashuganj (S) 230 kV line-2 | 2021-01-12 04:18 | 2021-01-12 07:54 | 3:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV line | 2021-01-17 07:09 | 2021-01-17 07:28 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kishoreganj 230 kV line-2 | 2021-01-18 06:53 | 2021-01-18 07:37 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
APR | APR-Shyampur 230 kV line | 2021-01-19 07:33 | 2021-01-19 07:34 | 0:01 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| APR -Shyampur 230 kV line | 2021-01-19 07:40 | 2021-01-19 09:31 | 1:51 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2021-01-19 12:31 | 2021-01-19 12:43 | 0:12 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Keranganj | Krraniganj-Hasnabad 230 kV line-2 | 2021-01-21 03:31 | 2021-01-21 08:02 | 4:31 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
APR | APR -Shyampur 230 kV line | 2021-01-21 04:07 | 2021-01-21 07:07 | 3:00 | T |  | 0 | 0 | No interruption
| APR-Shyampur 230 kV line | 2021-01-21 00:15 | 2021-01-21 00:34 | 0:19 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Shyampur | Shyampur-Meghnaghat 230 kV line-1 | 2021-01-22 00:16 | 2021-01-22 00:38 | 0:22 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2021-01-22 00:41 | 2021-01-22 00:41 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-3 | 2021-01-22 01:51 | 2021-01-22 01:51 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
APR | APR -Shyampur 230 kV line | 2021-01-22 00:56 | 2021-01-22 06:17 | 5:21 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Shyampur | Shyampur-Meghnaghat 230 kV line-1 | 2021-01-22 05:36 | 2021-01-23 17:15 | 35:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kishoreganj APR 132 kV line | 2021-01-22 06:07 | 2021-01-22 10:03 | 3:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2021-01-22 06:54 | 2021-01-22 07:14 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2021-01-23 00:57 | 2021-01-23 01:17 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
APR | APR -Shyampur 230 kV line | 2021-01-23 00:55 | 2021-01-23 01:07 | 0:12 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2021-01-23 02:32 | 2021-01-23 17:14 | 14:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-1 | 2021-01-23 02:19 | 2021-01-23 17:14 | 14:55 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2021-01-24 03:50 | 2021-01-24 04:02 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 92:43 |  | Unserved Energy: |  | 22
Chattogram Grid Circle :
Kaptai | Kaptai-Chandraghhona 132 kV line | 2021-01-02 21:29 | 2021-01-02 21:29 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line | 2021-01-07 17:05 | 2021-01-07 17:52 | 0:47 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2021-01-30 19:33 | 2021-01-30 19:33 | 0:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-3 | 2021-01-31 17:20 | 2021-01-31 19:04 | 1:44 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 2:31 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
| Ashuganj-Sirajganj 230 kV line-1 | 2021-01-01 06:53 | 2021-01-01 06:53 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2021-01-01 11:36 | 2021-01-01 12:11 | 0:35 | T |  | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2021-01-08 12:17 | 2021-01-08 13:11 | 0:54 | T |  | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Ramganj 132 kV line-1 & 2 | 2021-01-15 06:35 | 2021-01-15 07:15 | 0:40 | T | Tripped showing O/V.relay | 0 | 0 | No interruption
AShuganj | Ashuganj-Sirajganj 230 kV line-2 | 2021-01-17 01:46 | 2021-01-17 07:52 | 6:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line | 2021-01-24 22:31 | 2021-01-24 23:33 | 1:02 | T | Tripped showing auto reclose. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line | 2021-01-24 22:35 | 2021-01-24 23:09 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla (N) | Cumilla (N)-Daudkandi 132 kV line-1 | 2021-01-25 03:53 | 2021-01-25 04:12 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla (N)-Daudkandi 132 kV line-2 | 2021-01-25 04:58 | 2021-01-25 05:12 | 0:14 | T |  | 0 | 0 | No interruption
| Cumilla (N)-Daudkandi 132 kV line-1 | 2021-01-25 06:27 | 2021-01-25 07:25 | 0:58 | T |  | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2021-01-27 06:22 | 2021-01-27 16:34 | 10:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-2 | 2021-01-29 05:00 | 2021-01-29 10:20 | 5:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Daudkandi-Cumilla(N) 132 kV line-1 | 2021-01-29 05:15 | 2021-01-29 10:28 | 5:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2021-01-31 20:57 | 2021-01-31 21:18 | 0:21 | T | Tripped showing dist.& E/F relay | 40 | 14 | Power interruption
|  |  | Total : | 32:28 |  | Unserved Energy: |  | 14
Khulna Grid Circle :
Gopalganj(O) | Gopalganj(O)-Gopalganj P/S 132 kV line | 2021-01-04 10:40 | 2021-01-04 14:17 | 3:37 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2021-01-29 16:20 | 2021-01-29 16:48 | 0:28 | T | Tripped showing dist. relay | 286 | 30.9167 | Power interruption 16:20 to 16:55
| Faridpur-Bheramara 132 kV line-2 | 2021-01-29 16:20 | 2021-01-29 17:20 | 1:00 | T |  | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) 132 kV line-1 | 2021-01-29 16:21 | 2021-01-29 17:03 | 0:42 | T | VTripped showing dist.(B-phase) & O/V relay | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV line-2 | 2021-01-29 16:21 | 2021-01-29 17:16 | 0:55 | T |  | 0 | 0 | No interruption
| Madaripur-Gopalganj (N) 132 kV line-3 | 2021-01-29 16:21 | 2021-01-29 18:18 | 1:57 | T
|  |  | Total : | 8:39 |  | Unserved Energy: |  | 30.9167
HVDC Grid Circle :
Ishurdi | Ishurdi-Baghabari 230 kV line-1 & 2 | 2021-01-21 03:50 | 2021-01-21 04:23 | 0:33 | T | Tripped showing Gen.trip DT-1,Air Block relay | 0 | 0 | No interruption
Benapole | Benapole-Jessore 132 kV line-1 | 2021-01-22 21:46 | 2021-01-22 23:04 | 1:18 | E/O | Due to SF6 gas pressur low | 0 | 0 | No interruption
|  |  | Total : | 1:51 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Rajshahi(O) | Rajshahi(O)-NPSL P/S 132 kV line | 2021-01-07 04:11 | 2021-01-07 12:33 | 8:22 | E/O | Due to R-phase PT Burst | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Natore 132 kV line-1 | 2021-01-07 04:11 | 2021-01-07 05:02 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Thaurgaon | Thurgaon-Purbasadipur 132 kV line-2 | 2021-01-08 15:13 | 2021-01-08 15:30 | 0:17 | T | Tripped showing PT MCB tripped | 50 | 14.1667 | Power interruption
Bogura | Bogura -Sirajganj 230 kV line-1 | 2021-01-10 15:17 | 2021-01-10 17:17 | 2:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-1 | 2021-01-11 11:20 | 2021-01-11 13:41 | 2:21 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2021-01-13 05:30 | 2021-01-13 05:48 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-1 | 2021-01-16 02:10 | 2021-01-16 02:28 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi S/S | Rajshahi-PDB Katakhali PP 132 kV line | 2021-01-17 14:10 | 2021-01-17 15:39 | 1:29 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2021-01-27 10:52 | 2021-01-27 14:58 | 4:06 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 20:02 |  | Unserved Energy: |  | 14.1667
Others :
Ullon | Ullon-Haripur 132 kV line | 2021-01-22 07:27 | 2021-01-22 07:37 | 0:10 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 0:10 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 129:17 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T3 | 2021-01-02 07:24 | 2021-01-02 20:27 | 13:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi(N) | 132 kV Bus-1 | 2021-01-02 10:02 | 2021-01-02 13:59 | 3:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-Tr3 | 2021-01-02 09:59 | 2021-01-02 16:16 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-01-03 09:25 | 2021-01-03 17:13 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-Tr3 | 2021-01-03 08:17 | 2021-01-03 15:52 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2021-01-04 09:25 | 2021-01-04 18:45 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T01 | 2021-01-04 10:36 | 2021-01-04 17:08 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132 kV main Bus-2 | 2021-01-04 08:08 | 2021-01-04 16:28 | 8:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-01-04 08:51 | 2021-01-04 17:29 | 8:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2021-01-05 08:41 | 2021-01-05 20:22 | 11:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-01-05 09:20 | 2021-01-05 15:55 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2021-01-05 15:58 | 2021-01-05 17:04 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-TR2 | 2021-01-06 08:40 | 2021-01-06 15:25 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1 & T2 | 2021-01-06 08:33 | 2021-01-06 16:58 | 8:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2021-01-06 09:58 | 2021-01-06 17:48 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T03 | 2021-01-07 09:18 | 2021-01-07 17:38 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-TR2 | 2021-01-07 09:18 | 2021-01-07 16:00 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-01-07 08:39 | 2021-01-07 12:35 | 3:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T5 | 2021-01-07 09:26 | 2021-01-07 16:39 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T4 |  | 2021-01-07 15:19 |  | S/O | After maintenance work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T2 | 2021-01-08 07:05 | 2021-01-08 16:40 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-01-08 09:11 | 2021-01-08 17:19 | 8:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi(N) | 132 kV Bus-2 | 2021-01-09 09:12 | 2021-01-09 12:43 | 3:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2021-01-09 09:20 | 2021-01-09 19:30 | 10:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-GT2 | 2021-01-09 09:50 | 2021-01-09 13:52 | 4:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-1 | 2021-01-09 10:40 | 2021-01-09 17:15 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-01-09 08:52 | 2021-01-09 16:49 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T1 | 2021-01-09 08:03 | 2021-01-09 15:06 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 |  | 2021-01-09 10:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-01-09 09:16 | 2021-01-09 13:38 | 4:22 | S/O | Due to earthing installaton | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2021-01-10 08:45 | 2021-01-10 16:53 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2021-01-10 10:32 | 2021-01-10 10:50 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T1 | 2021-01-11 09:23 | 2021-01-11 16:55 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400 kV Bus-2 | 2021-01-11 08:25 | 2021-01-11 14:24 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2021-01-11 11:20 | 2021-01-11 20:35 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T1 | 2021-01-12 09:22 | 2021-01-12 16:36 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2021-01-13 08:57 | 2021-01-13 10:55 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-13 11:08 | 2021-01-13 20:15 | 9:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T1 | 2021-01-14 08:14 | 2021-01-14 16:48 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2021-01-14 10:31 | 2021-01-14 14:50 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2021-01-14 10:22 | 2021-01-14 15:30 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-01-14 09:32 | 2021-01-14 16:40 | 7:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T01 | 2021-01-14 09:36 | 2021-01-14 16:27 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2021-01-14 14:02 | 2021-01-14 15:41 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T4 | 2021-01-15 09:46 | 2021-01-15 09:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T1 | 2021-01-15 14:57 | 2021-01-15 16:03 | 1:06 | S/O | Due to PBS work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-15 16:06 | 2021-01-15 17:53 | 1:47 | S/O | Due to relay test | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2021-01-15 14:20 | 2021-01-15 15:55 | 1:35 | S/O |  | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-01-16 07:49 | 2021-01-16 16:55 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 230/132 kV Transformer-T01 |  | 2021-01-16 16:44 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-01-17 08:30 | 2021-01-17 20:30 | 12:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus-2 | 2021-01-17 10:50 | 2021-01-17 16:28 | 5:38 | S/O | Due to replacement work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformer-ATR1 | 2021-01-17 13:44 | 2021-01-17 14:35 | 0:51 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T02 | 2021-01-17 13:39 | 2021-01-17 17:04 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kochua | 132/33 kV Transformer-T1 |  | 2021-01-17 18:05 |  |  | New connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 |  | 2021-01-17 18:10 |  |  |  | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-01-18 08:27 | 2021-01-18 20:34 | 12:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2021-01-18 09:48 | 2021-01-18 16:56 | 7:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132 kV Bus-A | 2021-01-18 09:25 | 2021-01-18 14:05 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 132/33 kV Transformer-T1 | 2021-01-18 10:20 | 2021-01-18 13:53 | 3:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2021-01-19 08:24 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-01-19 08:35 | 2021-01-19 16:02 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kV Bus-A | 2021-01-19 10:15 | 2021-01-19 17:55 | 7:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-19 08:54 | 2021-01-19 17:54 | 9:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2021-01-19 09:51 | 2021-01-19 17:47 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 230/132 kV Transformer-T01 | 2021-01-19 11:25 | 2021-01-19 16:05 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2021-01-19 11:45 | 2021-01-19 15:01 | 3:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus-2 | 2021-01-20 10:30 | 2021-01-20 15:30 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2021-01-20 08:59 | 2021-01-20 17:40 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| 33 kV Bus-A | 2021-01-20 09:33 | 2021-01-20 14:16 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2021-01-20 11:05 | 2021-01-20 13:52 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230 kV Bus-1 | 2021-01-20 09:40 | 2021-01-20 12:42 | 3:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kV Bus-B | 2021-01-20 14:16 | 2021-01-20 17:17 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2021-01-21 10:17 | 2021-01-21 16:16 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2021-01-21 09:28 | 2021-01-21 16:49 | 7:21 | S/O | After maintenance work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 |  | 2021-01-21 10:50 |  | S/O |  | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2021-01-21 10:26 | 2021-01-21 13:22 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 |  | 2021-01-21 20:10 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & T2 | 2021-01-22 07:15 | 2021-01-22 18:24 | 11:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2021-01-23 11:48 | 2021-01-23 18:50 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Amibazar | 132 kV Bus-2 | 2021-01-24 09:56 | 2021-01-24 17:05 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2021-01-24 11:11 | 2021-01-24 17:21 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2021-01-24 08:46 | 2021-01-24 12:40 | 3:54 | S/O | Due to A/M work | 0 | 0
Mirpur | 132/33 kV Transformer-T3 | 2021-01-25 09:05 | 2021-01-25 17:46 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2021-01-25 10:42 | 2021-01-25 13:25 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2021-01-25 10:52 | 2021-01-25 16:58 | 6:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2021-01-25 10:51 | 2021-01-25 16:18 | 5:27 | S/O | Due to painting work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-01-25 13:38 | 2021-01-25 14:50 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | 132/33 kV Transformer-T1 | 2021-01-26 09:48 | 2021-01-26 17:45 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2021-01-26 09:48 | 2021-01-26 17:23 | 7:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2021-01-27 08:28 | 2021-01-27 17:07 | 8:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2021-01-27 10:25 | 2021-01-27 17:20 | 6:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Amibazar | 230/132 kV Transformer-T03 | 2021-01-27 11:16 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2021-01-27 13:12 | 2021-01-27 13:45 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2021-01-28 12:32 | 2021-01-28 13:36 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2021-01-28 10:43 | 2021-01-28 16:21 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformers-T1 & T3 | 2021-01-28 13:42 | 2021-01-28 15:10 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 | 2021-01-29 10:07 | 2021-01-29 17:22 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2021-01-29 10:38 | 2021-01-29 17:10 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 & 33 kV Bus | 2021-01-30 07:48 | 2021-01-30 10:35 | 2:47 | S/O | Due to A/M work | 42 | 116.9 | Power interruption
Joydevpur | 132/33 kV Transformer-T2 | 2021-01-31 12:15 | 2021-01-31 14:40 | 2:25 | S/O | Due to C/M work | 19 | 45.9167 | Power interruption
|  |  | Total : | 549:22 |  | Unserved Energy: |  | 162.8167
Dhaka (South) Grid Circle :
Rampura | 230/132 kV Transformer-T02 | 2021-01-01 07:34 | 2021-01-01 15:25 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | 132/33 kV Transformer-GT1 | 2021-01-01 09:17 | 2021-01-01 14:58 | 5:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132 kV reserve Bus | 2021-01-04 09:00 | 2021-01-04 20:46 | 11:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-05 09:47 | 2021-01-05 20:16 | 10:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 230 kV Bus-2 | 2021-01-05 08:24 | 2021-01-05 15:54 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV Bus-2 | 2021-01-06 08:44 | 2021-01-06 13:37 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132 kV main Bus-2 | 2021-01-06 12:41 | 2021-01-06 16:28 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2021-01-07 08:52 | 2021-01-07 16:06 | 7:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230 kV Bus-2 | 2021-01-07 10:00 | 2021-01-07 17:15 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2021-01-08 07:28 | 2021-01-08 15:57 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV AutoTransformer-T03 | 2021-01-08 07:28 | 2021-01-08 16:21 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T1 | 2021-01-08 09:07 | 2021-01-08 14:53 | 5:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T03 | 2021-01-09 08:30 | 2021-01-09 16:31 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-01-09 08:45 | 2021-01-09 13:25 | 4:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 132/33 kV Transformer-T1 | 2021-01-09 08:16 | 2021-01-09 08:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132/33 kV Transformer-T3 | 2021-01-10 07:42 | 2021-01-10 15:16 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2021-01-10 10:01 | 2021-01-10 18:02 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-2 | 2021-01-14 08:28 | 2021-01-14 17:28 | 9:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2021-01-15 07:48 | 2021-01-15 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-2 | 2021-01-15 08:19 | 2021-01-15 17:24 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-01-16 07:18 | 2021-01-16 21:33 | 14:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T02 | 2021-01-16 09:00 | 2021-01-16 21:01 | 12:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2021-01-19 10:21 | 2021-01-19 15:17 | 4:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132 kV Bus-1 |  | 2021-01-21 14:35 |  |  | New connection | 0 | 0 | No interruption
| 133 kV Bus-2 |  | 2021-01-21 14:40 |  |  |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2021-01-21 16:20 |  |  |  | 0 | 0 | No interruption
Page: 4/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Nawabganj | 132/33 kV Transformer-T2 |  | 2021-01-21 04:23 |  |  | New connection | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T01 | 2021-01-22 09:23 | 2021-01-22 20:01 | 10:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2021-01-22 08:45 | 2021-01-22 16:00 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T01 | 2021-01-23 07:47 | 2021-01-23 20:28 | 12:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV Transformer-AT01 | 2021-01-24 09:56 | 2021-01-24 15:38 | 5:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T01 | 2021-01-25 08:15 | 2021-01-25 16:17 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T1 | 2021-01-25 09:42 | 2021-01-25 16:20 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2021-01-27 08:39 | 2021-01-27 17:50 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-28 09:47 | 2021-01-28 17:09 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 | 2021-01-28 08:55 | 2021-01-31 10:30 | 73:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2021-01-29 10:50 | 2021-01-29 10:50 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | 132/33 kV Transformer-T1 | 2021-01-25 09:42 | 2021-01-25 16:20 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-31 08:35 | 2021-01-31 14:48 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV Transformer-T3 | 2021-01-31 12:05 | 2021-01-31 14:18 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 323:15 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T1 | 2021-01-01 09:29 | 2021-01-01 16:48 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-01-01 08:18 | 2021-01-01 13:43 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-02 12:18 | 2021-01-02 13:20 | 1:02 | S/O | Due to relay problem | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2021-01-03 08:06 | 2021-01-03 16:16 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 & CB | 2021-01-04 06:55 | 2021-01-04 06:55 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-01-06 06:53 | 2021-01-06 06:53 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2021-01-06 08:05 | 2021-01-06 11:18 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2021-01-08 08:48 | 2021-01-08 13:57 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-09 08:42 | 2021-01-09 14:04 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2021-01-10 07:57 | 2021-01-10 14:46 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2021-01-11 08:23 | 2021-01-11 11:58 | 3:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2021-01-11 07:57 | 2021-01-11 15:28 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV Transformer-T01 | 2021-01-13 09:48 | 2021-01-13 17:13 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2021-01-14 09:36 | 2021-01-14 16:27 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-1 | 2021-01-18 06:46 | 2021-01-18 06:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2021-01-19 09:03 | 2021-01-19 14:44 | 5:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-1 | 2021-01-22 11:28 | 2021-01-22 15:37 | 4:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2021-01-26 09:12 | 2021-01-26 13:11 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
GPH | 230/132 kV Transformer-T01 | 2021-01-30 12:01 | 2021-01-30 16:04 | 4:03 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 85:43 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
Sreemongal | 132/33 kV Transformer-T3 with 33 kV bus | 2021-01-01 08:15 | 2021-01-01 08:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2021-01-01 08:27 | 2021-01-01 10:55 | 2:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-01-02 08:23 | 2021-01-02 14:47 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-02 11:00 | 2021-01-02 14:44 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T3 | 2021-01-02 08:45 | 2021-01-02 08:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T2 & 33 kV Bus | 2021-01-02 08:30 | 2021-01-02 13:05 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2021-01-07 08:35 | 2021-01-07 11:18 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj P/S | 132 kV mai Bus | 2021-01-08 09:20 | 2021-01-08 17:54 | 8:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2021-01-08 09:20 | 2021-01-08 18:01 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 5/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sylhet | 132/33 kV Transformer-T1 | 2021-01-09 07:30 | 2021-01-09 07:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2021-01-09 08:33 | 2021-01-09 14:48 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2021-01-09 09:10 | 2021-01-09 17:59 | 8:49 | S/O | Due to SAS work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2021-01-09 09:02 | 2021-01-09 10:53 | 1:51 | S/O | Due to C/M work | 15 | 27.75 | Power interruption
Sylhet | 132/33 kV Transformer-T1 |  | 2021-01-09 10:51 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2021-01-11 09:54 | 2021-01-11 18:06 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-12 09:22 | 2021-01-12 16:36 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T1 | 2021-01-19 10:07 | 2021-01-19 16:28 | 6:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2021-01-20 10:33 | 2021-01-20 17:21 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T2 | 2021-01-20 10:13 | 2021-01-20 16:22 | 6:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T2 |  | 2021-01-21 10:18 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-21 10:27 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 |  | 2021-01-22 11:12 |  | S/O | After maintenance work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2021-01-23 07:44 | 2021-01-24 11:56 | 28:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2021-01-23 10:32 | 2021-01-23 17:50 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2021-01-23 09:10 | 2021-01-23 17:47 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2021-01-24 10:24 | 2021-01-24 17:14 | 6:50 | S/O | Due to SAS work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2021-01-24 10:47 | 2021-01-24 17:15 | 6:28 | S/O | Due to SAS work | 0 | 0 | No interruption
| 132/33 kV auxiliary Transformer-T2 | 2021-01-24 19:04 | 2021-01-25 12:40 | 17:36 | S/O | Due to safety work | 26 | 457.6 | Power interruption
Shahjibazar | 132/33 kV Transformer-T6 | 2021-01-26 07:50 | 2021-01-26 07:50 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2021-01-26 09:17 | 2021-01-26 13:36 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-26 13:56 | 2021-01-26 17:05 | 3:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132 kV Bus-2 | 2021-01-27 10:34 | 2021-01-27 10:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2021-01-28 07:54 | 2021-01-28 09:45 | 1:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 33 kV full Bus | 2021-01-30 07:17 | 2021-01-30 17:39 | 10:22 | S/O | Due to C/M work | 40 | 414.6667 | Power interruption
Ashuganj | 132 kV Bus-2 | 2021-01-30 08:30 | 2021-01-30 17:55 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T3 | 2021-01-30 09:05 | 2021-01-30 16:40 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-31 09:22 | 2021-01-31 21:15 | 11:53 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 212:23 |  | Unserved Energy : |  | 900.0167
Khulna Grid Circle :
Matarbari | 132/33 kV Transformer-T1 | 2021-01-04 10:22 | 2021-01-04 17:25 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV,25/41MVA Transformer-T2 | 2021-01-04 09:15 | 2021-01-04 09:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Shariatpur | 132/33 kV Transformer-T1 | 2021-01-08 06:29 | 2021-01-08 08:34 | 2:05 | S/O | Due to C/M work | 15 | 31.25 | Power interruption
Faridpur | 132/33 kV Transformer-T1 | 2021-01-08 08:50 | 2021-01-08 10:28 | 1:38 | S/O | Due to C/M work | 20 | 32.6667 | Power interruption
Barishal(N) | 33 kV Bus | 2021-01-08 08:53 | 2021-01-08 16:18 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 & T5 & 33 kV bus | 2021-01-09 09:19 | 2021-01-09 15:36 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 |  | 2021-01-10 10:20 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-10 10:43 | 2021-01-10 12:05 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T1 | 2021-01-14 08:41 | 2021-01-14 11:44 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-14 11:54 | 2021-01-14 20:40 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2021-01-15 09:44 | 2021-01-15 09:44 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2021-01-15 10:13 | 2021-01-15 10:26 | 0:13 | S/O | Due to replacement work at 33 kV side | 20 | 4.3333 | Power interruption
Gopalganj(O) | 132/33 kV Transformer-T2(New) |  | 2021-01-20 15:10 |  | S/O | New connection | 0 | 0 | No interruption
| 132/33 kV Transformer-AT01 | 2021-01-24 10:16 | 2021-01-24 10:16 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/132 kV Transformer-AT01 | 2021-01-24 08:34 | 2021-01-24 17:08 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/132 kV Transformer-T02 | 2021-01-25 09:13 | 2021-01-25 16:22 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400 kV Bus | 2021-01-26 09:34 | 2021-01-26 16:09 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/132 kV Transformer-T02 | 2021-01-26 09:22 | 2021-01-26 14:14 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/132 kV Transformer-AT01 | 2021-01-27 09:07 | 2021-01-27 17:27 | 8:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| 400 kV Bus-1 & 2 | 2021-01-27 09:18 | 2021-01-27 17:20 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 | 2021-01-28 08:12 | 2021-01-28 09:15 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 82:27 |  | Unserved Energy : |  | 68.25
Page: 6/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Kustia | 132 kV Busbar -A & B | 2021-01-01 08:15 | 2021-01-01 15:39 | 7:24 | S/O | Due to A/M work | 45 | 333 | Power interruption
Jhenidah | 132 kV Bus | 2021-01-02 07:11 | 2021-01-02 16:56 | 9:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Pabna | 132/33 kV,50/75MVA Transformer-T2 | 2021-01-04 08:34 | 2021-01-04 16:38 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-01-05 08:33 | 2021-01-05 17:45 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2021-01-05 08:10 | 2021-01-05 17:08 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2021-01-06 08:28 | 2021-01-06 16:40 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2021-01-06 08:13 | 2021-01-06 15:04 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2021-01-07 09:24 | 2021-01-07 15:50 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230 kV main Bus-1 | 2021-01-07 13:13 | 2021-01-07 15:44 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132 kV main Bus | 2021-01-08 09:20 | 2021-01-08 13:56 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-2 | 2021-01-10 08:45 | 2021-01-10 13:25 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2021-01-13 08:02 | 2021-01-13 21:12 | 13:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T-1 | 2021-01-14 10:40 | 2021-01-14 16:52 | 6:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kustia | 132/33 kV Transformer-T1 | 2021-01-14 14:01 | 2021-01-14 14:23 | 0:22 | S/O | Due to relay test | 0 | 0 | No interruption
Jessre | 132 kV Bus-A & B | 2021-01-15 07:14 | 2021-01-15 17:13 | 9:59 | S/O | Due to D/W work | 80 | 798.6667 | Power interruption
Shahjadpur | 132 kV man Bus | 2021-01-15 08:50 | 2021-01-15 15:25 | 6:35 | S/O | Due to A/M work | 10 | 65.8333 | Power interruption
Jessore | 132 kV Bus-1 & 2 | 2021-01-16 07:13 | 2021-01-16 09:01 | 1:48 | S/O | Due to D/W work | 60 | 108 | Power interruption
Shahjadpur | 132/33 kV Transformer-T2 | 2021-01-16 09:20 | 2021-01-16 16:10 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-01-17 10:10 | 2021-01-17 14:51 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | 132/33 kV Transformer-T-2 | 2021-01-18 11:12 | 2021-01-18 13:42 | 2:30 | S/O | Due to SPMC work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2021-01-18 11:02 | 2021-01-18 13:42 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC 400 kV | HVDC 400 kV reactor | 2021-01-18 15:04 | 2021-01-19 09:35 | 18:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 |  | 2021-01-18 16:40 |  | S/O | After maintenance work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T3 | 2021-01-19 09:57 | 2021-01-19 15:45 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC 400 kV | HVDC 20DF44 reactor | 2021-01-19 09:23 | 2021-01-19 14:46 | 5:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T-03 | 2021-01-20 09:41 | 2021-01-20 18:24 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV Reactor 10CF21 | 2021-01-20 09:18 | 2021-01-20 12:43 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC 400 kV Reactor 10CF22 | 2021-01-20 12:46 | 2021-01-20 15:57 | 3:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T3 | 2021-01-21 09:33 | 2021-01-21 20:37 | 11:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | 132 kV Bus-A & B | 2021-01-22 07:00 | 2021-01-22 10:45 | 3:45 | S/O | Due to D/W work | 100 | 375 | Power interruption
Ishurdi | 132/33 kV Transformer-T2 | 2021-01-24 09:14 | 2021-01-24 15:52 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T4 | 2021-01-24 09:02 | 2021-01-24 17:40 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | 132 kV Bus-2 | 2021-01-24 11:21 | 2021-01-24 15:49 | 4:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | 230 kV filter 20DF-13 |  | 2021-01-26 13:54 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T01 | 2021-01-27 09:59 | 2021-01-27 17:58 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV Bus |  | 2021-01-31 21:15 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 218:59 |  | Unserved Energy : |  | 1680.5
Bogura Grid Circle:
Purbasadipur | 132 kV Bus | 2021-01-02 07:31 | 2021-01-02 15:50 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-ATR-2 | 2021-01-02 09:51 | 2021-01-02 20:36 | 10:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132 kV Bus-B | 2021-01-03 08:02 | 2021-01-03 18:28 | 10:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-3 | 2021-01-03 09:45 | 2021-01-03 18:14 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-ATR-1 | 2021-01-03 12:23 | 2021-01-03 20:14 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-ATR-1 | 2021-01-04 12:18 | 2021-01-04 20:32 | 8:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Mahastangarth | 132/33 kV Transformer-T-1 | 2021-01-04 08:53 | 2021-01-04 11:51 | 2:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2021-01-04 08:53 | 2021-01-04 11:50 | 2:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-01-04 12:03 | 2021-01-04 16:09 | 4:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
| 132 kV Bus-2 | 2021-01-04 12:07 | 2021-01-04 12:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-2 & CB | 2021-01-04 09:35 | 2021-01-04 11:55 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2021-01-08 07:02 | 2021-01-08 20:13 | 13:11 | S/O | Due to C/M work | 8 | 105.4667 | Power interruption
| 132/33 kV Transformer-T-3 | 2021-01-09 08:43 | 2021-01-09 16:59 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2021-01-10 12:37 | 2021-01-10 20:09 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-ATR1 | 2021-01-11 09:32 | 2021-01-11 14:05 | 4:33 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-ATR1 | 2021-01-12 12:50 | 2021-01-12 14:29 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Niamatpur | 132/33 kV Transformer-T-1 & 33 kV Bus | 2021-01-12 15:50 | 2021-01-12 16:30 | 0:40 | S/O | Due to A/M work | 20 | 13.3333 | Power interruption
Rajshahi(New) | 230/132 kV Transformer-ATR2 | 2021-01-13 11:15 | 2021-01-13 16:25 | 5:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2021-01-14 10:58 | 2021-01-14 11:48 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-02 |  | 2021-01-14 22:33 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rangpur | 33 kV Bus-2 | 2021-01-15 08:20 | 2021-01-15 12:15 | 3:55 | S/O | Due to C/M work | 30 | 117.5 | Power interruption
Rajshahi | 230/132 kV Transformer-T2 | 2021-01-16 11:04 | 2021-01-16 16:12 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-02 | 2021-01-16 11:49 | 2021-01-16 14:44 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-4 | 2021-01-17 11:28 | 2021-01-17 12:22 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-01-17 09:56 | 2021-01-17 10:16 | 0:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-ATR1 | 2021-01-17 11:20 | 2021-01-17 20:09 | 8:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-ATR2 | 2021-01-18 10:53 | 2021-01-18 16:28 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-3 | 2021-01-19 10:21 | 2021-01-19 15:17 | 4:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2021-01-19 11:44 | 2021-01-19 14:36 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-02 | 2021-01-16 11:49 | 2021-01-16 14:44 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Mahastangarth | 132/33 kV Transformer-T-2 | 2021-01-23 10:52 | 2021-01-23 13:04 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T-1 | 2021-01-25 11:48 | 2021-01-25 14:30 | 2:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-01-25 15:06 | 2021-01-25 15:56 | 0:50 | S/O | Due to telecom work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-T-1 | 2021-01-26 13:12 | 2021-01-26 16:22 | 3:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-ATR-2 | 2021-01-27 12:47 | 2021-01-27 17:30 | 4:43 | S/O | Due to SAS work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-2 & 33 kV Bus | 2021-01-30 07:28 | 2021-01-30 08:49 | 1:21 | S/O | Due to C/M work | 35 | 47.25 | Power interruption
Saidpur | 132/33 kV Transformer-T-2 | 2021-01-30 11:32 | 2021-01-30 12:10 | 0:38 | S/O | Due to A/M work | 5 | 3.1667 | Power interruption
Bogra | 132/33 kV Transformers-T-1 |  | 2021-01-31 17:41 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2 |  | 2021-01-31 17:50 |  | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 162:11 |  | Unserved Energy : |  | 286.7167
Others :
Ashuganj | 230/132 kV Transformer-OAT-12 | 2021-01-17 08:30 | 2021-01-17 20:30 | 12:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total | 12:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1646:20 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2021-01-02 07:28 | 2021-01-02 17:16 | 9:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-02 09:41 | 2021-01-02 16:11 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2021-01-02 09:08 | 2021-01-02 16:18 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-01-04 08:44 | 2021-01-04 19:33 | 10:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Kabirpur 132 kV line-1 | 2021-01-04 11:48 | 2021-01-04 11:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jamalpur-Mymensingh 132 kV line-1 | 2021-01-04 14:22 | 2021-01-04 17:43 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2021-01-05 06:44 | 2021-01-05 06:44 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-2 | 2021-01-05 09:03 | 2021-01-05 09:03 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2021-01-06 06:51 | 2021-01-06 06:51 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2021-01-06 13:13 | 2021-01-06 14:45 | 1:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV line-2 | 2021-01-09 09:04 | 2021-01-09 16:58 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2021-01-09 10:46 | 2021-01-09 16:46 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Mymensingh Solar 132 kV line | 2021-01-09 09:26 | 2021-01-09 17:55 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Kishoreganj 132 kV line-1 | 2021-01-09 09:52 | 2021-01-09 13:06 | 3:14 | S/O | Due to A/M work | 0 | 0 | No interruption
kishoreganj | kishoreganj-Ashuganj 132 KV line-1 | 2021-01-09 08:43 | 2021-01-09 16:21 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-01-09 08:23 | 2021-01-09 18:28 | 10:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV line | 2021-01-09 09:58 | 2021-01-09 20:45 | 10:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-2 | 2021-01-09 13:08 | 2021-01-09 17:28 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P132 kV line-2 | 2021-01-10 09:08 | 2021-01-10 17:37 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2021-01-10 08:26 | 2021-01-10 16:26 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-2 | 2021-01-10 08:56 | 2021-01-10 08:56 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-01-10 09:49 | 2021-01-10 17:36 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
kishoreganj | kishoreganj-Ashuganj 132 KV line-1 | 2021-01-10 10:03 | 2021-01-10 10:59 | 0:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliyapur 132 kV line-1 | 2020-11-11 07:09 | 2020-11-11 13:40 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2021-01-11 09:01 | 2021-01-11 17:08 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 132 kV line-1 | 2021-01-11 09:19 | 2021-01-11 16:48 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi -Kabirpur 132 kV line-1 | 2021-01-11 10:20 | 2021-01-11 17:38 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Mymensingh Solar 132 kV line-1 | 2021-11-11 09:35 | 2021-11-11 09:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Netrakona 132 kV line-1 | 2021-01-11 11:35 | 2021-01-11 15:03 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-Netrakona 132 kV line-2 | 2021-01-11 15:12 | 2021-01-11 20:18 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2021-01-12 07:05 | 2021-01-12 17:33 | 10:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2021-01-12 08:26 | 2021-01-12 16:39 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2021-01-12 09:25 | 2021-01-12 16:18 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV line-1 | 2021-01-12 08:51 | 2021-01-12 15:21 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 162 MW P/P 132 kV line-1 | 2021-01-12 12:01 | 2021-01-12 13:19 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2021-01-12 09:03 | 2021-01-12 16:51 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Aminbazar 132 kV line-2 | 2021-01-12 13:26 | 2021-01-12 15:43 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2021-01-13 08:31 | 2021-01-13 16:50 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-01-13 09:39 | 2021-01-13 17:15 | 7:36 | S/O | Due to replacement work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-01-13 09:03 | 2021-01-13 12:48 | 3:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2021-01-13 10:19 | 2021-01-13 18:49 | 8:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2021-01-14 08:27 | 2021-01-14 17:04 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2021-01-14 09:43 | 2021-01-14 16:33 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-14 09:57 | 2021-01-14 10:53 | 0:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur united 132 kV line-1 | 2021-01-14 11:09 | 2021-01-14 12:46 | 1:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Sutiakhali 50 MW Solar 132 kV line | 2021-01-14 09:57 | 2021-01-14 17:47 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-01-14 10:18 | 2021-01-14 11:19 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Manikganj 162 MW P/P 132 kV line-2 | 2021-01-14 09:44 | 2021-01-14 14:29 | 4:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-UMPL 132 kV line-2 | 2021-01-14 13:21 | 2021-01-14 14:02 | 0:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamlpur 132 kV line-2 | 2021-01-15 07:10 | 2021-01-15 18:49 | 11:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV line-2 | 2021-01-16 10:09 | 2021-01-16 22:53 | 12:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 132 kV line-1 &2 | 2021-01-16 09:02 | 2021-01-16 16:33 | 7:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-16 10:17 | 2021-01-16 17:26 | 7:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2021-01-17 08:26 | 2021-01-17 17:03 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-2 | 2021-01-17 09:18 | 2021-01-17 17:18 | 8:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-17 10:34 | 2021-01-17 15:03 | 4:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2021-01-17 09:13 | 2021-01-17 09:13 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 162 MW P/P 132 kV line-2 |  | 2021-01-17 20:22 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2021-01-18 08:27 | 2021-01-18 16:55 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 162 MW P/P 132 kV line-2 | 2021-01-18 10:34 | 2021-01-18 20:20 | 9:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 162 MW P/S 132 kV line-1 | 2021-01-18 09:38 | 2021-01-18 20:47 | 11:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-18 08:38 | 2021-01-18 17:20 | 8:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensigh-Mymensingh Solar 132 kV line | 2021-01-18 09:14 | 2021-01-18 20:45 | 11:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2021-01-18 09:35 | 2021-01-18 16:48 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2021-01-19 08:54 | 2021-01-19 17:36 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2021-01-19 09:56 | 2021-01-19 16:08 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV line-1 | 2021-01-19 09:44 | 2021-01-19 17:11 | 7:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-01-19 09:21 | 2021-01-19 15:34 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kv line-2 |  | 2021-01-19 11:38 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2021-01-19 16:34 | 2021-01-19 17:03 | 0:29 | S/O | Due to relay test | 0 | 0 | No interruption
| Kishoreganj-Mymensingh 132 kV line-2 | 2021-01-19 17:05 | 2021-01-19 17:38 | 0:33 | S/O |  | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kv line-2 |  | 2021-01-19 11:38 |  | S/O | After maintenance work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.P.132 kV line-2 | 2021-01-20 09:59 | 2021-01-20 13:44 | 3:45 | S/O | Due to SAS work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2021-01-20 08:41 | 2021-01-20 17:14 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dhamrai-Kaliakoir 132 kV line-2 | 2021-01-21 08:24 | 2021-01-21 16:16 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-01-21 09:37 | 2021-01-21 17:42 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensigh-RPCL 132 kV line | 2021-01-22 12:55 | 2021-01-22 17:17 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensigh-Kishoreganj 132 kV line-1 | 2021-01-24 07:25 | 2021-01-24 13:15 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2021-01-24 07:57 | 2021-01-24 07:57 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara (O) 132 kV line | 2021-01-24 09:07 | 2021-01-24 16:20 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-01-24 08:11 | 2021-01-24 19:00 | 10:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 132 kV line-2 | 2021-01-24 09:10 | 2021-01-24 17:15 | 8:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2021-01-24 12:07 | 2021-01-24 13:29 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-1 |  | 2021-01-24 13:15 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensigh-Sutiakhali 50 MW Solar 132 kV line | 2021-01-24 13:22 | 2021-01-24 17:03 | 3:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-01-24 09:58 | 2021-01-24 11:57 | 1:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-1 | 2021-01-24 13:46 | 2021-01-24 19:46 | 6:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-1 | 2021-01-24 20:43 | 2021-01-24 20:43 | 0:00 | S/O | Due to cable problem | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-1 |  | 2021-01-24 13:15 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | Tongi -New Tongi 132 kV line-1 | 2021-01-25 10:57 | 2021-01-25 11:37 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Sutiakhali 50 MW Solar 132 kV line | 2021-01-25 10:07 | 2021-01-25 18:18 | 8:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensigh-Valuka 132 kV line | 2021-01-25 10:32 | 2021-01-25 17:35 | 7:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensigh | Mymensigh-Sutiakhali 50 MW Solar 132 kV line | 2021-01-26 09:16 | 2021-01-26 18:12 | 8:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-2 |  | 2021-01-26 15:46 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-1 | 2021-01-27 10:30 | 2021-01-27 17:11 | 6:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kaliakoir-Kabirpur 132 kV line-1 | 2021-01-27 08:24 | 2021-01-27 17:22 | 8:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Valuka 132 kV line-1 | 2021-01-27 09:26 | 2021-01-27 17:52 | 8:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2021-01-27 09:38 | 2021-01-27 23:15 | 13:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Valuka 132 kV line-2 | 2021-01-28 10:17 | 2021-01-28 16:45 | 6:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2021-01-28 08:39 | 2021-01-28 17:18 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kv line-1 | 2021-01-29 08:39 | 2021-01-29 18:00 | 9:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Valuka 132 kV line-1 | 2021-01-29 10:12 | 2021-01-29 17:51 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 |  | 2021-01-29 11:43 |  | S/O | After maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2021-01-30 09:38 | 2021-01-30 17:17 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi -Kabirpur 132 kV line-2 | 2021-01-30 10:01 | 2021-01-30 15:54 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi -Kaliakoir 230 kV line-2 | 2021-01-31 09:04 | 2021-01-31 16:07 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2021-01-31 09:19 | 2021-01-31 16:38 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 611:25 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | Haripur-Madanganj 132 kV line | 2021-01-01 08:28 | 2021-01-01 15:17 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2021-01-02 06:44 | 2021-01-02 17:18 | 10:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2021-01-02 06:48 | 2021-01-02 17:35 | 10:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2021-01-03 07:33 | 2021-01-03 21:45 | 14:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2021-01-04 07:38 | 2021-01-04 09:51 | 2:13 | S/O | Due to R-phase loop changing | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2021-01-04 08:28 | 2021-01-04 16:11 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2021-01-04 08:55 | 2021-01-04 11:47 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-APR 230 KV line | 2021-01-05 07:20 | 2021-01-05 18:02 | 10:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2021-01-05 08:29 | 2021-01-05 15:11 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV line-2 | 2021-01-06 07:29 | 2021-01-06 07:29 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV line-2 | 2021-01-07 07:36 | 2021-01-07 16:42 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2021-01-08 09:58 | 2021-02-09 13:40 | 771:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2021-01-08 09:09 | 2021-01-10 20:16 | 6:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2021-01-09 13:08 | 2021-01-09 17:28 | 1:44 | S/O | Due to relay test | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV line-1 | 2021-01-11 09:04 | 2021-01-11 15:07 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-2 |  | 2021-01-13 15:15 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2021-01-16 10:13 | 2021-01-16 16:08 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Madanganj 132 kV line-2 | 2021-01-17 08:44 | 2021-01-17 16:51 | 8:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-1 | 2021-01-17 08:37 | 2021-01-17 12:22 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-2 | 2021-01-18 12:27 | 2021-01-18 20:26 | 7:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-1 | 2021-01-19 08:17 | 2021-01-19 13:43 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-2 | 2021-01-19 13:44 | 2021-01-19 16:39 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Madertek 132 kV line-1 | 2021-01-20 08:50 | 2021-01-20 15:35 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Motijheel 132 kV line-1 |  | 2021-01-21 14:30 |  |  | New connection | 0 | 0 | No interruption
Keraniganj | Keraniganj -Nawabganj 132 kV line-1 |  | 2021-01-21 14:34 |  |  |  | 0 | 0 | No interruption
| Keraniganj -Nawabganj 132 kV line-2 |  | 2021-01-21 14:39 |  |  |  | 0 | 0 | No interruption
| Rampura-Bhulta 132 kV line-3 |  | 2021-01-22 17:56 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Rampura-Bhulta 132 kV line-4 |  | 2021-01-22 21:40 |  | S/O
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 |  | 2021-01-22 21:31 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2021-01-23 09:35 | 2021-01-23 17:49 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ashuganj 400 kV line-1 | 2021-01-23 08:53 | 2021-01-23 17:12 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV line-2 | 2021-01-24 09:26 | 2021-01-24 15:36 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hasnabad-Aminbazar 230 kV line-1 | 2021-01-24 09:06 | 2021-01-24 19:16 | 10:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 4/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Keraniganj | Keraniganj -Nawabganj 132 kV line-1 | 2021-01-24 09:42 | 2021-01-24 15:44 | 6:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Keraniganj -Nawabganj 132 kV line-2 | 2021-01-24 09:42 | 2021-01-24 15:45 | 6:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishudi 230 kV line-1 | 2021-01-25 09:47 | 2021-01-25 18:40 | 8:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorashal-Ishudi 230 kV line-2 | 2021-01-28 08:28 | 2021-01-28 17:38 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2021-01-29 10:08 | 2021-01-29 18:32 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-2 | 2021-01-29 10:18 | 2021-01-29 18:40 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj -Nawabganj 132 kV line-1 | 2021-01-30 12:42 | 2021-01-30 13:59 | 1:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-(Maniknagar-Siddhirganj)-Ullon 132 kV line | 2021-01-30 13:06 | 2021-01-30 17:34 | 4:28 | S/O | Due to WASA work | 0 | 0 | No interruption
Madanganj | Madanganj -Munsiganj 132 kV line-1 | 2021-01-31 09:08 | 2021-01-31 16:12 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur S/S-Haripur 412 MW 132 kV line |  | 2021-01-31 08:38 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2021-01-31 09:35 | 2021-01-31 11:11 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-1 | 2021-01-31 11:12 | 2021-01-31 12:05 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 998:31 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Sikalabha | Sikalbaha-Dohazari 132 kV line-2 | 2021-01-01 07:26 | 2021-01-01 16:58 | 9:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2021-01-02 07:04 | 2021-01-02 16:52 | 9:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2021-01-02 07:23 | 2021-01-02 07:23 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kv line-2 | 2021-01-02 08:21 | 2021-01-02 16:30 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV line-1 | 2021-01-03 09:16 | 2021-01-03 16:53 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kv line-2 | 2021-01-03 08:32 | 2021-01-03 15:24 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroaulia | Baroaulia-KSRM 132 kV line | 2021-01-03 09:43 | 2021-01-03 17:42 | 7:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baroaulia-Hathazari 132 kV line-1 | 2021-01-04 09:03 | 2021-01-04 16:15 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baroaulia-KSRM 132 kV line | 2021-01-04 09:58 | 2021-01-04 17:29 | 7:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line-1 | 2021-01-04 09:08 | 2021-01-04 14:33 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2021-01-04 09:33 | 2021-01-04 17:58 | 8:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Contarbari -Cos'sbazar 132 kV line-1 | 2021-01-05 11:05 | 2021-01-05 15:50 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2021-01-05 09:23 | 2021-01-05 16:05 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line-1 | 2021-01-05 09:05 | 2021-01-05 15:08 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2021-01-06 06:58 | 2021-01-06 16:21 | 9:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2021-01-06 07:22 | 2021-01-06 16:36 | 9:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-2 | 2021-01-06 08:52 | 2021-01-06 16:28 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line-1 | 2021-01-06 08:28 | 2021-01-06 15:06 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2021-01-07 09:53 | 2021-01-07 15:27 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line-1 | 2021-01-07 08:22 | 2021-01-07 14:45 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2021-01-07 08:15 | 2021-01-07 16:55 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2021-01-07 08:17 | 2021-01-07 17:00 | 8:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cos'sbazar 132 kV line-2 | 2021-01-07 08:42 | 2021-01-09 11:16 | 50:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2021-01-08 07:13 | 2021-01-08 16:58 | 9:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2021-01-09 07:17 | 2021-01-09 16:09 | 8:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2021-01-09 08:59 | 2021-01-09 15:32 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-AKSML 230 kV line | 2021-01-10 09:33 | 2021-01-10 17:51 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern steel 132 kV line | 2021-01-10 08:46 | 2021-01-10 16:57 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-1 | 2021-01-11 09:12 | 2021-01-11 16:51 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern steel 132 kV line | 2021-01-11 08:18 | 2021-01-11 15:02 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2021-01-11 08:48 | 2021-01-19 15:05 | 198:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2021-01-12 09:03 | 2021-01-12 16:26 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Modern | Modern-Khulshi 132 kV line | 2021-01-12 10:13 | 2021-01-12 13:47 | 3:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV line-2 | 2021-01-13 09:16 | 2021-01-13 16:09 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baraulia-Hathazari 132 kV line-2 | 2021-01-14 08:36 | 2021-01-14 15:00 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2021-01-14 08:22 | 2021-01-14 15:12 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2021-01-16 08:39 | 2021-01-16 15:29 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | Hathazari-GPS 230 kV line | 2021-01-16 11:08 | 2021-01-16 17:45 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Khushi | Khushi-Madunaghat 132 kV line-2 | 2021-01-17 08:49 | 2021-01-17 13:29 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-AKSPL 132 kV line | 2021-01-17 08:56 | 2021-01-17 15:40 | 6:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV line | 2021-01-17 08:33 | 2021-01-17 16:21 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV line | 2021-01-18 08:38 | 2021-01-18 15:31 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-1 | 2021-01-18 08:24 | 2021-01-18 15:48 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Juldah-Shahmirpur 132 kV line-2 | 2021-01-19 08:36 | 2021-01-19 15:47 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2021-01-19 11:05 | 2021-01-19 15:05 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2021-01-20 08:36 | 2021-01-20 16:07 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | T.K chemical-Sikalbaha 132 kV line | 2021-01-20 09:05 | 2021-01-20 14:44 | 5:39 | S/O | Due to C/M work | 0 | 0
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2021-01-21 08:53 | 2021-01-21 15:20 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-01-21 10:02 | 2021-01-21 20:14 | 10:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-01-22 06:56 | 2021-01-22 14:24 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-1 | 2021-01-24 06:58 | 2021-01-24 11:24 | 4:26 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV line-2 | 2021-01-24 08:29 | 2021-01-24 15:53 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Khushi | Khushi-Madunaghat 132 kV line | 2021-01-25 07:46 | 2021-01-25 15:59 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khushi-Madunaghat 132 kV line | 2021-01-26 08:26 | 2021-01-26 16:30 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV line-1 | 2021-01-27 08:58 | 2021-01-27 18:00 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Khushi | Khushi-Hathazari 132 kV line | 2021-01-27 08:36 | 2021-01-27 15:42 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV line-2 | 2021-01-29 09:22 | 2021-01-29 16:34 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K chemical 132 kV line | 2021-01-30 07:31 | 2021-01-30 07:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khushi-Hathazari 132 kV line-1 | 2021-01-30 08:44 | 2021-01-30 16:53 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2021-01-31 09:53 | 2021-01-31 19:07 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Khushi | Khushi-AKSML 132 kV line | 2021-01-31 08:43 | 2021-01-31 19:01 | 10:18 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 668:40 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2021-01-01 08:55 | 2021-01-01 16:51 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroerhat | Baroerhat-PHP 132 kV line | 2021-01-01 09:09 | 2021-01-01 15:34 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Pabna 132 kV line | 2021-01-02 08:21 | 2021-01-02 16:40 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Barierhat 132 kV line | 2021-01-02 09:06 | 2021-01-02 15:45 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2021-01-03 09:13 | 2021-01-03 17:38 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Barierhat 132 kV line-1 | 2021-01-03 09:18 | 2021-01-03 16:18 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Feni-Barierhat 132 kV line-1 | 2021-01-04 08:55 | 2021-01-04 17:27 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2021-01-04 09:17 | 2021-01-04 18:10 | 8:53 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2021-01-04 09:52 | 2021-01-04 17:32 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-04 09:06 | 2021-01-04 16:51 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2021-01-05 09:10 | 2021-01-05 17:08 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV line | 2021-01-05 08:44 | 2021-01-05 15:13 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-05 08:50 | 2021-01-05 17:02 | 8:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2021-01-05 09:32 | 2021-01-05 18:28 | 8:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhe | Sylhe-Chatak 132 kV line-2 | 2021-01-06 06:39 | 2021-01-06 06:39 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2021-01-06 10:02 | 2021-01-06 16:21 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2021-01-06 09:16 | 2021-01-06 16:49 | 7:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 & 2 | 2021-01-06 08:59 | 2021-01-06 17:16 | 8:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2021-01-06 09:04 | 2021-01-06 20:33 | 11:29 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV line-1 | 2021-01-07 08:49 | 2021-01-07 20:12 | 11:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2021-01-07 08:51 | 2021-01-07 20:05 | 11:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2021-01-07 09:42 | 2021-01-07 16:26 | 6:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2021-01-09 08:13 | 2021-01-09 16:35 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2021-01-10 08:29 | 2021-01-10 16:51 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV line-2 | 2021-01-10 09:54 | 2021-01-10 16:46 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-1 | 2021-01-10 09:38 | 2021-01-10 17:42 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | Chatak-Sylhet 132 kV line-1 | 2021-01-10 09:01 | 2021-01-10 12:18 | 3:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2021-01-11 08:57 | 2021-01-11 15:59 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-11 09:33 | 2021-01-11 15:50 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-12 10:13 | 2021-01-12 15:37 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line | 2021-01-12 09:32 | 2021-01-12 15:05 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-1 | 2021-01-12 09:08 | 2021-01-12 17:23 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2021-01-12 09:10 | 2021-01-12 18:30 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Chandpur 132 kV line-1 | 2021-01-12 16:25 | 2021-01-12 20:30 | 4:05 | S/O | Due to project work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-1 | 2021-01-13 09:05 | 2021-01-13 15:41 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Chandpur S/S 132 kV line-1 | 2021-01-13 10:21 | 2021-01-13 14:56 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-1 | 2021-01-13 13:08 | 2021-01-13 15:59 | 2:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Chandpur S/S 132 kV line-2 | 2021-01-13 15:06 | 2021-01-13 17:18 | 2:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S -Fenchuganj P/S 132 kV line-2 | 2021-01-15 09:24 | 2021-01-15 09:24 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2021-01-14 10:08 | 2021-01-14 13:28 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line-2 | 2021-01-14 13:30 | 2021-01-14 16:25 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2021-01-16 09:13 | 2021-01-16 16:19 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2021-01-17 08:48 | 2021-01-17 09:47 | 0:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhe | Sylhe-Fenchuganj S/S 132 kV line | 2021-01-17 09:22 | 2021-01-17 12:47 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-2 | 2021-01-17 09:11 | 2021-01-17 17:07 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 |  | 2021-01-17 09:47 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-2 | 2021-01-18 09:24 | 2021-01-18 15:05 | 5:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2021-01-18 10:16 | 2021-01-18 16:12 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.Baria-Narsinghdi 132 kV line | 2021-01-19 09:04 | 2021-01-19 17:00 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV line-2 | 2021-01-19 09:13 | 2021-01-19 17:41 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2021-01-19 08:46 | 2021-01-19 20:13 | 11:27 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.Baria-Narsinghdi 132 kV line-1 | 2021-01-20 09:06 | 2021-01-20 16:54 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghanghat 230 kV line-2 | 2021-01-20 08:48 | 2021-01-20 15:31 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroerhat | Baroerhat-PHP 132 kV line | 2021-01-20 09:40 | 2021-01-20 17:18 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-01-20 09:40 | 2021-01-20 11:43 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-20 11:44 | 2021-01-20 11:58 | 0:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-2 | 2021-01-20 09:30 | 2021-01-20 18:53 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
B.baria | B.Baria-Narsinghdi 132 kV line-1 | 2021-01-21 09:07 | 2021-01-21 17:47 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Desh Energy 132 kV line-1 | 2021-01-21 09:19 | 2021-01-21 17:10 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 |  | 2021-01-21 12:43 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV line-1 |  | 2021-01-21 13:15 |  | S/O |  | 0 | 0 | No interruption
Ramganj | Ramganj-Desh Energy 132 kV line-2 | 2021-01-21 09:48 | 2021-01-21 17:27 | 7:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2021-01-22 10:52 | 2021-01-22 14:03 | 3:11 | S/O | Due to C/W work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2021-01-23 10:46 | 2021-01-23 14:05 | 3:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2021-01-23 08:30 | 2021-01-23 17:11 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.Baria-Desh Narsinghdi 132 kV line-1 | 2021-01-23 09:55 | 2021-01-23 15:51 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Fenchuganj S/S 132 kV line |  | 2021-01-24 09:21 |  | S/O | After maintenance work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV line-2 | 2021-01-24 09:42 | 2021-01-24 14:38 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2021-01-24 08:16 | 2021-01-24 20:30 | 12:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2021-01-25 10:00 | 2021-01-25 16:40 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/P.132 kV line | 2021-01-25 09:15 | 2021-01-25 15:53 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2021-01-25 09:43 | 2021-01-25 17:16 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ramganj | Ramganj-Desh Energy 132 kV line-1 | 2021-01-25 09:32 | 2021-01-25 18:35 | 9:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-01-26 08:55 | 2021-01-26 10:55 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-2 | 2021-01-26 09:38 | 2021-01-26 16:12 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroerhat | Baroerhat-PHP 132 kV line | 2021-01-26 10:14 | 2021-01-26 16:44 | 6:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Fen 132 kV line-1 | 2021-01-26 09:42 | 2021-01-26 14:14 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-26 11:05 | 2021-01-26 13:15 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2021-01-26 13:34 | 2021-01-26 14:45 | 1:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-2 | 2021-01-26 14:47 | 2021-01-26 17:00 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2021-01-27 09:53 | 2021-01-27 15:43 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2021-01-28 10:21 | 2021-01-28 17:28 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroerhat | Baroerhat-Feni 132 kV line | 2021-01-28 09:43 | 2021-01-28 17:50 | 8:07 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroerhat-Hathazari 132 kV line | 2021-01-28 10:20 | 2021-01-28 19:18 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-01-28 09:34 | 2021-01-28 16:14 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-1 | 2021-01-29 11:59 | 2021-01-29 15:09 | 3:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Bibiyana 230 kV line-2 | 2021-01-29 15:16 | 2021-01-29 17:49 | 2:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2021-01-30 08:44 | 2021-01-30 16:53 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroerhat | Baroerhat-PHP 132 kV line | 2021-01-30 09:06 | 2021-01-30 17:13 | 8:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2021-01-31 08:55 | 2021-01-31 14:55 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-01-31 09:04 | 2021-01-31 16:19 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2021-01-31 09:32 | 2021-01-31 16:39 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 564:47 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goalpara | Goalpara-Rupsha Orion 132 kV line | 2021-01-02 08:30 | 2021-01-02 16:29 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2021-01-02 08:26 | 2021-01-02 13:25 | 4:59 | S/O | Due to D/W work | 30 | 207 | Power interruption 08:26 to 15:20
| Barishal(N)-Madaripur 132 kV line-2 | 2021-01-02 07:45 | 2021-01-02 13:08 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal-Barishal Summit 132 kV line | 2021-01-02 08:52 | 2021-01-02 14:08 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV line-2 | 2021-01-03 08:50 | 2021-01-03 17:00 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Orion | Orion-Bagerhat 132 kV line-2 | 2021-01-03 08:29 | 2021-01-03 16:39 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2021-01-04 08:39 | 2021-01-04 15:26 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Madhumati P/S 132 kV line | 2021-01-04 08:04 | 2021-01-04 16:27 | 8:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-KPCL 132 kV line-1 | 2021-01-05 08:40 | 2021-01-05 15:54 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Madhumati P/S 132 kV line | 2021-01-05 07:55 | 2021-01-05 15:59 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2021-01-06 08:45 | 2021-01-06 14:36 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Faridpur 150 MW 132 kV line | 2021-01-06 08:19 | 2021-01-06 14:15 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2021-01-07 09:01 | 2021-01-07 12:31 | 3:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Faridpur 150 MW 132 kV line | 2021-01-07 08:14 | 2021-01-07 12:53 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-NWPGCL 132 kV line-1 | 2021-01-07 08:04 | 2021-01-07 15:14 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj (N) 132 kV line | 2021-01-08 07:11 | 2021-01-08 12:46 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj(O)-Gopalganj (N) 132 kV line-2 | 2021-01-09 07:07 | 2021-01-09 07:07 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(C) | Khulna©-NWPGCL 132 kV line-2 | 2021-01-09 07:58 | 2021-01-09 07:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-01-09 08:07 | 2021-01-09 16:34 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal-Bhandaria 132 kV line | 2021-01-10 08:06 | 2021-01-10 16:45 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-01-11 08:16 | 2021-01-11 16:52 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 KV line-1 | 2021-01-11 08:50 | 2021-01-11 15:20 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-WPGCL 132 kV line-2 | 2021-01-11 08:44 | 2021-01-11 16:02 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-01-12 08:18 | 2021-01-12 17:01 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 KV line-1 | 2021-01-12 08:53 | 2021-01-12 16:46 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-01-13 08:57 | 2021-01-13 15:30 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(O) | Barishal(O)-Barishal(N) 132 kV line-1 | 2021-01-14 08:57 | 2021-01-14 16:21 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 8/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Shariatpur 132 KV line-2 | 2021-01-16 08:55 | 2021-01-16 16:16 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Barishal(O) 132 kV line-1 | 2021-01-16 07:56 | 2021-01-16 16:13 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(N)-Barishal(S) 132 kV line-1 | 2021-01-17 08:13 | 2021-01-17 16:29 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 KV line-2 | 2021-01-17 08:36 | 2021-01-17 15:32 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-2 | 2021-01-18 07:14 | 2021-01-18 20:12 | 12:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Barishal(O) 132 kV line-2 | 2021-01-18 08:37 | 2021-01-18 17:03 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-2 | 2021-01-18 07:14 | 2021-01-18 20:12 | 12:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 KV line-2 | 2021-01-18 11:30 | 2021-01-18 17:00 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-1 | 2021-01-19 07:38 | 2021-01-19 16:53 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Barishal(O) 132 kV line-2 | 2021-01-19 08:34 | 2021-01-19 15:11 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV line-1 | 2021-01-19 11:14 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Barishal(O) 132 kV line-2 | 2021-01-20 09:05 | 2021-01-20 15:48 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj (N) 400 kV line-2 | 2021-01-23 09:20 | 2021-01-23 09:20 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Payra-Gopalganj (N) 400 kV line-2 | 2021-01-24 09:00 | 2021-01-27 20:40 |  | S/O |  | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV line-2 |  | 2021-01-30 10:31 |  | S/O | After maintenance work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV line-1 |  | 2021-01-30 13:20 |  | S/O |  | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2021-01-31 08:48 | 2021-01-31 16:30 | 7:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 274:08 |  | Unserved Energy: |  | 207
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC-Rajshahi (N) 230 kV line-1 | 2021-01-01 08:27 | 2021-01-01 20:29 | 12:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Rppur 132 kV line-1 | 2021-01-02 09:38 | 2021-01-02 13:25 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi (N) 230 kV line-1 | 2021-01-03 08:26 | 2021-01-03 20:13 | 11:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Kustia 132 kV line-1 | 2021-01-03 07:48 | 2021-01-03 14:33 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Pabna 132 kV line | 2021-01-03 08:51 | 2021-01-03 16:40 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV line-2 | 2021-01-03 08:40 | 2021-01-03 16:12 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV 10CF15 filter | 2021-01-04 09:48 | 2021-01-04 09:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi (N) 230 kV line-1 | 2021-01-04 09:28 | 2021-01-04 20:28 | 11:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | Bottail-Bheramara 132 kV line-1 | 2021-01-04 09:17 | 2021-01-04 15:17 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara 230 S/S | Bheramara 230 S/S-Bheramara GT 132 kV line | 2021-01-04 11:34 | 2021-01-04 11:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | Bottail-Bheramara 132 kV line-1 | 2021-01-05 08:13 | 2021-01-05 15:32 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC 230 kV line-1 |  | 2021-01-05 21:11 |  |  | charged at 21:11 | 0 | 0 | No interruption
Bheramara | Bheramara -Kustia 132 kV line-2 | 2021-01-06 08:50 | 2021-01-06 14:15 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjiadpur 132 kV line-1 | 2021-01-06 09:36 | 2021-01-06 13:56 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC-Rajshahi 230 kV line-2 | 2021-01-06 09:22 | 2021-01-06 20:33 | 11:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara -Bottail 132 kV line-2 | 2021-01-07 07:49 | 2021-01-07 14:59 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi (N) 230 kV line-2 & Bay 20D05C | 2021-01-07 10:15 | 2021-01-07 20:38 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara -Bottail 132 kV line-2 | 2021-01-09 08:16 | 2021-01-09 14:15 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara -Bottail 132 kV line-2 | 2021-01-10 07:45 | 2021-01-10 17:20 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC-Bahrampur 400 kV line-2 | 2021-01-10 09:49 | 2021-01-10 13:15 | 3:26 | S/O | Due to replacement work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2021-01-11 09:07 | 2021-01-11 18:11 | 9:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2021-01-11 08:26 | 2021-01-11 15:37 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj exp 132 kV line | 2021-01-11 08:43 | 2021-01-11 15:43 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2021-01-12 08:37 | 2021-01-12 15:31 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC Bus reactor -1 & 2 |  | 2021-01-12 10:22 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bheramara HVDC 20DF41 filter | 2021-01-12 10:34 | 2021-01-12 11:57 | 1:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV line-1 & 2 | 2021-01-13 08:00 | 2021-01-13 10:58 | 2:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2021-01-13 08:32 | 2021-01-13 16:25 | 7:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kustia-Jhenidah 132 kV line-1 | 2021-01-14 08:32 | 2021-01-14 15:53 | 7:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC-Rajshahi 230 kV line-1 &2 | 2021-01-15 08:37 | 2021-01-15 15:30 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-2 | 2021-01-15 18:51 |  |  | S/O | Due to CB problem | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2021-01-17 08:17 | 2021-01-17 18:33 | 10:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 9/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Kustia | Kustia-Jhenidah 132 kV line-2 | 2021-01-18 08:29 | 2021-01-18 20:27 | 11:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara S/S | Bheramara S/S-Bheramara NWPGCL 132 kV line | 2021-01-18 08:12 | 2021-01-18 13:24 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2021-01-19 08:42 | 2021-01-19 20:27 | 11:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | Bottail-Bheramara 230 kV line-2 | 2021-01-19 11:03 | 2021-01-19 12:12 | 1:09 | S/O | Due to protection test | 0 | 0 | No interruption
| Bottail-Bheramara 230 kV line-1 | 2021-01-19 12:33 | 2021-01-19 13:35 | 1:02 | S/O |  | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 132 kV line-2 | 2021-01-20 08:20 | 2021-01-20 15:42 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jessore-Jhenidah 132 kV line-1 | 2021-01-21 08:08 | 2021-01-21 17:18 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-1 | 2021-01-21 10:08 | 2021-01-21 12:00 | 1:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV both CKTS |  | 2021-01-22 19:33 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Jessore-Benapole 132 kV-1 | 2021-01-22 21:46 | 2021-01-22 23:04 | 1:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Banapole | Banapole-Ishurdi 132 kV line-1 |  | 2021-01-22 12:48 |  | S/O | After maintenance work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-1 | 2021-01-25 08:50 | 2021-01-25 12:47 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 | 2021-01-26 08:17 | 2021-01-26 15:19 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2021-01-27 08:26 | 2021-01-27 17:10 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 132 kV line-1 | 2021-01-27 07:58 | 2021-01-27 16:09 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2021-01-29 08:42 | 2021-01-29 15:34 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 132 kV line-1 | 2021-01-30 09:24 | 2021-01-30 15:23 | 5:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 289:56 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Mohasthangarh 132 kV line-1 | 2021-01-02 10:04 | 2021-01-02 15:11 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Confidence P/P 132 kV line-1 |  | 2021-01-02 21:47 |  | S/O | After maintenance work | 0 | 0 | No interruption
Palashbari | Palashbari-Confidence P/P 132 kV line-2 |  | 2021-01-02 21:57 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rangpur | Rangpur-Confidence P/P 132 kV line-1 | 2021-01-03 07:18 | 2021-01-03 07:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarh 132 kV line-1 | 2021-01-03 09:42 | 2021-01-03 15:04 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Confidence P/P 132 kV line-1 | 2021-01-03 07:18 | 2021-01-03 18:36 | 11:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Confidence P/P 132 kV line-1 | 2021-01-04 08:00 | 2021-01-04 18:02 | 10:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarh 132 kV line-1 | 2021-01-04 09:08 | 2021-01-04 16:21 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi(N) 132 kV line | 2021-01-04 13:10 | 2021-01-04 19:50 | 6:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thurgaon 132 kV line-1 | 2021-01-04 10:10 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence 132 kV line-1 | 2021-01-04 08:02 | 2021-01-04 18:02 | 10:00 | S/O | Due to replacement work | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarh 132 kV line-2 | 2021-01-05 09:15 | 2021-01-05 16:04 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi(N) 132 kV line | 2021-01-05 08:26 | 2021-01-05 15:16 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rajshahi-Natore 132 kV line-1 | 2021-01-05 08:51 | 2021-01-05 13:52 | 5:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarh 132 kV line-2 | 2021-01-06 10:17 | 2021-01-06 15:05 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Mohasthangarh 132 kV line-2 | 2021-01-07 09:46 | 2021-01-07 14:53 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV line | 2021-01-08 11:30 | 2021-01-08 11:30 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-1 | 2021-01-09 08:26 | 2021-01-09 16:18 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2021-01-09 08:48 | 2021-01-09 15:37 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Saipur | Saipur-Barapukuria 132 kV line-2 | 2021-01-09 10:48 | 2021-01-09 17:26 | 6:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 |  | 2021-01-09 11:07 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2021-01-10 08:40 | 2021-01-10 15:01 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-1 | 2021-01-10 08:18 | 2021-01-10 21:36 | 13:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence 132 kV line-1 | 2021-01-11 10:44 | 2021-01-11 11:48 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV line | 2021-01-12 09:34 | 2021-01-12 14:28 | 4:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2021-01-12 08:18 | 2021-01-12 16:39 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| Natore-Ishurdi 132 kV line-1 & 2 | 2021-01-13 07:55 | 2021-01-13 07:55 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2021-01-13 09:26 | 2021-01-13 16:44 | 7:18 | S/O | Due to replacement work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2021-01-13 11:40 | 2021-01-13 14:21 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi 132 kV line-1 | 2021-01-16 08:08 | 2021-01-16 17:57 | 9:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 k line-2 |  | 2021-01-16 14:54 |  | S/O | After maintenance work | 0 | 0 | No interruption
Page: 10/10 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:January 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Rajshahi | Rajshahi-Bheramara HVDC 230 k line-1 | 2021-01-16 15:28 |  |  | S/O | Due to project work | 0 | 0 | No interruption
| Rajshahi(N)-Rajshahi 132 kV line-1 | 2021-01-18 08:19 | 2021-01-18 19:58 | 11:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2021-01-18 11:16 | 2021-01-18 15:39 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 k line-2 | 2021-01-18 11:29 | 2021-01-18 16:05 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line-1 | 2021-01-18 11:05 | 2021-01-18 13:43 | 2:38 | S/O | Due to SCADA work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 k line-1 | 2021-01-19 11:13 | 2021-01-19 11:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi 132 kV line-1 | 2021-01-19 08:08 | 2021-01-19 17:22 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2021-01-19 10:29 | 2021-01-19 15:25 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sherpur 132 kV line-2 | 2021-01-20 10:27 | 2021-01-20 15:01 | 4:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi 132 kV line-2 | 2021-01-20 08:12 | 2021-01-20 17:16 | 9:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV line |  | 2021-01-20 11:40 |  | S/O | After maintenance work | 0 | 0 | No interruption
Natore | Natore-Rajlanka P.P 132 kV line | 2021-01-21 08:07 | 2021-01-21 20:11 | 12:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi 132 kV line | 2021-01-21 08:11 | 2021-01-21 16:22 | 8:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2021-01-21 10:49 | 2021-01-21 21:51 | 11:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2021-01-24 10:40 | 2021-01-24 12:52 | 2:12 | S/O | Due to project work | 15 | 33 | Power interruption
Rajshahi(N) | Rajshahi(N)-Bheramara HVDC 230 kV line-2 | 2021-01-25 12:04 | 2021-01-25 16:37 | 4:33 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajshahi(N)-Bheramara HVDC 230 kV line-1 | 2021-01-25 16:45 | 2021-01-25 21:54 | 5:09 | S/O | Due to protection work | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2021-01-26 09:42 | 2021-01-26 14:14 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 132 kV line 230 kV line-1 | 2021-01-26 12:23 | 2021-01-26 13:25 | 1:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-1 & 2 | 2021-01-29 08:32 | 2021-01-29 15:40 | 7:08 | S/O | Due to O/V of Ishurdi-Natore 132 kV line-1 | 0 | 0 | No interruption
|  |  | Total : | 266:19 |  | Unserved Energy: |  | 33
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2020-01-15 09:25 | 2020-01-15 18:00 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Narinda 132 kV line-2 | 2020-01-16 13:26 | 2020-01-16 15:01 | 1:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2020-01-29 12:52 | 2020-01-29 18:19 | 5:27 | S/O | Due to work by WASA | 0 | 0 | No interruption
|  |  | Total : | 15:37 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3689:23 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January' 2021
| Area | Previous Month (December) 2020) |  |  |  | Current Month (January 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | 2 | 185 | 194 | 12 | 12 | 209 | 233
2 | Dhaka (South) Grid Circle. | 11 | 4 | 100 | 115 | 25 | 3 | 78 | 106
3 | Chattogram Grid Circle. | 3 |  | 93 | 96 | 3 | 2 | 80 | 85
4 | Cumilla Grid Circle. | 9 | 1 | 82 | 92 | 22 | 5 | 129 | 156
5 | Khulna Grid Circle. | 5 | 2 | 70 | 77 | 13 | 2 | 64 | 79
6 | HVDC Grid Circle | 5 | 21 | 59 | 85 | 3 | 2 | 84 | 89
7 | Bogura Grid Circle. | 3 | 1 | 116 | 120 | 8 | 8 | 91 | 107
8 | Others | 1 |  | 10 | 11 | 1 |  | 4 | 5
9 | Total | 44 | 31 | 715 | 790 | 87 | 34 | 739 | 860
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January' 2021
| Area | Previous Month (December 2020) |  |  |  | Current Month (January 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 283.83 |  | 339.17 | 623 | 97.33 | 488.67 | 162.82 | 748.82
2 | Dhaka (South) Grid Circle. | 33.94 |  | 159.58 | 193.52 | 35.33 | 34.8 |  | 70.13
3 | Chattogram Grid Circle. | 70.37 |  | 31.8 | 102.17 |  | 23.1 |  | 23.1
4 | Cumilla Grid Circle. | 21.98 |  |  | 21.98 | 180.34 | 106.67 | 900.02 | 1187.03
5 | Khulna Grid Circle. | 27.9 | 370 |  | 397.9 | 67.17 |  | 275.25 | 342.42
6 | HVDC Grid Circle |  | 500.62 | 2283.8 | 2784.42 | 5 |  | 1680.5 | 1685.5
7 | Bogura Grid Circle. | 21 |  |  | 21 | 34.97 | 24 | 319.72 | 378.69
8 | Others
9 | Total | 459.02 | 870.62 | 2814.35 | 4143.99 | 420.14 | 677.24 | 3338.31 | 4435.69
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 2 | 8 | 4 |  | 4 | 709.49
2 | Dhaka (South) | 5031.6 | 2 |  | 2 |  | 2 |  | 48.13
3 | Chattogram | 2042 | 1 |  | 1 |  | - | 1 | 23.1
4 | Khulna | 2434 | 5 | 3 | 8 | 6 |  | 2 | 104.05
5 | HVDC | 5954.3 | 1 | 5 | 6 | 1 | - | 5 | 1685.5
6 | Bogura | 3145.6 | 2 | 5 | 7 | - | 3 | 4 | 331.52
7 | Cumilla | 2981 | 6 | 3 | 9 | 2 | 1 | 6 | 1173.02
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 4074.81
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.99%
4 | Khulna | 99.97%
5 | HVDC | 99.97% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January' 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 2 | - |  | 39.33
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | 1 |  |  | 22
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | 1 | 1 | 2 | - | 1 | 1 | 237.92
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | 1 | 2 | 1 |  | 1 | 47.17
7 | Cumilla | 1648.16 | - | 1 | - | 1 | 1 | - | - | 14
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 360.42
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.78%
3 | Chattogram | 99.9%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.89% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January' 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-01-18 | 15 | - | 1 | 01hr30 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January' 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kadda | 1 | 0:22 | 160 | 58.6667 | Due to tripping of 33 kV bus
| 1 | 2:06 | 120 | 252 | Due to 33 kV Bus maintenance
Kabirpur |  | 0:20 | 70 | 23.3333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Tangail | 1 | 0:26 | 80 | 34.6667
Kabirpur | 1 | 1:30 | 90 | 138 | Due to Oil leakage of 132/33 kV Transformer T3
Tangail | 1 | 0:30 | 80 | 40 | Due to bursting of 33 kV feeder fault
Aminbazar | 2 | 0:12 | 110 | 22 | Due to tripping of Aminbazar-Savar 132 kV line-1 & 2
|  | 0:16 | 65 | 17.3333 | Due to tripping of Aminbazar-Manikganj P.P 132 kV line-1 & 2
Mymensingh |  | 2:47 | 42 | 116.9 | Due to S/D of 132/33 kV Transformer T3
Joydevpur |  | 2:25 | 19 | 45.9167 | Due to S/D of 132/33 kV Transformer T2
Bhulta |  | 0:36 | 58 | 34.8 | Due to tripping of 132/33 kV Transformers-T1 & T2
Narsinghdi |  | 0:40 | 20 | 13.3333 | Due to tripping of 132/33 kV Transformer-T2
Siddhirganj |  | 0:24 | 55 | 22 | Due to tripping of Siddhirganj-Matuail 132 kV line
Halishahar |  | 1:03 | 22 | 23.1 | Due red-hot maintenance of 132//33 kV Transformer T2
Cumilla(N) | 1 | 0:28 | 37 | 17.2667 | Due to tripping of 132/33 kV Transformers-T3 & T4
Kulaura |  | 0:24 | 9 | 3.6 | Due to red-hot maintenance of 132/33 kV Trasformer T2
Coumilla(N) |  | 0:22 | 60 | 22 | Due to tripping of 132/33 kV Transformers-T3 & T4
Sylhet | 1 | 4:38 | 20 | 92.6667 | Due to cable burst of 132/33 kV Transformer-T1
Kulaura | 2 | 0:48 | 13 | 10.4
|  | 15:53 | 8 | 127.0667 | Due to tripping of 132/33 kV Transformer-T1
Sylhet | 1 | 0:21 | 40 | 14 | Due to tripping of Sylhet-Fenchuganj 132 kV line
B.Baria |  | 1:51 | 15 | 27.75 | Due to S/D of 132/33 kV Transformer T2
Baroierhat | 1 | 17:36 | 26 | 457.6
Sylhet |  | 10:22 | 40 | 414.6667 | Due to S/D of 33 kV full Bus
Noapara | 1 | 0:03 | 25 | 1.25 | Due to tripping of 132/33 kV Transformer-T1 & T2
Faridpur | 1 | 0:10 | 120 | 20
Mongla | 1 | 0:17 | 36 | 10.2
Khulna© | 1 | 0:12 | 20 | 4 | Due to tripping of 132/33 kV Transformer-T3
Faridpur | 1 | 0:35 | 286 | 30.9167 | Due to tripping of Faridpur-Bheramara 132 kV line-1 & 2
Barishal | 1 | 6:54 | 30 | 207 | Due to S/D of Barishal-Patuakhali 132 kV line
Shariatpur | 1 | 2:05 | 15 | 31.25 | Due to S/D of 132/33 kV Transformer T1
Faridpur | 1 | 1:38 | 20 | 32.6667
Bagerhat | 1 | 0:13 | 20 | 4.3333 | Due to S/D of 132/33 kV Transformers T1 & T2
Bottail | 1 | 0:12 | 25 | 5 | Due to tripping of 132/33 kV Transformer-T2
Kustia | 1 | 7:24 | 45 | 333 | Due to S/D of 132 kV Bus-A & B
Jessre | 1 | 9:59 | 80 | 798.6667
Shahjadpur | 1 | 6:35 | 10 | 65.8333 | Due to S/D of 132 kV Bus
Jessore | 2 | 1:48 | 60 | 108 | Due to S/D of 132 kV Bus-A& B
|  | 3:45 | 100 | 375
Bogura | 1 | 0:32 | 39 | 20.8 | Due to tripping of 132/33 kV Transformer-T1
Barapukuria | 2 | 1:36 | 15 | 24 | Due to red-hot maintenance of 132/33 kV Trasformer T4
Thaurgaon | 1 | 0:17 | 50 | 14.1667 | Due to tripping of Thaurgaon -Purbasadipur 132 kV line-2
Rangpur | 1 | 2:12 | 15 | 33 | Due to S/D of Rangpur Kurigram 132 kV line
Rajshahi | 1 | 13:11 | 8 | 105.4667 | Due to S/D of 132/33 kV Transformer T3
Niamatpur | 1 | 0:40 | 20 | 13.3333 | Due to S/D of 132/33 kV Transformer T1
Rangpur | 2 | 3:55 | 30 | 117.5 | Due to S/D of 33 kV Bus-2
|  | 1:21 | 35 | 47.25 | Due to S/D of 132/33 kV Transformer T2
Saidpur | 1 | 0:38 | 5 | 3.1667
| Total Unserved energy : |  |  | 4434.8667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 106 | 23 | 2021-01-01 | 19:00
2 | Munsiganj | 91 | 12 | 2021-01-01 | 22:00
3 | Sonargaon | 71 | 7 | 2021-01-01 | 18:30
4 | Shyampur | 180 | 5 | 2021-01-01 | 10:00
5 | Bhulta | 170 | 11 | 2021-01-01 | 19:00
6 | Madanganj | 57 | 2 | 2021-01-01 | 18:00
7 | Shitalakhya | 106 | 12 | 2021-01-01 | 15:00
8 | Rahim steel | 28 | 11 | 2021-01-01 | 15:00
9 | Matuail | 56 | 10 | 2021-01-01 | 10:00
10 | Ghorasal | 69 | 16 | 2021-01-01 | 18:30
11 | Narsingdi | 131 | 11 | 2021-01-01 | 19:30
12 | Haripur (SBU) | 119 | 5 | 2021-01-01 | 19:30
13 | Ullon | 50 | 30 | 2021-01-01 | 18:00
14 | Hasnabad | 160 | 5 | 2021-01-01 | 19:30
15 | Magbazar | 73 | 11 | 2021-01-01 | 13:00
16 | Maniknagar | 76 | 11 | 2021-01-01 | 18:00
17 | Bangabhaban | 17 | 6 | 2021-01-01 | 12:00
18 | Narinda | 72 | 11 | 2021-01-01 | 13:00
19 | Dhanmondi | 102 | 6 | 2021-01-01 | 13:00
20 | Lalbag | 74 | 17 | 2021-01-01 | 14:00
21 | Madartek | 50 | 11 | 2021-01-01 | 18:00
22 | Dhaka University | - | - | 2021-01-01 | -
23 | Aftabnagar | 14 | 13 | 2021-01-01 | 13:00
24 | Fatullah | 48 | 13 | 2021-01-01 | 10:00
25 | Mirpur | 77 | 11 | 2021-01-01 | 18:30
26 | Kalyanpur | 75 | 11 | 2021-01-01 | 18:00
27 | Gulshan | 84 | 11 | 2021-01-01 | 13:00
28 | Uttara | 70 | 7 | 2021-01-01 | 13:00
29 | Uttara(new) | 30 | 20 | 2021-01-01 | 12:00
30 | Kamrangirchar | 81 | 21 | 2021-01-01 | 13:00
31 | Savar | 136 | 14 | 2021-01-01 | 12:00
32 | Bhasantec | 108 | 11 | 2021-01-01 | 18:00
33 | Agargaon | 50 | 11 | 2021-01-01 | 13:00
34 | Satmosjid | 67 | 6 | 2021-01-01 | 13:00
35 | Tongi | 92 | 19 | 2021-01-01 | 18:00
36 | Kabirpur | 190 | 27 | 2021-01-01 | 18:00
37 | Basundhara | 107 | 10 | 2021-01-01 | 13:00
38 | Manikganj | 68 | 20 | 2021-01-01 | 21:00
39 | Joydevpur | 129 | 13 | 2021-01-01 | 15:00
40 | New Tongi | 103 | 7 | 2021-01-01 | 12:00
41 | Kodda | 206 | 11 | 2021-01-01 | 18:30
42 | Dhamrai | 86 | 24 | 2021-01-01 | 10:00
43 | Rajendrapur | 80 | 11 | 2021-01-01 | 19:00
44 | Valuka | 104 | 26 | 2021-01-01 | 19:00
45 | Tangail | 164 | 25 | 2021-01-01 | 19:00
46 | Mymensing | 186 | 31 | 2021-01-01 | 19:00
47 | Kishorganj | 114 | 22 | 2021-01-01 | 18:30
48 | Netrokona | 127 | 17 | 2021-01-01 | 22:00
49 | Jamalpur | 99 | 26 | 2021-01-01 | 18:30
50 | Sherpur | 116 | 16 | 2021-01-01 | 18:00
51 | Srimongal | 47 | 5 | 2021-01-01 | 18:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
52 | Shahjibazar | 97 | 16 | 2021-01-01 | 19:00
53 | Fenchuganj | 28 | 24 | 2021-01-01 | 22:00
54 | Kulawara | 30 | 2 | 2021-01-01 | 18:00
55 | Sylhet | 127 | 30 | 2021-01-01 | 18:30
56 | Chatak | 22 | 7 | 2021-01-01 | 18:00
57 | Sunamganj | 30 | 19 | 2021-01-01 | 19:00
58 | Bianibazar | 45 | 30 | 2021-01-01 | 18:30
59 | Cumilla (S) | 118 | 30 | 2021-01-01 | 19:30
60 | Cumilla(N) | 89 | 18 | 2021-01-01 | 18:30
61 | Chandpur | 64 | 11 | 2021-01-01 | 20:00
62 | Feni | 87 | 31 | 2021-01-01 | 18:00
63 | Chowmuhani | 139 | 28 | 2021-01-01 | 18:00
64 | Ashuganj | 42 | 20 | 2021-01-01 | 13:00
65 | Daudkandi | 104 | 9 | 2021-01-01 | 19:30
66 | B.Baria | 116 | 16 | 2021-01-01 | 18:30
67 | Ramganj | 76 | 19 | 2021-01-01 | 19:30
68 | Chaddagram | 32 | 17 | 2021-01-01 | 14:00
69 | PHP | 11 | 8 | 2021-01-01 | 9:00
70 | Kochua | 43 | 31 | 2021-01-01 | 20:00
71 | Madanhat | 49 | 20 | 2021-01-01 | 19:30
72 | Hathazari | 67 | 8 | 2021-01-01 | 13:00
73 | Khulshi | 177 | 7 | 2021-01-01 | 12:00
74 | Halishahar | 120 | 21 | 2021-01-01 | 14:00
75 | Baraulia | 160 | 24 | 2021-01-01 | 10:00
76 | Sikalbaha | 23 | 23 | 2021-01-01 | 19:30
77 | Dohazari | 70 | 7 | 2021-01-01 | 18:30
78 | Cox'sbazar | 88 | 20 | 2021-01-01 | 18:00
79 | Chandraghona | 28 | 16 | 2021-01-01 | 19:00
80 | Kaptai | 3.8 | 2 | 2021-01-01 | 18:00
81 | A. Khaer Stl. | 18 | 28 | 2021-01-01 | 12:00
82 | Bakulia | 82 | 28 | 2021-01-01 | 20:00
83 | Julda | 22 | 10 | 2021-01-01 | 9:00
84 | TK chemical | 91 | 19 | 2021-01-01 | 18:00
85 | Modern Steel | 0 | 1 | 2021-01-01 | 1:00
86 | Shahmirpur | 21 | 19 | 2021-01-01 | 18:30
87 | Khagrachhari | 22 | 2 | 2021-01-01 | 7:00
88 | Matarbari | 29.5 | 7 | 2021-01-01 | 19:00
89 | Baroiar Hat | 44 | 22 | 2021-01-01 | 18:00
90 | Rangamati | 10 | 29 | 2021-01-01 | 18:00
91 | Abul Khair 230 | 212 | 22 | 2021-01-01 | 10:00
92 | BSRM | 158 | 18 | 2021-01-01 | 9:00
93 | GPH Ispat | 91 | 18 | 2021-01-01 | 10:00
94 | Goalpara | 21 | 26 | 2021-01-01 | 13:00
95 | Central s/s | 87 | 21 | 2021-01-01 | 13:00
96 | Noapara | 62 | 16 | 2021-01-01 | 18:30
97 | Jashore | 92 | 24 | 2021-01-01 | 18:30
98 | Benapol | 88 | 27 | 2021-01-01 | 18:00
99 | Jhenidah | 100 | 2 | 2021-01-01 | 18:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
100 | Bottail | 120 | 24 | 2021-01-01 | 18:30
101 | G.K Project | 46 | 4 | 2021-01-01 | 19:30
102 | Faridpur | 140 | 17 | 2021-01-01 | 19:30
103 | Madaripur | 68 | 16 | 2021-01-01 | 19:00
104 | Sariatpur | 46 | 18 | 2021-01-01 | 20:00
105 | Gopalganj | 66 | 9 | 2021-01-01 | 18:30
106 | Bagerhat | 87 | 19 | 2021-01-01 | 18:30
107 | Mongla | 42 | 14 | 2021-01-01 | 12:00
108 | Satkhira | 81 | 2 | 2021-01-01 | 18:30
109 | Gallamari | 23 | 8 | 2021-01-01 | 13:00
110 | Magura | 50 | 2 | 2021-01-01 | 18:00
111 | Norail | 29 | 30 | 2021-01-01 | 18:30
112 | Chuadanga | 74 | 2 | 2021-01-01 | 18:30
113 | Barsal(N) | 34 | 29 | 2021-01-01 | 18:00
114 | Barsal(S) | 76 | 13 | 2021-01-01 | 20:00
115 | Patuakhali | 93 | 31 | 2021-01-01 | 19:30
116 | Bhandaria | 42 | 1 | 2021-01-01 | 20:00
117 | Borhan Uddin | 28 | 19 | 2021-01-01 | 20:00
118 | Ishurdi | 51 | 31 | 2021-01-01 | 19:30
119 | Ruppur Paromanobik | 3 | 6 | 2021-01-01 | 15:00
120 | Natore | 94 | 31 | 2021-01-01 | 18:30
121 | Bogura | 124 | 23 | 2021-01-01 | 19:00
122 | Naogaon | 97 | 20 | 2021-01-01 | 18:00
123 | Rajshahi | 107 | 25 | 2021-01-01 | 20:00
124 | Rajshahi New | 14 | 27 | 2021-01-01 | 18:30
125 | C.Nawabganj | 71 | 30 | 2021-01-01 | 12:00
126 | Amnura | 46 | 15 | 2021-01-01 | 18:30
127 | Pabna | 80 | 3 | 2021-01-01 | 20:00
128 | Shahjadpur | 85 | 26 | 2021-01-01 | 19:00
129 | Serajganj | 93 | 27 | 2021-01-01 | 9:00
130 | Niyamatpur | 82 | 13 | 2021-01-01 | 20:00
131 | Joypurhat | 60 | 27 | 2021-01-01 | 18:30
132 | Sherpur(Bogura) | 48 | 27 | 2021-01-01 | 19:00
133 | Mohastangar | 40 | 27 | 2021-01-01 | 18:30
134 | Bangura | 18 | 15 | 2021-01-01 | 19:30
135 | Rangpur | 129 | 27 | 2021-01-01 | 18:30
136 | Lalmonirhat | 59 | 24 | 2021-01-01 | 18:30
137 | Saidpur | 110 | 24 | 2021-01-01 | 18:30
138 | Purbasadipur | 106 | 31 | 2021-01-01 | 19:00
139 | Thakurgaon | 72 | 31 | 2021-01-01 | 19:00
140 | Palshbari | 122 | 26 | 2021-01-01 | 18:30
141 | Barapukuria | 56 | 19 | 2021-01-01 | 10:00
142 | Panchugar | 48 | 2 | 2021-01-01 | 18:30
143 | Joldhaka | 33 | 19 | 2021-01-01 | 18:30
144 | Kurigram | 50 | 31 | 2021-01-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January' 2021
Area | MW | Date | Hour | Remarks
Dhaka | 3428 | 26.01.2021 | 21:00
Chattogram | 1101 | 18.01.2021 | 12:00
Khulna | 1149 | 02.01.2021 | 18:30
Rajshahi | 1001 | 27.01.2021 | 19:30
Cumilla | 771 | 28.01.2021 | 20:00
Mymensingh | 829 | 23.01.2021 | 19:00
Sylhet | 380 | 30.01.2021 | 18:30
Barisal | 255 | 31.01.2021 | 20:00
Rangpur | 732 | 26.01.2021 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 423 | 22 | 2021-01-01 | 22:00 | 394 | 17 | 2021-01-01 | 19:00
2 | Bheramara | 400 | 415 | 6 | 2021-01-01 | 3:00 | 385 | 10 | 2021-01-01 | 11:00
3 | Ashuganj(N) | 400 | 404 | 25 | 2021-01-01 | 2:00 | 367 | 6 | 2021-01-01 | 10:00
4 | Payra | 400 | 435 | 2 | 2021-01-01 | 22:00 | 391 | 3 | 2021-01-01 | 12:00
5 | Kaliakoir | 400 | 421 | 30 | 2021-01-01 | 2:00 | 339 | 19 | 2021-01-01 | 19:00
6 | Bhulta | 400 | 415 | 17 | 2021-01-01 | 21:00 | 326 | 10 | 2021-01-01 | 11:00
7 | Gopalganj | 400 | 435 | 2 | 2021-01-01 | 4:00 | 384 | 23 | 2021-01-01 | 10:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 1 | 2021-01-01 | 22:00 | 230 | 6 | 2021-01-01 | 15:00
2 | Ishurdi | 230 | 245 | 11 | 2021-01-01 | 3:00 | 227 | 6 | 2021-01-01 | 7:00
3 | Ashuganj | 230 | 247 | 25 | 2021-01-01 | 5:00 | 230 | 4 | 2021-01-01 | 14:00
4 | Serajganj | 230 | 237 | 31 | 2021-01-01 | 4:00 | 222 | 27 | 2021-01-01 | 8:00
5 | Baghabari | 230 | 248 | 4 | 2021-01-01 | 4:00 | 224 | 26 | 2021-01-01 | 11:00
6 | Barapukuria | 230 | 236 | 31 | 2021-01-01 | 22:00 | 218 | 27 | 2021-01-01 | 9:00
7 | Bogura | 230 | 240 | 15 | 2021-01-01 | 1:00 | 215 | 27 | 2021-01-01 | 9:00
8 | Rajshahi | 230 | 245 | 23 | 2021-01-01 | 21:00 | 220 | 4 | 2021-01-01 | 12:00
9 | Khulna South | 230 | 247 | 18 | 2021-01-01 | 1:00 | 221 | 1 | 2021-01-01 | 12:00
10 | Rampura | 230 | 238 | 25 | 2021-01-01 | 2:00 | 221 | 5 | 2021-01-01 | 11:00
11 | Haripur | 230 | 241 | 24 | 2021-01-01 | 23:00 | 217 | 6 | 2021-01-01 | 11:00
12 | Hasnabad | 230 | 241 | 22 | 2021-01-01 | 14:00 | 218 | 6 | 2021-01-01 | 11:00
13 | Shyampur | 230 | 241 | 25 | 2021-01-01 | 3:00 | 220 | 1 | 2021-01-01 | 16:00
14 | Aminbazar | 230 | 244 | 24 | 2021-01-01 | 24:00 | 216 | 6 | 2021-01-01 | 11:00
15 | Tongi | 230 | 239 | 21 | 2021-01-01 | 13:00 | 212 | 6 | 2021-01-01 | 11:00
16 | Comilla (N) | 230 | 247 | 25 | 2021-01-01 | 2:00 | 224 | 5 | 2021-01-01 | 11:00
17 | Hathazari | 230 | 236 | 29 | 2021-01-01 | 22:00 | 204 | 10 | 2021-01-01 | 12:00
18 | Megnaghat | 230 | 243 | 22 | 2021-01-01 | 4:00 | 221 | 4 | 2021-01-01 | 13:00
19 | Fenchuganj | 230 | 250 | 22 | 2021-01-01 | 21:00 | 236 | 6 | 2021-01-01 | 10:00
20 | Siddhirganj | 230 | 243 | 25 | 2021-01-01 | 5:00 | 219 | 5 | 2021-01-01 | 12:00
21 | Maniknagar | 230 | 243 | 25 | 2021-01-01 | 6:00 | 218 | 5 | 2021-01-01 | 16:00
22 | Old Airport | 230 | 244 | 25 | 2021-01-01 | 9:00 | 215 | 9 | 2021-01-01 | 15:00
23 | Barisal | 230 | 255 | 2 | 2021-01-01 | 17:00 | 238 | 27 | 2021-01-01 | 6:00
24 | Bhola 225 MW | 230 | 257 | 31 | 2021-01-01 | 24:00 | 222 | 19 | 2021-01-01 | 18:00
25 | AKSML | 230 | 254 | 17 | 2021-01-01 | 2:00 | 205 | 9 | 2021-01-01 | 17:00
26 | BSRM | 230 | 239 | 29 | 2021-01-01 | 21:00 | 206 | 9 | 2021-01-01 | 15:00
27 | Bibiyana | 230 | 251 | 22 | 2021-01-01 | 13:00 | 218 | 17 | 2021-01-01 | 5:00
28 | Bhulta | 230 | 287 | 10 | 2021-01-01 | 8:00 | 220 | 5 | 2021-01-01 | 17:00
29 | Ashuganj (S) | 230 | 245 | 25 | 2021-01-01 | 4:00 | 227 | 5 | 2021-01-01 | 12:00
30 | Kaliakoir | 230 | 242 | 25 | 2021-01-01 | 2:00 | 209 | 10 | 2021-01-01 | 12:00
31 | GPH | 230 | 237 | 29 | 2021-01-01 | 20:00 | 203 | 6 | 2021-01-01 | 15:00
132 kV Substation
1 | Siddhirganj | 132 | 142 | 15 | 2021-01-01 | 0.33333 | 130 | 6 | 2021-01-01 | 0.41667
2 | Munsiganj | 132 | 143 | 11 | 2021-01-01 | 0.83333 | 129 | 6 | 2021-01-01 | 0.41667
3 | Sonargaon | 132 | 140 | 15 | 2021-01-01 | 0.25 | 130 | 5 | 2021-01-01 | 0
4 | Shyampur | 132 | 137 | 15 | 2021-01-01 | 0.79167 | 122 | 8 | 2021-01-01 | 0.5
5 | Bhulta | 132 | 140 | 15 | 2021-01-01 | 0.41667 | 120 | 7 | 2021-01-01 | 0.91667
6 | Madanganj | 132 | 142 | 2 | 2021-01-01 | 0.70833 | 128 | 6 | 2021-01-01 | 0.45833
7 | Shitalakhya | 132 | 143 | 1 | 2021-01-01 | 0.33333 | 127 | 21 | 2021-01-01 | 0.29167
8 | Rahim Steal | 132 | 142 | 15 | 2021-01-01 | 0.75 | 118 | 27 | 2021-01-01 | 0.41667
9 | Matuail | 132 | 142 | 15 | 2021-01-01 | 0.33333 | 130 | 6 | 2021-01-01 | 0.41667
10 | Ghorasal | 132 | 142 | 1 | 2021-01-01 | 0.875 | 134 | 7 | 2021-01-01 | 0.041667
11 | Narsinghdi | 132 | 140 | 15 | 2021-01-01 | 0.33333 | 120 | 10 | 2021-01-01 | 0.54167
12 | Haripur (SBU) | 132 | 142 | 15 | 2021-01-01 | 0.58333 | 130 | 8 | 2021-01-01 | 0.16667
13 | Ullon | 132 | 137 | 25 | 2021-01-01 | 0.25 | 124 | 6 | 2021-01-01 | 0.45833
14 | Hasnabad | 132 | 141 | 1 | 2021-01-01 | 0.20833 | 128 | 19 | 2021-01-01 | 0.66667
15 | Magbazar | 132 | 137 | 30 | 2021-01-01 | 0.25 | 123 | 6 | 2021-01-01 | 0.5
16 | Maniknagar | 132 | 141 | 21 | 2021-01-01 | 0.83333 | 128 | 9 | 2021-01-01 | 0.625
17 | Bangabhaban | 132 | 141 | 21 | 2021-01-01 | 0.83333 | 128 | 9 | 2021-01-01 | 0.625
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
18 | Narinda | 132 | 141 | 21 | 2021-01-01 | 0.83333 | 128 | 9 | 2021-01-01 | 0.625
19 | Dhanmondi | 132 | 137 | 25 | 2021-01-01 | 0.25 | 124 | 6 | 2021-01-01 | 0.45833
20 | Lalbag | 132 | 141 | 25 | 2021-01-01 | 0.25 | 120 | 6 | 2021-01-01 | 0.5
21 | Madartek | 132 | 137 | 25 | 2021-01-01 | 0.25 | 123 | 9 | 2021-01-01 | 0.625
22 | Dhaka University | 132 | - | - | 2021-01-01 | - | - | - | 2021-01-01 | -
23 | Aftabnagar | 132 | 136 | 22 | 2021-01-01 | 0.041667 | 123 | 6 | 2021-01-01 | 0.45833
24 | Fatullah | 132 | 138 | 1 | 2021-01-01 | 0.83333 | 122 | 9 | 2021-01-01 | 0.41667
25 | Mirpur | 132 | 141 | 23 | 2021-01-01 | 0.25 | 120 | 7 | 2021-01-01 | 0.45833
26 | Kalyanpur | 132 | 141 | 24 | 2021-01-01 | 0.25 | 123 | 10 | 2021-01-01 | 0.5
27 | Gulshan | 132 | 137 | 19 | 2021-01-01 | 0.25 | 123 | 6 | 2021-01-01 | 0.45833
28 | Uttara | 132 | 141 | 25 | 2021-01-01 | 0.25 | 121 | 10 | 2021-01-01 | 0.5
29 | Uttara(New) | 132 | 142 | 22 | 2021-01-01 | 0.29167 | 123 | 4 | 2021-01-01 | 0.5
30 | Kamrangirchar | 132 | 144 | 15 | 2021-01-01 | 0.25 | 127 | 14 | 2021-01-01 | 0.5
31 | Savar | 132 | 141 | 25 | 2021-01-01 | 0.041667 | 120 | 10 | 2021-01-01 | 0.5
32 | Bhasantec | 132 | 140 | 20 | 2021-01-01 | 0.83333 | 124 | 6 | 2021-01-01 | 0.45833
33 | Agargaon | 132 | 141 | 20 | 2021-01-01 | 0.33333 | 126 | 6 | 2021-01-01 | 0.45833
34 | Satmosjid | 132 | 141 | 20 | 2021-01-01 | 0.33333 | 124 | 6 | 2021-01-01 | 0.45833
35 | Tongi | 132 | 144 | 22 | 2021-01-01 | 0.58333 | 129 | 6 | 2021-01-01 | 0.5
36 | Kabirpur | 132 | 139 | 1 | 2021-01-01 | 0.95833 | 123 | 10 | 2021-01-01 | 0.5
37 | Basundhara | 132 | 142 | 21 | 2021-01-01 | 0.54167 | 124 | 9 | 2021-01-01 | 0.625
38 | Manikganj | 132 | 148 | 25 | 2021-01-01 | 0.25 | 130 | 14 | 2021-01-01 | 0.5
39 | Joydevpur | 132 | 142 | 2 | 2021-01-01 | 0.75 | 131 | 7 | 2021-01-01 | 0.70833
40 | New Tongi | 132 | 143 | 15 | 2021-01-01 | 0.77083 | 127 | 6 | 2021-01-01 | 0.5
41 | Kodda | 132 | 142 | 2 | 2021-01-01 | 0.875 | 116 | 16 | 2021-01-01 | 0.16667
42 | Dhamrai | 132 | 139 | 8 | 2021-01-01 | 0.83819 | 120 | 10 | 2021-01-01 | 0.625
43 | Rajendrapur | 132 | 142 | 25 | 2021-01-01 | 0.25 | 127 | 9 | 2021-01-01 | 0.5
44 | Valuka | 132 | 133 | 24 | 2021-01-01 | 0.125 | 113 | 28 | 2021-01-01 | 0.54167
45 | Tangail | 132 | 139 | 24 | 2021-01-01 | 0.083333 | 123 | 10 | 2021-01-01 | 0.625
46 | Mymensing | 132 | 135 | 14 | 2021-01-01 | 0.041667 | 118 | 10 | 2021-01-01 | 0.625
47 | Kishorganj | 132 | 136 | 22 | 2021-01-01 | 0.25 | 122 | 10 | 2021-01-01 | 0.625
48 | Netrokona | 132 | 133 | 1 | 2021-01-01 | 0.16667 | 114 | 17 | 2021-01-01 | 0.54167
49 | Jamalpur | 132 | 142 | 1 | 2021-01-01 | 0.83333 | 119 | 21 | 2021-01-01 | 0.29167
50 | Sherpur | 132 | 140 | 23 | 2021-01-01 | 0.875 | 118 | 21 | 2021-01-01 | 0.29167
51 | Srimongal | 132 | 141 | 30 | 2021-01-01 | 0.16667 | 134 | 5 | 2021-01-01 | 0.875
52 | Shahjibazar | 132 | 139 | 25 | 2021-01-01 | 0.20833 | 131 | 10 | 2021-01-01 | 0.625
53 | Fenchuganj | 132 | 142 | 23 | 2021-01-01 | 0.29167 | 133 | 14 | 2021-01-01 | 0.625
54 | Khulawara | 132 | 141 | 25 | 2021-01-01 | 0.25 | 132 | 30 | 2021-01-01 | 0.75
55 | Sylhet | 132 | 139 | 30 | 2021-01-01 | 0.33333 | 127 | 30 | 2021-01-01 | 0.75
56 | Chattak | 132 | 138 | 25 | 2021-01-01 | 0.25 | 124 | 30 | 2021-01-01 | 0.79167
57 | Sunamganj | 132 | 137 | 25 | 2021-01-01 | 0.125 | 130 | 12 | 2021-01-01 | 0.5
58 | Biani Bazar | 132 | 139 | 25 | 2021-01-01 | 0.125 | 125 | 30 | 2021-01-01 | 0.77083
59 | Comilla(South) | 132 | 133 | 27 | 2021-01-01 | 0.041667 | 124 | 9 | 2021-01-01 | 0.75
60 | Comilla (North) | 132 | 147 | 22 | 2021-01-01 | 0.375 | 133 | 6 | 2021-01-01 | 0.5
61 | Chandpur | 132 | 145 | 7 | 2021-01-01 | 0.75 | 135 | 16 | 2021-01-01 | 0.33333
62 | Feni | 132 | 142 | 25 | 2021-01-01 | 0.375 | 130 | 6 | 2021-01-01 | 0.5
63 | Chowmuhani | 132 | 141 | 23 | 2021-01-01 | 0.125 | 129 | 27 | 2021-01-01 | 0.5
64 | Ashuganj | 132 | 142 | 25 | 2021-01-01 | 0.20833 | 131 | 10 | 2021-01-01 | 0.75
65 | Daudkandi | 132 | 143 | 22 | 2021-01-01 | 0.375 | 131 | 5 | 2021-01-01 | 0.5
66 | Brahminbaria | 132 | 137 | 22 | 2021-01-01 | 0.375 | 126 | 10 | 2021-01-01 | 0.625
67 | Ramganj | 132 | 141 | 23 | 2021-01-01 | 0.375 | 133 | 1 | 2021-01-01 | 0.33333
68 | Chaddagram | 132 | 143 | 24 | 2021-01-01 | 0.16667 | 131 | 9 | 2021-01-01 | 0.41667
69 | PHP | 132 | 142 | 24 | 2021-01-01 | 0.29167 | 129 | 5 | 2021-01-01 | 0.41667
70 | Kochua | 132 | 142 | 30 | 2021-01-01 | 0.29167 | 139 | 30 | 2021-01-01 | 0.625
71 | Madanhat | 132 | 144 | 22 | 2021-01-01 | 0.375 | 125 | 10 | 2021-01-01 | 0.5
72 | Hathazari | 132 | 142 | 25 | 2021-01-01 | 0.79167 | 128 | 6 | 2021-01-01 | 0.625
73 | Khulshi | 132 | 140 | 24 | 2021-01-01 | 0.25 | 123 | 10 | 2021-01-01 | 0.45833
74 | Halishahar | 132 | 142 | 22 | 2021-01-01 | 0.375 | 124 | 10 | 2021-01-01 | 0.5
75 | Baraulia | 132 | 141 | 22 | 2021-01-01 | 0.45833 | 121 | 5 | 2021-01-01 | 0.625
76 | Sikalbaha | 132 | 143 | 25 | 2021-01-01 | 0.16667 | 124 | 10 | 2021-01-01 | 0.5
77 | Dohazari | 132 | 140 | 23 | 2021-01-01 | 0.8125 | 120 | 7 | 2021-01-01 | 0.79167
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
78 | Cox'sbazar | 132 | 135 | 25 | 2021-01-01 | 0.25 | 110 | 7 | 2021-01-01 | 0.77083
79 | Chandraghona | 132 | 143 | 22 | 2021-01-01 | 0.58333 | 125 | 10 | 2021-01-01 | 0.45833
80 | Kaptai | 132 | 140 | 18 | 2021-01-01 | 0.75 | 128 | 10 | 2021-01-01 | 0.625
81 | A. Khaer Stl. | 132 | 139 | 20 | 2021-01-01 | 0.83333 | 123 | 10 | 2021-01-01 | 0.45833
82 | Bakulia | 132 | 141 | 22 | 2021-01-01 | 0.375 | 123 | 10 | 2021-01-01 | 0.5
83 | Julda | 132 | 141 | 24 | 2021-01-01 | 0.41667 | 125 | 6 | 2021-01-01 | 0.58333
84 | TK Chemical | 132 | 141 | 17 | 2021-01-01 | 0.77083 | 123 | 10 | 2021-01-01 | 0.5
85 | Modern Steel | 132 | 141 | 27 | 2021-01-01 | 0.25 | 125 | 10 | 2021-01-01 | 0.5
86 | Shahmirpur | 132 | 142 | 25 | 2021-01-01 | 0.625 | 125 | 10 | 2021-01-01 | 0.5
87 | Khagrachhari | 132 | 140 | 22 | 2021-01-01 | 0.29167 | 125 | 10 | 2021-01-01 | 0.5
88 | Matarbari | 132 | 138 | 26 | 2021-01-01 | 0.54167 | 110 | 7 | 2021-01-01 | 0.77083
89 | Baroiar Hat | 132 | 142 | 26 | 2021-01-01 | 0.375 | 129 | 10 | 2021-01-01 | 0.5
90 | Rangamati | 132 | 141 | 22 | 2021-01-01 | 0.8125 | 124 | 9 | 2021-01-01 | 0.41667
91 | Goalpara | 132 | 141 | 1 | 2021-01-01 | 0.083333 | 128 | 4 | 2021-01-01 | 0.70833
92 | Khulna Central | 132 | 141 | 2 | 2021-01-01 | 0.70833 | 127 | 4 | 2021-01-01 | 0.70833
93 | Noapara | 132 | 139 | 1 | 2021-01-01 | 0.91667 | 124 | 4 | 2021-01-01 | 0.75
94 | Jessore | 132 | 137 | 1 | 2021-01-01 | 0.70833 | 116 | 1 | 2021-01-01 | 0.5
95 | Benapol | 132 | 139 | 31 | 2021-01-01 | 0.125 | 118 | 1 | 2021-01-01 | 0.5
96 | Jhenida | 132 | 136 | 18 | 2021-01-01 | 0.125 | 114 | 1 | 2021-01-01 | 0.5
97 | Bottail | 132 | 139 | 31 | 2021-01-01 | 0.125 | 126 | 26 | 2021-01-01 | 0.5
98 | G.K Project | 132 | 143 | 29 | 2021-01-01 | 0.16667 | 129 | 26 | 2021-01-01 | 0.45833
99 | Faridpur | 132 | 141 | 29 | 2021-01-01 | 0.20833 | 130 | 2 | 2021-01-01 | 0.75
100 | Madaripur | 132 | 144 | 4 | 2021-01-01 | 0.20833 | 130 | 3 | 2021-01-01 | 0.54167
101 | Sariatpur | 132 | 145 | 2 | 2021-01-01 | 0.16667 | 128 | 26 | 2021-01-01 | 0.75
102 | Gopalganj | 132 | 149 | 1 | 2021-01-01 | 0.41667 | 127 | 29 | 2021-01-01 | 0.70833
103 | Bagerhat | 132 | 146 | 1 | 2021-01-01 | 0.16667 | 121 | 10 | 2021-01-01 | 0.75
104 | Mongla | 132 | 141 | 0 | 2021-01-01 | 0.5 | 122 | 4 | 2021-01-01 | 0.75
105 | Satkhira | 132 | 140 | 1 | 2021-01-01 | 0.083333 | 125 | 12 | 2021-01-01 | 0.33333
106 | Gallamari | 132 | 142 | 1 | 2021-01-01 | 0.91667 | 128 | 4 | 2021-01-01 | 0.70833
107 | Magura | 132 | 136 | 18 | 2021-01-01 | 0.125 | 108 | 1 | 2021-01-01 | 0.5
108 | Norail | 132 | 136 | 31 | 2021-01-01 | 0.20833 | 110 | 1 | 2021-01-01 | 0.5
109 | Chuadanga | 132 | 134 | 18 | 2021-01-01 | 0.125 | 107 | 1 | 2021-01-01 | 0.5
110 | Barisal(N) | 132 | 147 | 31 | 2021-01-01 | 0.54167 | 126 | 29 | 2021-01-01 | 0.70833
111 | Barisal(S) | 132 | 144 | 29 | 2021-01-01 | 0.16667 | 130 | 29 | 2021-01-01 | 0.70833
112 | Patuakhali | 132 | 143 | 1 | 2021-01-01 | 0.083333 | 126 | 29 | 2021-01-01 | 0.70833
113 | Bhandaria | 132 | 143 | 29 | 2021-01-01 | 0.16667 | 125 | 12 | 2021-01-01 | 0.5
114 | Ishurdi | 132 | 144 | 24 | 2021-01-01 | 0.041667 | 129 | 26 | 2021-01-01 | 0.5
115 | Ruppur paromanobik | 132 | 140 | 1 | 2021-01-01 | 0.041667 | 131 | 26 | 2021-01-01 | 0.5
116 | Natore | 132 | 141 | 1 | 2021-01-01 | 0.041667 | 128 | 29 | 2021-01-01 | 0.33333
117 | Bogra | 132 | 141 | 14 | 2021-01-01 | 0.041667 | 123 | 27 | 2021-01-01 | 0.375
118 | Noagaon | 132 | 137 | 1 | 2021-01-01 | 0.25 | 115 | 27 | 2021-01-01 | 0.375
119 | Rajshahi | 132 | 142 | 4 | 2021-01-01 | 0.20833 | 126 | 26 | 2021-01-01 | 0.5
120 | Rajshahi New | 132 | 144 | 4 | 2021-01-01 | 0.16667 | 124 | 26 | 2021-01-01 | 0.5
121 | C.Nawabganj | 132 | 142 | 3 | 2021-01-01 | 0.16667 | 123 | 29 | 2021-01-01 | 0.33333
122 | Amnura | 132 | 142 | 4 | 2021-01-01 | 0.083333 | 124 | 20 | 2021-01-01 | 0.33333
123 | Pabna | 132 | 141 | 19 | 2021-01-01 | 0.041667 | 129 | 26 | 2021-01-01 | 0.5
124 | Shahjadpur | 132 | 145 | 2 | 2021-01-01 | 0.25 | 132 | 28 | 2021-01-01 | 0.375
125 | Serajganj | 132 | 140 | 13 | 2021-01-01 | 0.20833 | 128 | 26 | 2021-01-01 | 0.54167
126 | Niyamatpur | 132 | 136 | 1 | 2021-01-01 | 0.083333 | 110 | 27 | 2021-01-01 | 0.375
127 | Joypurhat | 132 | 138 | 1 | 2021-01-01 | 0.083333 | 111 | 27 | 2021-01-01 | 0.375
128 | Sherpur(Bogura) | 132 | 141 | 12 | 2021-01-01 | 0.16667 | 124 | 27 | 2021-01-01 | 0.375
129 | Mohastangor | 132 | 139 | 2 | 2021-01-01 | 0.70833 | 120 | 29 | 2021-01-01 | 0.375
130 | Bhangura | 132 | 143 | 13 | 2021-01-01 | 0.83333 | 132 | 26 | 2021-01-01 | 0.45833
131 | Rangpur | 132 | 134 | 12 | 2021-01-01 | 0.16667 | 112 | 27 | 2021-01-01 | 0.375
132 | Lalmonirhat | 132 | 135 | 2 | 2021-01-01 | 0.5 | 110 | 27 | 2021-01-01 | 0.375
133 | Saidpur | 132 | 134 | 2 | 2021-01-01 | 0.29167 | 108 | 27 | 2021-01-01 | 0.375
134 | Purbasadipur | 132 | 133 | 4 | 2021-01-01 | 0.25 | 110 | 26 | 2021-01-01 | 0.375
135 | Thakurgaon | 132 | 134 | 28 | 2021-01-01 | 0.20833 | 109 | 26 | 2021-01-01 | 0.375
136 | Palashbari | 132 | 137 | 13 | 2021-01-01 | 0.125 | 115 | 26 | 2021-01-01 | 0.375
137 | Barapukuria | 132 | 135 | 12 | 2021-01-01 | 0.16667 | 118 | 27 | 2021-01-01 | 0.375
138 | Panchagar | 132 | 133 | 15 | 2021-01-01 | 0.16667 | 106 | 27 | 2021-01-01 | 0.375
139 | Joldhaka | 132 | 135 | 12 | 2021-01-01 | 0.125 | 106 | 27 | 2021-01-01 | 0.375
140 | Kurigram | 132 | 134 | 12 | 2021-01-01 | 0.083333 | 108 | 27 | 2021-01-01 | 0.375
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:January' 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 80 | 200
Hasnabad | TR2 | 225 | 72 | 200 | 05.01.2021 | 10:00
| TR3 | 225 | 70 | 200
| TR1 | 225 | 120 | 330
Tongi | TR2 | 225 | 120 | 330 | 19.01.2021 | 22:00
| TR3 | 225 | 120 | 330
Haripur | TR1 | 225 | 80 | 190 | 31.01.2021 | 23:00
| TR2 | 225 | 80 | 190
| TR3 | 225 | 80 | 190
| TR1 | 225 | 110 | 280 | 11.01.2021 | 13:00
Rampura | TR2 | 225 | 110 | 280
| TR3 | 225 | 110 | 280
| TR1 | 225 | 115 | 319 | 11.01.2021 | 12:00
Aminbazar | TR2 | 225 | 115 | 319 |  |  | S/D
| TR3 | 225 | 120 | 328
Maniknagar | TR1 | 300 | 79 | 240 | 07.01.2021 | 13:00
| TR2 | 300 | 79 | 240
Cumilla (N) | TR1 | 225 | 145 | 368
| TR2 | 225 | 143 | 368 | 03.01.2021 | 23:00:00 AM
Fenchuganj | AT2 | 300 | 244 | 665 | 30.01.2021 | 18:00
| MT1 | 150 | 58 | 160 | 10.01.2021
Hathazari | MT2 | 150 | 58 | 160
| MT3 | 150 | 58 | 160 |  | 07:00
| MT4 | 150 | 58 | 160
| TR1 | 225 | 106 | 280
Ishurdi | TR2 | 225 | 106 | 280
| TR3 | 225 | 106 | 280 | 26.01.2021 | 13:00
Khulna(S) | TR1 | 225 | 116 | 300
| TR2 | 225 | 116 | 300
| TR3 | 300 | 150 | 387 | 01.01.2021 | 13:00
Bogura | TR1 | 225 | 124 | 375
| TR2 | 225 | 124 | 375 | 29.01.2021 | 09:00
| TR3 | 225 | 166 | 486
Baghabari | TR1 | 300 | 116 | 325
| TR2 | 225 | 85 | 240 | 26.01.2021 | 20:00
Barapukuria | TR1 | 225 | 144 | 700 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 136 | 670 | 31.01.2021 | 9:00 | 132 kV current is being provided
| TR6 | 300 | 176 | 860
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:January' 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 194.3 | 283 | 30.01.2021 | 10:00
| TR2(400/230 kV) | 520 | 196.7 | 284
| TR1(400/132 kV) | 325 | 213 | 409 | 28.01.2021 | 18:30
| TR2(400/132 kV) | 325 | 215 | 409
Bibiyana | ICT1(400/230 kV) | 520 | 375 | 547 | 31.01.2021 | 7:00
| ICT2(400/230kV) | 520 | 367 | 532
Bhulta | ATR1(400/230 kV) | 520 | 194 | 358 | 07.01.2021 | 16:45
| ATR2(400/230kV) | 520 | 194 | 358
Ashuganj(N) | GSUT1 | 567 | 396 | 623.3 | 07.01.2021 | 21:00
Gopalganj | ATR1(400/132 kV) | 325 | 298 | 414 | 22.01.2021 | 21:00
| ATR2(400/132 kV) | 325 | 298 | 414
Payra | GSUT1 | 810 | 565 | 829 | 11.01.2021 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January' 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January' 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-01-21 | 7934 | 7934 | - | - | - | - | - | - | - | - | - | - | - | - | 01-01-21 | 6102 | 6102 | - | - | - | - | - | - | - | - | - | - | - | -
02-01-21 | 8946 | 8946 | - | - | - | - | - | - | - | - | - | - | - | - | 02-01-21 | 6500 | 6500 | - | - | - | - | - | - | - | - | - | - | - | -
03-01-21 | 8863 | 8863 | - | - | - | - | - | - | - | - | - | - | - | - | 03-01-21 | 7151 | 7151 | - | - | - | - | - | - | - | - | - | - | - | -
04-01-21 | 8921 | 8921 | - | - | - | - | - | - | - | - | - | - | - | - | 04-01-21 | 7183 | 7183 | - | - | - | - | - | - | - | - | - | - | - | -
05-01-21 | 8993 | 8993 | - | - | - | - | - | - | - | - | - | - | - | - | 05-01-21 | 7342 | 7342 | - | - | - | - | - | - | - | - | - | - | - | -
06-01-21 | 9073 | 9073 | - | - | - | - | - | - | - | - | - | - | - | - | 06-01-21 | 7533 | 7533 | - | - | - | - | - | - | - | - | - | - | - | -
07-01-21 | 9116 | 9116 | - | - | - | - | - | - | - | - | - | - | - | - | 07-01-21 | 7752 | 7752 | - | - | - | - | - | - | - | - | - | - | - | -
08-01-21 | 8158 | 8158 | - | - | - | - | - | - | - | - | - | - | - | - | 08-01-21 | 6485 | 6485 | - | - | - | - | - | - | - | - | - | - | - | -
09-01-21 | 9141 | 9141 | - | - | - | - | - | - | - | - | - | - | - | - | 09-01-21 | 7014 | 7014 | - | - | - | - | - | - | - | - | - | - | - | -
10-01-21 | 9200 | 9200 | - | - | - | - | - | - | - | - | - | - | - | - | 10-01-21 | 7635 | 7635 | - | - | - | - | - | - | - | - | - | - | - | -
11-01-21 | 9283 | 9283 | - | - | - | - | - | - | - | - | - | - | - | - | 11-01-21 | 7746 | 7746 | - | - | - | - | - | - | - | - | - | - | - | -
12-01-21 | 9245 | 9245 | - | - | - | - | - | - | - | - | - | - | - | - | 12-01-21 | 7666 | 7666 | - | - | - | - | - | - | - | - | - | - | - | -
13-01-21 | 9243 | 9243 | - | - | - | - | - | - | - | - | - | - | - | - | 13-01-21 | 7599 | 7599 | - | - | - | - | - | - | - | - | - | - | - | -
14-01-21 | 9125 | 9125 | - | - | - | - | - | - | - | - | - | - | - | - | 14-01-21 | 7847 | 7847 | - | - | - | - | - | - | - | - | - | - | - | -
15-01-21 | 8182 | 8182 | - | - | - | - | - | - | - | - | - | - | - | - | 15-01-21 | 6647 | 6647 | - | - | - | - | - | - | - | - | - | - | - | -
16-01-21 | 9165 | 9165 | - | - | - | - | - | - | - | - | - | - | - | - | 16-01-21 | 7421 | 7421 | - | - | - | - | - | - | - | - | - | - | - | -
17-01-21 | 9232 | 9232 | - | - | - | - | - | - | - | - | - | - | - | - | 17-01-21 | 7797 | 7797 | - | - | - | - | - | - | - | - | - | - | - | -
18-01-21 | 9297 | 9297 | - | - | - | - | - | - | - | - | - | - | - | - | 18-01-21 | 7758 | 7758 | - | - | - | - | - | - | - | - | - | - | - | -
19-01-21 | 9380 | 9380 | - | - | - | - | - | - | - | - | - | - | - | - | 19-01-21 | 7888 | 7888 | - | - | - | - | - | - | - | - | - | - | - | -
20-01-21 | 9241 | 9241 | - | - | - | - | - | - | - | - | - | - | - | - | 20-01-21 | 8147 | 8147 | - | - | - | - | - | - | - | - | - | - | - | -
21-01-21 | 9279 | 9279 | - | - | - | - | - | - | - | - | - | - | - | - | 21-01-21 | 8118 | 8118 | - | - | - | - | - | - | - | - | - | - | - | -
22-01-21 | 8189 | 8189 | - | - | - | - | - | - | - | - | - | - | - | - | 22-01-21 | 6681 | 6681 | - | - | - | - | - | - | - | - | - | - | - | -
23-01-21 | 9242 | 9242 | - | - | - | - | - | - | - | - | - | - | - | - | 23-01-21 | 7711 | 7711 | - | - | - | - | - | - | - | - | - | - | - | -
24-01-21 | 9104 | 9104 | - | - | - | - | - | - | - | - | - | - | - | - | 24-01-21 | 7846 | 7846 | - | - | - | - | - | - | - | - | - | - | - | -
25-01-21 | 9278 | 9278 | - | - | - | - | - | - | - | - | - | - | - | - | 25-01-21 | 7893 | 7893 | - | - | - | - | - | - | - | - | - | - | - | -
26-01-21 | 9240 | 9240 | - | - | - | - | - | - | - | - | - | - | - | - | 26-01-21 | 7917 | 7917 | - | - | - | - | - | - | - | - | - | - | - | -
27-01-21 | 9272 | 9272 | - | - | - | - | - | - | - | - | - | - | - | - | 27-01-21 | 7919 | 7919 | - | - | - | - | - | - | - | - | - | - | - | -
28-01-21 | 9240 | 9240 | - | - | - | - | - | - | - | - | - | - | - | - | 28-01-21 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-01-21 | 8348 | 8348 | - | - | - | - | - | - | - | - | - | - | - | - | 29-01-21 | 6916 | 6916 | - | - | - | - | - | - | - | - | - | - | - | -
30-01-21 | 9075 | 9075 | - | - | - | - | - | - | - | - | - | - | - | - | 30-01-21 | 7578 | 7578 | - | - | - | - | - | - | - | - | - | - | - | -
31-01-21 | 9188 | 9188 | - | - | - | - | - | - | - | - | - | - | - | - | 31-01-21 | 7989 | 7989 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January' 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9380 | 19-01-2021 | 19:00
2 | Maximum Day Peak Genaration | MW | 8147 | 20-01-2021 | 12:00
3 | Maximum Evening Peak Demand | MW | 9380 | 19-01-2021 | 19:00
4 | Minimum Generation | MW | 5153 | 02/01/21 | 4:00
5 | Average of the daily evening peak Genaration | MW | 9006.2258
6 | Average of the daily day peak Genaration | MW | 7478.5484
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5444.4455
12 | Total Generation by BPDB | MKWH | 2455.6397 | % of total Gen. | 45.1%
13 | Total Generation by IPP | MKWH | 1743.1517 | '' | 32.02%
14 | A) Total Generation by RPCL | MKWH | 96.2632 | '' | 1.768%
| B) Total Generation by REB | MKWH | 130.737 | " | 2.401%
| C) Total Generation by RENTAL | MKWH | 490.6295 | " | 9.012%
| D) Total Imported from India (BIPTC) | MKWH | 468.1808 | " | 8.599%
| E) Total Imported from Tripura, India (A.C) | MKWH | 59.8436 | " | 1.099%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3124.5982 | % of total Gen. | 57.39%
| B) Oil | MKWH | 1390.0964 | '' | 25.53%
| C) Hydro | MKWH | 34.537 | '' | 0.6344%
| D) Solar | MKWH | 8.8809 | '' | 0.1631%
| E) Coal | MKWH | 358.3085 | '' | 6.581%
| F) BIPTC (Import from India) | MKWH | 468.1808 | '' | 8.599%
| G) A.C (Import from Tripura, India) | MKWH | 59.8436 | '' | 1.099%
16 | Maximun of the daily total Generation . | MKWH | 186.6112 | 07-01-2021
17 | Monthly Load factor | % | 80.6155
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18157.9258
| A) Gas | M.Taka | 3160.4299
| B) Liquid fuel | M.Taka | 10458.7673
| C) Coal | M.Taka | 1690.4083
| D) BIPTC (Import from India) | M.Taka | 2387.7219
| E) Tripura(Import from India) | M.Taka | 460.5984
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 631.283 | 24/01/2021
| A) Gas | M.Taka | 112.9697 | 10/01/2021
| B) Liquid fuel | M.Taka | 521.0115 | 24/01/2021
| C) Coal | M.Taka | 70.817 | 22/01/2021
| D) BIPTC (Import from India) | M.Taka | 87.4344 | 26-01-2021
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.4221
| B) Excluding Hydro & Solar | Taka/KWHR | 3.4486
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.2 | 31/01/2021 | 06:00
b) | Actual | FT (MSL) | 95.92 | 31/01/2021 | 06:00
22 | Peak Genaration of January 2020 | MW | 9223 | 29/01/20 | 19:00
23 | Peak Demand of January 2020 | MW | 9223 | 29/01/20 | 19:00
24 | Maximum peak Generation recorded upto 31/01/2021 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/01/2021 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/01/2021 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.