## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-19 | Friday
|  |  | Date (day): | 2021-02-19 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12404.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13530 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-18 | 2021-02-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 180 | 200 | 220 | 220 |  | 145
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 52 | 52
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 366 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-1 Under maint. |  | 2021-10-02
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 38 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 275 | 300 | 300
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 99 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 31 | 38 | 60 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 140 | 99 | 100 | 100
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 30 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 32 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 6 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 45 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 213 | 262 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 71 | 144 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 40 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 18 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 131 | 144 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 29 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 2189 | 2796 | 3649 | 3871 | 108 | 1743
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 46 | 46
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 85 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 21 | 12 | 25
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 102 | 102
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 252 | 302 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 615 | 778 | 1317 | 1355 | 895 | 115
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 225 | 179 | 225 | 225
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 280 | 280 | 280 | 80 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 280 | 280 | 80 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 26 | 26 | 26 | 19 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 30 | 40 | 40 | 15 |  | Gas shortage
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 34 | 0 | 0 |  | 163 | Under maint.
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 68 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 116 | 135 | 147
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 19 | 19 |  | 6 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 34 | 55 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 27 | 0 | 0 | 0
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1141 | 1141 | 1558 | 1820 | 779 | 169
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 98 | 96 | 145 | 145 | 57 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 65 | 80 | 80 |  | 15 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 185 | 200 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 14 | 8 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 431 | 414 | 635.6 | 584 | 57 | 15
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 32 | 32 |  | 58 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 110 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 122 | 120 | 135 | 135 |  | 195 | GT-2 under maint.
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 67 | 75 | 72 | 72 |  | 14 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint |  | 20/04/2021
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 121 | 121 | 0 | 0 |  | 231
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 341 | 430 | 350 | 350
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 5 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 281 | 0 | 0 | 0 |  |  | On Test
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1492 | 1286 | 1201 | 1201 | 0 | 643
| 103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 824 | 846 | 645 | 838
| 104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
| 106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 2 | 25 | 60 | 60 |  | 49 | Engine problem
| 108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 210 | 160 | 350 | 410
| 109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 95 | 90 | 90 |  | 15 | Engine problem
| 112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1106 | 1241 | 1475 | 2014 | 0 | 93
| 113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 25 | 26 | 26 |  | 7 | Engine problem
| 115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 56 | 85 | 95 | 95
| 117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 470 | 620 | 620
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 496 | 628 | 1001 | 1001 | 0 | 201
| 119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 12 | 12 |  | 38 | Engine problem
| 123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 143 | 220 | 220 |  |  | FGMO
| 128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 331 | 404 | 400 | 400 |  |  | FGMO
| 129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 0 | 34
| 130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 104 | 104
| 135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 100 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 747 | 991 | 1297 | 1421 | 651 | 38
| 138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 104 | 113 | 113
| 143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 224 | 254 | 271 | 263 | 124 | 210
|  | Total |  |  |  |  | 21395 | 20929 | 8441 | 9529 | 12404.6 | 13530 | 2614 | 3227
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8119.4465 | 9166 | 11932.0562 | 13014.585
| A. |  | 2021-02-18 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 9529 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6093 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9529 | MW
| 3 | Day peak Generation : |  |  | 8441 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9166 | MW
| 4 | Evening peak Generation : |  |  | 9529 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 188.9854 | MKWHr | By Solar | 0.67353 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 104.161 | MKWHr |  | By Oil: | 46.8352 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.8703 | MKWHr |  | By Hydro: | 1.668 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2614 | MW | Dhaka | 3292 | 3292 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3227 | MW | Chittagong | 925 | 925 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5841 | MW | Khulna | 1139 | 1139 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 879.1 | MMCFD |  |  | Rajshahi | 962 | 962 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 111486207.854 | ii) Oil : | Taka | 291375790.17 | Comilla | 784 | 784 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69072768 | Total | Taka | 471934766.024 | Mymensingh | 817 | 817 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.29 | MKWHr. | Sylhet | 354 | 354 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -35 | MW (E to W) at | 19:00 | hrs | Barisal | 229 | 229 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -110 | MW at | 8:00 | hrs | Rangpur | 664 | 664 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 9166 | 9166 |  | 0
| B. |  | 2021-02-19 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13530 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4530 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 178.4939 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6242 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.4829 | MKWHr. | ii) HVDC Flow at Peak Time |  | 846 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2944 | MKWHr. | iii) Maximum HVDC Flow : |  | 848 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.15 |  | (b) Today: | 93.02 |  | (c) Rule Curve: |  | 94.48
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 51 | 0 | 341 | 0 |  | 0 | 225 | 270 | 0 | 30 | 0 | 0 | 0 | 120 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 0 | 260 | 240 | 205 | 8 | 80 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 84 | 107 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 195 | 0 | 16 | 0 | 10 | 70 | 0 | 340 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 50 | 270 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 539 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 167 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 |  | 4909 | 2001 | 6910 | 3092 | 539 | 1370 | 1091 | 640 | 70 | 24 | 84 | 0 | 0 | 93.2
2:00 | 0 | 0 | 0 | 190 | 20 | 51 | 0 | 345 | 0 |  | 0 | 225 | 260 | 0 | 15 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 250 | 230 | 193 | 8 | 74 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 80 | 109 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 130 | 118 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 285 | 8 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 15 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 539 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 177 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 |  | 4568 | 1959 | 6527 | 3085 | 539 | 1325 | 788 | 640 | 70 | 0 | 80 | 0 | 0 | 93.19
3:00 | 0 | 0 | 0 | 190 | 150 | 51 | 0 | 344 | 0 |  | 0 | 225 | 255 | 0 | 15 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 250 | 230 | 211 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 127 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 130 | 117 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 270 | 8 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 538 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 181 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 |  | 4437 | 1919 | 6356 | 3264 | 538 | 1287 | 541 | 580 | 70 | 0 | 76 | 0 | 0 | 93.18
4:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 342 | 0 |  | 0 | 225 | 260 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 250 | 230 | 207 | 8 | 74 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 76 | 159 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 75 | 0 | 120 | 0 | 0 | 5 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 538 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 188 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 |  | 4362 | 1820 | 6182 | 3331 | 538 | 1292 | 425 | 450 | 70 | 0 | 76 | 0 | 0 | 93.17
5:00 | 0 | 0 | 0 | 160 | 180 | 12 | 0 | 351 | 0 |  | 0 | 225 | 300 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 250 | 230 | 204 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 78 | 148 | 0 | 22 | 0 | 0 | 43 | 11 | 0 | 163 | 120 | 0 | 50 | 0 | 120 | 0 | 0 | 5 | 295 | 8 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 10 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 10 | 200 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 538 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 171 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 |  | 4268 | 1825 | 6093 | 3203 | 538 | 1257 | 487 | 460 | 70 | 0 | 78 | 0 | 0 | 93.16
6:00 | 0 | 0 | 0 | 100 | 180 | 12 | 0 | 361 | 0 |  | 0 | 225 | 280 | 0 | 1 | 0 | 0 | 0 | 95 | 0 | 0 | 32 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 0 | 0 | 250 | 230 | 204 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 82 | 150 | 0 | 22 | 0 | 0 | 43 | 11 | 0 | 163 | 119 | 0 | 69 | 0 | 120 | 0 | 0 | 5 | 320 | 8 | 8 | 0 | 0 | 0 | 0 | 62 | 0 | 4 | 0 | 40 | 23 | 0 | 340 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 88 | 140 | 0 | 0 | 38 | 0 | 0 | 0 | 0 |  | 738 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 171 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 4450 | 2078 | 6528 | 3086 | 738 | 1317 | 713 | 490 | 70 | 32 | 82 | 0 | 0 | 93.15
7:00 | 0 | 0 | 0 | 100 | 180 | 12 | 0 | 356 | 0 |  | 0 | 225 | 285 | 0 | 19 | 0 | 0 | 0 | 127 | 0 | 0 | 40 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 6 | 20 | 30 | 0 | 0 | 0 | 250 | 230 | 228 | 8 | 81 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 78 | 149 | 0 | 22 | 0 | 0 | 43 | 52 | 0 | 130 | 120 | 0 | 69 | 0 | 120 | 0 | 0 | 5 | 295 | 8 | 8 | 0 | 5 | 0 | 0 | 103 | 0 | 33 | 1 | 90 | 50 | 0 | 340 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 2 | 108 | 0 | 0 | 0 | 1 |  | 823 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 174 | 0 | 370 | 0 | 0 | 29 | 0 | 19 | 0 | 0 | 35 | 360 | 0 | 0 | 0 |  | 4765 | 2257 | 7022 | 3087 | 823 | 1279 | 1131 | 510 | 70 | 40 | 78 | 4 | 0 | 93.14
8:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 360 | 0 |  | 0 | 225 | 285 | 0 | 65 | 10 | 0 | 0 | 122 | 4 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 34 | 20 | 8 | 0 | 0 | 0 | 250 | 230 | 228 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 88 | 131 | 0 | 22 | 1 | 0 | 43 | 53 | 0 | 130 | 118 | 0 | 69 | 0 | 120 | 0 | 0 | 5 | 310 | 8 | 8 | 0 | 82 | 0 | 0 | 166 | 0 | 35 | 6 | 100 | 68 | 0 | 340 | 0 | 0 | 0 | 1 | 251 | 0 | 0 | 0 | 0 | 100 | 100 | 24 | 9 | 144 | 0 | 0 | 0 | 7 |  | 824 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 172 | 0 | 361 | 17 | 0 | 90 | 0 | 70 | 0 | 1 | 80 | 390 | 0 | 0 | 0 |  | 5199 | 2456 | 7655 | 3150 | 824 | 1256 | 1670 | 540 | 70 | 32 | 88 | 25 | 0 | 93.13
9:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 339 | 0 |  | 0 | 225 | 270 | 0 | 75 | 55 | 0 | 0 | 120 | 16 | 0 | 32 | 25 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 0 | 0 | 0 | 250 | 230 | 229 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 90 | 110 | 24 | 22 | 1 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 69 | 0 | 120 | 0 | 0 | 5 | 290 | 8 | 8 | 0 | 210 | 0 | 0 | 195 | 0 | 35 | 0 | 100 | 68 | 0 | 341 | 4 | 0 | 0 | 3 | 252 | 0 | 0 | 0 | 26 | 100 | 100 | 34 | 25 | 144 | 0 | 0 | 0 | 16 |  | 823 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 167 | 0 | 329 | 53 | 0 | 113 | 0 | 70 | 0 | 2 | 113 | 420 | 0 | 0 | 0 |  | 5477 | 2538 | 8015 | 3077 | 823 | 1196 | 2110 | 570 | 70 | 32 | 90 | 47 | 0 | 93.12
10:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 338 | 0 |  | 0 | 225 | 270 | 0 | 99 | 30 | 0 | 0 | 130 | 16 | 0 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 250 | 230 | 228 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 18 | 92 | 104 | 32 | 22 | 2 | 0 | 43 | 52 | 0 | 130 | 121 | 0 | 67 | 0 | 120 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 210 | 0 | 0 | 195 | 0 | 69 | 0 | 100 | 68 | 0 | 340 | 8 | 0 | 0 | 4 | 253 | 0 | 0 | 0 | 26 | 100 | 291 | 24 | 36 | 144 | 0 | 0 | 2 | 24 |  | 824 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 168 | 0 | 336 | 35 | 0 | 113 | 0 | 50 | 0 | 0 | 70 | 420 | 0 | 0 | 0 |  | 5698 | 2492 | 8190 | 3282 | 824 | 1222 | 2048 | 570 | 70 | 16 | 92 | 66 | 0 | 93.12
11:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 341 | 0 |  | 0 | 225 | 295 | 0 | 99 | 30 | 0 | 0 | 140 | 16 | 0 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 30 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 250 | 230 | 225 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 20 | 98 | 102 | 32 | 22 | 2 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 67 | 0 | 121 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 210 | 0 | 0 | 195 | 0 | 70 | 16 | 100 | 68 | 0 | 341 | 8 | 0 | 0 | 4 | 252 | 0 | 0 | 0 | 26 | 90 | 286 | 17 | 43 | 144 | 0 | 0 | 24 | 29 |  | 823 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 168 | 0 | 358 | 35 | 0 | 113 | 0 | 50 | 0 | 4 | 70 | 420 | 0 | 0 | 0 |  | 5769 | 2514 | 8283 | 3284 | 823 | 1251 | 2072 | 571 | 70 | 16 | 98 | 98 | 0 | 93.11
12:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 352 | 0 |  | 0 | 225 | 270 | 0 | 99 | 30 | 0 | 0 | 140 | 30 | 16 | 16 | 31 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 260 | 260 | 225 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 20 | 104 | 98 | 40 | 22 | 2 | 0 | 43 | 53 | 0 | 130 | 122 | 0 | 67 | 0 | 121 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 213 | 0 | 0 | 185 | 0 | 71 | 17 | 100 | 68 | 0 | 341 | 14 | 0 | 0 | 4 | 252 | 0 | 0 | 0 | 34 | 100 | 281 | 18 | 47 | 131 | 0 | 0 | 27 | 29 |  | 824 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 171 | 0 | 331 | 70 | 0 | 113 | 0 | 70 | 0 | 4 | 100 | 420 | 0 | 0 | 0 |  | 5868 | 2573 | 8441 | 3322 | 824 | 1240 | 2190 | 570 | 70 | 18 | 104 | 103 | 0 | 93.11
13:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 341 | 0 |  | 0 | 225 | 250 | 0 | 99 | 40 | 0 | 0 | 140 | 50 | 16 | 16 | 37 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 23 | 0 | 0 | 47 | 20 | 4 | 0 | 0 | 0 | 260 | 260 | 225 | 8 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 20 | 104 | 98 | 16 | 22 | 2 | 0 | 43 | 53 | 0 | 130 | 120 | 0 | 72 | 0 | 120 | 0 | 0 | 5 | 280 | 8 | 11 | 0 | 195 | 0 | 0 | 194 | 0 | 124 | 17 | 100 | 68 | 0 | 338 | 8 | 0 | 0 | 4 | 253 | 0 | 0 | 0 | 55 | 100 | 210 | 104 | 46 | 144 | 0 | 0 | 32 | 28 |  | 824 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 206 | 0 | 318 | 70 | 0 | 113 | 0 | 97 | 0 | 5 | 113 | 420 | 0 | 0 | 0 |  | 5979 | 2624 | 8603 | 3256 | 824 | 1197 | 2434 | 570 | 70 | 46 | 104 | 102 | 8603 | 93.1
14:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 353 | 0 |  | 0 | 225 | 245 | 0 | 64 | 40 | 0 | 0 | 150 | 24 | 16 | 16 | 50 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 26 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 34 | 0 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 285 | 270 | 222 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 20 | 106 | 98 | 16 | 22 | 2 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 72 | 0 | 122 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 195 | 0 | 0 | 160 | 0 | 120 | 15 | 60 | 68 | 0 | 341 | 8 | 0 | 0 | 4 | 252 | 0 | 0 | 0 | 55 | 100 | 208 | 53 | 40 | 144 | 0 | 0 | 32 | 27 |  | 823 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 183 | 0 | 373 | 70 | 0 | 70 | 0 | 70 | 0 | 4 | 70 | 390 | 0 | 0 | 0 |  | 5751 | 2499 | 8250 | 3197 | 823 | 1242 | 2122 | 540 | 70 | 58 | 106 | 92 | 0 | 93.1
15:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 352 | 0 |  | 0 | 225 | 255 | 0 | 64 | 40 | 0 | 0 | 92 | 24 | 16 | 0 | 49 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 17 | 3 | 0 | 0 | 0 | 285 | 265 | 220 | 8 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 106 | 95 | 16 | 22 | 1 | 0 | 43 | 53 | 0 | 110 | 119 | 0 | 69 | 0 | 122 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 195 | 0 | 0 | 130 | 0 | 120 | 12 | 60 | 68 | 0 | 341 | 8 | 0 | 0 | 3 | 252 | 0 | 0 | 0 | 55 | 100 | 140 | 53 | 32 | 128 | 0 | 0 | 27 | 21 |  | 824 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 160 | 0 | 415 | 70 | 0 | 70 | 0 | 70 | 0 | 2 | 70 | 390 | 0 | 0 | 0 |  | 5565 | 2498 | 8063 | 3073 | 824 | 1290 | 2083 | 540 | 70 | 6 | 106 | 71 | 0 | 93.09
16:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 354 | 0 |  | 0 | 225 | 260 | 0 | 64 | 40 | 0 | 0 | 90 | 24 | 16 | 32 | 41 | 0 | 0 | 0 | 35 | 35 | 0 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 0 | 0 | 0 | 285 | 270 | 223 | 8 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 19 | 100 | 95 | 16 | 22 | 1 | 0 | 43 | 50 | 0 | 110 | 119 | 0 | 73 | 0 | 122 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 195 | 0 | 0 | 130 | 0 | 82 | 7 | 60 | 68 | 0 | 338 | 8 | 0 | 0 | 1 | 252 | 0 | 0 | 0 | 55 | 100 | 140 | 53 | 16 | 126 | 0 | 0 | 34 | 11 |  | 823 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 149 | 0 | 357 | 35 | 0 | 70 | 0 | 70 | 0 | 2 | 70 | 390 | 0 | 0 | 0 |  | 5541 | 2370 | 7911 | 3056 | 823 | 1238 | 2012 | 540 | 70 | 34 | 100 | 38 | 0 | 93.09
17:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 345 | 0 |  | 0 | 225 | 270 | 0 | 64 | 47 | 0 | 0 | 88 | 24 | 16 | 40 | 38 | 0 | 0 | 0 | 35 | 35 | 0 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 5 | 0 | 48 | 19 | 10 | 0 | 0 | 0 | 275 | 270 | 225 | 8 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 100 | 95 | 16 | 22 | 0 | 0 | 42 | 53 | 0 | 110 | 121 | 0 | 75 | 0 | 122 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 195 | 0 | 0 | 139 | 0 | 70 | 2 | 60 | 68 | 0 | 337 | 8 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 55 | 100 | 140 | 53 | 2 | 144 | 0 | 0 | 17 | 3 |  | 824 | 0 | 150 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 142 | 0 | 285 | 35 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 390 | 0 | 0 | 0 |  | 5531 | 2306 | 7837 | 3037 | 824 | 1177 | 2039 | 540 | 70 | 43 | 100 | 7 | 0 | 93.08
18:00 | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 324 | 0 |  | 0 | 225 | 285 | 6 | 64 | 55 | 0 | 0 | 35 | 30 | 24 | 120 | 38 | 0 | 0 | 0 | 35 | 35 | 20 | 22 | 25 | 20 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 53 | 10 | 12 | 45 | 19 | 12 | 0 | 0 | 0 | 290 | 300 | 191 | 8 | 40 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 112 | 98 | 32 | 22 | 0 | 0 | 44 | 53 | 0 | 110 | 121 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 204 | 0 | 0 | 173 | 0 | 78 | 0 | 100 | 68 | 0 | 381 | 8 | 1 | 0 | 0 | 252 | 14 | 0 | 0 | 55 | 100 | 0 | 59 | 0 | 144 | 0 | 0 | 0 | 0 |  | 823 | 0 | 160 | 0 | 27 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 8 | 17 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 139 | 0 | 336 | 48 | 0 | 81 | 0 | 99 | 0 | 0 | 90 | 390 | 0 | 0 | 0 |  | 5721 | 2578 | 8299 | 2888 | 823 | 1245 | 2359 | 540 | 70 | 262 | 112 | 0 | 0 | 93.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 200 | 12 | 0 | 366 | 0 |  | 0 | 225 | 275 | 38 | 97 | 55 | 0 | 0 | 99 | 100 | 32 | 150 | 38 | 0 | 0 | 6 | 35 | 35 | 45 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 10 | 12 | 50 | 20 | 21 | 0 | 0 | 0 | 280 | 260 | 179 | 8 | 34 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 116 | 96 | 65 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 262 | 0 | 0 | 200 | 0 | 144 | 0 | 100 | 68 | 0 | 430 | 8 | 40 | 0 | 0 | 302 | 17 | 0 | 0 | 55 | 100 | 0 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 846 | 0 | 160 | 0 | 115 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 143 | 0 | 404 | 95 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 470 | 0 | 0 | 0 |  | 6415 | 3114 | 9529 | 3008 | 846 | 1385 | 3120 | 620 | 70 | 364 | 116 | 0 | 0 | 93.06
19:30 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 340 | 0 |  | 0 | 225 | 265 | 50 | 101 | 55 | 0 | 0 | 99 | 100 | 32 | 150 | 38 | 0 | 0 | 6 | 35 | 35 | 55 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 0 | 0 | 50 | 20 | 12 | 0 | 0 | 0 | 280 | 260 | 179 | 8 | 36 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 112 | 98 | 73 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 271 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 68 | 0 | 428 | 8 | 17 | 0 | 0 | 305 | 17 | 0 | 0 | 55 | 100 | 0 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 848 | 0 | 140 | 0 | 59 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 52 | 8 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 143 | 0 | 388 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 6384 | 3077 | 9461 | 2984 | 848 | 1350 | 3066 | 670 | 70 | 361 | 112 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 341 | 0 |  | 0 | 225 | 275 | 50 | 101 | 55 | 0 | 0 | 99 | 100 | 16 | 150 | 38 | 0 | 0 | 6 | 35 | 35 | 55 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 0 | 0 | 50 | 20 | 23 | 0 | 0 | 0 | 280 | 260 | 172 | 8 | 36 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 112 | 98 | 73 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 267 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 68 | 0 | 427 | 8 | 0 | 0 | 0 | 306 | 17 | 0 | 0 | 55 | 100 | 0 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 848 | 0 | 140 | 0 | 16 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 141 | 0 | 386 | 95 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 6329 | 3026 | 9355 | 2976 | 848 | 1360 | 3000 | 670 | 70 | 319 | 112 | 0 | 0 | 93.07
21:00 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 346 | 0 |  | 0 | 225 | 265 | 50 | 101 | 55 | 0 | 0 | 97 | 100 | 0 | 150 | 47 | 0 | 0 | 6 | 35 | 17 | 17 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 20 | 26 | 0 | 0 | 0 | 260 | 260 | 168 | 8 | 36 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 112 | 99 | 24 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 121 | 0 | 75 | 0 | 122 | 0 | 0 | 5 | 300 | 8 | 11 | 0 | 269 | 0 | 0 | 200 | 0 | 120 | 0 | 100 | 68 | 0 | 425 | 0 | 0 | 0 | 0 | 306 | 17 | 0 | 0 | 55 | 100 | 0 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 847 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 139 | 0 | 323 | 95 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 6128 | 2884 | 9012 | 2959 | 847 | 1291 | 2779 | 670 | 70 | 284 | 112 | 0 | 0 | 93.06
22:00 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 358 | 0 |  | 0 | 225 | 275 | 7 | 99 | 30 | 0 | 0 | 97 | 84 | 0 | 150 | 58 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 20 | 26 | 0 | 0 | 0 | 270 | 260 | 214 | 8 | 32 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 108 | 99 | 24 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 267 | 0 | 0 | 200 | 0 | 60 | 0 | 100 | 68 | 0 | 421 | 0 | 0 | 0 | 0 | 306 | 17 | 0 | 0 | 8 | 100 | 0 | 104 | 0 | 134 | 0 | 0 | 0 | 0 |  | 848 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 139 | 0 | 300 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 5914 | 2754 | 8668 | 3011 | 848 | 1263 | 2455 | 670 | 70 | 243 | 108 | 0 | 0 | 93.06
23:00 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 346 | 0 |  | 0 | 225 | 315 | 7 | 64 | 15 | 0 | 0 | 97 | 36 | 0 | 150 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 |  | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 20 | 30 | 0 | 0 | 0 | 270 | 260 | 210 | 8 | 25 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 102 | 102 | 8 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 104 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 215 | 0 | 0 | 192 | 0 | 39 | 0 | 100 | 68 | 0 | 425 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 8 | 100 | 0 | 40 | 0 | 144 | 0 | 0 | 0 | 0 |  | 847 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 140 | 0 | 270 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 70 | 520 | 0 | 0 | 0 |  | 5618 | 2473 | 8091 | 3004 | 847 | 1216 | 1981 | 670 | #VALUE! | 201 | 102 | 0 | 0 | 93.05
24:00 | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 341 | 0 |  | 0 | 225 | 250 | 0 | 30 | 0 | 0 | 0 | 92 | 0 | 0 | 100 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 25 | 20 | 35 | 0 | 0 | 0 | 270 | 260 | 214 | 8 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 94 | 105 | 0 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 105 | 0 | 0 | 5 | 280 | 8 | 11 | 0 | 215 | 0 | 0 | 170 | 0 | 0 | 0 | 100 | 68 | 0 | 418 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 847 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 149 | 0 | 270 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 520 | 0 | 0 | 0 |  | 5223 | 2405 | 7628 | 3004 | 847 | 1212 | 1631 | 670 | 70 | 100 | 94 | 0 | 0 | 93.05
KWH | 0 | 0 | 0 | 4362550 | 3989500 | 444318 | 0 | 8463360 | 0 |  | 0 | 5164050 | 6485498 | 179520 | 1577736 | 685439 | 0 | 0 | 2889000 | 705600 | 166896 | 1249920 | 734743 | 0 | 0 | 22752 | 548280 | 323405 | 191015 | 465948 | 600000 | 702360 | 623600 | 321900 | 0 | 0 | 0 | 1668000 | 0 | 0 | 24926 | 0 | 0 | 0 | 0 |  | 385680 | 0 | 216893 | 21600 | 24960 | 828000 | 466608 | 470400 | 0 | 0 | 0 | 6667000 | 6169000 | 4995000 | 200727 | 1356270 | 295344 | 258720 | 0 | 0 | 0 | 0 | 0 | 443916 | 255240 | 820700 | 467800 | 2294400 | 258288 | 493440 | 524340 | 13400 | 0 | 1017720 | 1165800 | 0 | 3003382 | 2680000 | 0 | 1704960 | 0 | 2868030 | 0 | 0 | 123120 | 7426000 | 290832 | 246000 | 0 | 3781199 | 0 | 0 | 3852000 | 0 | 1502640 | 100305 | 1676160 | 1379520 | 0 | 8665000 | 152400 | 71472 | 0 | 29400 | 5966618 | 99832 | 0 | 0 | 723240 | 1923840 | 3448400 | 1005120 | 298290 | 2913120 | 0 | 0 | 198360 | 199939 |  | 18482909 | 0 | 4590432 | 0 | 165120 | 0 | 0 | 0 | 0 | 106240 | 0 | 0 | 485800 | 191328 | 0 | 0 | 0 | 0 | 0 | 527008 | 35510 | 0 | 0 | 144000 | 34110 | 500400 | 0 | 215352 | 0 | 0 | 3681700 | 0 | 0 | 0 | 0 | 0 | 0 | 1373368 | 0 | 4147436 | 0 | 8533000 | 959520 | 0 | 1723872 | 0 | 1296960 | 0 | 32200 | 1539744 | 11188600 | 0 | 0 | 0 |  | 129030741 | 59954609 | 188985350 | 73306926 | 18482909 | 30854045 | 44701065 | 14870300 | 1668000 | 2134171 | 2294400 | 673534 | 0
Fuel Cost | 0 | 0 | 0 | 6412948.5 | 4428345 | 586499.76 | 0 | 8547993.6 | 0 |  | 0 | 5628814.5 | 7198902.78 | 1362556.8 | 10870601.04 | 5798813.94 | 0 | 0 | 4997970 | 5313168 | 1522091.52 | 12299212.8 | 6774330.46 | 0 | 0 | 206815.68 | 4002444 | 2499920.65 | 1883407.9 | 349461 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 450360 | 0 | 0 | 231562.54 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2103862.1 | 206280 | 217152 | 6557760 | 587926.08 | 1397088 | 0 | 0 | 0 | 4933580 | 6169000 | 4595400 | 258937.83 | 1559710.5 | 333738.72 | 362208 | 0 | 0 | 0 | 0 | 0 | 563773.32 | 191430 | 1436225 | 350850 | 17208000 | 273785.28 | 4480435.2 | 665911.8 | 213596 | 0 | 1628352 | 2075124 | 0 | 3423855.48 | 2787200 | 0 | 3256473.6 | 0 | 4961691.9 | 0 | 0 | 251164.8 | 7500260 | 218124 | 186960 | 0 | 28585864.44 | 0 | 0 | 20030400 | 0 | 14785977.6 | 1172565.45 | 13660704 | 14967792 | 0 | 8058450 | 1389888 | 675410.4 | 0 | 0 | 45107632.08 | 869536.72 | 0 | 0 | 6198166.8 | 12812774.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 106461555.84 | 0 | 4819953.6 | 0 | 1297843.2 | 0 | 0 | 0 | 0 | 1113395.2 | 0 | 0 | 752990 | 1867361.28 | 0 | 0 | 0 | 0 | 0 | 4664020.8 | 273427 | 0 | 0 | 1395360 | 330867 | 960768 | 0 | 163021.464 | 0 | 0 | 19954814 | 0 | 0 | 0 | 0 | 0 | 0 | 2060052 | 0 | 4852500.12 | 0 | 8447670 | 10017388.8 | 0 | 16359545.28 | 0 | 10064409.6 | 0 | 355810 | 11378708.16 | 49117954 | 0 | 0 | 0 |  | 341087237.97 | 256709415.344 | 597796653.314 | 74524301.884 | 106461555.84 | 36961905.97 | 270864432.27 | 69072768 | 450360 | 20511357.9 | 17208000 | 1741971.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 180 | 12 | 0 | 352 | 0 |  | 0 | 225 | 270 | 0 | 99 | 30 | 0 | 0 | 140 | 30 | 16 | 16 | 31 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 260 | 260 | 225 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 33 | 20 | 104 | 98 | 40 | 22 | 2 | 0 | 43 | 53 | 0 | 130 | 122 | 0 | 67 | 0 | 121 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 213 | 0 | 0 | 185 | 0 | 71 | 17 | 100 | 68 | 0 | 341 | 14 | 0 | 0 | 4 | 252 | 0 | 0 | 0 | 34 | 100 | 281 | 18 | 47 | 131 | 0 | 0 | 27 | 29 |  | 824 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 171 | 0 | 331 | 70 | 0 | 113 | 0 | 70 | 0 | 4 | 100 | 420 | 0 | 0 | 0 |  | 8441 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 200 | 12 | 0 | 366 | 0 | 0 | 0 | 225 | 275 | 38 | 97 | 55 | 0 | 0 | 99 | 100 | 32 | 150 | 38 | 0 | 0 | 6 | 35 | 35 | 45 | 22 | 25 | 32 | 25 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 68 | 10 | 12 | 50 | 20 | 21 | 0 | 0 | 0 | 280 | 260 | 179 | 8 | 34 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 116 | 96 | 65 | 22 | 0 | 0 | 43 | 53 | 0 | 110 | 120 | 0 | 75 | 0 | 121 | 0 | 0 | 5 | 310 | 8 | 11 | 0 | 262 | 0 | 0 | 200 | 0 | 144 | 0 | 100 | 68 | 0 | 430 | 8 | 40 | 0 | 0 | 302 | 17 | 0 | 0 | 55 | 100 | 0 | 104 | 0 | 144 | 0 | 0 | 0 | 0 |  | 846 | 0 | 160 | 0 | 115 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 0 | 0 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 143 | 0 | 404 | 95 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 470 | 0 | 0 | 0 |  | 9529 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 220 | 52 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 102 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 25 | 0 | 0 | 0 | 280 | 280 | 225 | 8 | 0 | 26 | 40 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 19 | 147 | 145 | 80 | 22 | 0 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 144 | 116 | 0 |  |  |  | 838 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 |  |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 220 | 52 | 0 | 412 | 0 | 0 | 0 | 225 | 300 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 46 | 22 | 12 | 0 | 0 | 0 | 280 | 280 | 225 | 8 | 0 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 19 | 135 | 145 | 80 | 22 | 1.6 | 0 | 32 | 51 | 0 | 163 | 135 | 0 | 72 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 50 | 144 | 116 | 0 |  | 30 |  | 645 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 220 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 220 | 12 | 0 | 324 | 0 | 0 | 0 | 225 | 285 | 28 | 64 | 30 | 0 | 0 | 60 | 50 | 0 | 32 | 50 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 26 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 20 | 25 | 0 | 0 | 0 | 270 | 260 | 217 | 8 | 0 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 25 | 17 | 78 | 128 | 32 | 22 | 1 | 0 | 43 | 48 | 0 | 110 | 120 | 0 | 69 | 0 | 0 | 0 | 0 | 5 | 290 | 8 | 11 | 0 | 125 | 0 | 0 | 200 | 0 | 48 | 6 | 20 | 17 | 0 | 363 | 8 | 0 | 0 | 2 | 180 | 17 | 0 | 0 | 36 | 43 | 0 | 0 | 9 | 90 | 0 | 0 | 0 | 5 | 0 | 633 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 179 | 0 | 320 | 35 | 0 | 35 | 0 | 37 | 0 | 1 | 35 | 350 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6093 | 5:00
| Highest Generation |  | 9529 | 19:00
| Day Peak Generation |  | 8441 | 12:00
| Evening Peak Generation |  | 9529 | 19:00
| HVDC Max Flow |  | 848 | 19:30
| HVDC EvPeak Flow |  | 846 | 19:00
| Load factor L.F |  | 82.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8441 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6242 | MW
Evening Peak Generation : |  | 9529 | MW Hour : | 19:00 | Available Max Generation : |  | 13530 | MW
E.P. Demand (at gen end) : |  | 9529 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 9529 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4530 | MW
Total Gen. (MKWH) : |  | 188.9854 | System Load Factor : | 82.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -110 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-19
Actual : | 93.02 | Ft.(MSL) , | Rule curve : | 94.48 | Ft.( MSL )
Gas Consumed : | Total = | 879.1 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111486207.854
: |  | Coal : | 69072768 | Oil : | 291375790.17 | Total : | 471934766.024
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3232.2865 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1093.9678 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 979.2343 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 884.4926 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 799.4842 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 645.1423 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 367.4087 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 166.2835 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 497.5338 |  |  | 0 | 0%
Total | 0 |  | 8665.8337 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Haripur 360 MW
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Shahjibazar 330 MW GT-2
5) Kaptai-2
6) Raozan #1,2
7) Siddirganj-335 MW
8) Sirajganj #1CCPP
9) Megnaghat-450 MW GT-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Mirpur 132 kV Ckt-2 was under shut down from 09:45 to 17:39 for A/M.
b) Bhaluka 132/33 kV T-2 transformer was under shut down from 09:43 to 17:52 for A/M.
c) Bogura 132/33 kV T-4 transformer was under shut down from 09:35 to 11:40 for C/M.
d) Ghorashal-Joydevpur 132 kV Ckt-1 tripped at 12:42 showing dist Z3,3 phase and was
switched on at 13:02.
e) Julda-Shahmirpur 132 kV Ckt-1 was under shut down from 08:33 to 13:14 for A/M.
f) Kabirpur-Manikganj 132 kV Ckt-1 was shut down from 08:16 to 23:05 for D/W.
g) Kallyanpur 132/33 kV T-2 transformer was under shut down from 09:12 to 14:18 for A/M.
h) Khagrachori 132/33 kV T-2 transformer was under shut down from 08:33 to 16:45 for A/M.
i) Kishoreganj 132/33 kV T-3 transformer was under shut down from 09:42 to 15:35 for D/W.
j) Khulna(C)-Goalpara 132 kV Ckt-2 was shut down from 12:30 to 22:24 for removing wave trap
k) Khulna(C)-Noapara 132 kV Ckt-1 was shut down from 10:15 to 13:35 for removing wave trap
l) Khulna(C)-Noapara 132 kV Ckt-2 was shut down from 13:38 to 15:58 for removing wave trap
m) Kishoreganj 132/33 kV T-1 & T2 transformer tripped at 14:12 showing E/F relay at 33 kV side due |  |  |  |  | About 50 MW power interruption occurred under Kishoreganj S/S area
to 33 kV feeder fault and were switched on at 14:38. |  |  |  |  | from 14:12 to 14:38.
n) Kishoreganj 132/33 kV T-1 transformer was under shut down from 17:10 to 18:06 due to red hot |  |  |  |  | About 15 MW power interruption occurred under Kishoreganj S/S area
maintenance at bus section isolator. |  |  |  |  | from 17:10 to 18:06.
o) Hathazari 132/33 kV T-1 transformer was under shut down from 16:13 to 17:06 due to cable maint work.
p) Bibiyana South CCPP was under shut down since at 17:15 due to inspection after PG test.
q) Chandpur CCPP GT was synchronized at 14:25 and was shut down at 23:18 due to air filter replacement work.
r) Mongla 132/33 kV T1 transformer was under shut down since 07:06(19-02-2021) for A/M.
s) Sikalbaha-TK 132 kV Ckt was under shut down since 06:54(19-02-2021) for D/W.
t) Sonargaon-Orion Sonargaon 132 kV Ckt was under shut down since 07:40(19-02-2021) for D/W.
u) Sunamganj 132/33 kV T-1 & T2 transformer tripped at 03:10 due to 33 kV feeder fault and were |  |  |  |  | About 14 MW power interruption occurred under Sunamganj S/S area
switched on at 03:39(19-02-2021). |  |  |  |  | from 03:10 to 03:39.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4362550
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 3989500
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 444318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 366 | 8463360 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5164050 | GT-1 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 38 | 179520 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6485498 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1577736
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 685439
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 38 | 734743 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 465948
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 2889000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 705600
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 166896 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 6 | 22752 | High Voltage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 548280 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1249920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 323405 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 45 | 191015 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1302360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 623600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 321900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 262 | 3781199 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 144 | 1502640
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 40 | 71472 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1005120
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2913120 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 199939
| Dhaka area Total |  |  |  | 5972 | 2796 | 50370880
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 24926 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 100305
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 828000
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1668000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 216893
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 21600 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1676160
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 466608 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 470400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 24960 | High Voltage.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29400
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 302 | 5966618
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 99832 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1923840
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 778 | 13517542
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4995000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6667000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6169000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 295344 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 258720 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Engine problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 34 | 1356270 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 1379520 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 443916
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2294400
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820700
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 467800
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 723240 | High Voltage.
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 198360
| Cumilla Area Total |  |  |  | 2980 | 1141 | 26525237
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 96 | 258288 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 524340
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 65 | 493440 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3852000 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 152400 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 298290
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 385680
| Mymensingh Area Total |  |  |  | 709 | 414 | 5977838
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage & GT-2 under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1017720 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3003382 | Frequency control
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 120 | 2680000 | GT-2 & STG under shut down
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1165800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Under maint.
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 246000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-8,9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1704960 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | On test.
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 121 | 2868030 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 290832 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7426000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 430 | 8665000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 5 | 123120 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 3448400 | On test.
| Sylhet Area Total |  |  |  | 1988 | 1286 | 32639244
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 846 | 18482909
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 165120
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 106240 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 4590432 | Gas Shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 959520 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1241 | 24304221
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 191328 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 485800 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 85 | 1373368 | High Voltage.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 11188600 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 628 | 13239096
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 35510 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 143 | 4147436 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 404 | 8533000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 34110 | Low demand
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 500400
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 215352
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 144000
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 527008
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1723872
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1539744
| Rajshahi Area Total |  |  |  | 2183 | 991 | 17400432
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3681700 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 104 | 1296960
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32200
| Rangpur Area Total |  |  |  | 605 | 254 | 5010860
| Total |  |  |  | 20929 | 9529 | 188985350
| Eastern Grid Total |  |  |  | 14031 | 6415 | 129030741
| Western Grid Total |  |  |  | 6898 | 3114 | 59954609
| National Grid Total |  |  |  | 20929 | 9529 | 188985350
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-18
(a) ENTIRE EASTERN GRID : |  | 6172 | MW | (b) ENTIRE WESTERN GRID : |  | 2994 | MW
i) Dhaka area |  | 3292 | MW | i) Khulna area |  | 1139 | MW
ii) Chittagong area |  | 925 | MW | ii) Rajshahi area |  | 962 | MW
iii) Comilla area |  | 784 | MW | iii) Barisal area |  | 229 | MW
iv) Mymensingh area |  | 817 | MW | iv) Rangpur area |  | 664 | MW
v) Sylhet area |  | 354 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9166 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 11:00 | Netrokona | 97 | 9:00 | Jessore | 86 | 19:00
Munsiganj | 86 | 21:00 | Jamalpur | 114 | 7:00 | Benapol | 46 | 19:00
Sonargaon | 71 | 18:00 | Sherpur | 102 | 18:30 | Jhenida | 84 | 19:00
Shyampur | 190 | 11:00 | Srimongal | 32 | 18:30 | Bottail | 97 | 18:30
Bhulta | 165 | 21:00 | Shahjibazar | 89 | 18:30 | G.K Project | 37 | 19:00
Madanganj | 52 | 13:00 | Fenchuganj | 27 | 19:30 | Faridpur | 132 | 19:00
Shitalakhya | 112 | 16:00 | Kulawara | 29 | 18:30 | Madaripur | 63 | 19:30
Rahim steel | 25 | 12:00 | Sylhet | 90 | 18:30 | Sariatpur | 42 | 20:00
Matuail | 92 | 11:00 | Chatak | 21 | 18:30 | Gopalganj | 60 | 19:00
Ghorasal | 64 | 22:00 | Sunamganj | 30 | 18:30 | Bagerhat | 86 | 18:30
Narsingdi | 127 | 20:00 | Biani Bazar | 40 | 19:30 | Mongla | 40 | 19:30
Haripur (SBU) | 82 | 10:00 | Comilla (S) | 116 | 18:30 | Satkhira | 73 | 19:30
Sreenagar |  |  | Comilla(N) | 77 | 20:00 | Gallamari | 23 | 13:00
Ullon | 60 | 18:30 | Chandpur | 43 | 19:00 | Magura | 42 | 19:00
Hasnabad | 84 | 21:00 | Feni | 86 | 18:00 | Norail | 25 | 19:00
Magbazar | 70 | 13:00 | Chowmuhani | 124 | 19:30 | Chuadanga | 63 | 18:30
Maniknagar | 54 | 11:00 | Ashuganj | 41 | 20:00 | Borguna | 8 | 1:00
Bangabhaban | 16 | 10:00 | Daudkandi | 80 | 20:00 | Barisal(N) | 28 | 20:00
Narinda | 60 | 18:00 | B.Baria | 104 | 20:00 | Barisal (S) | 72 | 18:30
Dhanmondi | 135 | 14:00 | Ramganj | 56 | 20:00 | Patuakhali | 77 | 21:00
Lalbag | 85 | 12:00 | Chaddagram | 26 | 19:30 | Bhandaria | 40 | 19:30
Madartek | 48 | 18:30 | PHP | 10 | 14:00 | Borhan Uddin | 26 | 19:30
Dhaka University |  |  | Kochua | 40 | 19:30 | Ishurdi | 40 | 19:00
Aftabnagar | 7 | 12:00 | Madunaghat | 47 | 21:00 | Ruppur Paromanobik | 2 | 1:00
Fatullah | 48 | 9:00 | Hathazari | 62 | 19:30 | Natore | 95 | 18:30
Nawabganj | 32 | 19:00 | Khulshi | 160 | 14:00 | Bogra | 128 | 19:30
Mirpur | 79 | 12:00 | Halishahar | 99 | 15:00 | Noagaon | 94 | 9:00
Kalyanpur | 60 | 19:00 | Baraulia | 148 | 9:00 | Rajshahi | 96 | 20:00
Gulshan | 81 | 14:00 | Sikalbaha | 21 | 19:00 | Rajshahi New | 11 | 19:00
Uttara | 55 | 13:00 | Dohazari | 60 | 19:00 | C.Nawabganj | 65 | 8:00
Uttara New | 27 | 12:00 | Cox'sbazar | 80 | 18:30 | Amnura | 39 | 18:30
Kamrangirchar | 78 | 13:00 | Chandraghona | 24 | 18:00 | Pabna | 68 | 18:30
Savar | 124 | 18:30 | Kaptai | 0 | 1:00 | Shahjadpur | 90 | 12:00
Bhasantec | 108 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 70 | 19:30
Agargaon | 55 | 13:00 | Bakulia | 75 | 18:00 | Niyamatpur | 68 | 8:00
Satmosjid | 73 | 13:00 | Julda | 21 | 13:00 | Joypurhat | 56 | 8:00
Tongi | 78 | 19:30 | TK chemical | 19.5 | 18:30 | Sherpur(Bogura) | 48 | 18:30
Kabirpur | 206 | 19:00 | Modern Steel | 0 | 1:00 | Mohastangor | 36 | 19:00
Basundhara | 109 | 18:30 | Shahmirpur | 20.5 | 18:00 | Bangura | 19 | 18:30
Manikganj | 28 | 21:00 | Khagrachhari | 20 | 0:00 | Rangpur | 115 | 18:30
Joydevpur | 143 | 13:00 | Matarbari | 28 | 21:00 | Lalmonirhat | 46 | 19:00
New Tongi | 103 | 12:00 | Baroiar Hat | 26 | 18:30 | Saidpur | 101 | 9:00
Korda | 172 | 12:00 | Rangamati | 10 | 18:30 | Purbasadipur | 92 | 13:00
Dhamrai | 86 | 12:00 | Abul Khair 230 | 131 | 13:00 | Thakurgaon | 63 | 19:00
Rajendrapur | 74 | 18:30 | BSRM | 146 | 16:00 | Palashbari | 96 | 9:00
Valuka | 80 | 9:00 | GPH Ispat | 18 | 14:00 | Barapukuria | 49 | 9:00
Tangail | 179 | 8:00 | Goalpara | 17 | 19:00 | Panchagar | 46 | 19:00
Mymensing | 180 | 19:30 | Central s/s | 78 | 19:00 | Joldhaka | 25 | 9:00
Kishorganj | 106 | 19:30 | Noapara | 53 | 18:30 | Kurigram | 49 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 19:30 | 405 | 11:00 | Kaliakoir | 407 | 0.16667 | 395 | 0.45833
| Bheramara | 406 | 24:00 | 391 | 19:00 | Bhulta | 398 | 0.8125 | 384 | 0.45833
| Ashuganj(N) | 400 | 6:00 | 387 | 11:00 | Gopalganj | 413 | 0.625 | 400 | 0.41667
| Payra | 414 | 8:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 242 | 8:00 | 240 | 1:00 | Hathazari | 234 | 24:00 | 222 | 10:00
| Ishurdi | 242 | 4:00 | 232 | 8:00 | Megnaghat | 243 | 24:00 | 238 | 15:00
| Ashuganj | 245 | 18:00 | 235 | 11:00 | Fenchuganj | 244 | 21:00 | 238 | 15:00
| Serajganj | 235 | 1:00 | 229 | 10:00 | Siddhirganj | 241 | 1:00 | 232 | 11:00
| Baghabari | 238 | 2:00 | 230 | 9:00 | Maniknagar | 0 | 1:00 | 0 | 1:00
| Barapukuria | 236 | 22:00 | 228 | 9:00 | Agargaon | 239 | 5:00 | 231 | 12:00
| Bogra | 235 | 22:00 | 224 | 8:00 | Barisal | 253 | 21:00 | 242 | 12:00
| Rajshahi | 240 | 6:00 | 224 | 8:00 | Bhola 225 MW | 254 | 5:00 | 131 | 17:00
| Khulna South | 244 | 5:00 | 225 | 8:00 | AKSML | 236 | 21:00 | 220 | 3:00
| Rampura | 239 | 6:00 | 231 | 12:00 | BSRM | 235 | 19:00 | 219 | 3:00
| Haripur | 239 | 19:00 | 231 | 12:00 | Bibiyana | 244 | 9:00 | 240 | 16:00
| Hasnabad | 240 | 7:00 | 230 | 11:00 | Bhulta | 241 | 6:00 | 234 | 10:00
| Shyampur | 238 | 8:00 | 220 | 12:00 | Ashuganj (S) | 241 | 18:30 | 233 | 12:00
| Aminbazar | 240 | 8:00 | 232 | 15:00 | Kaliakoir | 238 | 19:00 | 223 | 11:00
| Tongi | 235 | 19:30 | 226 | 11:00 | GPH | 230 | 4:00 | 222 | 24:00
| Comilla (N) | 238 | 20:00 | 230 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 20:00 | 134 | 11:00 | Madanhat | 140 | 0.29167 | 133 | 0.41667
| Munsiganj | 141 | 19:00 | 136 | 1:00 | Hathazari | 139 | 0.79167 | 133 | 0.41667
| Sonargaon | 140 | 19:00 | 134 | 10:00 | Khulshi | 137 | 0.875 | 130 | 0.41667
| Shyampur | 135 | 8:00 | 130 | 10:00 | Halishahar | 139 | 0.79167 | 129 | 0.125
| Bhulta | 134 | 8:00 | 129 | 11:00 | Baraulia | 136 | 0.29167 | 130 | 0.45833
| Madanganj | 139 | 2:00 | 132 | 0:00 | Sikalbaha | 140 | 0.8125 | 133 | 0.45833
| Shitalakhya | 137 | 18:30 | 128 | 11:00 | Dohazari | 136 | 0.58333 | 128 | 0.66667
| Rahim steal | 139 | 18:00 | 134 | 11:00 | Cox'sbazar | 129 | 0.375 | 121 | 0.20833
| Matuail | 140 | 20:00 | 134 | 11:00 | Chandraghona | 139 | 0.79167 | 129 | 0.16667
| Ghorasal | 145 | 8:00 | 140 | 1:00 | Kaptai | 0 | 0.041667 | 0 | 0.041667
| Narsinghdi | 136 | 5:00 | 131 | 11:00 | A. Khaer Stl. | 135 | 0.041667 | 130 | 0.45833
| Haripur (SBU) | 139 | 20:00 | 135 | 12:00 | Bakulia | 138 | 0.79167 | 132 | 0.41667
| Sreenagar |  |  |  |  | Julda | 139 | 0.29167 | 132 | 0.5
| Ullon | 136 | 23:00 | 130 | 11:00 | TK Chemical | 140 | 0.79167 | 131 | 0.5
| Hasnabad | 135 | 7:00 | 130 | 10:00 | Modern Steel | 0 | 0.041667 | 0 | 0.041667
| Magbazar | 135 | 1:00 | 130 | 11:00 | Shahmirpur | 140 | 0.79167 | 132 | 0.45833
| Maniknagar | 137 | 7:00 | 132 | 11:00 | Khagrachhari | 139 | 0 | 130 | 0.16667
| Bangabhaban | 137 | 7:00 | 132 | 11:00 | Matarbari | 132 | 0.375 | 128 | 0.45833
| Narinda | 137 | 7:00 | 132 | 11:00 | Baroiar Hat | 139 | 0.33333 | 134 | 0.45833
| Dhanmondi | 136 | 23:00 | 130 | 11:00 | Rangamati | 138 | 0.79167 | 129 | 0.16667
| Lalbag | 135 | 8:00 | 127 | 11:00 | Goalpara S/S | 139 | 19:00 | 127 | 8:00
| Madartek | 136 | 6:00 | 130 | 12:00 | Khulna Central S/S | 139 | 18:30 | 127 | 8:00
| Dhaka University |  |  |  |  | Noapara | 137 | 4:00 | 125 | 0.33333
| Aftabnagar | 136 | 6:00 | 130 | 11:00 | Jessore | 133 | 17:00 | 121 | 0.33333
| Fatullah | 136 | 19:00 | 130 | 12:00 | Benapol | 135 | 3:00 | 121 | 0.33333
| Nawabganj | 133 | 18:30 | 130 | 16:00 | Jhenida | 135 | 4:00 | 122 | 0.33333
| Mirpur | 139 | 20:00 | 134 | 12:00 | Bottail | 138 | 0.125 | 130 | 0.33333
| Kalyanpur | 140 | 20:00 | 135 | 12:00 | G.K Project | 142 | 4:00 | 137 | 0.33333
| Gulshan | 135 | 20:00 | 134 | 12:00 | Faridpur | 140 | 0.16667 | 134 | 0.54167
| Uttara | 138 | 20:00 | 130 | 12:00 | Madaripur | 143 | 0.16667 | 137 | 0.54167
| Uttara New | 139 | 20:00 | 130 | 12:00 | Shariyatpur S/S | 143 | 0.20833 | 137 | 0.54167
| Kamrangirchar | 136 | 7:00 | 132 | 12:00 | Gopalganj | 146 | 0.25 | 140 | 0.54167
| Savar | 140 | 20:00 | 130 | 12:00 | Bagerhat | 137 | 19:00 | 127 | 0.45833
| Bhasantec | 135 | 20:00 | 135 | 12:00 | Mongla | 134 | 0.77083 | 124 | 0.33333
| Agargaon | 136 | 20:00 | 131 | 12:00 | Satkhira | 137 | 2:00 | 125 | 0.29167
| Satmosjid | 136 | 20:00 | 132 | 12:00 | Gallamari | 138 | 3:00 | 128 | 0.33333
| Tongi | 140 | 19:30 | 134 | 11:00 | Magura | 135 | 2:00 | 122 | 8:00
| Kabirpur | 134 | 23:00 | 128 | 16:00 | Narail | 134 | 0.25 | 124 | 0.375
| Basundhara | 139 | 18:30 | 132 | 11:00 | Chuadanga | 132 | 4:00 | 119 | 0.33333
| Manikganj | 145 | 18:30 | 135 | 12:00 | Borguna | 140 | 0.20833 | 135 | 0.77083
| Joydevpur | 143 | 13:00 | 137 | 17:00 | Barisal(N) | 144 | 4:00 | 137 | 0.75
| New Tongi | 139 | 21:00 | 132 | 11:00 | Barisal (S) | 143 | 5:00 | 133 | 0.54167
| Kodda | 138 | 19:00 | 127 | 12:00 | Patuakhali(S) | 137 | 17:00 | 132 | 7:00
| Dhamrai | 134 | 0:00 | 127 | 10:00 | Bhandaria | 140 | 0.125 | 134 | 0.77083
| Rajendrapur | 138 | 19:00 | 126 | 12:00 | Ishurdi | 140 | 0.083333 | 134 | 0.33333
| Valuka | 131 | 24:00 | 119 | 8:00 | Ruppur Paromanobik | 139 | 0.125 | 135 | 0.625
| Tangail | 133 | 1:00 | 123 | 11:00 | Natore | 138 | 18:30 | 130 | 8:00
| Mymensing | 133 | 24:00 | 122 | 8:00 | Bogra | 137 | 17:00 | 129 | 7:00
| Kishorganj | 133 | 24:00 | 126 | 16:00 | Noagaon | 132 | 4:00 | 123 | 8:00
| Netrokona | 132 | 24:00 | 119 | 8:00 | Rajshahi | 136 | 5:00 | 128 | 8:00
| Jamalpur | 141 | 18:30 | 125 | 7:00 | Rajshahi New | 136 | 3:00 | 127 | 8:00
| Sherpur | 138 | 19:30 | 126 | 8:00 | C.Nawabganj | 136 | 18:00 | 123 | 8:00
| Srimongal | 141 | 7:00 | 136 | 15:00 | Amnura | 137 | 18:00 | 124 | 8:00
| Shahjibazar | 137 | 1:00 | 134 | 18:00 | Pabna | 139 | 4:00 | 133 | 8:00
| Fenchuganj | 140 | 1:00 | 135 | 16:00 | Shahjadpur | 141 | 1:00 | 137 | 10:00
| Khulawara | 139 | 1:00 | 137 | 10:00 | Serajganj | 136 | 1:00 | 130 | 7:00
| Sylhet | 137 | 1:00 | 135 | 11:00 | Niyamatpur | 131 | 4:00 | 120 | 8:00
| Chatak | 137 | 4:00 | 133 | 18:30 | Joypurhat | 133 | 1:00 | 120 | 8:00
| Sunamganj | 136 | 1:00 | 133 | 18:00 | Sherpur(Bogura) | 137 | 18:00 | 130 | 10:00
| Biani Bazar | 137 | 4:00 | 133 | 19:30 | Mohastangor | 136 | 3:00 | 129 | 8:00
| Comilla(s) | 130 | 1:00 | 127 | 10:00 | Bangura | 138 | 1:00 | 134 | 9:00
| Comilla(n) | 143 | 19:00 | 138 | 11:00 | Rangpur | 133 | 4:00 | 124 | 8:00
| Chandpur | 144 | 9:00 | 135 | 16:00 | Lalmonirhat | 132 | 3:00 | 121 | 8:00
| Feni | 139 | 17:00 | 135 | 16:00 | Saidpur | 133 | 5:00 | 122 | 8:00
| Chowmuhani | 137 | 3:00 | 135 | 18:00 | Purbasadipur | 131 | 2:00 | 117 | 9:00
| Ashuganj | 140 | 1:00 | 134 | 16:00 | Thakurgaon | 132 | 3:00 | 116 | 9:00
| Daudkandi | 140 | 18:30 | 135 | 11:00 | Palashbari | 132 | 4:00 | 124 | 7:00
| B.Baria | 135 | 0:00 | 132 | 13:00 | Barapukuria | 134 | 1:00 | 128 | 9:00

## L-Curve
Date | 2021-02-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 92 | 5223 | 2405 | 7628 |  |  |  | QF-LDC-11
0:30 | 77 | 5066 | 2203 | 7269 | Date: | 2021-02-18
1:00 | 62 | 4909 | 2001 | 6910
1:30 | 54.5 | 4738.5 | 1980 | 6718.5
2:00 | 47 | 4568 | 1959 | 6527
2:30 | 58 | 4502.5 | 1939 | 6441.5 | [5 empty] | Gen. at Eve. Peak | 9529 | 9529 MW (19:00 )
3:00 | 69 | 4437 | 1919 | 6356 | [6 empty] | 19:00
3:30 | 40 | 4399.5 | 1869.5 | 6269 | [5 empty] | Gen. at Day Peak | 8441 | 8441 MW (12:00 )
4:00 | 11 | 4362 | 1820 | 6182 | [6 empty] | 12:00
4:30 | 15.5 | 4315 | 1822.5 | 6137.5 | [5 empty] | Highest Generation | 9529
5:00 | 20 | 4268 | 1825 | 6093 | [6 empty] | 19:00
5:30 | 77.5 | 4359 | 1951.5 | 6310.5
6:00 | 135 | 4450 | 2078 | 6528
6:30 | 96 | 4607.5 | 2167.5 | 6775
7:00 | 57 | 4765 | 2257 | 7022
7:30 | 83.5 | 4982 | 2356.5 | 7338.5
8:00 | 110 | 5199 | 2456 | 7655
8:30 | 74 | 5338 | 2497 | 7835
9:00 | 38 | 5477 | 2538 | 8015
9:30 | 32.5 | 5587.5 | 2515 | 8102.5
10:00 | 27 | 5698 | 2492 | 8190
10:30 | 38.5 | 5733.5 | 2503 | 8236.5
11:00 | 50 | 5769 | 2514 | 8283
11:30 | 39.5 | 5818.5 | 2543.5 | 8362
12:00 | 29 | 5868 | 2573 | 8441
12:30 | 26 | 5923.5 | 2598.5 | 8522
13:00 | 23 | 5979 | 2624 | 8603
13:30 | 42.5 | 5865 | 2561.5 | 8426.5
14:00 | 62 | 5751 | 2499 | 8250
14:30 | 138 | 5658 | 2498.5 | 8156.5
15:00 | 214 | 5565 | 2498 | 8063
15:30 | 212 | 5553 | 2434 | 7987
16:00 | 210 | 5541 | 2370 | 7911
16:30 | 194 | 5536 | 2338 | 7874
17:00 | 178 | 5531 | 2306 | 7837
17:30 | 157 | 5626 | 2442 | 8068
18:00 | 136 | 5721 | 2578 | 8299
18:30 | 85.5 | 6068 | 2846 | 8914
19:00 | 35 | 6415 | 3114 | 9529
19:30 | 53 | 6384 | 3077 | 9461
20:00 | 87 | 6329 | 3026 | 9355 |  |  |  | Executive Engineer
20:30 | 94.5 | 6228.5 | 2955 | 9183.5 |  |  |  | Network Operation Division
21:00 | 102 | 6128 | 2884 | 9012
21:30 | 68 | 6021 | 2819 | 8840
22:00 | 34 | 5914 | 2754 | 8668 |  |  |  |  | Page 6 of 7
22:30 | 43.5 | 5766 | 2613.5 | 8379.5
23:00 | 53 | 5618 | 2473 | 8091
23:30 | 72.5 | 5420.5 | 2439 | 7859.5
24:00 | 92 | 5223 | 2405 | 7628
9529 MW (19:00 )
8441 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-18 |  | Energy | 188985350
[11 empty] | 2021-02-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3004 | 847 | 1212 | 1981 | 670 | 70 | 100 | 0 | 94 | 0
0:30 | 3048 | 693 | 1291 | 1536 | 655 | 70 | 62 | 0 | 89 | 0 | Date: | 2021-02-18
1:00 | 3092 | 539 | 1370 | 1091 | 640 | 70 | 24 | 0 | 84 | 0
1:30 | 3088.5 | 539 | 1347.5 | 939.5 | 640 | 70 | 12 | 0 | 82 | 0 | [7 empty] | Total Energy | 188.9854 | Total Energy Gen 188.985 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 188.985 MKWHr
2:00 | 3085 | 539 | 1325 | 788 | 640 | 70 | 0 | 0 | 80 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3174.5 | 538.5 | 1306 | 664.5 | 610 | 70 | 0 | 0 | 78 | 0 | [7 empty] | Energy Requirement | 188.9854
3:00 | 3264 | 538 | 1287 | 541 | 580 | 70 | 0 | 0 | 76 | 0
3:30 | 3297.5 | 538 | 1289.5 | 483 | 515 | 70 | 0 | 0 | 76 | 0 | [6 empty] | Shortage
4:00 | 3331 | 538 | 1292 | 425 | 450 | 70 | 0 | 0 | 76 | 0
4:30 | 3267 | 538 | 1274.5 | 456 | 455 | 70 | 0 | 0 | 77 | 0
5:00 | 3203 | 538 | 1257 | 487 | 460 | 70 | 0 | 0 | 78 | 0
5:30 | 3144.5 | 638 | 1287 | 600 | 475 | 70 | 16 | 0 | 80 | 0
6:00 | 3086 | 738 | 1317 | 713 | 490 | 70 | 32 | 0 | 82 | 0
6:30 | 3086.5 | 780.5 | 1298 | 922 | 500 | 70 | 36 | 0 | 80 | 2 |  |  |  |  | Coal
7:00 | 3087 | 823 | 1279 | 1131 | 510 | 70 | 40 | 0 | 78 | 4
7:30 | 3118.5 | 823.5 | 1267.5 | 1400.5 | 525 | 70 | 36 | 0 | 83 | 14.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3150 | 824 | 1256 | 1670 | 540 | 70 | 32 | 0 | 88 | 25
8:30 | 3113.5 | 823.5 | 1226 | 1890 | 555 | 70 | 32 | 0 | 89 | 36
9:00 | 3077 | 823 | 1196 | 2110 | 570 | 70 | 32 | 0 | 90 | 47
9:30 | 3179.5 | 823.5 | 1209 | 2079 | 570 | 70 | 24 | 0 | 91 | 56.5
10:00 | 3282 | 824 | 1222 | 2048 | 570 | 70 | 16 | 0 | 92 | 66
10:30 | 3283 | 823.5 | 1236.5 | 2060 | 570.5 | 70 | 16 | 0 | 95 | 82
11:00 | 3284 | 823 | 1251 | 2072 | 571 | 70 | 16 | 0 | 98 | 98
11:30 | 3303 | 823.5 | 1245.5 | 2131 | 570.5 | 70 | 17 | 0 | 101 | 100.5
12:00 | 3322 | 824 | 1240 | 2190 | 570 | 70 | 18 | 0 | 104 | 103
12:30 | 3289 | 824 | 1218.5 | 2312 | 570 | 70 | 32 | 0 | 104 | 102.5
13:00 | 3256 | 824 | 1197 | 2434 | 570 | 70 | 46 | 0 | 104 | 102
13:30 | 3256 | 824 | 1197 | 2434 | 570 | 70 | 46 | 0 | 104 | 102
14:00 | 3256 | 824 | 1197 | 2434 | 570 | 70 | 46 | 0 | 104 | 102
14:30 | 3164.5 | 824 | 1243.5 | 2258.5 | 555 | 70 | 26 | 0 | 105 | 86.5
15:00 | 3073 | 824 | 1290 | 2083 | 540 | 70 | 6 | 0 | 106 | 71
15:30 | 3064.5 | 823.5 | 1264 | 2047.5 | 540 | 70 | 20 | 0 | 103 | 54.5
16:00 | 3056 | 823 | 1238 | 2012 | 540 | 70 | 34 | 0 | 100 | 38
16:30 | 3046.5 | 823.5 | 1207.5 | 2025.5 | 540 | 70 | 38.5 | 0 | 100 | 22.5
17:00 | 3037 | 824 | 1177 | 2039 | 540 | 70 | 43 | 0 | 100 | 7
17:30 | 2962.5 | 823.5 | 1211 | 2199 | 540 | 70 | 152.5 | 0 | 106 | 3.5
18:00 | 2888 | 823 | 1245 | 2359 | 540 | 70 | 262 | 0 | 112 | 0
18:30 | 2948 | 834.5 | 1315 | 2739.5 | 580 | 70 | 313 | 0 | 114 | 0
19:00 | 3008 | 846 | 1385 | 3120 | 620 | 70 | 364 | 0 | 116 | 0
19:30 | 2984 | 848 | 1350 | 3066 | 670 | 70 | 361 | 0 | 112 | 0
20:00 | 2976 | 848 | 1360 | 3000 | 670 | 70 | 319 | 0 | 112 | 0
20:30 | 2967.5 | 847.5 | 1325.5 | 2889.5 | 670 | 70 | 301.5 | 0 | 112 | 0
21:00 | 2959 | 847 | 1291 | 2779 | 670 | 70 | 284 | 0 | 112 | 0
21:30 | 2985 | 847.5 | 1277 | 2617 | 670 | 70 | 263.5 | 0 | 110 | 0
22:00 | 3011 | 848 | 1263 | 2455 | 670 | 70 | 243 | 0 | 108 | 0
22:30 | 3007.5 | 847.5 | 1239.5 | 2218 | 670 | #VALUE! | 222 | 0 | 105 | 0
23:00 | 3004 | 847 | 1216 | 1981 | 670 | #VALUE! | 201 | 0 | 102 | 0
23:30 | 3004 | 847 | 1214 | 1981 | 670 | #VALUE! | 150.5 | 0 | 98 | 0 | Max Temp. in Dhaka |  | 31.8° C
24:00 | 3004 | 847 | 1212 | 1981 | 670 | 70 | 100 | 0 | 94 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 188.985 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 188.985 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1668000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 0 | 8 |  | 8 | 8 | 8 |  |  |  |  | 24926
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 |  |  | 16 | 17 | 17 | 15 | 12 | 7 | 2 | [9 empty] | 100305
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 0 |  | 23 | 34 |  |  |  | 53 |  | 68 | 68 | 34 |  |  |  |  | 216893
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 120 | 120 | 100 | 95 | 127 | 122 | 120 | 130 | 140 | 140 | 140 | 150 | 92 | 90 | 88 | 35 |  | 99 | 99 | 99 | 97 | 97 | 97 | 92 | 2889000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 5 | 82 | 210 | 210 | 210 | 213 | 195 | 195 | 195 | 195 | 195 | 204 |  | 262 | 271 | 267 | 269 | 267 | 215 | 215 | 3781199
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 160 | 100 | 100 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4362550
24
25 | Ghorasal 365 MW CCPP Unit-7 | 0 | 20 | 150 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 200 | 220 | 220 | 220 | 220 | 220 | 220 | 3989500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 5 | [9 empty] | 5 | 26 |  | 26 | 26 | 26 | 26 | 5 | 5 | 5 | 295344
33 | Ashuganj 225 MW CCPP | 205 | 193 | 211 | 207 | 204 | 204 | 228 | 228 | 229 | 228 | 225 | 225 | 225 | 222 | 220 | 223 | 225 | 191 |  | 179 | 179 | 172 | 168 | 214 | 210 | 214 | 4995000
34 | Ashuganj 450 MW CCPP(South) | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 260 | 260 | 270 | 265 | 270 | 270 | 300 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6169000
| Ashuganj 450 MW CCPP(North) | 260 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 260 | 285 | 285 | 285 | 275 | 290 |  | 280 | 280 | 280 | 260 | 270 | 270 | 270 | 6667000
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 5 | 5 | 5 | 5 | 5 | [10 empty] | 10 |  | 30 | 30 | 30 | 20 | 5 | 5 | 5 | 258720
36 | Chandpur 150 MW CCPP | 80 | 74 | 80 | 74 | 80 | 80 | 81 | 78 | 75 | 78 | 76 | 75 | 72 |  | 50 | 50 | 50 | 40 |  | 34 | 36 | 36 | 36 | 32 | 25 |  | 1356270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 345 | 344 | 342 | 351 | 361 | 356 | 360 | 339 | 338 | 341 | 352 | 341 | 353 | 352 | 354 | 345 | 324 |  | 366 | 340 | 341 | 346 | 358 | 346 | 341 | 8463360
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5164050
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 107 | 109 | 127 | 159 | 148 | 150 | 149 | 131 | 110 | 104 | 102 | 98 | 98 | 98 | 95 | 95 | 95 | 98 |  | 96 | 98 | 98 | 99 | 99 | 102 | 105 | 258288
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 9 | 25 | 36 | 43 | 47 | 46 | 40 | 32 | 16 | 2 | 0 | [8 empty] | 298290
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 44 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1017720
46 | Shajibazar 330 MW CCPP | 120 | 118 | 117 | 120 | 120 | 119 | 120 | 118 | 120 | 121 | 120 | 122 | 120 | 120 | 119 | 119 | 121 | 121 |  | 120 | 120 | 120 | 121 | 120 | 120 | 120 | 2680000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 50 | 69 | 69 | 69 | 69 | 67 | 67 | 67 | 72 | 72 | 69 | 73 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1704960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 121 | 120 | 122 | 122 | 122 | 122 | 121 |  | 121 | 121 | 121 | 122 | 121 | 104 | 105 | 2868030
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 123120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 11 | 11 | 52 | 53 | 53 | 52 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1165800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 290832
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 270 | 300 | 295 | 320 | 295 | 310 | 290 | 290 | 300 | 310 | 280 | 290 | 300 | 310 | 300 | 300 |  | 310 | 300 | 300 | 300 | 310 | 290 | 280 | 7426000
| Bibiyana South 400 MW | 270 | 270 | 270 | 270 | 200 | 140 | 100 | 100 | 100 | 291 | 286 | 281 | 210 | 208 | 140 | 140 | 140 | [9 empty] | 3448400
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 20 |  | 45 | 55 | 55 | 17 |  |  |  | 191015
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 3 | 21 | 24 | 24 | 18 | 23 | 21 | 20 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 385680
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 18 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 466608
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465948
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524340
63 | Impoprt (Tripura) | 84 | 80 | 76 | 76 | 78 | 82 | 78 | 88 | 90 | 92 | 98 | 104 | 104 | 106 | 106 | 100 | 100 | 112 |  | 116 | 112 | 112 | 112 | 108 | 102 | 94 | 2294400
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 30 | 30 | 8 | 3 | 2 | 2 | 2 | 4 | 2 | 3 | 2 | 10 | 12 |  | 21 | 12 | 23 | 26 | 26 | 30 | 35 | 470400
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 443916
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 467800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 30 | 32 | 32 | 26 | 32 | 32 | 32 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 702360
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 623600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 25 | 25 | 25 | 25 | 321900
73 | Ghorashal 108MW PP (Regent) | 51 | 51 | 51 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 444318
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [7 empty] | 0 | 26 | 26 | 26 | 34 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 8 | 8 |  | 723240
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 0 | 0 | 2 | 38 | 108 | 144 | 144 | 144 | 144 | 131 | 144 | 144 | 128 | 126 | 144 | 144 |  | 144 | 144 | 144 | 144 | 134 | 144 | 144 | 2913120
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 4 | 16 | 16 | 16 | 30 | 50 | 24 | 24 | 24 | 24 | 30 |  | 100 | 100 | 100 | 100 | 84 | 36 |  | 705600
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | 16 | 0 |  |  | 0 | 32 | 40 | 32 | 32 | 16 | 16 | 16 | 16 | 16 |  | 32 | 40 | 120 |  | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 1249920
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 24 | 32 | 32 | 40 | 16 | 16 | 16 | 16 | 16 | 32 |  | 65 | 73 | 73 | 24 | 24 | 8 |  | 493440
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [17 empty] | 1 |  | 40 | 17 | [5 empty] | 71472
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 29400
| Jodiac Power | [17 empty] | 14 |  | 17 | 17 | 17 | 17 | 17 |  |  | 99832
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 15 | 15 | 0 | 0 | 1 | 19 | 65 | 75 | 99 | 99 | 99 | 99 | 64 | 64 | 64 | 64 | 64 |  | 97 | 101 | 101 | 101 | 99 | 64 | 30 | 1577736
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) |  |  |  |  | 0 | 1 | 14 | 24 | 25 | 25 | 25 | 31 | 37 | 50 | 49 | 41 | 38 | 38 |  | 38 | 38 | 38 | 47 | 58 | 60 | 61 | 734743
86 | Meghnaghat CCPP(Summit) | 270 | 260 | 255 | 260 | 300 | 280 | 285 | 285 | 270 | 270 | 295 | 270 | 250 | 245 | 255 | 260 | 270 | 285 |  | 275 | 265 | 275 | 265 | 275 | 315 | 250 | 6485498
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 6 |  | 38 | 50 | 50 | 50 | 7 | 7 |  | 179520
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 24 | 34 | 24 | 17 | 18 | 104 | 53 | 53 | 53 | 53 | 59 |  | 104 | 104 | 104 | 104 | 104 | 40 |  | 1005120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 5 | 10 |  | 10 | [6 empty] | 21600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 32 | 32 | 16 |  |  |  |  | 166896
95 | Patenga 50MW PP (Baraka) | [6 empty] | 6 | 34 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 48 | 45 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 828000
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 12 |  | 12 | [6 empty] | 24960
97 | katpotti 52 MW | [19 empty] | 6 | 6 | 6 | 6 |  |  |  | 22752
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 10 | 55 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 47 | 55 |  | 55 | 55 | 55 | 55 | 30 | 15 |  | 685439
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 |  |  |  | 323405
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3003382
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 54 | 35 | 35 | 35 | 53 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 17 |  |  | 548280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 195 | 130 | 110 | 40 | 40 | 62 | 103 | 166 | 195 | 195 | 195 | 185 | 194 | 160 | 130 | 130 | 139 | 173 |  | 200 | 200 | 200 | 200 | 200 | 192 | 170 | 3852000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 16 | 15 | 0 |  | 0 | 4 | 33 | 35 | 35 | 69 | 70 | 71 | 124 | 120 | 120 | 82 | 70 | 78 |  | 144 | 149 | 149 | 120 | 60 | 39 |  | 1502640
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 0 |  | 0 | 10 | 40 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1676160
116 | Chandpur 200MW (Desh energy) | 70 | 0 |  |  | 0 | 23 | 50 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1379520
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 341 | 340 | 341 | 341 | 338 | 341 | 341 | 338 | 337 | 381 |  | 430 | 428 | 427 | 425 | 421 | 425 | 418 | 8665000
| Jamalpur 115 MW PP (United) | [8 empty] | 4 | 8 | 8 | 14 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 |  |  |  |  | 152400
| Anwara 300 MW PP (United) | 306 | 224 | 161 | 125 | 125 | 176 | 232 | 251 | 252 | 253 | 252 | 252 | 253 | 252 | 252 | 252 | 252 | 252 |  | 302 | 305 | 306 | 306 | 306 | 306 | 306 | 5966618
| Juldah unit-2 (Acorn) | 50 | 0 |  | 0 | 10 | 88 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1923840
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | [9 empty] | 2 | 24 | 27 | 32 | 32 | 27 | 34 | 17 | [9 empty] | 198360
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 16 | 24 | 29 | 29 | 28 | 27 | 21 | 11 | 3 | [9 empty] | 199939
120 | Eastern Zone Total | 4909 | 4568 | 4437 | 4362 | 4268 | 4450 | 4765 | 5199 | 5477 | 5698 | 5769 | 5868 | 5979 | 5751 | 5565 | 5541 | 5531 | 5721 |  | 6415 | 6384 | 6329 | 6128 | 5914 | 5618 | 5223 | 129030741
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 4 | 27 |  | 115 | 59 | 16 |  |  |  |  | 165120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 17 | 53 | 35 | 35 | 70 | 70 | 70 | 70 | 35 | 35 | 48 |  | 95 | 95 | 95 | 95 | 53 | 17 |  | 959520
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 48 | 48 | 48 | 48 | 32 |  |  | 191328
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 73 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 33 | 55 | 53 | 56 | 55 | 57 | 55 | 53 | 55 | 56 |  | 85 | 85 | 85 | 86 | 87 | 87 | 87 | 1373368
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 25 | 23 | 23 | 22 | 21 | 22 | 22 | 19 | 17 | 18 | 17 | 20 | 14 | 14 | 14 | 12 | 18 | 22 |  | 25 | 25 | 26 | 26 | 25 | 24 | 25 | 485800
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 2 | 7 | 8 | 6 | 2 | 3 | 12 |  | 25 | 33 | 33 | 32 |  |  |  | 106240
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 539 | 539 | 538 | 538 | 538 | 738 | 823 | 824 | 823 | 824 | 823 | 824 | 824 | 823 | 824 | 823 | 824 | 823 |  | 846 | 848 | 848 | 847 | 848 | 847 | 847 | 18482909
147 | Bheramara 410 MW CCPP | 185 | 185 | 190 | 200 | 208 | 205 | 208 | 215 | 215 | 220 | 220 | 210 | 200 | 185 | 170 | 155 | 150 | 160 |  | 160 | 140 | 140 | 120 | 135 | 160 | 185 | 4590432
148 | Payra 1320 MW | 490 | 490 | 430 | 300 | 310 | 340 | 360 | 390 | 420 | 420 | 420 | 420 | 420 | 390 | 390 | 390 | 390 | 390 |  | 470 | 520 | 520 | 520 | 520 | 520 | 520 | 11188600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3681700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 167 | 177 | 181 | 188 | 171 | 171 | 174 | 172 | 167 | 168 | 168 | 171 | 206 | 183 | 160 | 149 | 142 | 139 |  | 143 | 143 | 141 | 139 | 139 | 140 | 149 | 4147436
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 334 | 333 | 345 | 360 | 365 | 390 | 370 | 361 | 329 | 336 | 358 | 331 | 318 | 373 | 415 | 357 | 285 | 336 |  | 404 | 388 | 386 | 323 | 300 | 270 | 270 | 8533000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 215352
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 12 | 12 |  |  |  |  | 35510
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 8 | 0
168 | Santahar 50 MW Peaking PP | [17 empty] | 17 |  | 19 | 8 | [5 empty] | 34110
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 8 |  | 52 | 52 | 52 | 24 |  |  |  | 144000
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 60 |  | 102 | 102 | 102 | 102 | 93 | 51 |  | 527008
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 29 | 90 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 81 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 1723872
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 35 | 80 | 113 | 70 | 70 | 100 | 113 | 70 | 70 | 70 | 70 | 90 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1539744
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 19 | 70 | 70 | 50 | 50 | 70 | 97 | 70 | 70 | 70 | 70 | 99 |  | 104 | 110 | 113 | 113 | 113 | 34 | 34 | 1296960
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 |  | 4 | 4 | 5 | 4 | 2 | 2 | 0 | [9 empty] | 32200
178
178