## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-02-27 | Saturday
|  | Date (day): | 2021-02-27 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13228.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14488 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-02-26 | 2021-02-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 |  |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 382 | 340 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 400 | 450 | 450 |  |  |  |  | 2021-10-02
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 260 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 64 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 28 | 84 | 60 | 84 |  | 16 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 92 | 93 | 100 | 100 |  |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 115 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 24 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 102 | 135 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 17 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 126 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 32 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 1863 | 2491 | 3914 | 4160 | 108 | 1414
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 50 | 46 | 46
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 85 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 36 | 40 | 20 | 30
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 250 | 251 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 536 | 646 | 1325 | 1360 | 895 | 115
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 218 | 203 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 300 | 300 | 60 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 225 | 240 | 285 | 285 | 75 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 40 | 40 | 15 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 92 | 96 | 96 |  | 67 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 28 | 68 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 126 | 135 | 147
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 20 | 0 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 991 | 1064 | 1680 | 1942 | 754 | 72
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 143 | 150 | 150 | 52 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 64 | 80 | 80 |  | 15 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 8 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 24 | 24
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 397 | 456 | 642.6 | 591 | 52 | 15
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 164 | 163 | 162 | 162 |  | 168 | under maint.
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 22 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 15 | 36 | 36 | 36 |  | 66 | Under maint
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 81 | 75 | 81 |  | 5 | Engine problem
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 163 | 163 | 163 |  | 68
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 324 | 316 | 350 | 350
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 5 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 300 | 300 | 300 | 300 |  |  | On Test
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1661 | 1604 | 1741 | 1747 | 0 | 433
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 708 | 802 | 636 | 846
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 340 | 410 | 410
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 90 | 90 |  | 15 | Engine problem
112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1008 | 1228 | 1526 | 2022 | 0 | 93
113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 29 | 26 | 26 |  | 7 | Engine problem
115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 41 | 49 | 95 | 95
117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 460 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 41 | 44 | 51 | 51 |  |  | On Test
118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 470 | 614 | 1052 | 1052 | 0 | 201
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 12 | 12 |  | 38 | Engine problem
123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 130 | 0 | 150 |  |  | FGMO
128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 332 | 400 | 400 |  |  | FGMO
129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 58 | 104 | 104
135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 645 | 779 | 1077 | 1351 | 651 | 38
138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 70 | 113 | 113
143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 184 | 220 | 271 | 263 | 124 | 210
| Total |  |  |  |  | 21395 | 20929 | 7755 | 9102 | 13228.6 | 14488 | 2584 | 2591
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7392.8955 | 8677 | 12610.9165 | 13811.5113
A. |  | 2021-02-26 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 9102 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6537 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9102 | MW
3 | Day peak Generation : |  |  | 7755 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8677 | MW
4 | Evening peak Generation : |  |  | 9102 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 185.2419 | MKWHr | By Solar | 0.62564 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 118.3893 | MKWHr |  | By Oil: | 30.9016 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.4859 | MKWHr |  | By Hydro: | 1.672 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2584 | MW | Dhaka | 2980 | 2980 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2591 | MW | Chittagong | 857 | 857 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 5175 | MW | Khulna | 1096 | 1096 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 913.09 | MMCFD |  |  | Rajshahi | 969 | 969 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121899155.014 | ii) Oil : | Taka | 181177284.47 | Comilla | 834 | 834 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 67362798 | Total | Taka | 370439237.484 | Mymensingh | 784 | 784 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.5755 | MKWHr. | Sylhet | 324 | 324 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -217 | MW (E to W) at | 19:30 | hrs | Barisal | 242 | 242 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -217 | MW at | 19:30 | hrs | Rangpur | 591 | 591 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 8677 | 8677 |  | 0
B. |  | 2021-02-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14488 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 4388 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 205.553 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6678 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0189 | MKWHr. | ii) HVDC Flow at Peak Time |  | 802 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1485 | MKWHr. | iii) Maximum HVDC Flow : |  | 803 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.94 |  | (b) Today: | 91.82 |  | (c) Rule Curve: |  | 93.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-02-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 340 | 0 |  | 0 | 420 | 285 | 0 | 30 | 0 | 0 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 31 | 0 | 0 | 0 | 275 | 220 | 203 | 0 | 92 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 94 | 108 | 0 | 20 | 0 | 0 | 43 | 50 | 0 | 130 | 161 | 0 | 81 | 0 | 162 | 19 | 0 | 5 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 38 | 0 | 10 | 34 | 0 | 315 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 126 | 0 | 0 | 0 | 0 |  | 613 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 162 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 49 | 0 | 0 |  | 5228 | 2296 | 7524 | 3478 | 613 | 1565 | 1059 | 629 | 70 | 16 | 94 | 0 | 0 | 91.96
2:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 339 | 0 |  | 0 | 420 | 265 | 0 | 15 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 31 | 0 | 0 | 0 | 275 | 220 | 206 | 0 | 93 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 94 | 158 | 0 | 20 | 0 | 0 | 43 | 50 | 0 | 130 | 162 | 0 | 81 | 0 | 162 | 19 | 0 | 5 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 95 | 0 | 30 | 0 | 10 | 17 | 0 | 319 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 10 | 300 | 0 | 0 | 53 | 0 | 0 | 0 | 0 |  | 613 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 163 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 49 | 0 | 0 |  | 4893 | 2231 | 7124 | 3534 | 613 | 1512 | 692 | 609 | 70 | 0 | 94 | 0 | 0 | 91.96
3:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 342 | 0 |  | 0 | 420 | 270 | 0 | 15 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 275 | 220 | 212 | 0 | 93 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 158 | 0 | 20 | 0 | 0 | 43 | 13 | 0 | 130 | 162 | 0 | 40 | 0 | 162 | 19 | 0 | 5 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 0 | 10 | 17 | 0 | 318 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 10 | 300 | 0 | 0 | 21 | 0 | 0 | 0 | 0 |  | 613 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 170 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 49 | 0 | 0 |  | 4793 | 2118 | 6911 | 3519 | 613 | 1435 | 635 | 549 | 70 | 0 | 90 | 0 | 0 | 91.95
4:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 339 | 0 |  | 0 | 380 | 260 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 0 | 0 | 0 | 275 | 220 | 214 | 0 | 94 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 138 | 0 | 20 | 0 | 0 | 43 | 13 | 0 | 110 | 161 | 0 | 10 | 0 | 162 | 19 | 0 | 5 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 0 | 10 | 17 | 0 | 319 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 10 | 300 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 613 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 169 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 49 | 0 | 0 |  | 4649 | 2084 | 6733 | 3466 | 613 | 1325 | 620 | 549 | 70 | 0 | 90 | 0 | 0 | 91.95
5:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 339 | 0 |  | 0 | 340 | 260 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 275 | 220 | 214 | 0 | 99 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 86 | 138 | 0 | 20 | 0 | 0 | 43 | 13 | 0 | 110 | 161 | 0 | 10 | 0 | 162 | 19 | 0 | 5 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 15 | 0 | 10 | 17 | 0 | 319 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 10 | 300 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 612 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 169 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 45 | 0 | 0 |  | 4587 | 1950 | 6537 | 3471 | 612 | 1249 | 600 | 449 | 70 | 0 | 86 | 0 | 0 | 91.94
6:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 378 | 0 |  | 0 | 225 | 300 | 0 | 15 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 275 | 220 | 221 | 0 | 96 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 86 | 157 | 0 | 20 | 0 | 0 | 30 | 50 | 0 | 163 | 161 | 0 | 78 | 0 | 162 | 19 | 0 | 5 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 79 | 0 | 15 | 0 | 40 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 0 | 23 | 0 | 0 | 0 | 0 |  | 613 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 175 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 47 | 0 | 0 |  | 4564 | 2152 | 6716 | 3295 | 613 | 1353 | 770 | 529 | 70 | 0 | 86 | 0 | 0 | 91.94
7:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 359 | 0 |  | 0 | 225 | 150 | 0 | 20 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 0 | 0 | 275 | 220 | 219 | 0 | 93 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 84 | 157 | 0 | 20 | 0 | 0 | 29 | 50 | 0 | 163 | 162 | 0 | 78 | 0 | 162 | 19 | 0 | 5 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 132 | 0 | 16 | 1 | 40 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 2 | 78 | 0 | 0 | 0 | 2 |  | 613 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 175 | 0 | 400 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 48 | 0 | 0 |  | 4536 | 2262 | 6798 | 3223 | 613 | 1383 | 871 | 549 | 70 | 0 | 84 | 5 | 0 | 91.93
8:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 344 | 0 |  | 0 | 225 | 150 | 0 | 48 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 35 | 0 | 0 | 0 | 275 | 220 | 223 | 0 | 91 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 70 | 161 | 0 | 20 | 1 | 0 | 29 | 50 | 0 | 163 | 162 | 0 | 78 | 0 | 163 | 19 | 0 | 5 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 46 | 2 | 70 | 17 | 0 | 70 | 0 | 0 | 0 | 1 | 270 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 11 | 126 | 0 | 0 | 0 | 5 |  | 707 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 175 | 0 | 359 | 0 | 0 | 111 | 0 | 50 | 0 | 1 | 20 | 430 | 49 | 0 | 0 |  | 4892 | 2470 | 7362 | 3336 | 707 | 1353 | 1225 | 580 | 70 | 0 | 70 | 21 | 0 | 91.93
9:00 | 0 | 0 | 0 | 100 | 300 | 12 | 0 | 338 | 0 |  | 0 | 225 | 150 | 0 | 48 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 35 | 0 | 0 | 0 | 275 | 220 | 225 | 0 | 92 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 64 | 140 | 0 | 20 | 1 | 0 | 29 | 50 | 0 | 163 | 161 | 0 | 78 | 0 | 163 | 18 | 0 | 5 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 93 | 3 | 70 | 17 | 0 | 80 | 0 | 0 | 0 | 2 | 255 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 22 | 126 | 0 | 0 | 0 | 17 |  | 707 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 174 | 0 | 284 | 0 | 0 | 113 | 0 | 49 | 0 | 0 | 35 | 400 | 37 | 0 | 0 |  | 4903 | 2349 | 7252 | 3241 | 707 | 1253 | 1306 | 550 | 70 | 16 | 64 | 45 | 0 | 91.92
10:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 341 | 0 |  | 0 | 225 | 270 | 0 | 30 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 0 | 275 | 220 | 224 | 0 | 91 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 60 | 107 | 8 | 20 | 2 | 0 | 29 | 46 | 0 | 130 | 161 | 0 | 47 | 0 | 162 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 93 | 8 | 20 | 17 | 0 | 231 | 5 | 0 | 0 | 4 | 189 | 0 | 0 | 0 | 0 | 70 | 300 | 0 | 31 | 54 | 0 | 0 | 0 | 26 |  | 708 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 140 | 0 | 311 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 350 | 48 | 0 | 0 |  | 4950 | 2213 | 7163 | 3410 | 708 | 1233 | 1111 | 500 | 70 | 0 | 60 | 71 | 0 | 91.92
11:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 343 | 0 |  | 0 | 225 | 285 | 0 | 30 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 0 | 0 | 275 | 220 | 221 | 0 | 94 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 58 | 104 | 24 | 20 | 2 | 0 | 29 | 48 | 0 | 130 | 160 | 0 | 50 | 0 | 162 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 102 | 16 | 20 | 17 | 0 | 240 | 8 | 8 | 0 | 4 | 178 | 0 | 0 | 0 | 0 | 70 | 300 | 0 | 41 | 54 | 0 | 0 | 0 | 30 |  | 707 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 140 | 0 | 333 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 350 | 43 | 0 | 0 |  | 4946 | 2218 | 7164 | 3369 | 707 | 1254 | 1113 | 500 | 70 | 0 | 58 | 93 | 0 | 91.91
12:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 382 | 0 |  | 0 | 225 | 275 | 0 | 30 | 0 | 0 | 0 | 92 | 0 | 0 | 32 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 36 | 0 | 0 | 0 | 275 | 225 | 218 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 20 | 20 | 70 | 102 | 24 | 17 | 2 | 0 | 43 | 48 | 0 | 163 | 164 | 15 | 72 | 0 | 162 | 18 | 0 | 5 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 102 | 17 | 50 | 28 | 0 | 324 | 8 | 17 | 0 | 4 | 250 | 0 | 0 | 0 | 0 | 90 | 300 | 0 | 44 | 54 | 0 | 0 | 0 | 32 |  | 708 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 143 | 0 | 401 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 370 | 41 | 0 | 0 |  | 5448 | 2307 | 7755 | 3588 | 708 | 1407 | 1261 | 520 | 70 | 32 | 70 | 99 | 0 | 91.91
13:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 343 | 0 |  | 0 | 300 | 235 | 0 | 35 | 0 | 0 | 0 | 57 | 5 | 0 | 32 | 40 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 15 | 18 | 42 | 0 | 0 | 0 | 275 | 240 | 221 | 0 | 91 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 84 | 102 | 24 | 17 | 2 | 0 | 43 | 50 | 0 | 130 | 162 | 35 | 81 | 0 | 162 | 18 | 0 | 5 | 280 | 16 | 11 | 0 | 21 | 0 | 0 | 200 | 0 | 102 | 16 | 50 | 60 | 0 | 341 | 8 | 17 | 0 | 4 | 250 | 0 | 0 | 0 | 0 | 100 | 300 | 6 | 43 | 87 | 0 | 0 | 0 | 30 |  | 707 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 150 | 0 | 297 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 420 | 39 | 0 | 0 |  | 5583 | 2266 | 7849 | 3571 | 707 | 1317 | 1403 | 570 | 70 | 32 | 84 | 95 | 7849 | 91.9
14:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 341 | 0 |  | 0 | 370 | 270 | 0 | 22 | 0 | 0 | 0 | 36 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 18 | 18 | 42 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 91 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 20 | 80 | 102 | 24 | 17 | 2 | 0 | 43 | 25 | 0 | 110 | 163 | 35 | 50 | 0 | 162 | 18 | 0 | 5 | 270 | 16 | 11 | 0 | 30 | 0 | 0 | 200 | 0 | 92 | 14 | 40 | 34 | 0 | 316 | 0 | 0 | 0 | 3 | 140 | 0 | 0 | 0 | 0 | 50 | 300 | 17 | 38 | 54 | 0 | 0 | 0 | 26 |  | 707 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 306 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 350 | 45 | 0 | 0 |  | 5227 | 2125 | 7352 | 3466 | 707 | 1317 | 1113 | 500 | 70 | 16 | 80 | 83 | 0 | 91.9
15:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 342 | 0 |  | 0 | 350 | 265 | 0 | 15 | 0 | 0 | 0 | 33 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 18 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 92 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 20 | 78 | 102 | 24 | 17 | 2 | 0 | 43 | 25 | 0 | 110 | 163 | 35 | 50 | 0 | 162 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 200 | 0 | 107 | 11 | 40 | 17 | 0 | 316 | 0 | 0 | 0 | 2 | 141 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 27 | 54 | 0 | 0 | 13 | 20 |  | 708 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 130 | 0 | 333 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 350 | 44 | 0 | 0 |  | 5182 | 2141 | 7323 | 3489 | 708 | 1339 | 1061 | 500 | 70 | 16 | 78 | 62 | 0 | 91.89
16:00 | 0 | 0 | 0 | 190 | 270 | 12 | 0 | 333 | 0 |  | 0 | 350 | 260 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 10 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 18 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 94 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 20 | 70 | 101 | 24 | 17 | 1 | 0 | 43 | 5 | 0 | 110 | 163 | 35 | 10 | 0 | 162 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 200 | 0 | 113 | 7 | 40 | 17 | 0 | 316 | 0 | 0 | 0 | 1 | 177 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 15 | 17 | 0 | 0 | 15 | 13 |  | 708 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 130 | 0 | 323 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 350 | 44 | 0 | 0 |  | 5021 | 2155 | 7176 | 3488 | 708 | 1268 | 1019 | 500 | 70 | 16 | 70 | 37 | 0 | 91.89
17:00 | 0 | 0 | 0 | 190 | 270 | 12 | 0 | 301 | 0 |  | 0 | 225 | 270 | 0 | 15 | 0 | 0 | 0 | 37 | 0 | 0 | 16 | 10 | 0 | 0 | 0 | 5 | 0 | 0 | 10 | 25 | 10 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 13 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 92 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 70 | 107 | 24 | 17 | 0 | 0 | 43 | 5 | 0 | 110 | 163 | 35 | 10 | 0 | 162 | 18 | 0 | 5 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 200 | 0 | 115 | 2 | 40 | 17 | 0 | 316 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 5 | 17 | 0 | 0 | 0 | 5 |  | 707 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 130 | 0 | 351 | 0 | 0 | 35 | 0 | 15 | 0 | 0 | 10 | 350 | 45 | 0 | 0 |  | 4867 | 2222 | 7089 | 3474 | 707 | 1186 | 1054 | 500 | 70 | 16 | 70 | 12 | 0 | 91.88
18:00 | 0 | 0 | 0 | 190 | 270 | 12 | 0 | 300 | 0 |  | 0 | 300 | 275 | 0 | 22 | 11 | 0 | 0 | 35 | 6 | 0 | 48 | 15 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 25 | 10 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 0 | 16 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 82 | 124 | 25 | 17 | 0 | 0 | 43 | 8 | 0 | 110 | 162 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 285 | 16 | 11 | 0 | 19 | 0 | 0 | 193 | 0 | 126 | 0 | 50 | 17 | 0 | 315 | 4 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 17 | 90 | 300 | 17 | 0 | 17 | 0 | 0 | 0 | 0 |  | 707 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 130 | 0 | 356 | 17 | 0 | 38 | 0 | 90 | 0 | 0 | 70 | 350 | 43 | 0 | 0 |  | 5239 | 2488 | 7727 | 3455 | 707 | 1333 | 1396 | 500 | 70 | 184 | 82 | 0 | 0 | 91.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 329 | 0 |  | 0 | 400 | 255 | 7 | 64 | 27 | 0 | 0 | 62 | 16 | 0 | 115 | 54 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 25 | 28 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 0 | 35 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 200 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 120 | 142 | 68 | 17 | 0 | 0 | 43 | 22 | 0 | 110 | 162 | 31 | 81 | 0 | 163 | 18 | 0 | 5 | 280 | 16 | 11 | 0 | 136 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 49 | 0 | 316 | 8 | 17 | 0 | 0 | 251 | 0 | 0 | 0 | 17 | 100 | 300 | 44 | 0 | 108 | 0 | 0 | 0 | 0 |  | 803 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 314 | 105 | 0 | 106 | 0 | 113 | 0 | 0 | 113 | 400 | 43 | 0 | 0 |  | 6136 | 2849 | 8985 | 3573 | 803 | 1402 | 2203 | 550 | 70 | 264 | 120 | 0 | 0 | 91.86
19:30 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 340 | 0 |  | 0 | 400 | 260 | 0 | 64 | 0 | 0 | 0 | 93 | 0 | 0 | 115 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 50 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 203 | 0 | 92 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 126 | 143 | 64 | 17 | 0 | 0 | 43 | 22 | 0 | 130 | 163 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 135 | 0 | 100 | 68 | 0 | 316 | 8 | 17 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 17 | 0 | 126 | 0 | 0 | 0 | 0 |  | 802 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 130 | 0 | 332 | 70 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 460 | 44 | 0 | 0 |  | 6261 | 2841 | 9102 | 3639 | 802 | 1471 | 2194 | 610 | 70 | 190 | 126 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 342 | 0 |  | 0 | 400 | 275 | 0 | 64 | 0 | 0 | 0 | 92 | 0 | 0 | 115 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 17 | 0 | 0 | 50 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 219 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 126 | 142 | 40 | 17 | 0 | 0 | 43 | 22 | 0 | 163 | 162 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 305 | 16 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 115 | 0 | 100 | 68 | 0 | 316 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 20 | 0 | 126 | 0 | 0 | 0 | 0 |  | 803 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 130 | 0 | 360 | 70 | 0 | 113 | 0 | 70 | 0 | 0 | 70 | 470 | 45 | 0 | 0 |  | 6218 | 2846 | 9064 | 3658 | 803 | 1546 | 2051 | 620 | 70 | 190 | 126 | 0 | 0 | 91.87
21:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 351 | 0 |  | 0 | 400 | 285 | 0 | 64 | 0 | 0 | 0 | 92 | 0 | 0 | 82 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 17 | 0 | 0 | 50 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 216 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 128 | 143 | 16 | 17 | 0 | 0 | 43 | 22 | 0 | 163 | 161 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 315 | 16 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 53 | 0 | 100 | 68 | 0 | 327 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 100 | 300 | 17 | 0 | 144 | 0 | 0 | 0 | 0 |  | 803 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 130 | 0 | 358 | 70 | 0 | 113 | 0 | 70 | 0 | 0 | 70 | 510 | 49 | 0 | 0 |  | 6155 | 2868 | 9023 | 3667 | 803 | 1562 | 1976 | 660 | 70 | 157 | 128 | 0 | 0 | 91.86
22:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 350 | 0 |  | 0 | 430 | 280 | 0 | 48 | 0 | 0 | 0 | 92 | 0 | 0 | 82 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 31 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 0 | 0 | 18 | 18 | 38 | 0 | 0 | 0 | 275 | 240 | 208 | 0 | 94 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 126 | 144 | 16 | 17 | 0 | 0 | 43 | 22 | 0 | 163 | 163 | 31 | 81 | 0 | 163 | 18 | 0 | 5 | 305 | 16 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 50 | 0 | 100 | 68 | 0 | 327 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 803 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 130 | 0 | 359 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 520 | 49 | 0 | 0 |  | 5971 | 2696 | 8667 | 3646 | 803 | 1580 | 1640 | 670 | 70 | 132 | 126 | 0 | 0 | 91.86
23:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 347 | 0 |  | 0 | 430 | 285 | 0 | 30 | 0 | 0 | 0 | 85 | 0 | 0 | 62 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 31 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 38 | 0 | 0 | 0 | 275 | 240 | 197 | 0 | 93 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 120 | 144 | 0 | 14 | 0 | 0 | 43 | 22 | 0 | 163 | 163 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 305 | 16 | 11 | 0 | 85 | 0 | 0 | 200 | 0 | 50 | 0 | 100 | 68 | 0 | 328 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 803 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 130 | 0 | 346 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 490 | 49 | 0 | 0 |  | 5853 | 2462 | 8315 | 3627 | 803 | 1565 | 1428 | 640 | 70 | 62 | 120 | 0 | 0 | 91.85
24:00 | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 348 | 0 |  | 0 | 430 | 265 | 0 | 15 | 0 | 0 | 0 | 62 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 0 | 0 | 275 | 240 | 190 | 0 | 94 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 112 | 144 | 0 | 14 | 0 | 0 | 43 | 22 | 0 | 130 | 162 | 37 | 81 | 0 | 162 | 18 | 0 | 5 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 40 | 0 | 30 | 68 | 0 | 328 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 0 | 144 | 0 | 0 | 0 | 0 |  | 803 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 130 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 49 | 0 | 0 |  | 5474 | 2384 | 7858 | 3587 | 803 | 1501 | 1113 | 640 | 70 | 32 | 112 | 0 | 0 | 91.85
KWH | 0 | 0 | 0 | 3811500 | 7153791 | 296909 | 0 | 8329220 | 0 |  | 0 | 7851250 | 5996393 | 8640 | 838200 | 47692 | 0 | 0 | 1442000 | 0 | 0 | 684000 | 730846 | 0 | 0 | 0 | 112680 | 0 | 0 | 251100 | 600000 | 547020 | 649000 | 585800 | 0 | 0 | 0 | 1672000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199200 | 0 | 130864 | 0 | 0 | 311520 | 410880 | 879840 | 0 | 0 | 0 | 6929500 | 5662000 | 5088000 | 0 | 2211940 | 285480 | 140160 | 0 | 0 | 0 | 0 | 0 | 512964 | 214920 | 557700 | 498540 | 2148480 | 3027720 | 390720 | 403056 | 13650 | 0 | 952920 | 732000 | 0 | 3419263 | 3753000 | 415584 | 1420800 | 0 | 3910700 | 421000 | 0 | 123300 | 7322500 | 386352 | 264000 | 0 | 870654 | 0 | 0 | 4207200 | 0 | 1707264 | 97065 | 1230720 | 838560 | 0 | 6193000 | 55200 | 84744 | 0 | 26520 | 5394545 | 0 | 0 | 0 | 46200 | 1607040 | 7218700 | 148800 | 280080 | 1903680 | 0 | 0 | 42480 | 207417 |  | 17018909 | 0 | 7870176 | 0 | 31680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496272 | 124512 | 0 | 0 | 0 | 1613 | 0 | 306328 | 0 | 0 | 0 | 0 | 0 | 492960 | 0 | 235062 | 0 | 0 | 3659900 | 0 | 0 | 0 | 0 | 0 | 0 | 1087582 | 0 | 3847809 | 0 | 8359454 | 360960 | 0 | 1207104 | 0 | 652800 | 0 | 912 | 628800 | 10826000 | 1126582 | 0 | 0 |  | 126906463 | 58335415 | 185241878 | 84640434 | 17018909 | 33748872 | 29778834 | 14485900 | 1672000 | 1122805 | 2148480 | 625644 | 0
Fuel Cost | 0 | 0 | 0 | 5602905 | 7940708.01 | 391919.88 | 0 | 8412512.2 | 0 |  | 0 | 8557862.5 | 6655996.23 | 65577.6 | 5775198 | 403474.32 | 0 | 0 | 2494660 | 0 | 0 | 6730560 | 6738400.12 | 0 | 0 | 0 | 822564 | 0 | 0 | 188325 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 451440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1269380.8 | 0 | 0 | 2467238.4 | 517708.8 | 2613124.8 | 0 | 0 | 0 | 5127830 | 5662000 | 4680960 | 0 | 2543731 | 322592.4 | 196224 | 0 | 0 | 0 | 0 | 0 | 651464.28 | 161190 | 975975 | 373905 | 16113600 | 3209383.2 | 3547737.6 | 511881.12 | 217581 | 0 | 1524672 | 1302960 | 0 | 3897959.82 | 3903120 | 818700.48 | 2713728 | 0 | 6765511 | 921990 | 0 | 251532 | 7395725 | 289764 | 200640 | 0 | 6582144.24 | 0 | 0 | 21877440 | 0 | 16799477.76 | 1134689.85 | 10030368 | 9098376 | 0 | 5759490 | 503424 | 800830.8 | 0 | 0 | 40782760.2 | 0 | 0 | 0 | 395934 | 10702886.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98028915.84 | 0 | 8263684.8 | 0 | 249004.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769221.6 | 1215237.12 | 0 | 0 | 0 | 15871.92 | 0 | 2711002.8 | 0 | 0 | 0 | 0 | 0 | 946483.2 | 0 | 177941.934 | 0 | 0 | 19836658 | 0 | 0 | 0 | 0 | 0 | 0 | 1631373 | 0 | 4501936.53 | 0 | 8275859.46 | 3768422.4 | 0 | 11455416.96 | 0 | 5065728 | 0 | 10077.6 | 4646832 | 47526140 | 0 | 0 | 0 |  | 267299733.81 | 219095807.964 | 486395541.774 | 82955181.754 | 98028915.84 | 38943973.26 | 170450468.95 | 67362798 | 451440 | 10726815.52 | 16113600 | 1362348.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 382 | 0 |  | 0 | 225 | 275 | 0 | 30 | 0 | 0 | 0 | 92 | 0 | 0 | 32 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 36 | 0 | 0 | 0 | 275 | 225 | 218 | 0 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 20 | 20 | 70 | 102 | 24 | 17 | 2 | 0 | 43 | 48 | 0 | 163 | 164 | 15 | 72 | 0 | 162 | 18 | 0 | 5 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 102 | 17 | 50 | 28 | 0 | 324 | 8 | 17 | 0 | 4 | 250 | 0 | 0 | 0 | 0 | 90 | 300 | 0 | 44 | 54 | 0 | 0 | 0 | 32 |  | 708 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 143 | 0 | 401 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 370 | 41 | 0 | 0 |  | 7755 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 340 | 0 | 0 | 0 | 400 | 260 | 0 | 64 | 0 | 0 | 0 | 93 | 0 | 0 | 115 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 50 | 18 | 40 | 0 | 0 | 0 | 275 | 240 | 203 | 0 | 92 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 126 | 143 | 64 | 17 | 0 | 0 | 43 | 22 | 0 | 130 | 163 | 36 | 81 | 0 | 163 | 18 | 0 | 5 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 135 | 0 | 100 | 68 | 0 | 316 | 8 | 17 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 100 | 300 | 17 | 0 | 126 | 0 | 0 | 0 | 0 |  | 802 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 130 | 0 | 332 | 70 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 460 | 44 | 0 | 0 |  | 9102 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 102 | 149 | 84 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 |  | 85 | 100 | 102 | 46 | 22 | 30 | 0 | 0 | 0 | 300 | 285 | 225 | 8 | 96 | 26 | 40 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 147 | 150 | 80 | 22 | 0 | 0 | 43 | 51 | 0 | 163 | 162 | 36 | 81 | 0 | 163 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 104 | 0 | 144 | 116 | 0 |  |  |  | 846 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 150 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 51 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 300 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 149 | 60 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 |  | 85 | 100 | 102 | 46 | 22 | 20 | 0 | 0 | 0 | 300 | 285 | 225 | 8 | 96 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 135 | 150 | 80 | 22 | 1.6 | 0 | 43 | 51 | 0 | 163 | 162 | 36 | 75 | 0 | 163 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 104 | 50 | 144 | 116 | 0 |  | 30 |  | 636 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 51 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 270 | 12 | 0 | 292 | 0 | 0 | 0 | 300 | 285 | 0 | 30 | 15 | 0 | 0 | 60 | 0 | 0 | 32 | 55 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 2 | 0 | 0 | 0 | 275 | 240 | 223 | 0 | 96 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 88 | 147 | 11 | 17 | 1 | 0 | 43 | 22 | 0 | 110 | 161 | 36 | 50 | 0 | 162 | 0 | 0 | 5 | 290 | 16 | 0 | 0 | 142 | 0 | 0 | 190 | 0 | 130 | 0 | 80 | 22 | 0 | 351 | 0 | 17 | 0 | 1 | 287 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 8 | 79 | 0 | 0 | 0 | 6 | 0 | 643 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 22 | 0 | 345 | 0 | 0 | 39 | 0 | 35 | 0 | 1 | 35 | 300 | 49 | 0 | 0 | 0
199
| Minimum Generation |  | 6537 | 5:00
| Highest Generation |  | 9102 | 19:30
| Day Peak Generation |  | 7755 | 12:00
| Evening Peak Generation |  | 9102 | 19:30
| HVDC Max Flow |  | 803 | 19:00
| HVDC EvPeak Flow |  | 802 | 19:30
| Load factor L.F |  | 84.8%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-02-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-02-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7755 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6678 | MW
Evening Peak Generation : |  | 9102 | MW Hour : | 19:30 | Available Max Generation : |  | 14488 | MW
E.P. Demand (at gen end) : |  | 9102 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10100 | MW
Maximum Generation : |  | 9102 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4388 | MW
Total Gen. (MKWH) : |  | 185.2419 | System Load Factor : | 84.8% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -217 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-02-27
Actual : | 91.82 | Ft.(MSL) , | Rule curve : | 93.3 | Ft.( MSL )
Gas Consumed : | Total = | 913.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 121899155.014
: |  | Coal : | 67362798 | Oil : | 181177284.47 | Total : | 370439237.484
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3589.913 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1218.1734 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1090.9805 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 985.6286 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 890.7889 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 718.8286 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 405.2739 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 185.1674 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 554.3803 |  |  | 0 | 0%
Total | 0 |  | 9639.1346 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Kaptai-2
5) Raozan #1,2
6) Siddirganj-335 MW
7) Sirajganj #1CCPP
8) Haripur 360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) B.Baria-Narshindi 132 kV Ckt-2 was under shut down from 09:09 to 17:29 for A/M.
b) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 09:30 to 17:40 for A/M.
c) Kabirpur-Tongi 132 kV Ckt-2 was under shut down from 10:00 to for C/M.
d) Ashuganj-Ghorasal 132 kV Ckt-1 was under shut down from 12:15 to 15:13 for A/M.
e) Haripur-Haripur HPL P/P 230 kV Ckt-1& 2 were shut down at 09:52 for HPL work.
f) Bibiyana unit-3 was synchronized at 09:37.
g) Kishoreganj 132/33 kV T-1 transformer was under shut down from 08:42 to 09:40 for D/W.
h) Hathazari 230 kV Bus-1 was under shut down from 09:08 to 16:38 for D/W.
i) Hathazari 230/132 kV T-03 transformer was under shut down from 11:10 to 15:30 for D/W.
j) Meghnaghat 450 MW CCPP GT-2 was synchronized at 12:21.
k) Barullia 132/33 kV T-1 transformer was under shut down from 09:05 to 11:53 for D/W.
l) Barullia 132/33 kV T-2 transformer was under shut down from 12:00 to 14:10 for D/W.
m) Kabirpur 132/33 kV T-2 transformer was under shut down from 07:32 to 09:10 for C/M.
n) Feni 132/33 kV T-2 transformer was under shut down from 07:17 to 09:49 for PBS work. |  |  |  |  | About 12 MW power interruption occurred under Feni S/S area
from 07:17 to 09:49.
o) Gopalganj(Old)-Gopalganj 100 MW P/P 132 kV Ckt was under shut down from 10:58 to 17:56
for D/W.
p) Summit Meghnaghat 305 MW CCPP GT-2 was synchronized at 09:06.
q) Meghnaghat 450 MW CCPP GT-2 tripped at 16:23 due to burner problem and was synchronized
at 17:40.
r) Matuail 132/33 kV T2 transformer was switched on at 20:11.
s) Ishurdi-Ghorasal 230 kV Ckt-2 tripped at 01:05(27-02-2021) showing Dist. Relay at Ishurdi end
and was switched on at 01:37(27-02-2021).
t) Shyampur-APR 230 kV Ckt tripped at 01:37(27-02-2021) showing O/C, E/F realy at APR end
and was switched on at 01:56(27-02-2021).
u) Hasnabad-APR 230 kV Ckt tripped at 01:37(27-02-2021) showing O/C, E/F realy at APR end
and Dist. Z1 realy at Hasnabad end.
v) Sirajganj unit-3 STG was shut down at 06:47(27-02-2021).
w) Kaliakoir 400/132 kV T-01 transformer was shut down at 06:32(27/02/2021) for C/M.
x) Mymensing 132/33 kV T-1 & T2 transformer were shut down at 07:10(27/02/2021) for C/M. |  |  |  |  | About 90 MW power interruption occurred under Mymensing S/S
area from 07:10(27-02-2021) to till.
y) Sikalbaha-TK Chemical 132 kV Ckt was shut down at 07:00(27-02-2021) for D/W.
z) Gopalganj(Old)-Gollamari 132 kV Ckt-2 was switched on at 22:08(27-02-2021).
for D/W.
aa) Shahjadpur 132/33 kV T-3 transformer tripped at 03:29(27/02/2021) showing no relay and was
switched on at 04:54(27-02-2021).
ab) Shahjadpur 132/33 kV T-2 transformer tripped at 03:29(27/02/2021) showing E/F relay and was |  |  |  |  | About 06 MW power interruption occurred under Shahjadpur S/S
switched on at 04:33(27-02-2021). |  |  |  |  | area from 03:29(27-02-2021) to 04:33(27-02-2021).
ac) Sylhet-Chatak 132 kV Ckt tripped at 07:33(27/02/2021) showing Dist. Z1 C-Phase relay at Sylhet
end and was switched on at 07:55(27-02-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-02-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 3811500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7153791
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 296909 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8329220 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 7851250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 8640 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 5996393 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 838200 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 47692
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 84 | 730846 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 251100
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 93 | 1442000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 112680 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 684000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1147020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 649000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 585800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 870654 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 1707264 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 84744 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 148800 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1903680 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 207417
| Dhaka area Total |  |  |  | 5972 | 2491 | 44858600
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 97065
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 311520
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1672000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 130864 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1230720
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 410880 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 879840
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26520
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 251 | 5394545
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1607040
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 646 | 11760994
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 5088000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6929500 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5662000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 285480 | Macine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 140160 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve.
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2211940 | Macine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 68 | 838560 | Low demand
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512964
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 214920 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2148480
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 557700 | Engine problem
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 498540
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 46200 | Reserve.
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 42480
| Cumilla Area Total |  |  |  | 2980 | 1064 | 25176924
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 143 | 3027720 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 403056 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 64 | 390720 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13650
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4207200 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 55200 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 280080
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 199200
| Mymensingh Area Total |  |  |  | 709 | 456 | 8576826
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Under Shut down
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 952920 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3419263 | Frequency Control.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 163 | 3753000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 732000 | High Voltage.
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 36 | 415584 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1420800
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 3910700 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 386352 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7322500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 6193000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 5 | 123300 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 300 | 7218700 | On Test
| Sylhet Area Total |  |  |  | 1988 | 1604 | 36533119
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 802 | 17018909
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 31680 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7870176 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 360960 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1228 | 25281725
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 124512 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 496272
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 49 | 1087582 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 460 | 10826000 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 44 | 1126582
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 614 | 13660948
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 1613 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3847809 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 332 | 8359454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 492960
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235062
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 58 | 306328 | Low demand
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1207104
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 628800
| Rajshahi Area Total |  |  |  | 2183 | 779 | 15079130
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3659900 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 652800 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 912
| Rangpur Area Total |  |  |  | 605 | 220 | 4313612
| Total |  |  |  | 20929 | 9102 | 185241878
| Eastern Grid Total |  |  |  | 14031 | 6261 | 126906463
| Western Grid Total |  |  |  | 6898 | 2841 | 58335415
| National Grid Total |  |  |  | 20929 | 9102 | 185241878
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-02-26
(a) ENTIRE EASTERN GRID : |  | 5779 | MW | (b) ENTIRE WESTERN GRID : |  | 2898 | MW
i) Dhaka area |  | 2980 | MW | i) Khulna area |  | 1096 | MW
ii) Chittagong area |  | 857 | MW | ii) Rajshahi area |  | 969 | MW
iii) Comilla area |  | 834 | MW | iii) Barisal area |  | 242 | MW
iv) Mymensingh area |  | 784 | MW | iv) Rangpur area |  | 591 | MW
v) Sylhet area |  | 324 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8677 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 96 | 23:00 | Netrokona | 99 | 18:30 | Jessore | 95 | 19:00
Munsiganj | 86 | 21:00 | Jamalpur | 106 | 8:00 | Benapol | 42 | 19:00
Sonargaon | 67 | 22:00 | Sherpur | 100 | 18:30 | Jhenida | 90 | 19:00
Shyampur | 166 | 7:00 | Srimongal | 31 | 20:00 | Bottail | 82 | 19:00
Bhulta | 177 | 1:00 | Shahjibazar | 87 | 20:00 | G.K Project | 36 | 18:30
Madanganj | 46 | 9:00 | Fenchuganj | 25 | 18:30 | Faridpur | 122 | 19:00
Shitalakhya | 85 | 1:00 | Kulawara | 27 | 18:00 | Madaripur | 67 | 20:00
Rahim steel | 4 | 6:00 | Sylhet | 74 | 18:00 | Sariatpur | 44 | 19:30
Matuail | 66 | 0:00 | Chatak | 19 | 19:30 | Gopalganj | 63 | 19:00
Ghorasal | 60 | 12:00 | Sunamganj | 30 | 19:30 | Bagerhat | 85 | 19:00
Narsingdi | 129 | 21:00 | Biani Bazar | 39 | 19:30 | Mongla | 30 | 1:00
Haripur (SBU) | 77 | 2:00 | Comilla (S) | 128 | 21:00 | Satkhira | 79 | 19:30
Sreenagar |  |  | Comilla(N) | 86 | 19:30 | Gallamari | 22 | 13:00
Ullon | 64 | 19:00 | Chandpur | 46 | 19:00 | Magura | 40 | 18:30
Hasnabad | 75 | 22:00 | Feni | 86 | 18:30 | Norail | 26 | 19:00
Magbazar | 59 | 20:00 | Chowmuhani | 128 | 20:00 | Chuadanga | 68 | 19:00
Maniknagar | 51 | 20:00 | Ashuganj | 44 | 22:00 | Borguna | 12 | 18:30
Bangabhaban | 8 | 19:00 | Daudkandi | 84 | 21:00 | Barisal(N) | 30 | 20:00
Narinda | 54 | 20:00 | B.Baria | 116 | 21:00 | Barisal (S) | 78 | 20:00
Dhanmondi | 105 | 19:00 | Ramganj | 60 | 19:30 | Patuakhali | 81 | 23:00
Lalbag | 60 | 1:00 | Chaddagram | 26 | 20:00 | Bhandaria | 38 | 20:00
Madartek | 58 | 21:00 | PHP | 10 | 10:00 | Borhan Uddin | 27 | 20:00
Dhaka University | 0 | #NUM! | Kochua | 45 | 18:30 | Ishurdi | 42 | 19:00
Aftabnagar | 7 | 12:00 | Madunaghat | 49 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Fatullah | 44 | 1:00 | Hathazari | 59 | 19:30 | Natore | 101 | 19:00
Nawabganj | 34 | 19:30 | Khulshi | 139 | 12:00 | Bogra | 125 | 19:00
Mirpur | 78 | 21:00 | Halishahar | 101 | 18:30 | Noagaon | 92 | 8:00
Kalyanpur | 66 | 18:30 | Baraulia | 158 | 1:00 | Rajshahi | 94 | 19:30
Gulshan | 76 | 18:30 | Sikalbaha | 21 | 20:00 | Rajshahi New | 15 | 19:30
Uttara | 63 | 18:30 | Dohazari | 63 | 19:00 | C.Nawabganj | 62 | 8:00
Uttara New | 14 | 12:00 | Cox'sbazar | 82 | 18:30 | Amnura | 44 | 18:00
Kamrangirchar | 65 | 18:30 | Chandraghona | 24 | 18:30 | Pabna | 64 | 19:00
Savar | 89 | 18:30 | Kaptai | 0 | 0:00 | Shahjadpur | 74 | 7:00
Bhasantec | 113 | 19:30 | A. Khaer Stl. | 0 | 0:00 | Serajganj | 69 | 19:30
Agargaon | 50 | 19:00 | Bakulia | 71 | 19:00 | Niyamatpur | 71 | 8:00
Satmosjid | 74 | 19:00 | Julda | 17 | 1:00 | Joypurhat | 54 | 19:00
Tongi | 96 | 18:00 | TK chemical | 21 | 18:30 | Sherpur(Bogura) | 46 | 18:30
Kabirpur | 147 | 18:30 | Modern Steel | 0 | #N/A | Mohastangor | 40 | 19:00
Basundhara | 110 | 18:30 | Shahmirpur | 15 | 1:00 | Bangura | 20 | 18:30
Manikganj | 74 | 19:00 | Khagrachhari | 20 | 6:00 | Rangpur | 115 | 19:00
Joydevpur | 101 | 13:00 | Matarbari | 29 | 19:30 | Lalmonirhat | 44 | 18:30
New Tongi | 61 | 11:00 | Baroiar Hat | 26 | 19:30 | Saidpur | 102 | 9:00
Korda | 138 | 16:00 | Rangamati | 10 | 18:30 | Purbasadipur | 88 | 9:00
Dhamrai | 50 | 8:00 | Abul Khair 230 | 151 | 8:00 | Thakurgaon | 56 | 8:00
Rajendrapur | 60 | 19:30 | BSRM | 150 | 15:00 | Palashbari | 97 | 7:00
Valuka | 70 | 18:30 | GPH Ispat | 10 | 5:00 | Barapukuria | 45 | 8:00
Tangail | 176 | 7:00 | Goalpara | 12 | 13:00 | Panchagar | 44 | 20:00
Mymensing | 179 | 18:30 | Central s/s | 81 | 19:00 | Joldhaka | 16 | 8:00
Kishorganj | 100 | 18:30 | Noapara | 46 | 19:00 | Kurigram | 50 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-02-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 6:00 | 404 | 2:00 | Kaliakoir | 403 | 0.20833 | 391 | 0.5
| Bheramara | 407 | 9:00 | 393 | 10:00 | Bhulta | 397 | 0.25 | 382 | 0.5
| Ashuganj(N) | 400 | 19:00 | 386 | 12:00 | Gopalganj | 409 | 0.625 | 392 | 0.91667
| Payra | 410 | 6:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 236 | 1:00 | Hathazari | 233 | 8:00 | 215 | 11:00
| Ishurdi | 240 | 5:00 | 229 | 18:00 | Megnaghat | 240 | 10:00 | 234 | 16:00
| Ashuganj | 242 | 18:30 | 233 | 12:00 | Fenchuganj | 243 | 8:00 | 238 | 15:00
| Serajganj | 232 | 5:00 | 229 | 12:00 | Siddhirganj | 237 | 8:00 | 231 | 12:00
| Baghabari | 238 | 2:00 | 228 | 7:00 | Maniknagar | 236 | 8:00 | 229 | 15:00
| Barapukuria | 236 | 5:00 | 224 | 8:00 | Agargaon | 236 | 6:00 | 223 | 17:00
| Bogra | 236 | 13:00 | 228 | 8:00 | Barisal | 251 | 9:00 | 243 | 19:00
| Rajshahi | 237 | 18:00 | 228 | 8:00 | Bhola 225 MW | 251 | 5:00 | 244 | 18:30
| Khulna South | 243 | 5:00 | 226 | 12:00 | AKSML | 236 | 9:00 | 214 | 14:00
| Rampura | 233 | 5:00 | 229 | 11:00 | BSRM | 235 | 9:00 | 215 | 15:00
| Haripur | 235 | 7:00 | 229 | 12:00 | Bibiyana | 244 | 9:00 | 238 | 19:30
| Hasnabad | 238 | 19:00 | 225 | 11:00 | Bhulta | 240 | 9:00 | 230 | 15:00
| Shyampur | 237 | 6:00 | 220 | 12:00 | Ashuganj (S) | 239 | 18:00 | 234 | 23:00
| Aminbazar | 236 | 8:00 | 228 | 15:00 | Kaliakoir | 236 | 18:30 | 228 | 12:00
| Tongi | 232 | 18:00 | 223 | 11:00 | GPH | 233 | 9:00 | 214 | 2:00
| Comilla (N) | 235 | 9:00 | 227 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 6:00 | 133 | 12:00 | Madanhat | 137 | 0.33333 | 127 | 0.625
| Munsiganj | 137 | 18:30 | 133 | 1:00 | Hathazari | 137 | 0.33333 | 128 | 0.58333
| Sonargaon | 135 | 6:00 | 131 | 12:00 | Khulshi | 1216 | 0.58333 | 125 | 0.45833
| Shyampur | 135 | 6:00 | 129 | 12:00 | Halishahar | 138 | 0.375 | 127 | 0.58333
| Bhulta | 132 | 18:30 | 126 | 16:00 | Baraulia | 138 | 0.25 | 128 | 0.45833
| Madanganj | 137 | 19:00 | 131 | 1:00 | Sikalbaha | 137 | 0.25 | 127 | 0.45833
| Shitalakhya | 135 | 18:30 | 124 | 12:00 | Dohazari | 136 | 0.375 | 125 | 0.58333
| Rahim steal | 137 | 19:00 | 133 | 12:00 | Cox'sbazar | 131 | 0.375 | 118 | 0.70833
| Matuail | 138 | 6:00 | 133 | 12:00 | Chandraghona | 138 | 0.375 | 125 | 0.45833
| Ghorasal | 136 | 1:00 | 136 | 1:00 | Kaptai | 0 | #N/A | 0 | #N/A
| Narsinghdi | 136 | 9:00 | 129 | 0:00 | A. Khaer Stl. | 134 | 0.77083 | 128 | 0.375
| Haripur (SBU) | 137 | 19:30 | 133 | 15:00 | Bakulia | 136 | 0.20833 | 126 | 0.45833
| Sreenagar |  |  |  |  | Julda | 137 | 0.77083 | 127 | 0.45833
| Ullon | 134 | 2:00 | 125 | 12:00 | TK Chemical | 136 | 0.20833 | 130 | 0.45833
| Hasnabad | 133 | 19:00 | 125 | 15:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 133 | 8:00 | 125 | 12:00 | Shahmirpur | 137 | 0.29167 | 127 | 0.58333
| Maniknagar | 137 | 10:00 | 133 | 15:00 | Khagrachhari | 136 | 0.25 | 126 | 0.625
| Bangabhaban | 137 | 10:00 | 133 | 15:00 | Matarbari | 133 | 0.375 | 120 | 0.58333
| Narinda | 137 | 10:00 | 133 | 15:00 | Baroiar Hat | 137 | 0.29167 | 131 | 0.41667
| Dhanmondi | 134 | 2:00 | 125 | 12:00 | Rangamati | 135 | 0.33333 | 125 | 0.625
| Lalbag | 134 | 9:00 | 126 | 12:00 | Goalpara S/S | 138 | 3:00 | 128 | 12:00
| Madartek | 134 | 6:00 | 125 | 12:00 | Khulna Central S/S | 138 | 5:00 | 128 | 12:00
| Dhaka University |  |  |  |  | Noapara | 138 | 4:00 | 127 | 0.5
| Aftabnagar | 133 | 6:00 | 125 | 11:00 | Jessore | 135 | 6:00 | 124 | 0.5
| Fatullah | 134 | 6:00 | 129 | 24:00 | Benapol | 137 | 4:00 | 125 | 0.5
| Nawabganj | 132 | 6:00 | 125 | 12:00 | Jhenida | 135 | 5:00 | 124 | 0.875
| Mirpur | 137 | 8:00 | 130 | 15:00 | Bottail | 137 | 0.20833 | 130 | 0.5
| Kalyanpur | 138 | 8:00 | 132 | 12:00 | G.K Project | 141 | 4:00 | 137 | 0.5
| Gulshan | 133 | 6:00 | 124 | 12:00 | Faridpur | 139 | 0.20833 | 134 | 0.875
| Uttara | 136 | 19:00 | 131 | 24:00 | Madaripur | 143 | 0.25 | 135 | 0.875
| Uttara New | 137 | 19:00 | 131 | 24:00 | Shariyatpur S/S | 142 | 0.125 | 135 | 0.875
| Kamrangirchar | 130 | 18:30 | 125 | 12:00 | Gopalganj | 144 | 0.16667 | 137 | 0.875
| Savar | 139 | 9:00 | 130 | 12:00 | Bagerhat | 135 | 4:00 | 125 | 0.45833
| Bhasantec | 134 | 6:00 | 127 | 12:00 | Mongla | 134 | 0.20833 | 125 | 0.5
| Agargaon | 135 | 6:00 | 128 | 12:00 | Satkhira | 137 | 6:00 | 126 | 0.875
| Satmosjid | 135 | 6:00 | 128 | 12:00 | Gallamari | 139 | 4:00 | 128 | 0.5
| Tongi | 138 | 7:00 | 134 | 11:00 | Magura | 135 | 2:00 | 125 | 8:00
| Kabirpur | 132 | 5:00 | 127 | 12:00 | Narail | 134 | 0.125 | 124 | 0.5
| Basundhara | 136 | 8:00 | 131 | 0:00 | Chuadanga | 134 | 6:00 | 129 | 0.75
| Manikganj | 136 | 9:00 | 130 | 21:00 | Borguna | 141 | 0.375 | 134 | 0.77083
| Joydevpur | 139 | 20:00 | 135 | 10:00 | Barisal(N) | 142 | 6:00 | 136 | 0.79167
| New Tongi | 137 | 8:00 | 132 | 12:00 | Barisal (S) | 140 | 3:00 | 134 | 0.79167
| Kodda | 135 | 18:30 | 127 | 144:00 | Patuakhali(S) | 139 | 5:00 | 130 | 19:00
| Dhamrai | 134 | 144:00 | 126 | 12:00 | Bhandaria | 140 | 0.16667 | 134 | 0.79167
| Rajendrapur | 134 | 9:00 | 126 | 0:00 | Ishurdi | 139 | 0.20833 | 134 | 0.33333
| Valuka | 130 | 2:00 | 119 | 13:00 | Ruppur Paromanobik | 138 | 0.041667 | 134 | 0.54167
| Tangail | 130 | 1:00 | 124 | 8:00 | Natore | 137 | 18:00 | 130 | 12:00
| Mymensing | 131 | 1:00 | 122 | 13:00 | Bogra | 136 | 18:00 | 129 | 8:00
| Kishorganj | 131 | 5:00 | 121 | 13:00 | Noagaon | 131 | 5:00 | 122 | 8:00
| Netrokona | 130 | 1:00 | 119 | 13:00 | Rajshahi | 135 | 1:00 | 130 | 7:00
| Jamalpur | 139 | 18:00 | 128 | 13:00 | Rajshahi New | 135 | 3:00 | 129 | 8:00
| Sherpur | 137 | 19:00 | 125 | 13:00 | C.Nawabganj | 134 | 18:00 | 125 | 8:00
| Srimongal | 138 | 3:00 | 135 | 18:00 | Amnura | 134 | 2:00 | 126 | 8:00
| Shahjibazar | 135 | 6:00 | 133 | 12:00 | Pabna | 138 | 3:00 | 132 | 8:00
| Fenchuganj | 138 | 6:00 | 135 | 15:00 | Shahjadpur | 140 | 1:00 | 135 | 11:00
| Khulawara | 138 | 6:00 | 136 | 12:00 | Serajganj | 136 | 2:00 | 130 | 8:00
| Sylhet | 136 | 1:00 | 134 | 18:00 | Niyamatpur | 130 | 4:00 | 121 | 8:00
| Chatak | 136 | 4:00 | 133 | 19:30 | Joypurhat | 131 | 1:00 | 120 | 8:00
| Sunamganj | 135 | 1:00 | 133 | 18:30 | Sherpur(Bogura) | 136 | 18:00 | 130 | 7:00
| Biani Bazar | 136 | 1:00 | 133 | 18:30 | Mohastangor | 134 | 3:00 | 127 | 8:00
| Comilla(s) | 133 | 5:00 | 124 | 18:30 | Bangura | 140 | 3:00 | 134 | 8:00
| Comilla(n) | 141 | 3:00 | 124 | 9:00 | Rangpur | 133 | 18:00 | 122 | 8:00
| Chandpur | 142 | 1:00 | 138 | 23:00 | Lalmonirhat | 130 | 1:00 | 120 | 8:00
| Feni | 138 | 7:00 | 129 | 14:00 | Saidpur | 132 | 5:00 | 122 | 8:00
| Chowmuhani | 137 | 1:00 | 130 | 21:00 | Purbasadipur | 132 | 3:00 | 118 | 8:00
| Ashuganj | 138 | 9:00 | 135 | 13:00 | Thakurgaon | 132 | 3:00 | 118 | 8:00
| Daudkandi | 139 | 9:00 | 132 | 15:00 | Palashbari | 131 | 1:00 | 123 | 7:00
| B.Baria | 134 | 15:00 | 130 | 21:00 | Barapukuria | 136 | 5:00 | 128 | 7:00

## L-Curve
Date | 2021-02-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 30 | 5474 | 2384 | 7858 |  |  |  | QF-LDC-11
0:30 | 65.5 | 5351 | 2340 | 7691 | Date: | 2021-02-26
1:00 | 101 | 5228 | 2296 | 7524
1:30 | 107.5 | 5060.5 | 2263.5 | 7324
2:00 | 114 | 4893 | 2231 | 7124
2:30 | 120.5 | 4843 | 2174.5 | 7017.5 | [5 empty] | Gen. at Eve. Peak | 9102 | 9102 MW (19:30 )
3:00 | 127 | 4793 | 2118 | 6911 | [6 empty] | 19:30
3:30 | 122.5 | 4721 | 2101 | 6822 | [5 empty] | Gen. at Day Peak | 7755 | 7755 MW (12:00 )
4:00 | 118 | 4649 | 2084 | 6733 | [6 empty] | 12:00
4:30 | 100 | 4618 | 2017 | 6635 | [5 empty] | Highest Generation | 9102
5:00 | 82 | 4587 | 1950 | 6537 | [6 empty] | 19:30
5:30 | 84 | 4575.5 | 2051 | 6626.5
6:00 | 86 | 4564 | 2152 | 6716
6:30 | 73 | 4550 | 2207 | 6757
7:00 | 60 | 4536 | 2262 | 6798
7:30 | 75.5 | 4714 | 2366 | 7080
8:00 | 91 | 4892 | 2470 | 7362
8:30 | 73 | 4897.5 | 2409.5 | 7307
9:00 | 55 | 4903 | 2349 | 7252
9:30 | 47 | 4926.5 | 2281 | 7207.5
10:00 | 39 | 4950 | 2213 | 7163
10:30 | 20.5 | 4948 | 2215.5 | 7163.5
11:00 | 2 | 4946 | 2218 | 7164
11:30 | 10.5 | 5197 | 2262.5 | 7459.5
12:00 | 19 | 5448 | 2307 | 7755
12:30 | 90 | 5515.5 | 2286.5 | 7802
13:00 | 161 | 5583 | 2266 | 7849
13:30 | 97.5 | 5405 | 2195.5 | 7600.5
14:00 | 34 | 5227 | 2125 | 7352
14:30 | 22 | 5204.5 | 2133 | 7337.5
15:00 | 10 | 5182 | 2141 | 7323
15:30 | 53 | 5101.5 | 2148 | 7249.5
16:00 | 96 | 5021 | 2155 | 7176
16:30 | 144 | 4944 | 2188.5 | 7132.5
17:00 | 192 | 4867 | 2222 | 7089
17:30 | 193.5 | 5053 | 2355 | 7408
18:00 | 195 | 5239 | 2488 | 7727
18:30 | 205 | 5687.5 | 2668.5 | 8356
19:00 | 215 | 6136 | 2849 | 8985
19:30 | 217 | 6261 | 2841 | 9102
20:00 | 155 | 6218 | 2846 | 9064 |  |  |  | Executive Engineer
20:30 | 107.5 | 6186.5 | 2857 | 9043.5 |  |  |  | Network Operation Division
21:00 | 60 | 6155 | 2868 | 9023
21:30 | 48 | 6063 | 2782 | 8845
22:00 | 36 | 5971 | 2696 | 8667 |  |  |  |  | Page 6 of 7
22:30 | 19.5 | 5912 | 2579 | 8491
23:00 | 3 | 5853 | 2462 | 8315
23:30 | 16.5 | 5663.5 | 2423 | 8086.5
24:00 | 30 | 5474 | 2384 | 7858
9102 MW (19:30 )
7755 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-02-26 |  | Energy | 185241878
[11 empty] | 2021-02-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3587 | 803 | 1501 | 1428 | 640 | 70 | 32 | 0 | 112 | 0
0:30 | 3532.5 | 708 | 1533 | 1243.5 | 634.5 | 70 | 24 | 0 | 103 | 0 | Date: | 2021-02-26
1:00 | 3478 | 613 | 1565 | 1059 | 629 | 70 | 16 | 0 | 94 | 0
1:30 | 3506 | 613 | 1538.5 | 875.5 | 619 | 70 | 8 | 0 | 94 | 0 | [7 empty] | Total Energy | 185.2419 | Total Energy Gen 185.242 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.242 MKWHr
2:00 | 3534 | 613 | 1512 | 692 | 609 | 70 | 0 | 0 | 94 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3526.5 | 613 | 1473.5 | 663.5 | 579 | 70 | 0 | 0 | 92 | 0 | [7 empty] | Energy Requirement | 185.2419
3:00 | 3519 | 613 | 1435 | 635 | 549 | 70 | 0 | 0 | 90 | 0
3:30 | 3492.5 | 613 | 1380 | 627.5 | 549 | 70 | 0 | 0 | 90 | 0 | [6 empty] | Shortage
4:00 | 3466 | 613 | 1325 | 620 | 549 | 70 | 0 | 0 | 90 | 0
4:30 | 3468.5 | 612.5 | 1287 | 610 | 499 | 70 | 0 | 0 | 88 | 0
5:00 | 3471 | 612 | 1249 | 600 | 449 | 70 | 0 | 0 | 86 | 0
5:30 | 3383 | 612.5 | 1301 | 685 | 489 | 70 | 0 | 0 | 86 | 0
6:00 | 3295 | 613 | 1353 | 770 | 529 | 70 | 0 | 0 | 86 | 0
6:30 | 3259 | 613 | 1368 | 820.5 | 539 | 70 | 0 | 0 | 85 | 2.5 |  |  |  |  | Coal
7:00 | 3223 | 613 | 1383 | 871 | 549 | 70 | 0 | 0 | 84 | 5
7:30 | 3279.5 | 660 | 1368 | 1048 | 564.5 | 70 | 0 | 0 | 77 | 13 |  |  |  | Oil |  |  |  | ,
8:00 | 3336 | 707 | 1353 | 1225 | 580 | 70 | 0 | 0 | 70 | 21
8:30 | 3288.5 | 707 | 1303 | 1265.5 | 565 | 70 | 8 | 0 | 67 | 33
9:00 | 3241 | 707 | 1253 | 1306 | 550 | 70 | 16 | 0 | 64 | 45
9:30 | 3325.5 | 707.5 | 1243 | 1208.5 | 525 | 70 | 8 | 0 | 62 | 58
10:00 | 3410 | 708 | 1233 | 1111 | 500 | 70 | 0 | 0 | 60 | 71
10:30 | 3389.5 | 707.5 | 1243.5 | 1112 | 500 | 70 | 0 | 0 | 59 | 82
11:00 | 3369 | 707 | 1254 | 1113 | 500 | 70 | 0 | 0 | 58 | 93
11:30 | 3478.5 | 707.5 | 1330.5 | 1187 | 510 | 70 | 16 | 0 | 64 | 96
12:00 | 3588 | 708 | 1407 | 1261 | 520 | 70 | 32 | 0 | 70 | 99
12:30 | 3579.5 | 707.5 | 1362 | 1332 | 545 | 70 | 32 | 0 | 77 | 97
13:00 | 3571 | 707 | 1317 | 1403 | 570 | 70 | 32 | 0 | 84 | 95
13:30 | 3571 | 707 | 1317 | 1403 | 570 | 70 | 32 | 0 | 84 | 95
14:00 | 3571 | 707 | 1317 | 1403 | 570 | 70 | 32 | 0 | 84 | 95
14:30 | 3530 | 707.5 | 1328 | 1232 | 535 | 70 | 24 | 0 | 81 | 78.5
15:00 | 3489 | 708 | 1339 | 1061 | 500 | 70 | 16 | 0 | 78 | 62
15:30 | 3488.5 | 708 | 1303.5 | 1040 | 500 | 70 | 16 | 0 | 74 | 49.5
16:00 | 3488 | 708 | 1268 | 1019 | 500 | 70 | 16 | 0 | 70 | 37
16:30 | 3481 | 707.5 | 1227 | 1036.5 | 500 | 70 | 16 | 0 | 70 | 24.5
17:00 | 3474 | 707 | 1186 | 1054 | 500 | 70 | 16 | 0 | 70 | 12
17:30 | 3464.5 | 707 | 1259.5 | 1225 | 500 | 70 | 100 | 0 | 76 | 6
18:00 | 3455 | 707 | 1333 | 1396 | 500 | 70 | 184 | 0 | 82 | 0
18:30 | 3514 | 755 | 1367.5 | 1799.5 | 525 | 70 | 224 | 0 | 101 | 0
19:00 | 3573 | 803 | 1402 | 2203 | 550 | 70 | 264 | 0 | 120 | 0
19:30 | 3639 | 802 | 1471 | 2194 | 610 | 70 | 190 | 0 | 126 | 0
20:00 | 3658 | 803 | 1546 | 2051 | 620 | 70 | 190 | 0 | 126 | 0
20:30 | 3662.5 | 803 | 1554 | 2013.5 | 640 | 70 | 173.5 | 0 | 127 | 0
21:00 | 3667 | 803 | 1562 | 1976 | 660 | 70 | 157 | 0 | 128 | 0
21:30 | 3656.5 | 803 | 1571 | 1808 | 665 | 70 | 144.5 | 0 | 127 | 0
22:00 | 3646 | 803 | 1580 | 1640 | 670 | 70 | 132 | 0 | 126 | 0
22:30 | 3636.5 | 803 | 1572.5 | 1534 | 655 | 70 | 97 | 0 | 123 | 0
23:00 | 3627 | 803 | 1565 | 1428 | 640 | 70 | 62 | 0 | 120 | 0
23:30 | 3607 | 803 | 1533 | 1428 | 640 | 70 | 47 | 0 | 116 | 0 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3587 | 803 | 1501 | 1428 | 640 | 70 | 32 | 0 | 112 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 185.242 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.242 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-02-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1672000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 2 | 3 | 8 | 16 | 17 | 16 | 14 | 11 | 7 | 2 | [9 empty] | 97065
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 17 | 17 | 17 | 17 |  |  | 130864
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 37 | 35 | 35 | 92 | 35 | 92 | 35 | 37 | 37 | 92 | 57 | 36 | 33 | 35 | 37 | 35 |  | 62 | 93 | 92 | 92 | 92 | 85 | 62 | 1442000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 21 | 30 | 30 | 15 | 15 | 19 |  | 136 | 195 | 145 | 145 | 95 | 85 |  | 870654
19 | Ashuganj 195MW PP (APSCL-United) | [13 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 3811500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7153791
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 285480
33 | Ashuganj 225 MW CCPP | 203 | 206 | 212 | 214 | 214 | 221 | 219 | 223 | 225 | 224 | 221 | 218 | 221 | 200 | 200 | 200 | 200 | 200 |  | 200 | 203 | 219 | 216 | 208 | 197 | 190 | 5088000
34 | Ashuganj 450 MW CCPP(South) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 225 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5662000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 6929500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 140160
36 | Chandpur 150 MW CCPP | 92 | 93 | 93 | 94 | 99 | 96 | 93 | 91 | 92 | 91 | 94 | 95 | 91 | 91 | 92 | 94 | 92 | 95 |  | 95 | 92 | 95 | 95 | 94 | 93 | 94 | 2211940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 339 | 342 | 339 | 339 | 378 | 359 | 344 | 338 | 341 | 343 | 382 | 343 | 341 | 342 | 333 | 301 | 300 |  | 329 | 340 | 342 | 351 | 350 | 347 | 348 | 8329220
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 380 | 340 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 300 | 370 | 350 | 350 | 225 | 300 |  | 400 | 400 | 400 | 400 | 430 | 430 | 430 | 7851250
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 108 | 158 | 158 | 138 | 138 | 157 | 157 | 161 | 140 | 107 | 104 | 102 | 102 | 102 | 102 | 101 | 107 | 124 |  | 142 | 143 | 142 | 143 | 144 | 144 | 144 | 3027720
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 11 | 22 | 31 | 41 | 44 | 43 | 38 | 27 | 15 | 5 | 0 | [8 empty] | 280080
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 30 | 29 | 29 | 29 | 29 | 29 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 952920
46 | Shajibazar 330 MW CCPP | 161 | 162 | 162 | 161 | 161 | 161 | 162 | 162 | 161 | 161 | 160 | 164 | 162 | 163 | 163 | 163 | 163 | 162 |  | 162 | 163 | 162 | 161 | 163 | 163 | 162 | 3753000
47 | Shahjibazar GTPP Unit- 8 & 9 | [11 empty] | 15 | 35 | 35 | 35 | 35 | 35 | 36 |  | 31 | 36 | 36 | 36 | 31 | 36 | 37 | 415584
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 40 | 10 | 10 | 78 | 78 | 78 | 78 | 47 | 50 | 72 | 81 | 50 | 50 | 10 | 10 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1420800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 163 | 163 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 162 | 3910700
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 123300
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 13 | 13 | 13 | 50 | 50 | 50 | 50 | 46 | 48 | 48 | 50 | 25 | 25 | 5 | 5 | 8 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 732000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 386352
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 300 | 290 | 280 | 290 | 280 | 290 | 280 | 290 | 290 | 320 | 280 | 270 | 290 | 290 | 300 | 285 |  | 280 | 300 | 305 | 315 | 305 | 305 | 300 | 7322500
| Bibiyana South 400 MW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7218700
58 | Nababganj 55 MW PP (Southern power )
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 10 | 13 | 12 | 13 | 24 | 24 |  | 24 | 24 | 25 | 25 | 12 |  |  | 199200
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 410880
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | [10 empty] | 10 | 10 | 10 |  | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 251100
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 403056
63 | Impoprt (Tripura) | 94 | 94 | 90 | 90 | 86 | 86 | 84 | 70 | 64 | 60 | 58 | 70 | 84 | 80 | 78 | 70 | 70 | 82 |  | 120 | 126 | 126 | 128 | 126 | 120 | 112 | 2148480
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 32 | 25 | 32 | 33 | 34 | 35 | 35 | 34 | 34 | 36 | 42 | 42 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 38 | 38 | 38 | 879840
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512964
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 214920
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 20 | 33 | 33 | 33 | 33 | 33 | [9 empty] | 557700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 498540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 20 | 26 | 32 | 26 | 22 | 22 | 17 | 10 | 10 | 10 | 10 | 10 | 10 |  | 28 | 30 | 31 | 31 | 31 | 31 | 28 | 547020
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 649000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 585800
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 296909
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [17 empty] | 17 |  | 17 | [6 empty] | 46200
| Manikgonj 162MW PP(MPGL) | 126 | 53 | 21 | 17 | 17 | 23 | 78 | 126 | 126 | 54 | 54 | 54 | 87 | 54 | 54 | 17 | 17 | 17 |  | 108 | 126 | 126 | 144 | 144 | 144 | 144 | 1903680
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 5 |  |  |  |  | 6 |  | 16
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | 16 | [7 empty] | 16 |  |  | 32 | 32 | 16 | 16 | 16 | 16 | 48 |  | 115 | 115 | 115 | 82 | 82 | 62 | 32 | 684000
80 | Jamalpur 95 MW PP(Powerpac) | [9 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 |  | 68 | 64 | 40 | 16 | 16 |  |  | 390720
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [10 empty] | 8 | 17 | 17 | [6 empty] | 17 | 17 | [5 empty] | 84744
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26520
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 15 | 15 | 15 | 15 | 15 | 20 | 48 | 48 | 30 | 30 | 30 | 35 | 22 | 15 | 15 | 15 | 22 |  | 64 | 64 | 64 | 64 | 48 | 30 | 15 | 838200
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 25 | 50 | 50 | 20 | 28 | 40 | 40 | 40 | 10 | 10 | 15 |  | 54 | 84 | 84 | 84 | 50 | 45 |  | 730846
86 | Meghnaghat CCPP(Summit) | 285 | 265 | 270 | 260 | 260 | 300 | 150 | 150 | 150 | 270 | 285 | 275 | 235 | 270 | 265 | 260 | 270 | 275 |  | 255 | 260 | 275 | 285 | 280 | 285 | 265 | 5996393
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 0 |  | 7 | [6 empty] | 8640
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 6 | 17 |  |  |  | 17 |  | 44 | 17 | 20 | 17 |  |  |  | 148800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [11 empty] | 1 | 15 | 18 | 18 | 18 | 13 | 16 |  | 35 | 50 | 50 | 50 | 18 | 18 |  | 311520
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 11 |  | 27 | [6 empty] | 47692
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 110 | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 163 | 130 | 110 | 110 | 110 | 110 | 110 |  | 110 | 130 | 163 | 163 | 163 | 163 | 130 | 3419263
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 13650
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 |  |  |  | 5 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 112680
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 95 | 80 | 80 | 60 | 79 | 132 | 192 | 200 | 200 | 192 | 200 | 200 | 200 | 200 | 200 | 200 | 193 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4207200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 38 | 30 | 15 | 15 | 15 | 15 | 16 | 46 | 93 | 93 | 102 | 102 | 102 | 92 | 107 | 113 | 115 | 126 |  | 133 | 135 | 115 | 53 | 50 | 50 | 40 | 1707264
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 70 | 70 | 20 | 20 | 50 | 50 | 40 | 40 | 40 | 40 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 30 | 1230720
116 | Chandpur 200MW (Desh energy) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 60 | 34 | 17 | 17 | 17 | 17 |  | 49 | 68 | 68 | 68 | 68 | 68 | 68 | 838560
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 315 | 319 | 318 | 319 | 319 |  |  | 70 | 80 | 231 | 240 | 324 | 341 | 316 | 316 | 316 | 316 | 315 |  | 316 | 316 | 316 | 327 | 327 | 328 | 328 | 6193000
| Jamalpur 115 MW PP (United) | [9 empty] | 5 | 8 | 8 | 8 |  |  |  |  | 4 |  | 8 | 8 | [5 empty] | 55200
| Anwara 300 MW PP (United) | 306 | 197 | 197 | 196 | 196 | 231 | 270 | 270 | 255 | 189 | 178 | 250 | 250 | 140 | 141 | 177 | 179 | 204 |  | 251 | 251 | 251 | 253 | 251 | 251 | 251 | 5394545
| Juldah unit-2 (Acorn) | 30 | 10 | 10 | 10 | 10 | 50 | 100 | 100 | 100 | 70 | 70 | 90 | 100 | 50 | 50 | 50 | 50 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1607040
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | [14 empty] | 13 | 15 | [10 empty] | 42480
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 5 | 17 | 26 | 30 | 32 | 30 | 26 | 20 | 13 | 5 | [9 empty] | 207417
120 | Eastern Zone Total | 5228 | 4893 | 4793 | 4649 | 4587 | 4564 | 4536 | 4892 | 4903 | 4950 | 4946 | 5448 | 5583 | 5227 | 5182 | 5021 | 4867 | 5239 |  | 6136 | 6261 | 6218 | 6155 | 5971 | 5853 | 5474 | 126906463
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 | 16 |  |  |  |  | 31680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 17 |  |  |  |  | 17 |  | 105 | 70 | 70 | 70 | 53 | 17 |  | 360960
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 49 | 49 | 49 | 49 | 45 | 47 | 48 | 49 | 37 | 48 | 43 | 41 | 39 | 45 | 44 | 44 | 45 | 43 |  | 43 | 44 | 45 | 49 | 49 | 49 | 49 | 1126582
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 20 | 32 | 32 | 32 | 16 |  |  | 124512
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 43 | 43 | 42 | 42 | 42 | 40 | 41 | 41 | 41 | 42 | 42 | 41 | 41 | 42 | 41 | 43 | 44 | 43 |  | 42 | 49 | 58 | 62 | 61 | 60 | 60 | 1087582
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 23 | 21 | 20 | 20 | 17 | 20 | 19 | 16 | 16 | 17 | 18 | 15 | 15 | 15 | 12 | 13 | 23 |  | 26 | 29 | 28 | 28 | 28 | 27 | 26 | 496272
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 613 | 613 | 613 | 613 | 612 | 613 | 613 | 707 | 707 | 708 | 707 | 708 | 707 | 707 | 708 | 708 | 707 | 707 |  | 803 | 802 | 803 | 803 | 803 | 803 | 803 | 17018909
147 | Bheramara 410 MW CCPP | 330 | 330 | 300 | 270 | 270 | 335 | 335 | 325 | 310 | 310 | 300 | 300 | 295 | 280 | 305 | 330 | 340 | 340 |  | 340 | 340 | 340 | 335 | 325 | 325 | 325 | 7870176
148 | Payra 1320 MW | 480 | 460 | 400 | 400 | 300 | 380 | 400 | 430 | 400 | 350 | 350 | 370 | 420 | 350 | 350 | 350 | 350 | 350 |  | 400 | 460 | 470 | 510 | 520 | 490 | 490 | 10826000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3659900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 1613
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 163 | 170 | 169 | 169 | 175 | 175 | 175 | 174 | 140 | 140 | 143 | 150 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3847809
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 371 | 344 | 342 | 313 | 366 | 400 | 359 | 284 | 311 | 333 | 401 | 297 | 306 | 333 | 323 | 351 | 356 |  | 314 | 332 | 360 | 358 | 359 | 346 | 321 | 8359454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 19 | 19 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 235062
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 85 |  | 98 | 58 | 58 | 58 | 33 |  |  | 306328
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 48 | 111 | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 38 |  | 106 | 113 | 113 | 113 | 70 | 35 |  | 1207104
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 20 | 35 | 35 | 35 | 35 | 35 |  |  |  | 10 | 70 |  | 113 | 113 | 70 | 70 | 35 |  |  | 628800
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 50 | 49 | 35 | 35 | 34 | 34 | 34 |  |  | 15 | 90 |  | 113 | 70 | 70 | 70 | 34 |  |  | 652800
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | [18 empty] | 912
178
178