## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-04 | Thursday
|  | Date (day): | 2021-03-04 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13080.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13951 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-03 | 2021-03-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 200 | 200 |  |  | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 350 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 380 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 86 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 280 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 45 | 38 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 85 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 9 | 37 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 48 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 53 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 290 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 95 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 86 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 121 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 20 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2543 | 3134 | 3732 | 3954 | 204 | 1555
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 18 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 125 | 105 | 0 | 0 | 150 |  | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 16 | 16 | 16 |  | 6 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 80 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 303 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 31 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 90 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 818 | 985 | 1313 | 1348 | 895 | 104
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 159 | 202 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 265 | 300 | 300 | 60 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 300 | 300 | 60 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 35 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 33 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 139 | 0 | 0 |  | 163 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 103 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 10 | 148 | 135 | 147
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 23 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 16 | 20 | 20
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 68 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 56 | 56 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1111 | 1422 | 1540 | 1802 | 798 | 163
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 82 | 103 | 110 | 110 | 92 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 81 | 82 | 82 |  | 13 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 192 | 200 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 35 | 92 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 25 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 421 | 518 | 597.6 | 546 | 92 | 18
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 8 | 43 | 43 | 43 |  | 27 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under S/D
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 161 | 162 | 162 |  | 168 | GT-1 under S/D for Gas shortage
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 49 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 35 | 36 | 36 | 36 |  | 30 | GT-9 Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 91 | 137 | 137 | 137
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 330 | 330 | 350 | 350
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 5 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 322 | 320 | 320 | 320 |  |  | On Test
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1538 | 1641 | 1735 | 1735 | 0 | 442
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 717 | 716 | 723 | 723
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 80 | 115 | 115
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 4 | 25 | 25 |  | 29 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 210 | 175 | 240 | 240 | 170 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 8 | 40 | 40
110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1060 | 1088 | 1458 | 1744 | 170 | 78
113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 32 | 26 | 27 |  | 6 | Engine problem
115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 83 | 90 | 95 | 95
117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 350 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 10 | 10 | 51 | 51 |  |  | On Test
118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 10 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 559 | 602 | 1052 | 1053 | 0 | 200
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 12 | 0 | 40
122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 12 | 12 | 12 |  | 38 | Engine problem
123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 16 | 50 | 50
124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 50 | 50
125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 167 | 138 | 170 | 170 | 50 |  | Gas shortage and FGMO
128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 338 | 324 | 400 | 400 |  |  | FGMO
129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 34
130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 45 | 52 | 52
134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 104 | 104
135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113 |  | 0 | Engine problem
137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 778 | 1000 | 1297 | 1421 | 651 | 38
138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 111 | 108 | 85 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 107 | 113 | 113
143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 381 | 365 | 356 | 348 | 124 | 125
| Total |  |  |  |  | 21395 | 20929 | 9209 | 10755 | 13080.6 | 13951 | 2934 | 2723
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8829.68 | 10312 | 12541.8082 | 13376.3563
A. |  | 2021-03-03 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10755 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7437 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10755 | MW
3 | Day peak Generation : |  |  | 9209 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10312 | MW
4 | Evening peak Generation : |  |  | 10755 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 220.6457 | MKWHr | By Solar | 0.68884 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 123.439 | MKWHr |  | By Oil: | 57.8586 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 17.0553 | MKWHr |  | By Hydro: | 1.673 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2934 | MW | Dhaka | 3639 | 3639 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2723 | MW | Chittagong | 1115 | 1115 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 5657 | MW | Khulna | 1254 | 1254 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 924.35 | MMCFD |  |  | Rajshahi | 1074 | 1074 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 128750416.006 | ii) Oil : | Taka | 394796343.77 | Comilla | 947 | 947 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 82489177.16 | Total | Taka | 606035936.936 | Mymensingh | 895 | 895 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.7815 | MKWHr. | Sylhet | 388 | 388 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -417 | MW (E to W) at | 19:00 | hrs | Barisal | 294 | 294 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -417 | MW at | 19:00 | hrs | Rangpur | 706 | 706 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 10312 | 10312 |  | 0
B. |  | 2021-03-04 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13951 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
4 | Reserve(Generation end) |  |  |  | 3151 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 221.5689 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6990 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3236 | MKWHr. | ii) HVDC Flow at Peak Time |  | 716 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6074 | MKWHr. | iii) Maximum HVDC Flow : |  | 719 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.04 |  | (b) Today: | 90.92 |  | (c) Rule Curve: |  | 92.52
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 335 | 0 |  | 0 | 370 | 255 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 16 | 38 | 0 | 0 | 0 | 285 | 260 | 196 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 116 | 105 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 162 | 36 | 83 | 0 | 100 | 19 | 0 | 3 | 290 | 8 | 11 | 0 | 195 | 0 | 0 | 120 | 0 | 72 | 0 | 50 | 100 | 0 | 330 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 100 | 270 | 47 | 0 | 0 | 0 | 0 | 55 | 0 |  | 716 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 153 | 0 | 344 | 0 | 0 | 94 | 0 | 50 | 0 | 0 | 70 | 470 | 53 | 0 | 0 |  | 5778 | 2510 | 8288 | 3458 | 716 | 1493 | 1727 | 704 | 70 | 4 | 116 | 0 | 0 | 91.07
2:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 336 | 0 |  | 0 | 370 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 38 | 0 | 0 | 0 | 285 | 260 | 196 | 0 | 138 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 112 | 106 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 161 | 36 | 83 | 0 | 100 | 18 | 0 | 3 | 300 | 8 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 71 | 0 | 10 | 100 | 0 | 335 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 717 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 153 | 0 | 355 | 0 | 0 | 70 | 0 | 10 | 0 | 0 | 35 | 470 | 53 | 0 | 0 |  | 5478 | 2419 | 7897 | 3491 | 717 | 1510 | 1289 | 704 | 70 | 4 | 112 | 0 | 0 | 91.06
3:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 341 | 0 |  | 0 | 370 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 39 | 0 | 0 | 0 | 285 | 260 | 200 | 0 | 138 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 112 | 106 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 161 | 36 | 80 | 0 | 100 | 18 | 0 | 3 | 310 | 8 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 70 | 0 | 10 | 100 | 0 | 328 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 100 | 289 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 717 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 153 | 0 | 357 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 440 | 53 | 0 | 0 |  | 5387 | 2333 | 7720 | 3502 | 717 | 1520 | 1119 | 676 | 70 | 4 | 112 | 0 | 0 | 91.06
4:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 335 | 0 |  | 0 | 370 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 40 | 0 | 0 | 0 | 285 | 260 | 200 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 110 | 106 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 162 | 36 | 40 | 0 | 100 | 19 | 0 | 3 | 290 | 8 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 70 | 0 | 10 | 65 | 0 | 331 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 100 | 275 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 716 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 153 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 400 | 53 | 0 | 0 |  | 5144 | 2299 | 7443 | 3511 | 716 | 1443 | 953 | 636 | 70 | 4 | 110 | 0 | 0 | 91.05
5:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 335 | 0 |  | 0 | 370 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 40 | 0 | 0 | 0 | 285 | 260 | 203 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 104 | 107 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 162 | 36 | 40 | 0 | 100 | 18 | 0 | 3 | 295 | 8 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 70 | 0 | 10 | 65 | 0 | 331 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 716 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 87 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 153 | 0 | 344 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 400 | 53 | 0 | 0 |  | 5134 | 2303 | 7437 | 3509 | 716 | 1451 | 946 | 637 | 70 | 4 | 104 | 0 | 0 | 91.05
6:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 344 | 0 |  | 0 | 370 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 40 | 0 | 0 | 0 | 285 | 260 | 204 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 102 | 107 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 161 | 37 | 77 | 0 | 100 | 18 | 0 | 3 | 300 | 8 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 70 | 0 | 10 | 68 | 0 | 329 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 100 | 270 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 717 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 153 | 0 | 328 | 0 | 0 | 45 | 0 | 17 | 0 | 0 | 10 | 400 | 53 | 0 | 0 |  | 5210 | 2329 | 7539 | 3514 | 717 | 1477 | 1019 | 636 | 70 | 4 | 102 | 0 | 0 | 91.04
7:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 337 | 0 |  | 0 | 370 | 290 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 3 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 36 | 0 | 0 | 0 | 285 | 260 | 197 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 100 | 107 | 0 | 17 | 0 | 20 | 0 | 51 | 0 | 110 | 162 | 37 | 77 | 0 | 100 | 18 | 0 | 3 | 300 | 8 | 11 | 0 | 86 | 0 | 0 | 98 | 0 | 105 | 2 | 10 | 98 | 0 | 334 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 0 | 0 | 100 | 300 | 0 | 3 | 0 | 0 | 0 | 54 | 2 |  | 717 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 153 | 0 | 356 | 0 | 0 | 94 | 0 | 57 | 0 | 0 | 70 | 400 | 53 | 0 | 0 |  | 5460 | 2540 | 8000 | 3571 | 717 | 1500 | 1395 | 636 | 70 | 4 | 100 | 7 | 0 | 91.04
8:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 343 | 0 |  | 0 | 370 | 280 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 0 | 0 | 100 | 0 |  | 2 | 0 | 0 | 0 | 0 | 19 | 16 | 7 | 0 | 0 | 0 | 285 | 260 | 187 | 0 | 137 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 96 | 108 | 17 | 17 | 1 | 20 | 0 | 51 | 0 | 110 | 160 | 36 | 77 | 0 | 100 | 18 | 0 | 3 | 305 | 8 | 11 | 0 | 160 | 0 | 0 | 192 | 0 | 124 | 3 | 10 | 98 | 0 | 330 | 0 | 0 | 0 | 1 | 269 | 0 | 0 | 0 | 0 | 100 | 270 | 11 | 15 | 0 | 0 | 0 | 56 | 10 |  | 716 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 158 | 0 | 332 | 53 | 0 | 94 | 0 | 106 | 0 | 1 | 105 | 420 | 53 | 0 | 0 |  | 5719 | 2634 | 8353 | 3531 | 716 | 1415 | 1836 | 654 | 70 | 4 | 96 | 31 | 0 | 91.03
9:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 343 | 0 |  | 0 | 370 | 260 | 0 | 0 | 40 | 0 | 0 | 0 | 45 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 35 | 10 | 22 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 0 | 0 | 100 | 0 |  | 24 | 0 | 0 | 0 | 0 | 39 | 16 | 4 | 0 | 0 | 0 | 285 | 260 | 157 | 0 | 130 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 102 | 106 | 40 | 17 | 1 | 20 | 0 | 48 | 0 | 163 | 162 | 36 | 80 | 0 | 30 | 18 | 0 | 3 | 305 | 8 | 11 | 0 | 225 | 0 | 0 | 194 | 0 | 132 | 4 | 30 | 94 | 0 | 326 | 0 | 8 | 0 | 2 | 304 | 6 | 0 | 0 | 0 | 100 | 270 | 65 | 23 | 0 | 0 | 0 | 56 | 20 |  | 716 | 0 | 245 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 84 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 165 | 0 | 338 | 70 | 0 | 94 | 0 | 110 | 0 | 3 | 113 | 430 | 12 | 0 | 0 |  | 6042 | 2746 | 8788 | 3411 | 716 | 1463 | 2305 | 664 | 70 | 4 | 102 | 53 | 0 | 91.03
10:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 336 | 0 |  | 0 | 370 | 265 | 0 | 10 | 40 | 0 | 0 | 0 | 50 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 35 | 17 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 0 | 0 | 100 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 14 | 3 | 0 | 0 | 0 | 285 | 260 | 163 | 0 | 136 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 104 | 103 | 32 | 17 | 2 | 20 | 0 | 48 | 0 | 163 | 162 | 35 | 80 | 0 | 21 | 18 | 0 | 3 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 194 | 0 | 149 | 10 | 30 | 83 | 0 | 330 | 0 | 35 | 0 | 3 | 306 | 17 | 0 | 0 | 0 | 100 | 270 | 98 | 36 | 0 | 0 | 0 | 56 | 13 |  | 717 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 105 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 167 | 0 | 330 | 90 | 0 | 94 | 0 | 106 | 0 | 5 | 113 | 430 | 10 | 0 | 0 |  | 6144 | 2761 | 8905 | 3371 | 717 | 1439 | 2446 | 685 | 70 | 4 | 104 | 69 | 0 | 91.02
11:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 337 | 0 |  | 0 | 370 | 250 | 2 | 15 | 40 | 0 | 0 | 0 | 55 | 12 | 0 | 60 | 0 | 0 | 0 | 54 | 35 | 17 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 0 | 0 | 100 | 0 |  | 21 | 0 | 0 | 0 | 0 | 48 | 14 | 3 | 0 | 0 | 0 | 265 | 260 | 152 | 0 | 126 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 112 | 103 | 24 | 17 | 2 | 20 | 0 | 48 | 0 | 163 | 160 | 35 | 83 | 0 | 30 | 18 | 0 | 3 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 194 | 0 | 149 | 17 | 90 | 84 | 0 | 330 | 0 | 40 | 0 | 4 | 306 | 19 | 0 | 0 | 16 | 90 | 320 | 104 | 45 | 1 | 0 | 0 | 56 | 21 |  | 717 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 167 | 0 | 311 | 94 | 0 | 94 | 0 | 108 | 0 | 6 | 113 | 430 | 10 | 0 | 0 |  | 6254 | 2746 | 9000 | 3363 | 717 | 1419 | 2529 | 692 | 70 | 3 | 112 | 95 | 0 | 91.02
12:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 370 | 260 | 16 | 45 | 50 | 0 | 0 | 0 | 85 | 16 | 0 | 68 | 0 | 0 | 9 | 54 | 35 | 35 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 18 | 0 | 0 | 125 | 0 |  | 21 | 0 | 0 | 0 | 0 | 45 | 14 | 3 | 0 | 0 | 0 | 265 | 260 | 159 | 0 | 138 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 10 | 82 | 24 | 17 | 2 | 8 | 0 | 45 | 0 | 130 | 162 | 35 | 83 | 0 | 91 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 149 | 17 | 90 | 100 | 0 | 330 | 35 | 50 | 0 | 4 | 307 | 35 | 0 | 0 | 26 | 90 | 322 | 104 | 48 | 17 | 0 | 0 | 56 | 20 |  | 717 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 111 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 167 | 0 | 338 | 105 | 0 | 94 | 0 | 113 | 0 | 7 | 113 | 430 | 10 | 0 | 0 |  | 6431 | 2778 | 9209 | 3425 | 717 | 1415 | 2779 | 691 | 70 | 4 | 10 | 98 | 0 | 91.01
13:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 400 | 240 | 16 | 81 | 55 | 0 | 0 | 0 | 100 | 16 | 0 | 67 | 0 | 0 | 24 | 54 | 35 | 35 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 123 | 0 |  | 19 | 0 | 0 | 0 | 0 | 45 | 14 | 5 | 0 | 0 | 0 | 265 | 260 | 154 | 0 | 128 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 74 | 84 | 24 | 17 | 2 | 17 | 0 | 48 | 0 | 163 | 163 | 34 | 80 | 0 | 113 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 258 | 0 | 0 | 200 | 0 | 149 | 17 | 90 | 99 | 0 | 331 | 45 | 50 | 0 | 4 | 300 | 35 | 0 | 0 | 26 | 90 | 313 | 104 | 49 | 17 | 0 | 0 | 56 | 31 |  | 717 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 115 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 164 | 0 | 303 | 105 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 450 | 9 | 0 | 0 |  | 6691 | 2743 | 9434 | 3443 | 717 | 1453 | 2849 | 715 | 70 | 4 | 74 | 109 | 9434 | 91.01
14:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 350 | 290 | 0 | 48 | 55 | 0 | 0 | 0 | 60 | 7 | 0 | 62 | 0 | 0 | 12 | 54 | 35 | 35 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 19 | 0 | 0 | 0 | 0 | 46 | 14 | 4 | 0 | 0 | 0 | 265 | 260 | 164 | 0 | 138 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 106 | 84 | 24 | 17 | 2 | 18 | 0 | 48 | 0 | 130 | 162 | 34 | 82 | 0 | 113 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 269 | 0 | 0 | 200 | 0 | 131 | 15 | 100 | 99 | 0 | 331 | 24 | 35 | 0 | 3 | 306 | 35 | 0 | 0 | 8 | 90 | 334 | 104 | 44 | 0 | 0 | 0 | 55 | 30 |  | 717 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 110 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 158 | 0 | 346 | 53 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 420 | 10 | 0 | 0 |  | 6523 | 2674 | 9197 | 3460 | 717 | 1407 | 2653 | 680 | 70 | 4 | 106 | 100 | 0 | 91
15:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 340 | 0 |  | 0 | 350 | 290 | 0 | 48 | 55 | 0 | 0 | 0 | 60 | 7 | 0 | 60 | 0 | 0 | 12 | 54 | 35 | 45 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 19 | 0 | 0 | 0 | 0 | 50 | 14 | 3 | 0 | 0 | 0 | 265 | 260 | 187 | 0 | 140 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 104 | 100 | 24 | 17 | 1 | 18 | 0 | 49 | 0 | 130 | 162 | 34 | 82 | 0 | 137 | 18 | 0 | 5 | 310 | 8 | 11 | 0 | 272 | 0 | 0 | 200 | 0 | 132 | 12 | 100 | 100 | 0 | 329 | 24 | 35 | 0 | 3 | 306 | 35 | 0 | 0 | 8 | 90 | 320 | 104 | 34 | 0 | 0 | 0 | 56 | 23 |  | 717 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 107 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 146 | 0 | 330 | 53 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 420 | 10 | 0 | 0 |  | 6584 | 2640 | 9224 | 3479 | 717 | 1408 | 2687 | 677 | 70 | 4 | 104 | 78 | 0 | 91
16:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 347 | 0 |  | 0 | 350 | 290 | 0 | 30 | 55 | 0 | 0 | 0 | 30 | 0 | 0 | 60 | 0 | 0 | 12 | 54 | 35 | 55 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 20 | 0 | 0 | 0 | 0 | 50 | 14 | 3 | 0 | 0 | 0 | 265 | 260 | 184 | 0 | 135 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 11 | 102 | 100 | 24 | 17 | 1 | 20 | 0 | 53 | 0 | 130 | 162 | 34 | 82 | 0 | 137 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 149 | 7 | 70 | 99 | 0 | 329 | 24 | 35 | 0 | 2 | 303 | 17 | 0 | 0 | 8 | 90 | 350 | 104 | 20 | 0 | 0 | 0 | 56 | 14 |  | 716 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 107 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 138 | 0 | 328 | 53 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 420 | 10 | 0 | 0 |  | 6466 | 2603 | 9069 | 3466 | 716 | 1401 | 2582 | 677 | 70 | 7 | 102 | 48 | 0 | 90.99
17:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 343 | 0 |  | 0 | 350 | 260 | 1 | 30 | 55 | 0 | 0 | 0 | 30 | 4 | 20 | 72 | 0 | 0 | 12 | 54 | 17 | 17 | 22 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 19 | 0 | 0 | 0 | 4 | 50 | 16 | 4 | 0 | 0 | 0 | 265 | 260 | 184 | 0 | 131 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 11 | 88 | 103 | 32 | 17 | 0 | 43 | 0 | 53 | 0 | 110 | 163 | 34 | 84 | 0 | 137 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 270 | 0 | 0 | 170 | 0 | 149 | 2 | 40 | 100 | 0 | 329 | 24 | 35 | 0 | 0 | 250 | 17 | 0 | 0 | 8 | 90 | 320 | 89 | 6 | 0 | 0 | 0 | 55 | 5 |  | 716 | 0 | 175 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 138 | 0 | 294 | 35 | 0 | 94 | 0 | 74 | 0 | 2 | 113 | 420 | 9 | 0 | 0 |  | 6251 | 2522 | 8773 | 3479 | 716 | 1355 | 2344 | 678 | 70 | 28 | 88 | 15 | 0 | 90.99
18:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 340 | 0 |  | 0 | 320 | 280 | 19 | 30 | 55 | 0 | 0 | 0 | 30 | 40 | 82 | 98 | 0 | 0 | 13 | 54 | 17 | 17 | 0 | 25 | 10 | 25 | 33 | 15 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 24 | 0 | 73 | 10 | 33 | 50 | 16 | 5 | 0 | 0 | 0 | 265 | 260 | 197 | 0 | 132 | 10 | 5 | 0 | 0 | 0 | 0 | 4 | 22 | 5 | 33 | 16 | 94 | 103 | 24 | 17 | 0 | 43 | 0 | 14 | 0 | 110 | 162 | 20 | 60 | 0 | 137 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 286 | 0 | 0 | 170 | 0 | 149 | 0 | 74 | 100 | 0 | 305 | 34 | 36 | 0 | 0 | 215 | 17 | 0 | 34 | 40 | 90 | 320 | 71 | 0 | 24 | 0 | 0 | 55 | 0 |  | 716 | 0 | 175 | 0 | 43 | 0 | 0 | 0 | 7 | 0 | 8 | 0 | 27 | 48 | 0 | 0 | 0 | 5 | 5 | 60 | 12 | 16 | 10 | 22 | 27 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 138 | 0 | 334 | 70 | 0 | 94 | 0 | 52 | 0 | 0 | 113 | 350 | 9 | 0 | 0 |  | 6501 | 2718 | 9219 | 3439 | 716 | 1312 | 2711 | 608 | 70 | 269 | 94 | 0 | 0 | 90.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 350 | 0 |  | 0 | 380 | 280 | 86 | 38 | 55 | 0 | 0 | 0 | 85 | 102 | 115 | 100 | 0 | 0 | 37 | 54 | 35 | 48 | 0 | 25 | 28 | 25 | 33 | 25 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 25 | 0 | 85 | 10 | 80 | 50 | 16 | 20 | 0 | 0 | 0 | 265 | 260 | 202 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 33 | 23 | 22 | 5 | 33 | 16 | 148 | 103 | 81 | 17 | 0 | 43 | 0 | 49 | 0 | 130 | 161 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 310 | 8 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 103 | 0 | 330 | 92 | 95 | 0 | 0 | 303 | 31 | 0 | 34 | 68 | 90 | 320 | 86 | 0 | 121 | 0 | 0 | 56 | 0 |  | 716 | 0 | 175 | 0 | 80 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 32 | 110 | 0 | 0 | 0 | 50 | 12 | 100 | 12 | 16 | 40 | 45 | 27 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 138 | 0 | 324 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 350 | 10 | 0 | 10 |  | 7700 | 3055 | 10755 | 3519 | 716 | 1471 | 3757 | 608 | 70 | 466 | 148 | 0 | 0 | 90.97
19:30 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 380 | 280 | 100 | 64 | 55 | 0 | 0 | 0 | 100 | 76 | 82 | 100 | 0 | 0 | 18 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 24 | 0 | 85 | 0 | 62 | 50 | 16 | 30 | 0 | 0 | 0 | 265 | 260 | 202 | 0 | 135 | 10 | 5 | 0 | 0 | 0 | 33 | 0 | 22 | 5 | 33 | 16 | 142 | 105 | 81 | 17 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 130 | 0 | 331 | 75 | 52 | 0 | 0 | 303 | 54 | 0 | 0 | 75 | 90 | 320 | 104 | 0 | 108 | 0 | 0 | 55 | 0 |  | 716 | 0 | 175 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 32 | 110 | 0 | 0 | 0 | 50 | 27 | 100 | 12 | 0 | 40 | 52 | 27 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 138 | 0 | 291 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 380 | 3 | 0 | 27 |  | 7570 | 3046 | 10616 | 3530 | 716 | 1422 | 3650 | 638 | 70 | 448 | 142 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 339 | 0 |  | 0 | 400 | 260 | 100 | 72 | 55 | 0 | 0 | 0 | 100 | 74 | 48 | 100 | 0 | 0 | 18 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 |  | 24 | 0 | 17 | 0 | 56 | 50 | 16 | 30 | 0 | 0 | 0 | 265 | 260 | 203 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 152 | 105 | 81 | 17 | 0 | 43 | 0 | 50 | 0 | 130 | 162 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 280 | 8 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 131 | 0 | 331 | 75 | 17 | 0 | 0 | 306 | 54 | 0 | 0 | 75 | 90 | 321 | 100 | 0 | 108 | 0 | 0 | 52 | 0 |  | 718 | 0 | 175 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 32 | 110 | 0 | 0 | 0 | 50 | 0 | 60 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 108 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 138 | 0 | 307 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 390 | 35 | 0 | 27 |  | 7408 | 2989 | 10397 | 3546 | 718 | 1481 | 3604 | 647 | 70 | 179 | 152 | 0 | 0 | 90.97
21:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 400 | 270 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 40 | 32 | 100 | 0 | 0 | 18 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 104 | 0 |  | 25 | 0 | 17 | 0 | 23 | 50 | 16 | 30 | 0 | 0 | 0 | 265 | 260 | 198 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 146 | 106 | 81 | 17 | 0 | 43 | 0 | 50 | 0 | 130 | 162 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 295 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 150 | 0 | 331 | 75 | 0 | 0 | 0 | 306 | 54 | 0 | 0 | 75 | 90 | 320 | 104 | 0 | 72 | 0 | 0 | 56 | 0 |  | 719 | 0 | 180 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 107 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 139 | 0 | 311 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 440 | 37 | 0 | 17 |  | 7345 | 2917 | 10262 | 3545 | 719 | 1500 | 3533 | 696 | 70 | 53 | 146 | 0 | 0 | 90.97
22:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 400 | 275 | 62 | 100 | 55 | 0 | 0 | 0 | 100 | 0 | 16 | 97 | 0 | 0 | 18 | 54 | 35 | 55 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 16 | 35 | 0 | 0 | 0 | 265 | 260 | 201 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 142 | 106 | 81 | 17 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 295 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 150 | 0 | 330 | 35 | 0 | 0 | 0 | 306 | 54 | 0 | 0 | 75 | 90 | 320 | 104 | 0 | 17 | 0 | 0 | 54 | 0 |  | 718 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 21 | 0 | 8 | 102 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 144 | 0 | 307 | 53 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 450 | 36 | 0 | 0 |  | 7070 | 2740 | 9810 | 3534 | 718 | 1498 | 3130 | 702 | 70 | 16 | 142 | 0 | 0 | 90.96
23:00 | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 345 | 0 |  | 0 | 350 | 265 | 0 | 80 | 55 | 0 | 0 | 0 | 75 | 0 | 16 | 50 | 0 | 0 | 18 | 54 | 35 | 55 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 60 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 16 | 39 | 0 | 0 | 0 | 265 | 260 | 204 | 0 | 141 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 140 | 106 | 81 | 17 | 0 | 44 | 0 | 50 | 0 | 110 | 162 | 35 | 83 | 0 | 137 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 140 | 0 | 100 | 150 | 0 | 330 | 0 | 0 | 0 | 0 | 306 | 54 | 0 | 0 | 8 | 90 | 341 | 81 | 0 | 0 | 0 | 0 | 55 | 0 |  | 718 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 103 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 144 | 0 | 330 | 53 | 0 | 94 | 0 | 70 | 0 | 0 | 70 | 450 | 72 | 0 | 0 |  | 6564 | 2604 | 9168 | 3494 | 718 | 1481 | 2546 | 703 | 70 | 16 | 140 | 0 | 0 | 90.96
24:00 | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 364 | 0 |  | 0 | 420 | 265 | 0 | 16 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 16 | 40 | 0 | 0 | 0 | 265 | 260 | 213 | 0 | 141 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 128 | 106 | 56 | 17 | 0 | 44 | 0 | 50 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 310 | 8 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 122 | 0 | 50 | 150 | 0 | 338 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 90 | 350 | 40 | 0 | 0 | 0 | 0 | 56 | 0 |  | 717 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 103 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 144 | 0 | 335 | 0 | 0 | 94 | 0 | 50 | 0 | 0 | 35 | 440 | 72 | 0 | 0 |  | 6191 | 2451 | 8642 | 3503 | 717 | 1613 | 1918 | 693 | 70 | 0 | 128 | 0 | 0 | 90.95
KWH | 0 | 0 | 0 | 4315500 | 7155564 | 300045 | 0 | 8309760 | 0 |  | 0 | 8994750 | 6551069 | 415680 | 896784 | 932155 | 0 | 0 | 0 | 1106880 | 310176 | 319200 | 1556975 | 0 | 0 | 268464 | 1093680 | 525664 | 601693 | 343116 | 600000 | 514980 | 604100 | 711300 | 30108 | 0 | 0 | 1673000 | 0 | 0 | 345974 | 0 | 0 | 2377632 | 0 |  | 391680 | 0 | 185985 | 25560 | 202560 | 1002240 | 372768 | 497280 | 0 | 0 | 0 | 6920000 | 6342000 | 4516000 | 0 | 3250240 | 272088 | 139200 | 0 | 0 | 0 | 41312 | 34171 | 487008 | 218160 | 819500 | 492300 | 2607360 | 2388800 | 740160 | 3888908 | 14600 | 599000 | 0 | 1143000 | 0 | 3221672 | 3733000 | 831552 | 1858560 | 0 | 2562090 | 425000 | 0 | 99000 | 7367000 | 190656 | 264000 | 0 | 5003125 | 0 | 0 | 4039200 | 0 | 2973888 | 101250 | 1387200 | 2543520 | 0 | 7986000 | 516000 | 569136 | 0 | 26508 | 6694255 | 556442 | 0 | 52440 | 692160 | 2256960 | 7367000 | 1574400 | 320310 | 459360 | 0 | 0 | 1249200 | 180773 |  | 17323636 | 0 | 5027040 | 0 | 446400 | 0 | 0 | 0 | 83040 | 0 | 60375 | 0 | 544510 | 714624 | 0 | 0 | 0 | 93152 | 27085 | 232240 | 166580 | 31757 | 59853 | 322560 | 70523 | 504480 | 0 | 192708 | 2338472 | 0 | 3671300 | 0 | 0 | 0 | 0 | 0 | 0 | 2004739 | 0 | 3859345 | 0 | 8045400 | 1271520 | 0 | 2079648 | 0 | 1896000 | 0 | 45400 | 2088192 | 11045500 | 782209 | 0 | 69600 |  | 155547786 | 65097888 | 220645674 | 87937115 | 17323636 | 35501845 | 56746215 | 17055272 | 1673000 | 1112390 | 2607360 | 688841 | 0
Fuel Cost | 0 | 0 | 0 | 6343785 | 7942676.04 | 396059.4 | 0 | 8392857.6 | 0 |  | 0 | 9804277.5 | 7271686.59 | 3155011.2 | 6178841.76 | 7886031.3 | 0 | 0 | 0 | 8334806.4 | 2828805.12 | 3140928 | 14355309.5 | 0 | 0 | 2440337.76 | 7983864 | 4063382.72 | 5932692.98 | 257337 | 450000 | 0 | 0 | 0 | 291144.36 | 0 | 0 | 451710 | 0 | 0 | 3214098.46 | 0 | 0 | 4041974.4 | 0 |  | 0 | 0 | 1804054.5 | 244098 | 1762272 | 7937740.8 | 469687.68 | 1476921.6 | 0 | 0 | 0 | 5120800 | 6342000 | 4154720 | 0 | 3737776 | 307459.44 | 194880 | 0 | 0 | 0 | 417251.2 | 326333.05 | 618500.16 | 163620 | 1434125 | 369225 | 19555200 | 2532128 | 6720652.8 | 4938913.16 | 232724 | 982360 | 0 | 2034540 | 0 | 3672706.08 | 3882320 | 1638157.44 | 3549849.6 | 0 | 4432415.7 | 930750 | 0 | 201960 | 7440670 | 142992 | 200640 | 0 | 37823625 | 0 | 0 | 21003840 | 0 | 29263057.92 | 1183612.5 | 11305680 | 27597192 | 0 | 7426980 | 4705920 | 5378335.2 | 0 | 0 | 50608567.8 | 4846609.82 | 0 | 523351.2 | 5931811.2 | 15031353.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99784143.36 | 0 | 5278392 | 0 | 3508704 | 0 | 0 | 0 | 871089.6 | 0 | 629107.5 | 0 | 843990.5 | 6974730.24 | 0 | 0 | 0 | 916615.68 | 275183.6 | 2055324 | 1282666 | 429354.64 | 579975.57 | 3125606.4 | 684073.1 | 968601.6 | 0 | 145879.956 | 14100986.16 | 0 | 19898446 | 0 | 0 | 0 | 0 | 0 | 0 | 3007108.5 | 0 | 4515433.65 | 0 | 7964946 | 13274668.8 | 0 | 19735859.52 | 0 | 14712960 | 0 | 501670 | 15431738.88 | 48489745 | 0 | 0 | 0 |  | 437757996.54 | 289987000.256 | 727744996.796 | 87193905.226 | 99784143.36 | 41556510.78 | 384051848.52 | 82489177.16 | 451710 | 10744495.25 | 19555200 | 1918006.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 370 | 260 | 16 | 45 | 50 | 0 | 0 | 0 | 85 | 16 | 0 | 68 | 0 | 0 | 9 | 54 | 35 | 35 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 18 | 0 | 0 | 125 | 0 |  | 21 | 0 | 0 | 0 | 0 | 45 | 14 | 3 | 0 | 0 | 0 | 265 | 260 | 159 | 0 | 138 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 10 | 82 | 24 | 17 | 2 | 8 | 0 | 45 | 0 | 130 | 162 | 35 | 83 | 0 | 91 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 149 | 17 | 90 | 100 | 0 | 330 | 35 | 50 | 0 | 4 | 307 | 35 | 0 | 0 | 26 | 90 | 322 | 104 | 48 | 17 | 0 | 0 | 56 | 20 |  | 717 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 111 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 167 | 0 | 338 | 105 | 0 | 94 | 0 | 113 | 0 | 7 | 113 | 430 | 10 | 0 | 0 |  | 9209 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 350 | 0 | 0 | 0 | 380 | 280 | 86 | 38 | 55 | 0 | 0 | 0 | 85 | 102 | 115 | 100 | 0 | 0 | 37 | 54 | 35 | 48 | 0 | 25 | 28 | 25 | 33 | 25 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 105 | 0 | 0 | 25 | 0 | 85 | 10 | 80 | 50 | 16 | 20 | 0 | 0 | 0 | 265 | 260 | 202 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 33 | 23 | 22 | 5 | 33 | 16 | 148 | 103 | 81 | 17 | 0 | 43 | 0 | 49 | 0 | 130 | 161 | 36 | 83 | 0 | 137 | 18 | 0 | 5 | 310 | 8 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 103 | 0 | 330 | 92 | 95 | 0 | 0 | 303 | 31 | 0 | 34 | 68 | 90 | 320 | 86 | 0 | 121 | 0 | 0 | 56 | 0 |  | 716 | 0 | 175 | 0 | 80 | 0 | 0 | 0 | 4 | 0 | 8 | 0 | 32 | 110 | 0 | 0 | 0 | 50 | 12 | 100 | 12 | 16 | 40 | 45 | 27 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 138 | 0 | 324 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 350 | 10 | 0 | 10 |  | 10755 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 200 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 16 | 20 | 0 | 0 | 0 | 300 | 300 | 225 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 147 | 110 | 82 | 17 | 0 | 43 | 0 | 51 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 20 | 0 | 10 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 320 | 104 | 0 | 144 | 116 | 0 |  |  |  | 723 | 16 | 240 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 85 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 170 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 51 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 200 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 16 | 10 | 0 | 0 | 0 | 300 | 300 | 225 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 135 | 110 | 82 | 17 | 1.6 | 43 | 0 | 51 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 20 | 0 | 10 | 341 | 8 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 320 | 104 | 50 | 144 | 116 | 0 |  | 30 |  | 723 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 85 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 170 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 51 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 338 | 0 | 0 | 0 | 360 | 265 | 0 | 0 | 22 | 0 | 0 | 0 | 20 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 35 | 0 | 22 | 25 | 22 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 26 | 16 | 10 | 0 | 0 | 0 | 265 | 260 | 181 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 0 | 100 | 108 | 16 | 17 | 1 | 43 | 0 | 50 | 0 | 110 | 161 | 37 | 83 | 0 | 137 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 98 | 0 | 0 | 192 | 0 | 105 | 7 | 50 | 100 | 0 | 331 | 0 | 0 | 0 | 1 | 305 | 16 | 0 | 0 | 0 | 90 | 320 | 46 | 17 | 0 | 0 | 0 | 56 | 9 | 0 | 717 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 160 | 0 | 365 | 53 | 0 | 92 | 0 | 95 | 0 | 2 | 70 | 430 | 72 | 0 | 0 | 0
199
| Minimum Generation |  | 7437 | 5:00
| Highest Generation |  | 10755 | 19:00
| Day Peak Generation |  | 9209 | 12:00
| Evening Peak Generation |  | 10755 | 19:00
| HVDC Max Flow |  | 719 | 21:00
| HVDC EvPeak Flow |  | 716 | 19:00
| Load factor L.F |  | 85.48%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9209 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6990 | MW
Evening Peak Generation : |  | 10755 | MW Hour : | 19:00 | Available Max Generation : |  | 13951 | MW
E.P. Demand (at gen end) : |  | 10755 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10800 | MW
Maximum Generation : |  | 10755 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3151 | MW
Total Gen. (MKWH) : |  | 220.6457 | System Load Factor : | 85.48% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -417 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-04
Actual : | 90.92 | Ft.(MSL) , | Rule curve : | 92.52 | Ft.( MSL )
Gas Consumed : | Total = | 924.35 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 128750416.006
: |  | Coal : | 82489177.16 | Oil : | 394796343.77 | Total : | 606035936.936
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3856.4141 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1310.7307 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1174.253 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1060.9946 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 958.8286 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 773.7391 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 433.4908 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 199.2396 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 596.7419 |  |  | 0 | 0%
Total | 0 |  | 10364.4324 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Kaptai-2
5) Raozan #1,2
6) Haripur 360 MW
7) Sirajganj #1 CCPP
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bhaluka 132/33 kV T-1 transformer was under shut down from 09:52 to 16:12 for D/W.
b) Bibiyana-Shahjibazar 230 kV Ckt-1 was under shut down from 09:05 to 15:59 for A/M.
c) Srimongal-Shahjibazar 132 kV Ckt-2 was under shut down from 09:22 to 18:23 for A/M.
d) Savar-Manikganj PP 132 kV Ckt-1 was under shut down from 08:53 to 12:13 for A/M.
e) Savar-Manikganj PP 132 kV Ckt-2 was under shut down from 12:14 to 13:55 for A/M.
f) Maniknagar 132 kV Reserve Bus was under shut down from 10:05 to 13:14 for D/W.
g) Khulshi-AKS 132 kV Ckt was under shut down from 08:34 to 18:43 for A/M.
h) Aminbazar-Manikganj PP 132 kV Ckt-1 was under shut down from 10:01 to 16:32 for A/M.
i) Amnura-Rajshahi(N) 132 kV Ckt was under shut down from 12:12 to 15:33 for C/M.
j) Daudkandi 132/33 kV T-1 transformer was under shut down from 09:49 to 10:26 for C/M.
k) Ghorashal-Ishurdi 230 kV Ckt-2 was under shut down from 08:15 to 17:58 for D/W..
l) Goalpara-Bagerhat 132 kV Ckt was under shut down from 08:16 to 13:28 for D/W.
m) Goalpara-Madaripur 132 kV Ckt-3 was under shut down from 08:11 to 20:58 for C/M.
n) Haripur-Meghnaghat 230 kV Ckt-1 was under shut down from 09:15 to 10:34 for D/W..
o) Haripur-Meghnaghat 230 kV Ckt-2 was under shut down from 12:21 to 13:28 for D/W..
p) Haripur-HPL 230 kV Ckt-2 was under shut down from 11:21 to 13:16 for D/W.
q) Hathazari 132 kV 801B, 812B Bus breakers were under shut down from 10:14 to 12:40 for D/W.
r) Joydevpur 132/33 kV GT-2 transformer was under shut down from 08:20 to 15:25 for C/M.
s) Kabirpur-Manikganj 132 kV Ckt-2 was under shut down from 09:51 to 20:40 for C/M.
t) Kallyanpur 132/33 kV GT-3 transformer was under shut down from 09:15 to 16:27 for D/W.
u) Keraniganj 230/132 kV T-2 transformer was under shut down from 11:13 to 13:23 for D/W. |  |  |  |  | About 42 MW power interruption occurred under Manikganj S/S area
v) Sylhet 225 MW ST was synchronized at 08:34 to 18:43 for A/M. |  |  |  |  | from 11:28 to 11:33.
w) Manikganj 132/33 kV GT-3 transformer tripped at 11:28 due to the tripping of solar power plant
and was switched on at 11:33.
x) Maniknagar 132 kV reserve Bus was under shut down from 10:05 to 13:14 for D/W. |  |  |  |  | About 110 MW power interruption occurred under Comilla(S) S/S area
y) Rajshahi 132/33 kV T-2 transformer was under shut down from 09:05 to 14:37 for C/M. |  |  |  |  | from 11:23 to 11:56.
z) Comilla(S)-Tripura 132 kV Ckts 1,2 tripped at 11:23 from Tripura end showing SPS malfunction |  |  |  |  | About 110 MW power interruption occurred under Comilla(S) S/S area
and was switched on at 11:56. |  |  |  |  | from 12:17 to 12:44.
aa) Comilla(S)-Tripura 132 kV Ckts 1,2 again tripped at 12:17 from Tripura end showing SPS malfunction
and was switched on at 12:44..
ab) Seven circle Cement 132/33 kV T-1 and T-2 transformers were switched on at 15:42 and 15:52. |  |  |  |  | About 42 MW power interruption occurred under Cox's Bazar S/S area
ac) Fenchuganj-Sreemangal 132 kV Ckt tripped at 14:29 from Fenchuganj end and was switched on at 16:14. |  |  |  |  | from 18:33 to 18:45.
ad) Cox's Bazar 132/33 kV T-3 transformer tripped at 18:33 showing Definite O/C,TCS not healthy at |  |  |  |  | About 36 MW power interruption occurred under Cox's Bazar S/S area
132 kV side and was switched on at 18:45. |  |  |  |  | from 19:08 to 19:35.
ae) Cox's Bazar 132/33 kV T-3 transformer again tripped at 19:08 showing Definite O/C,TCs not healthy
at 132 kV side and was switched on at 19:35.
af) Sherpur-Sirajganj 132 kV Ckt-2 was under shut down from 16:09 to 18:05 for protection test.
ag) Sherpur-Sirajganj 132 kV Ckt-1 was under shut down from 18:50 to 21:08 for protection test.
ah) Hathazari-Raozan 230 kV Ckt-1 was under shut down from 14:32 to 17:01 for CB timing test.
ai) Payra Unit-1 was synchronized at 19:07.
aj) Goalpara-Bagerhat 132 kV Ckt was shut down at 07:51(04/03/2021) for D/W.
ak) Sikalbaha 150 MW was under shut down at 23:20 for gas shortage.
al) Payra unit-2 was shut down at 00:13(04/03/2021).
am) Chandpur 150 MW CCPP tripped at 01:45(04/03/2021) due to problem with GBC.
an) B.Baria-Shahjibazar 132 kV Ckt-2 was shut down at 06:22(04/03/2021) for D/W.
ao) Barishal 132/33 kV T-1 transformer was under shut down from 06:57(04/03/2021) to 08:14 for C/M.
ap) Kallyanpur 132/33 kV GT-1 transformer was shut down at 07:18(04/03/2021) for C/M.
aq) Hathazari 132/33 kVT-1 transformer was under shut down from 07:55(04/03/2021) for sparking at
R,pole connector of 33 kV breaker.
ar) Ghorashal-Ishurdi 230 kV Ckt-2 was shut down at 07:37(04/03/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7155564
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 300045 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8309760 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8994750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 86 | 415680 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6551069 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 38 | 896784 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 932155
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1556975
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 343116 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 85 | 1106880 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 310176
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 37 | 268464 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1093680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 319200 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 525664 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 48 | 601693 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1114980 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 604100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 711300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 30108 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 290 | 5003125
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2973888
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 95 | 569136 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 86 | 1574400 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 121 | 459360 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 180773
| Dhaka area Total |  |  |  | 5972 | 3134 | 57218325
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 345974
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 101250
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1002240
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1673000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 105 | 2377632 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 185985
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 25560 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1387200
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 372768 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 497280
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 202560 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26508
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 303 | 6694255
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 31 | 556442 | Engine problem
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 2256960 | Engine problem
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 985 | 17705614
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 202 | 4516000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 6920000 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6342000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 272088 | Macine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 139200 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 41312
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 139 | 3250240 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 103 | 2543520 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 487008
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 218160 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2607360
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819500
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 23 | 34171 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 16 | 492300 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 52440 | Low demand
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 68 | 692160 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 56 | 1249200
| Cumilla Area Total |  |  |  | 2980 | 1422 | 30676659
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2388800 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 3888908 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 81 | 740160 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14600
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4039200 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 92 | 516000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 320310
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 391680
| Mymensingh Area Total |  |  |  | 709 | 518 | 12299658
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 599000
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3221672 | Frequency control.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3733000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1143000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 36 | 831552 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1858560
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 137 | 2562090 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 190656 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7367000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 330 | 7986000 | Gas shortage
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 5 | 99000 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 320 | 7367000 | On Test
| Sylhet Area Total |  |  |  | 1988 | 1641 | 37647530
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 716 | 17323636
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 80 | 446400 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 83040 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 5027040 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 8 | 60375 | Low demand
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1271520
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1088 | 24212011
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 714624
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 544510
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 90 | 2004739
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 350 | 11045500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 10 | 782209
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 10 | 69600 | Low demand
| Barisal Area Total |  |  |  | 1826 | 602 | 15161182
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 93152
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 12 | 27085 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 166580 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 31757 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 59853
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 138 | 3859345 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 324 | 8045400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 70523 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 504480
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 192708 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 45 | 322560 | Engine problem
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 232240
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2079648 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2088192
| Rajshahi Area Total |  |  |  | 2183 | 1000 | 17773523
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 108 | 2338472
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3671300 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1896000
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45400
| Rangpur Area Total |  |  |  | 605 | 365 | 7951172
| Total |  |  |  | 20929 | 10755 | 220645674
| Eastern Grid Total |  |  |  | 14031 | 7700 | 155547786
| Western Grid Total |  |  |  | 6898 | 3055 | 65097888
| National Grid Total |  |  |  | 20929 | 10755 | 220645674
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-03
(a) ENTIRE EASTERN GRID : |  | 6984 | MW | (b) ENTIRE WESTERN GRID : |  | 3328 | MW
i) Dhaka area |  | 3639 | MW | i) Khulna area |  | 1254 | MW
ii) Chittagong area |  | 1115 | MW | ii) Rajshahi area |  | 1074 | MW
iii) Comilla area |  | 947 | MW | iii) Barisal area |  | 294 | MW
iv) Mymensingh area |  | 895 | MW | iv) Rangpur area |  | 706 | MW
v) Sylhet area |  | 388 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10312 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 18:00 | Netrokona | 100 | 18:00 | Jessore | 105 | 19:00
Munsiganj | 92 | 20:00 | Jamalpur | 117 | 19:00 | Benapol | 54 | 19:00
Sonargaon | 50 | 19:00 | Sherpur | 110 | 18:30 | Jhenida | 92 | 19:00
Shyampur | 182 | 11:00 | Srimongal | 37 | 18:30 | Bottail | 106 | 19:00
Bhulta | 184 | 21:00 | Shahjibazar | 103 | 18:30 | G.K Project | 42 | 19:00
Madanganj | 53 | 12:00 | Fenchuganj | 29 | 19:00 | Faridpur | 142 | 19:00
Shitalakhya | 106 | 12:00 | Kulawara | 31 | 18:30 | Madaripur | 74 | 20:00
Rahim steel | 24 | 11:00 | Sylhet | 101 | 18:30 | Sariatpur | 48 | 19:00
Matuail | 78 | 9:00 | Chatak | 23 | 19:00 | Gopalganj | 68 | 19:00
Ghorasal | 85 | 0:00 | Sunamganj | 31 | 18:30 | Bagerhat | 88 | 18:30
Narsingdi | 145 | 20:00 | Biani Bazar | 42 | 18:30 | Mongla | 41 | 1:00
Haripur (SBU) | 101 | 15:00 | Comilla (S) | 152 | 20:00 | Satkhira | 87 | 19:00
Sreenagar |  |  | Comilla(N) | 109 | 18:00 | Gallamari | 20 | 8:00
Ullon | 69 | 20:00 | Chandpur | 53 | 19:30 | Magura | 42 | 19:00
Hasnabad | 85 | 12:00 | Feni | 103 | 18:30 | Norail | 27 | 19:00
Magbazar | 81 | 14:00 | Chowmuhani | 150 | 19:00 | Chuadanga | 75 | 19:00
Maniknagar | 63 | 13:00 | Ashuganj | 34 | 13:00 | Borguna | 12 | 18:30
Bangabhaban | 20 | 11:00 | Daudkandi | 116 | 20:00 | Barisal(N) | 31 | 18:30
Narinda | 74 | 19:00 | B.Baria | 131 | 21:00 | Barisal (S) | 94 | 18:30
Dhanmondi | 158 | 13:00 | Ramganj | 74 | 20:00 | Patuakhali | 92 | 21:00
Lalbag | 88 | 12:00 | Chaddagram | 33 | 18:30 | Bhandaria | 42 | 21:00
Madartek | 57 | 22:00 | PHP | 10 | 19:00 | Borhan Uddin | 31 | 22:00
Dhaka University |  |  | Kochua | 53 | 20:00 | Ishurdi | 47 | 19:00
Aftabnagar | 8 | 13:00 | Madunaghat | 63 | 18:30 | Ruppur Paromanobik | 2 | 1:00
Fatullah | 53 | 12:00 | Hathazari | 75 | 18:30 | Natore | 114 | 19:00
Nawabganj | 34 | 18:30 | Khulshi | 184 | 15:00 | Bogra | 140 | 18:30
Mirpur | 92 | 18:30 | Halishahar | 119 | 19:30 | Noagaon | 95 | 13:00
Kalyanpur | 81 | 19:00 | Baraulia | 149 | 23:00 | Rajshahi | 102 | 19:30
Gulshan | 106 | 15:00 | Sikalbaha | 24 | 19:30 | Rajshahi New | 13 | 18:30
Uttara | 70 | 18:30 | Dohazari | 72 | 18:30 | C.Nawabganj | 65 | 19:30
Uttara New | 23 | 18:30 | Cox'sbazar | 93 | 21:00 | Amnura | 40 | 19:00
Kamrangirchar | 90 | 13:00 | Chandraghona | 28 | 18:30 | Pabna | 81 | 18:30
Savar | 140 | 19:00 | Kaptai | 0 | #N/A | Shahjadpur | 88 | 19:30
Bhasantec | 130 | 14:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 80 | 8:00
Agargaon | 59 | 14:00 | Bakulia | 99 | 18:30 | Niyamatpur | 81 | 19:00
Satmosjid | 80 | 13:00 | Julda | 21 | 18:30 | Joypurhat | 57 | 19:00
Tongi | 106 | 18:00 | TK chemical | 24 | 18:30 | Sherpur(Bogura) | 46 | 8:00
Kabirpur | 225 | 18:30 | Modern Steel | 0 | #N/A | Mohastangor | 40 | 19:00
Basundhara | 123 | 19:00 | Shahmirpur | 23 | 18:30 | Bangura | 21 | 20:00
Manikganj | 59 | 13:00 | Khagrachhari | 22 | 19:30 | Rangpur | 129 | 19:00
Joydevpur | 145 | 18:30 | Matarbari | 33 | 19:30 | Lalmonirhat | 35 | 18:30
New Tongi | 88 | 18:30 | Baroiar Hat | 30 | 18:30 | Saidpur | 101 | 9:00
Korda | 246 | 15:00 | Rangamati | 10 | 18:30 | Purbasadipur | 89 | 19:00
Dhamrai | 104 | 19:30 | Abul Khair 230 | 143 | 2:00 | Thakurgaon | 67 | 19:00
Rajendrapur | 88 | 12:00 | BSRM | 155 | 5:00 | Palashbari | 106 | 19:00
Valuka | 96 | 18:30 | GPH Ispat | 18 | 15:00 | Barapukuria | 50 | 9:00
Tangail | 175 | 8:00 | Goalpara | 17 | 13:00 | Panchagar | 45 | 19:00
Mymensing | 204 | 19:00 | Central s/s | 93 | 20:00 | Joldhaka | 46 | 19:00
Kishorganj | 102 | 19:00 | Noapara | 52 | 19:00 | Kurigram | 50 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 21:00 | 402 | 15:00 | Kaliakoir | 401 | 0.75 | 389 | 0.625
| Bheramara | 397 | 20:00 | 392 | 19:00 | Bhulta | 393 | 0.875 | 379 | 0.625
| Ashuganj(N) | 396 | 19:00 | 385 | 16:00 | Gopalganj | 409 | 0.625 | 393 | 0.54167
| Payra | 411 | 3:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 234 | 15:00 | Hathazari | 229 | 18:30 | 222 | 4:00
| Ishurdi | 240 | 18:00 | 229 | 8:00 | Megnaghat | 241 | 18:30 | 234 | 9:00
| Ashuganj | 240 | 1:00 | 233 | 16:00 | Fenchuganj | 242 | 22:00 | 238 | 1:00
| Serajganj | 234 | 1:00 | 230 | 7:00 | Siddhirganj | 237 | 20:00 | 228 | 15:00
| Baghabari | 237 | 18:00 | 231 | 7:00 | Maniknagar | 235 | 20:00 | 226 | 16:00
| Barapukuria | 236 | 1:00 | 230 | 8:00 | Agargaon | 235 | 20:00 | 226 | 16:00
| Bogra | 234 | 1:00 | 225 | 8:00 | Barisal | 252 | 20:00 | 247 | 24:00
| Rajshahi | 237 | 5:00 | 227 | 8:00 | Bhola 225 MW | 255 | 18:00 | 249 | 1:00
| Khulna South | 241 | 18:00 | 225 | 7:00 | AKSML | 232 | 20:00 | 221 | 5:00
| Rampura | 232 | 18:00 | 227 | 15:00 | BSRM | 233 | 22:00 | 221 | 5:00
| Haripur | 237 | 19:00 | 229 | 12:00 | Bibiyana | 243 | 13:00 | 237 | 17:00
| Hasnabad | 234 | 7:00 | 228 | 12:00 | Bhulta | 237 | 20:00 | 228 | 16:00
| Shyampur | 292 | 3:00 | 220 | 16:00 | Ashuganj (S) | 238 | 22:00 | 232 | 10:00
| Aminbazar | 0 | 1:00 | 0 | 2:00 | Kaliakoir | 236 | 20:00 | 220 | 16:00
| Tongi | 233 | 21:00 | 224 | 15:00 | GPH | 232 | 19:30 | 222 | 5:00
| Comilla (N) | 235 | 19:00 | 226 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 20:00 | 131 | 15:00 | Madanhat | 138 | 0.8125 | 132 | 0.66667
| Munsiganj | 140 | 19:00 | 132 | 16:00 | Hathazari | 136 | 0.79167 | 132 | 0.625
| Sonargaon | 137 | 21:00 | 132 | 1:00 | Khulshi | 136 | 0.8125 | 130 | 0.625
| Shyampur | 133 | 21:00 | 127 | 16:00 | Halishahar | 137 | 0.77083 | 131 | 0.5
| Bhulta | 130 | 18:00 | 124 | 16:00 | Baraulia | 137 | 0.125 | 131 | 0.625
| Madanganj | 140 | 19:30 | 132 | 10:00 | Sikalbaha | 137 | 0.75 | 132 | 0.625
| Shitalakhya | 139 | 19:00 | 128 | 5:00 | Dohazari | 139 | 0.8125 | 128 | 0.66667
| Rahim steal | 137 | 20:00 | 132 | 1:00 | Cox'sbazar | 130 | 0.8125 | 120 | 0.95833
| Matuail | 138 | 20:00 | 131 | 15:00 | Chandraghona | 138 | 0.79167 | 131 | 0.041667
| Ghorasal | 140 | 18:30 | 135 | 15:00 | Kaptai | 0 | 0.041667 | 0 | 0.083333
| Narsinghdi | 131 | 8:00 | 129 | 13:00 | A. Khaer Stl. | 135 | 0.77083 | 130 | 0.625
| Haripur (SBU) | 137 | 19:00 | 131 | 16:00 | Bakulia | 137 | 0.77083 | 130 | 0.625
| Sreenagar |  |  |  |  | Julda | 139 | 0.77083 | 132 | 0.625
| Ullon | 132 | 20:00 | 127 | 12:00 | TK Chemical | 138 | 0.77083 | 132 | 0.20833
| Hasnabad | 135 | 18:30 | 128 | 16:00 | Modern Steel | 0 | 0.041667 | 0 | 0.083333
| Magbazar | 132 | 2:00 | 125 | 15:00 | Shahmirpur | 137 | 0.79167 | 132 | 0.041667
| Maniknagar | 136 | 21:00 | 131 | 16:00 | Khagrachhari | 136 | 0.8125 | 131 | 0.5
| Bangabhaban | 136 | 21:00 | 131 | 16:00 | Matarbari | 135 | 0.8125 | 122 | 0.70833
| Narinda | 136 | 21:00 | 131 | 16:00 | Baroiar Hat | 136 | 0.79167 | 131 | 0.041667
| Dhanmondi | 132 | 20:00 | 127 | 12:00 | Rangamati | 136 | 0.79167 | 131 | 0.083333
| Lalbag | 134 | 19:30 | 126 | 16:00 | Goalpara S/S | 137 | 10:00 | 127 | 7:00
| Madartek | 132 | 22:00 | 127 | 12:00 | Khulna Central S/S | 139 | 18:00 | 126 | 7:00
| Dhaka University |  |  |  |  | Noapara | 136 | 18:00 | 125 | 0.29167
| Aftabnagar | 132 | 18:30 | 127 | 15:00 | Jessore | 132 | 18:00 | 122 | 0.29167
| Fatullah | 134 | 21:00 | 128 | 16:00 | Benapol | 132 | 11:00 | 122 | 0.29167
| Nawabganj | 131 | 21:00 | 126 | 12:00 | Jhenida | 131 | 4:00 | 122 | 0.33333
| Mirpur | 137 | 20:00 | 129 | 15:00 | Bottail | 136 | 0.75 | 130 | 0.29167
| Kalyanpur | 136 | 20:00 | 130 | 15:00 | G.K Project | 141 | 4:00 | 138 | 0.54167
| Gulshan | 131 | 20:00 | 127 | 15:00 | Faridpur | 138 | 0.75 | 135 | 0.041667
| Uttara | 136 | 19:30 | 127 | 15:00 | Madaripur | 142 | 0.75 | 137 | 0.16667
| Uttara New | 136 | 20:00 | 128 | 15:00 | Shariyatpur S/S | 141 | 0.75 | 137 | 0.54167
| Kamrangirchar | 131 | 20:00 | 123 | 16:00 | Gopalganj | 144 | 0.16667 | 139 | 0.54167
| Savar | 137 | 20:00 | 128 | 15:00 | Bagerhat | 138 | 18:00 | 120 | 0.29167
| Bhasantec | 132 | 20:00 | 127 | 15:00 | Mongla | 133 | 0.75 | 122 | 0.29167
| Agargaon | 131 | 20:00 | 128 | 15:00 | Satkhira | 138 | 18:00 | 125 | 0.29167
| Satmosjid | 131 | 20:00 | 127 | 15:00 | Gallamari | 139 | 18:00 | 126 | 0.29167
| Tongi | 138 | 18:00 | 131 | 15:00 | Magura | 132 | 3:00 | 118 | 8:00
| Kabirpur | 137 | 18:30 | 125 | 15:00 | Narail | 132 | 0.20833 | 121 | 0.79167
| Basundhara | 136 | 19:00 | 129 | 15:00 | Chuadanga | 127 | 18:00 | 119 | 0.8125
| Manikganj | 139 | 23:00 | 128 | 11:00 | Borguna | 141 | 0.75 | 137 | 0.45833
| Joydevpur | 139 | 18:00 | 134 | 16:00 | Barisal(N) | 143 | 20:00 | 139 | 0.041667
| New Tongi | 137 | 19:00 | 130 | 15:00 | Barisal (S) | 141 | 18:00 | 138 | 0.041667
| Kodda | 137 | 19:00 | 124 | 16:00 | Patuakhali(S) | 138 | 6:00 | 134 | 17:00
| Dhamrai | 134 | 19:00 | 124 | 18:30 | Bhandaria | 139 | 0.375 | 135 | 0.041667
| Rajendrapur | 136 | 18:30 | 123 | 16:00 | Ishurdi | 139 | 0.75 | 133 | 0.29167
| Valuka | 127 | 22:00 | 116 | 7:00 | Ruppur Paromanobik | 139 | 0.75 | 133 | 0.29167
| Tangail | 134 | 2:00 | 125 | 7:00 | Natore | 137 | 20:00 | 130 | 8:00
| Mymensing | 129 | 22:00 | 119 | 7:00 | Bogra | 137 | 16:00 | 130 | 8:00
| Kishorganj | 132 | 4:00 | 124 | 18:30 | Noagaon | 132 | 1:00 | 121 | 8:00
| Netrokona | 127 | 24:00 | 114 | 7:00 | Rajshahi | 135 | 18:00 | 129 | 8:00
| Jamalpur | 141 | 19:00 | 121 | 7:00 | Rajshahi New | 136 | 18:00 | 129 | 8:00
| Sherpur | 140 | 21:00 | 123 | 5:00 | C.Nawabganj | 136 | 18:00 | 125 | 8:00
| Srimongal | 137 | 4:00 | 134 | 15:00 | Amnura | 137 | 18:00 | 127 | 13:00
| Shahjibazar | 134 | 6:00 | 132 | 16:00 | Pabna | 138 | 18:00 | 132 | 8:00
| Fenchuganj | 137 | 1:00 | 135 | 12:00 | Shahjadpur | 141 | 1:00 | 135 | 7:00
| Khulawara | 136 | 1:00 | 134 | 14:00 | Serajganj | 135 | 3:00 | 130 | 7:00
| Sylhet | 134 | 18:00 | 132 | 9:00 | Niyamatpur | 128 | 1:00 | 119 | 8:00
| Chatak | 133 | 24:00 | 131 | 1:00 | Joypurhat | 131 | 1:00 | 120 | 8:00
| Sunamganj | 132 | 1:00 | 130 | 11:00 | Sherpur(Bogura) | 137 | 1:00 | 129 | 8:00
| Biani Bazar | 134 | 24:00 | 131 | 7:00 | Mohastangor | 135 | 1:00 | 128 | 8:00
| Comilla(s) | 132 | 12:00 | 124 | 18:30 | Bangura | 140 | 18:00 | 136 | 7:00
| Comilla(n) | 142 | 19:00 | 135 | 15:00 | Rangpur | 136 | 1:00 | 125 | 8:00
| Chandpur | 144 | 19:00 | 140 | 1:00 | Lalmonirhat | 133 | 1:00 | 123 | 8:00
| Feni | 137 | 9:00 | 130 | 15:00 | Saidpur | 132 | 3:00 | 121 | 7:00
| Chowmuhani | 137 | 19:30 | 131 | 1:00 | Purbasadipur | 132 | 1:00 | 119 | 8:00
| Ashuganj | 136 | 1:00 | 134 | 15:00 | Thakurgaon | 130 | 1:00 | 120 | 8:00
| Daudkandi | 138 | 18:30 | 131 | 16:00 | Palashbari | 134 | 1:00 | 126 | 8:00
| B.Baria | 132 | 9:00 | 129 | 15:00 | Barapukuria | 136 | 1:00 | 130 | 8:00

## L-Curve
Date | 2021-03-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 62 | 6191 | 2451 | 8642 |  |  |  | QF-LDC-11
0:30 | 62 | 5984.5 | 2480.5 | 8465 | Date: | 2021-03-03
1:00 | 62 | 5778 | 2510 | 8288
1:30 | 68.5 | 5628 | 2464.5 | 8092.5
2:00 | 75 | 5478 | 2419 | 7897
2:30 | 74.5 | 5432.5 | 2376 | 7808.5 | [5 empty] | Gen. at Eve. Peak | 10755 | 9201 MW (19:30 )
3:00 | 74 | 5387 | 2333 | 7720 | [6 empty] | 19:00
3:30 | 80 | 5265.5 | 2316 | 7581.5 | [5 empty] | Gen. at Day Peak | 9209 | 8127 MW (12:00 )
4:00 | 86 | 5144 | 2299 | 7443 | [6 empty] | 12:00
4:30 | 88 | 5139 | 2301 | 7440 | [5 empty] | Highest Generation | 10755
5:00 | 90 | 5134 | 2303 | 7437 | [6 empty] | 19:00
5:30 | 81.5 | 5172 | 2316 | 7488
6:00 | 73 | 5210 | 2329 | 7539
6:30 | 85.5 | 5335 | 2434.5 | 7769.5
7:00 | 98 | 5460 | 2540 | 8000
7:30 | 145.5 | 5589.5 | 2587 | 8176.5
8:00 | 193 | 5719 | 2634 | 8353
8:30 | 113.5 | 5880.5 | 2690 | 8570.5
9:00 | 34 | 6042 | 2746 | 8788
9:30 | 69.5 | 6093 | 2753.5 | 8846.5
10:00 | 105 | 6144 | 2761 | 8905
10:30 | 102 | 6199 | 2753.5 | 8952.5
11:00 | 99 | 6254 | 2746 | 9000
11:30 | 55 | 6342.5 | 2762 | 9104.5
12:00 | 11 | 6431 | 2778 | 9209
12:30 | 25.5 | 6561 | 2760.5 | 9321.5
13:00 | 40 | 6691 | 2743 | 9434
13:30 | 33 | 6607 | 2708.5 | 9315.5
14:00 | 26 | 6523 | 2674 | 9197
14:30 | 45.5 | 6553.5 | 2657 | 9210.5
15:00 | 65 | 6584 | 2640 | 9224
15:30 | 64 | 6525 | 2621.5 | 9146.5
16:00 | 63 | 6466 | 2603 | 9069
16:30 | 67 | 6358.5 | 2562.5 | 8921
17:00 | 71 | 6251 | 2522 | 8773
17:30 | 76.5 | 6376 | 2620 | 8996
18:00 | 82 | 6501 | 2718 | 9219
18:30 | 249.5 | 7100.5 | 2886.5 | 9987
19:00 | 417 | 7700 | 3055 | 10755
19:30 | 344 | 7570 | 3046 | 10616
20:00 | 339 | 7408 | 2989 | 10397 |  |  |  | Executive Engineer
20:30 | 316 | 7376.5 | 2953 | 10329.5 |  |  |  | Network Operation Division
21:00 | 293 | 7345 | 2917 | 10262
21:30 | 260.5 | 7207.5 | 2828.5 | 10036
22:00 | 228 | 7070 | 2740 | 9810 |  |  |  |  | Page 6 of 7
22:30 | 160.5 | 6817 | 2672 | 9489
23:00 | 93 | 6564 | 2604 | 9168
23:30 | 77.5 | 6377.5 | 2527.5 | 8905
24:00 | 62 | 6191 | 2451 | 8642
9201 MW (19:30 )
8127 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-03 |  | Energy | 220645674
[11 empty] | 2021-03-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3503 | 717 | 1613 | 2546 | 693 | 70 | 0 | 0 | 128 | 0
0:30 | 3480.5 | 716.5 | 1553 | 2136.5 | 698.5 | 70 | 2 | 0 | 122 | 0 | Date: | 2021-03-03
1:00 | 3458 | 716 | 1493 | 1727 | 704 | 70 | 4 | 0 | 116 | 0
1:30 | 3474.5 | 716.5 | 1501.5 | 1508 | 704 | 70 | 4 | 0 | 114 | 0 | [7 empty] | Total Energy | 220.6457 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 3491 | 717 | 1510 | 1289 | 704 | 70 | 4 | 0 | 112 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3496.5 | 717 | 1515 | 1204 | 690 | 70 | 4 | 0 | 112 | 0 | [7 empty] | Energy Requirement | 220.6457
3:00 | 3502 | 717 | 1520 | 1119 | 676 | 70 | 4 | 0 | 112 | 0
3:30 | 3506.5 | 716.5 | 1481.5 | 1036 | 656 | 70 | 4 | 0 | 111 | 0 | [6 empty] | Shortage
4:00 | 3511 | 716 | 1443 | 953 | 636 | 70 | 4 | 0 | 110 | 0
4:30 | 3510 | 716 | 1447 | 949.5 | 636.5 | 70 | 4 | 0 | 107 | 0
5:00 | 3509 | 716 | 1451 | 946 | 637 | 70 | 4 | 0 | 104 | 0
5:30 | 3511.5 | 716.5 | 1464 | 982.5 | 636.5 | 70 | 4 | 0 | 103 | 0
6:00 | 3514 | 717 | 1477 | 1019 | 636 | 70 | 4 | 0 | 102 | 0
6:30 | 3542.5 | 717 | 1488.5 | 1207 | 636 | 70 | 4 | 0 | 101 | 3.5 |  |  |  |  | Coal
7:00 | 3571 | 717 | 1500 | 1395 | 636 | 70 | 4 | 0 | 100 | 7
7:30 | 3551 | 716.5 | 1457.5 | 1615.5 | 645 | 70 | 4 | 0 | 98 | 19 |  |  |  | Oil |  |  |  | ,
8:00 | 3531 | 716 | 1415 | 1836 | 654 | 70 | 4 | 0 | 96 | 31
8:30 | 3471 | 716 | 1439 | 2070.5 | 659 | 70 | 4 | 0 | 99 | 42
9:00 | 3411 | 716 | 1463 | 2305 | 664 | 70 | 4 | 0 | 102 | 53
9:30 | 3391 | 716.5 | 1451 | 2375.5 | 674.5 | 70 | 4 | 0 | 103 | 61
10:00 | 3371 | 717 | 1439 | 2446 | 685 | 70 | 4 | 0 | 104 | 69
10:30 | 3367 | 717 | 1429 | 2487.5 | 688.5 | 70 | 3.5 | 0 | 108 | 82
11:00 | 3363 | 717 | 1419 | 2529 | 692 | 70 | 3 | 0 | 112 | 95
11:30 | 3394 | 717 | 1417 | 2654 | 691.5 | 70 | 3.5 | 0 | 61 | 96.5
12:00 | 3425 | 717 | 1415 | 2779 | 691 | 70 | 4 | 0 | 10 | 98
12:30 | 3434 | 717 | 1434 | 2814 | 703 | 70 | 4 | 0 | 42 | 103.5
13:00 | 3443 | 717 | 1453 | 2849 | 715 | 70 | 4 | 0 | 74 | 109
13:30 | 3443 | 717 | 1453 | 2849 | 715 | 70 | 4 | 0 | 74 | 109
14:00 | 3443 | 717 | 1453 | 2849 | 715 | 70 | 4 | 0 | 74 | 109
14:30 | 3461 | 717 | 1430.5 | 2768 | 696 | 70 | 4 | 0 | 89 | 93.5
15:00 | 3479 | 717 | 1408 | 2687 | 677 | 70 | 4 | 0 | 104 | 78
15:30 | 3472.5 | 716.5 | 1404.5 | 2634.5 | 677 | 70 | 5.5 | 0 | 103 | 63
16:00 | 3466 | 716 | 1401 | 2582 | 677 | 70 | 7 | 0 | 102 | 48
16:30 | 3472.5 | 716 | 1378 | 2463 | 677.5 | 70 | 17.5 | 0 | 95 | 31.5
17:00 | 3479 | 716 | 1355 | 2344 | 678 | 70 | 28 | 0 | 88 | 15
17:30 | 3459 | 716 | 1333.5 | 2527.5 | 643 | 70 | 148.5 | 0 | 91 | 7.5
18:00 | 3439 | 716 | 1312 | 2711 | 608 | 70 | 269 | 0 | 94 | 0
18:30 | 3479 | 716 | 1391.5 | 3234 | 608 | 70 | 367.5 | 0 | 121 | 0
19:00 | 3519 | 716 | 1471 | 3757 | 608 | 70 | 466 | 0 | 148 | 0
19:30 | 3530 | 716 | 1422 | 3650 | 638 | 70 | 448 | 0 | 142 | 0
20:00 | 3546 | 718 | 1481 | 3604 | 647 | 70 | 179 | 0 | 152 | 0
20:30 | 3545.5 | 718.5 | 1490.5 | 3568.5 | 671.5 | 70 | 116 | 0 | 149 | 0
21:00 | 3545 | 719 | 1500 | 3533 | 696 | 70 | 53 | 0 | 146 | 0
21:30 | 3539.5 | 718.5 | 1499 | 3331.5 | 699 | 70 | 34.5 | 0 | 144 | 0
22:00 | 3534 | 718 | 1498 | 3130 | 702 | 70 | 16 | 0 | 142 | 0
22:30 | 3514 | 718 | 1489.5 | 2838 | 702.5 | 70 | 16 | 0 | 141 | 0
23:00 | 3494 | 718 | 1481 | 2546 | 703 | 70 | 16 | 0 | 140 | 0
23:30 | 3498.5 | 717.5 | 1547 | 2546 | 698 | 70 | 8 | 0 | 134 | 0 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3503 | 717 | 1613 | 2546 | 693 | 70 | 0 | 0 | 128 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1673000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 3 | 16 | 16 | 16 | 16 | 18 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 |  |  |  | 345974
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 3 | 4 | 10 | 17 | 17 | 17 | 15 | 12 | 7 | 2 | [9 empty] | 101250
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 123 | 110 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 104 | 104 | 60 | 0 | 2377632
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 73 |  | 85 | 85 | 17 | 17 |  |  |  | 185985
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 33 | 33 | [5 empty] | 41312
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 45 | 15 | 15 | 15 | 15 | 86 | 160 | 225 | 245 | 245 | 245 | 258 | 269 | 272 | 270 | 270 | 286 |  | 290 | 290 | 285 | 295 | 295 | 200 | 200 | 5003125
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 7155564
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 272088
33 | Ashuganj 225 MW CCPP | 196 | 196 | 200 | 200 | 203 | 204 | 197 | 187 | 157 | 163 | 152 | 159 | 154 | 164 | 187 | 184 | 184 | 197 |  | 202 | 202 | 203 | 198 | 201 | 204 | 213 | 4516000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6342000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 |  | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 6920000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 139200
36 | Chandpur 150 MW CCPP | 137 | 138 | 138 | 137 | 137 | 137 | 137 | 137 | 130 | 136 | 126 | 138 | 128 | 138 | 140 | 135 | 131 | 132 |  | 139 | 135 | 139 | 139 | 139 | 141 | 141 | 3250240
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 336 | 341 | 335 | 335 | 344 | 337 | 343 | 343 | 336 | 337 | 338 | 338 | 338 | 340 | 347 | 343 | 340 |  | 350 | 338 | 339 | 338 | 338 | 345 | 364 | 8309760
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 400 | 350 | 350 | 350 | 350 | 320 |  | 380 | 380 | 400 | 400 | 400 | 350 | 420 | 8994750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 105 | 106 | 106 | 106 | 107 | 107 | 107 | 108 | 106 | 103 | 103 | 82 | 84 | 84 | 100 | 100 | 103 | 103 |  | 103 | 105 | 105 | 106 | 106 | 106 | 106 | 2388800
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 15 | 23 | 36 | 45 | 48 | 49 | 44 | 34 | 20 | 6 | [9 empty] | 320310
44 | Fenchugonj CCPP Phase-1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8 | 17 | 18 | 18 | 20 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 599000
45 | Fenchugonj CCPP Phase-2 | [9 empty] | 0
46 | Shajibazar 330 MW CCPP | 162 | 161 | 161 | 162 | 162 | 161 | 162 | 160 | 162 | 162 | 160 | 162 | 163 | 162 | 162 | 162 | 163 | 162 |  | 161 | 160 | 162 | 162 | 161 | 162 | 162 | 3733000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 36 | 36 | 35 | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 20 |  | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 831552
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 80 | 40 | 40 | 77 | 77 | 77 | 80 | 80 | 83 | 83 | 80 | 82 | 82 | 82 | 84 | 60 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1858560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 30 | 21 | 30 | 91 | 113 | 113 | 137 | 137 | 137 | 137 |  | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 2562090
51 | Sylhet 20 MW GTPP | 19 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 99000
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 48 | 48 | 45 | 48 | 48 | 49 | 53 | 53 | 14 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 1143000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190656
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 310 | 290 | 295 | 300 | 300 | 305 | 305 | 290 | 290 | 290 | 300 | 290 | 310 | 300 | 300 | 300 |  | 310 | 290 | 280 | 290 | 290 | 300 | 310 | 7367000
| Bibiyana South 400 MW | 270 | 300 | 289 | 275 | 270 | 270 | 300 | 270 | 270 | 270 | 320 | 322 | 313 | 334 | 320 | 350 | 320 | 320 |  | 320 | 320 | 321 | 320 | 320 | 341 | 350 | 7367000
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 10 | 17 | 17 | 35 | 35 | 35 | 45 | 55 | 17 | 17 |  | 48 | 55 | 55 | 55 | 55 | 55 |  | 601693
59 | Tangail Palli Power Gen 22 MW | 24 | [6 empty] | 2 | 24 | 24 | 21 | 21 | 19 | 19 | 19 | 20 | 19 | 24 |  | 25 | 24 | 24 | 25 | 24 | 25 | 24 | 391680
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 372768
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 |  | 22 |  |  |  | 22 | 22 | 22 |  |  | 22 | 343116
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 3888908
63 | Impoprt (Tripura) | 116 | 112 | 112 | 110 | 104 | 102 | 100 | 96 | 102 | 104 | 112 | 10 | 74 | 106 | 104 | 102 | 88 | 94 |  | 148 | 142 | 152 | 146 | 142 | 140 | 128 | 2607360
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 40 | 40 | 40 | 36 | 7 | 4 | 3 | 3 | 3 | 5 | 4 | 3 | 3 | 4 | 5 |  | 20 | 30 | 30 | 30 | 35 | 39 | 40 | 497280
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 487008
66 | Feni 11 MW PP (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 218160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 19 | 20 | 20 | 20 | 11 | 11 | 16 |  | 16 | 16 | 20 | 20 | 20 | 20 | 21 | 492300
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 514980
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 711300
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 300045
| Feni Lanka Power | [17 empty] | 34 |  | 34 | [6 empty] | 52440
| Chowmuhani 113 MW | [10 empty] | 16 | 26 | 26 | 8 | 8 | 8 | 8 | 40 |  | 68 | 75 | 75 | 75 | 75 | 8 |  | 692160
| Manikgonj 162MW PP(MPGL) | [10 empty] | 1 | 17 | 17 |  |  |  |  | 24 |  | 121 | 108 | 108 | 72 | 17 |  |  | 459360
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 45 | 50 | 55 | 85 | 100 | 60 | 60 | 30 | 30 | 30 |  | 85 | 100 | 100 | 100 | 100 | 75 | 30 | 1106880
78 | Gazipur 52 MW PP | [17 empty] | 15 |  | 25 | [6 empty] | 30108
79 | Kodda 150MW PP | [16 empty] | 20 | 82 |  | 115 | 82 | 48 | 32 | 16 | 16 |  | 319200
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 17 | 40 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 24 |  | 81 | 81 | 81 | 81 | 81 | 81 | 56 | 740160
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 4 |  | 23 | [6 empty] | 34171
| Gazipur 100 MW PP | [8 empty] | 8 | 35 | 40 | 50 | 50 | 35 | 35 | 35 | 35 | 36 |  | 95 | 52 | 17 |  |  |  |  | 569136
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 3 | 2 | 0 | [9 empty] | 26508
| Jodiac Power | [8 empty] | 6 | 17 | 19 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 31 | 54 | 54 | 54 | 54 | 54 |  | 556442
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [9 empty] | 10 | 15 | 45 | 81 | 48 | 48 | 30 | 30 | 30 |  | 38 | 64 | 72 | 100 | 100 | 80 | 16 | 896784
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 87 | 87 | 87 | 10 | 10 | 10 | 10 | 35 | 60 | 60 | 60 | 68 | 67 | 62 | 60 | 60 | 72 | 98 |  | 100 | 100 | 100 | 100 | 97 | 50 |  | 1556975
86 | Meghnaghat CCPP(Summit) | 255 | 285 | 280 | 280 | 275 | 270 | 290 | 280 | 260 | 265 | 250 | 260 | 240 | 290 | 290 | 290 | 260 | 280 |  | 280 | 280 | 260 | 270 | 275 | 265 | 265 | 6551069
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 2 | 16 | 16 |  |  |  | 1 | 19 |  | 86 | 100 | 100 | 100 | 62 |  |  | 415680
| Meghnaghat 104 MW PP (OPCL) | 47 | [6 empty] | 11 | 65 | 98 | 104 | 104 | 104 | 104 | 104 | 104 | 89 | 71 |  | 86 | 104 | 100 | 104 | 104 | 81 | 40 | 1574400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 10 | [6 empty] | 25560
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 12 | 16 | 16 | 7 | 7 |  | 4 | 40 |  | 102 | 76 | 74 | 40 |  |  |  | 310176
95 | Patenga 50MW PP (Baraka) | 50 | 32 | 19 | 18 | 18 | 19 | 19 | 19 | 39 | 50 | 48 | 45 | 45 | 46 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1002240
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 4 | 33 |  | 80 | 62 | 56 | 23 |  |  |  | 202560
97 | katpotti 52 MW | [11 empty] | 9 | 24 | 12 | 12 | 12 | 12 | 13 |  | 37 | 18 | 18 | 18 | 18 | 18 |  | 268464
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | [5 empty] | 15 | 35 | 40 | 40 | 40 | 50 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 932155
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 525664
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 130 | 163 | 130 | 130 | 130 | 110 | 110 |  | 130 | 130 | 130 | 130 | 130 | 110 | 163 | 3221672
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14600
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1093680
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 120 | 100 | 100 | 80 | 80 | 80 | 98 | 192 | 194 | 194 | 194 | 192 | 200 | 200 | 200 | 200 | 170 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4039200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 72 | 71 | 70 | 70 | 70 | 70 | 105 | 124 | 132 | 149 | 149 | 149 | 149 | 131 | 132 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 140 | 122 | 2973888
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 90 | 90 | 90 | 100 | 100 | 70 | 40 | 74 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1387200
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 65 | 65 | 68 | 98 | 98 | 94 | 83 | 84 | 100 | 99 | 99 | 100 | 99 | 100 | 100 |  | 103 | 130 | 131 | 150 | 150 | 150 | 150 | 2543520
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 330 | 335 | 328 | 331 | 331 | 329 | 334 | 330 | 326 | 330 | 330 | 330 | 331 | 331 | 329 | 329 | 329 | 305 |  | 330 | 331 | 331 | 331 | 330 | 330 | 338 | 7986000
| Jamalpur 115 MW PP (United) | [11 empty] | 35 | 45 | 24 | 24 | 24 | 24 | 34 |  | 92 | 75 | 75 | 75 | 35 |  |  | 516000
| Anwara 300 MW PP (United) | 308 | 272 | 231 | 198 | 196 | 233 | 269 | 269 | 304 | 306 | 306 | 307 | 300 | 306 | 306 | 303 | 250 | 215 |  | 303 | 303 | 306 | 306 | 306 | 306 | 306 | 6694255
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2256960
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 56 | 55 | 55 |  | 56 | 55 | 52 | 56 | 54 | 55 | 56 | 1249200
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 10 | 20 | 13 | 21 | 20 | 31 | 30 | 23 | 14 | 5 | [9 empty] | 180773
120 | Eastern Zone Total | 5778 | 5478 | 5387 | 5144 | 5134 | 5210 | 5460 | 5719 | 6042 | 6144 | 6254 | 6431 | 6691 | 6523 | 6584 | 6466 | 6251 | 6501 |  | 7700 | 7570 | 7408 | 7345 | 7070 | 6564 | 6191 | 155547786
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [8 empty] | 32 | 32 | 32 | 16 | 16 | 16 | 16 |  | 5 | 43 |  | 80 | 66 | 83 | 66 |  |  |  | 446400
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | 7 | 8 | 7 |  | 4 | 4 | 4 | 4 |  |  |  | 83040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 53 | 70 | 90 | 94 | 105 | 105 | 53 | 53 | 53 | 35 | 70 |  | 105 | 105 | 105 | 105 | 53 | 53 | 0 | 1271520
130
131
132 | United Payra Power Ltd. | [19 empty] | 10 | 27 | 27 | 17 |  |  |  | 69600
133 | Bhola Nutan Biddut BD LTD (GAS) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 12 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 9 | 9 |  | 10 | 3 | 35 | 37 | 36 | 72 | 72 | 782209
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 16 | 16 | 16 | 32 | 32 | 32 | 48 |  | 110 | 110 | 110 | 110 | 96 | 32 | 0 | 714624
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 84 | 84 | 84 | 84 | 83 | 83 | 85 | 54 | 84 | 85 | 81 | 83 | 83 | 84 | 80 | 81 | 87 | 90 |  | 90 | 90 | 91 | 92 | 92 | 76 | 75 | 2004739
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 28 | 24 | 24 | 23 | 23 | 23 | 20 | 14 | 17 | 18 | 19 | 20 | 19 | 20 | 21 | 21 | 21 | 27 |  | 32 | 32 | 32 | 33 | 32 | 27 | 21 | 544510
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 24 | 8 | 8 | 8 | [5 empty] | 8 |  | 8 | [6 empty] | 60375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 716 | 717 | 717 | 716 | 716 | 717 | 717 | 716 | 716 | 717 | 717 | 717 | 717 | 717 | 717 | 716 | 716 | 716 |  | 716 | 716 | 718 | 719 | 718 | 718 | 717 | 17323636
147 | Bheramara 410 MW CCPP | 180 | 180 | 200 | 225 | 225 | 230 | 265 | 260 | 245 | 230 | 225 | 210 | 200 | 195 | 180 | 175 | 175 | 175 |  | 175 | 175 | 175 | 180 | 185 | 185 | 185 | 5027040
148 | Payra 1320 MW | 470 | 470 | 440 | 400 | 400 | 400 | 400 | 420 | 430 | 430 | 430 | 430 | 450 | 420 | 420 | 420 | 420 | 350 |  | 350 | 380 | 390 | 440 | 450 | 450 | 440 | 11045500
149
150 | Barapukuria TPP Unit-1 | 84 | 84 | 86 | 86 | 87 | 86 | 86 | 84 | 84 | 105 | 112 | 111 | 115 | 110 | 107 | 107 | 108 | 108 |  | 108 | 108 | 108 | 107 | 102 | 103 | 103 | 2338472
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 3671300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 5 |  | 50 | 50 | 50 |  |  |  |  | 93152
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 158 | 165 | 167 | 167 | 167 | 164 | 158 | 146 | 138 | 138 | 138 |  | 138 | 138 | 138 | 139 | 144 | 144 | 144 | 3859345
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 344 | 355 | 357 | 340 | 344 | 328 | 356 | 332 | 338 | 330 | 311 | 338 | 303 | 346 | 330 | 328 | 294 | 334 |  | 324 | 291 | 307 | 311 | 307 | 330 | 335 | 8045400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 12 | 27 | [5 empty] | 27085
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 21 | 22 | 22 | 504480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192708
165 | Amnura 50 MW PP(Sinha) | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  |  | 166580
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 |  | 16 | [6 empty] | 31757
167 | Katakhali 50 MW Peaking PP | [17 empty] | 10 |  | 40 | 40 | [5 empty] | 59853
168 | Santahar 50 MW Peaking PP | [17 empty] | 27 |  | 27 | 27 | [5 empty] | 70523
169 | Natore 52 MW PP (Rajlanka) | [8 empty] | 25 | 25 | 25 | 25 | 25 | 8 | 8 |  |  | 22 |  | 45 | 52 | 52 | 52 | 26 |  |  | 322560
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 60 |  | 100 | 100 | 60 |  |  |  |  | 232240
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 70 | 35 | 35 | 35 | 45 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2079648
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 35 |  |  |  | 10 | 70 | 105 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 2088192
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 50 | 10 |  |  |  | 17 | 57 | 106 | 110 | 106 | 108 | 113 | 113 | 113 | 113 | 113 | 74 | 52 |  | 107 | 107 | 107 | 107 | 113 | 70 | 50 | 1896000
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 6 | 7 | 6 | 6 | 5 | 4 | 2 | 0 | [8 empty] | 45400
178
178