## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-05 | Friday
|  | Date (day): | 2021-03-05 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13713.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14581 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-04 | 2021-03-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 180 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 357 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27-02-2021
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 1 | 64 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 260 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 80 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 61 | 87 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 80 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 72 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 25 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 82 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 44 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 49 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 230 | 265 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 118 | 122 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 70 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 5 | 72 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 29 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2466 | 2988 | 3832 | 4054 | 204 | 1555
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 46 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 10 | 100 | 100 | 50
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 85 | 85
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 70 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 16 | 16 |  | 6 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 21 | 30 | 30
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 287 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 39 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 702 | 947 | 1433 | 1458 | 795 | 104
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 161 | 199 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 300 | 300 | 300 | 60 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 300 | 300 | 60 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 3 | 10 | 10 | 35 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 94 | 92 | 94 |  | 163 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 114 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 146 | 135 | 147
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 16 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 11 | 21 | 20 | 20
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 72 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 56 | 56 | 55 | 55
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 949 | 1339 | 1687 | 1951 | 798 | 163
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 85 | 105 | 150 | 150 | 52 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 17 | 17 |  | 5 | Engine problem
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 46 | 82 | 82 |  | 13 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 192 | 193 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 39 | 76 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 409 | 444 | 637.6 | 586 | 52 | 18
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under S/D
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 162 | 162 | 162 |  | 168 | GT-1 under S/D for Gas shortage
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 48 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 36 | 36 | 36 |  | 30 | GT-9 Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 136 | 163 | 137 | 137
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 360 | 330 | 350 | 350
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 7 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 342 | 320 | 370 | 400 |  |  | On Test
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1708 | 1710 | 1793 | 1823 | 0 | 434
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 717 | 836 | 852 | 827
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 17 | 66 | 115 | 115
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 6 | 60 | 60 |  | 49 | Engine problem
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 190 | 180 | 240 | 240 | 170 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
110 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
111 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
112 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 977 | 1233 | 1587 | 1848 | 170 | 78
113 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 110 | 110
114 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 26 | 26 | 27 |  | 6 | Engine problem
115 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
116 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 44 | 75 | 95 | 95
117 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 410 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 70 | 70 | 70 | 70 |  |  | On Test
118 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 545 | 629 | 1071 | 1072 | 0 | 200
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
122 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 12 | 12 |  | 38 | Engine problem
123 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
124 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
125 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 150 | 170 | 170 | 50 |  | Gas shortage and FGMO
128 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 408 | 354 | 400 | 400 |  |  | FGMO
129 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 34
130 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
131 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
133 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
134 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 104 | 104
135 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
136 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113 |  | 0 | Engine problem
137 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 866 | 981 | 1297 | 1421 | 651 | 38
138 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 124 | 112 | 105 | 105
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
139 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage
140 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
141 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
142 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 107 | 113 | 113
143 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 392 | 369 | 376 | 368 | 124 | 125
| Total |  |  |  |  | 21395 | 20929 | 9014 | 10640 | 13713.6 | 14581 | 2794 | 2715
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8661.5729 | 10224 | 13177.4292 | 14010.9158
A. |  | 2021-03-04 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10640 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6990 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10640 | MW
3 | Day peak Generation : |  |  | 9014 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10224 | MW
4 | Evening peak Generation : |  |  | 10640 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 213.0809 | MKWHr | By Solar | 0.71043 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 118.3506 | MKWHr |  | By Oil: | 53.6431 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 17.5333 | MKWHr |  | By Hydro: | 1.7 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2794 | MW | Dhaka | 3643 | 3643 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2715 | MW | Chittagong | 1139 | 1139 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 5509 | MW | Khulna | 1257 | 1257 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 926.94 | MMCFD |  |  | Rajshahi | 1065 | 1065 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 118935029.63 | ii) Oil : | Taka | 370877728.34 | Comilla | 914 | 914 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 84941881.16 | Total | Taka | 574754639.13 | Mymensingh | 879 | 879 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.788 | MKWHr. | Sylhet | 369 | 369 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -192 | MW (E to W) at | 19:00 | hrs | Barisal | 278 | 278 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -215 | MW at | 20:00 | hrs | Rangpur | 680 | 680 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.4° C |  |  | Total | 10224 | 10224 |  | 0
B. |  | 2021-03-05 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14581 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 4981 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 192.2534 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7363 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.2895 | MKWHr. | ii) HVDC Flow at Peak Time |  | 836 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8541 | MKWHr. | iii) Maximum HVDC Flow : |  | 837 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.92 |  | (b) Today: | 70.73 |  | (c) Rule Curve: |  | 92.36
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 362 | 0 |  | 0 | 420 | 270 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 40 | 0 | 0 | 0 | 265 | 260 | 206 | 0 | 139 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 126 | 107 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 19 | 0 | 5 | 315 | 8 | 11 | 0 | 100 | 0 | 0 | 140 | 0 | 82 | 0 | 0 | 130 | 0 | 344 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 719 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 103 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 144 | 0 | 380 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 440 | 73 | 0 | 0 |  | 5455 | 2420 | 7875 | 3230 | 719 | 1670 | 1367 | 693 | 70 | 0 | 126 | 0 | 0 | 90.95
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 346 | 0 |  | 0 | 390 | 260 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 265 | 260 | 200 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 104 | 107 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 162 | 37 | 83 | 0 | 137 | 18 | 0 | 5 | 300 | 8 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 68 | 0 | 0 | 100 | 0 | 333 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 0 | 0 | 0 | 0 | 56 | 0 |  | 718 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 144 | 0 | 400 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 450 | 73 | 0 | 0 |  | 4967 | 2439 | 7406 | 3055 | 718 | 1608 | 1151 | 700 | 70 | 0 | 104 | 0 | 0 | 90.94
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 345 | 0 |  | 0 | 390 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 41 | 0 | 0 | 0 | 265 | 260 | 201 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 104 | 107 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 163 | 37 | 83 | 0 | 137 | 18 | 0 | 5 | 305 | 8 | 11 | 0 | 15 | 0 | 0 | 60 | 0 | 64 | 0 | 0 | 100 | 0 | 327 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 0 | 0 | 0 | 0 | 56 | 0 |  | 718 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 102 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 144 | 0 | 400 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 430 | 72 | 0 | 0 |  | 4826 | 2378 | 7204 | 3045 | 718 | 1600 | 985 | 682 | 70 | 0 | 104 | 0 | 0 | 90.94
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 343 | 0 |  | 0 | 390 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 0 | 0 | 0 | 265 | 260 | 205 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 106 | 108 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 160 | 37 | 80 | 0 | 137 | 19 | 0 | 5 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 0 | 100 | 0 | 329 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 718 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 102 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 145 | 0 | 380 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 430 | 72 | 0 | 0 |  | 4772 | 2304 | 7076 | 3043 | 718 | 1563 | 894 | 682 | 70 | 0 | 106 | 0 | 0 | 90.93
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 337 | 0 |  | 0 | 360 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 0 | 0 | 0 | 265 | 260 | 212 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 104 | 108 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 160 | 37 | 80 | 0 | 137 | 18 | 0 | 5 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 100 | 0 | 329 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 90 | 327 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 718 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 101 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 150 | 0 | 370 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 430 | 73 | 0 | 0 |  | 4695 | 2295 | 6990 | 3022 | 718 | 1505 | 890 | 681 | 70 | 0 | 104 | 0 | 0 | 90.93
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 348 | 0 |  | 0 | 360 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 0 | 0 | 0 | 265 | 260 | 200 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 96 | 108 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 155 | 37 | 80 | 0 | 136 | 18 | 0 | 5 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 81 | 0 | 57 | 0 | 0 | 100 | 0 | 349 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 0 | 0 | 0 | 0 | 55 | 0 |  | 718 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 102 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 151 | 0 | 397 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 430 | 74 | 0 | 0 |  | 4803 | 2369 | 7172 | 3104 | 718 | 1542 | 960 | 682 | 70 | 0 | 96 | 0 | 0 | 90.92
7:00 | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 357 | 0 |  | 0 | 360 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 34 | 0 | 0 | 0 | 265 | 260 | 193 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 88 | 108 | 0 | 17 | 0 | 44 | 0 | 50 | 0 | 130 | 155 | 37 | 80 | 0 | 136 | 18 | 0 | 5 | 310 | 8 | 11 | 0 | 17 | 0 | 0 | 132 | 0 | 103 | 2 | 20 | 100 | 0 | 352 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 90 | 350 | 0 | 4 | 0 | 0 | 0 | 55 | 2 |  | 719 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 152 | 0 | 397 | 0 | 0 | 39 | 0 | 54 | 0 | 1 | 10 | 430 | 74 | 0 | 0 |  | 5278 | 2506 | 7784 | 3398 | 719 | 1537 | 1283 | 680 | 70 | 0 | 88 | 9 | 0 | 90.92
8:00 | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 338 | 0 |  | 0 | 360 | 265 | 0 | 0 | 22 | 0 | 0 | 0 | 20 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 35 | 0 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 26 | 16 | 10 | 0 | 0 | 0 | 265 | 260 | 181 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 0 | 100 | 108 | 16 | 17 | 1 | 43 | 0 | 50 | 0 | 110 | 161 | 37 | 83 | 0 | 137 | 18 | 0 | 5 | 290 | 8 | 11 | 0 | 98 | 0 | 0 | 192 | 0 | 105 | 7 | 50 | 100 | 0 | 331 | 0 | 0 | 0 | 1 | 305 | 16 | 0 | 0 | 0 | 90 | 320 | 46 | 17 | 0 | 0 | 0 | 56 | 9 |  | 717 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 160 | 0 | 365 | 53 | 0 | 92 | 0 | 95 | 0 | 2 | 70 | 430 | 72 | 0 | 0 |  | 5606 | 2686 | 8292 | 3298 | 717 | 1442 | 1948 | 680 | 70 | 0 | 100 | 37 | 0 | 90.91
9:00 | 0 | 0 | 0 | 180 | 270 | 12 | 0 | 337 | 0 |  | 0 | 330 | 260 | 0 | 12 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 60 | 0 | 0 | 0 | 46 | 35 | 7 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 41 | 16 | 5 | 0 | 0 | 0 | 265 | 260 | 172 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 0 | 100 | 106 | 48 | 17 | 1 | 43 | 0 | 50 | 0 | 110 | 162 | 35 | 80 | 0 | 136 | 18 | 0 | 5 | 280 | 16 | 11 | 0 | 180 | 0 | 0 | 200 | 0 | 130 | 12 | 70 | 162 | 0 | 331 | 12 | 0 | 0 | 3 | 306 | 17 | 0 | 0 | 0 | 90 | 320 | 84 | 28 | 0 | 0 | 0 | 56 | 18 |  | 717 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 101 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 167 | 0 | 324 | 53 | 0 | 94 | 0 | 113 | 0 | 3 | 113 | 430 | 73 | 0 | 0 |  | 5947 | 2704 | 8651 | 3298 | 717 | 1351 | 2370 | 680 | 70 | 0 | 100 | 65 | 0 | 90.91
10:00 | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 338 | 0 |  | 0 | 330 | 260 | 0 | 15 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 61 | 0 | 0 | 0 | 35 | 35 | 10 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 45 | 16 | 4 | 0 | 0 | 0 | 265 | 260 | 164 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 11 | 102 | 104 | 24 | 17 | 2 | 43 | 0 | 45 | 0 | 110 | 161 | 35 | 80 | 0 | 136 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 193 | 0 | 0 | 200 | 0 | 144 | 15 | 70 | 200 | 0 | 329 | 16 | 5 | 0 | 4 | 306 | 17 | 0 | 0 | 0 | 90 | 320 | 104 | 37 | 0 | 0 | 0 | 56 | 25 |  | 718 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 108 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 169 | 0 | 363 | 56 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 400 | 73 | 0 | 0 |  | 5954 | 2715 | 8669 | 3200 | 718 | 1392 | 2443 | 657 | 70 | 0 | 102 | 87 | 0 | 90.9
11:00 | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 354 | 0 |  | 0 | 360 | 290 | 0 | 15 | 55 | 0 | 0 | 0 | 54 | 0 | 0 | 61 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 45 | 16 | 4 | 0 | 0 | 0 | 265 | 260 | 166 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 11 | 108 | 103 | 24 | 17 | 2 | 43 | 0 | 48 | 0 | 110 | 164 | 34 | 83 | 0 | 136 | 18 | 0 | 5 | 310 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 144 | 18 | 88 | 200 | 0 | 346 | 16 | 25 | 0 | 4 | 304 | 17 | 0 | 0 | 0 | 90 | 350 | 104 | 43 | 0 | 0 | 0 | 56 | 29 |  | 717 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 109 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 168 | 0 | 363 | 53 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 400 | 72 | 0 | 0 |  | 6139 | 2709 | 8848 | 3235 | 717 | 1450 | 2509 | 658 | 70 | 0 | 108 | 101 | 0 | 90.9
12:00 | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 367 | 0 |  | 0 | 450 | 270 | 1 | 30 | 55 | 0 | 0 | 0 | 80 | 32 | 0 | 61 | 0 | 0 | 0 | 35 | 0 | 44 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 45 | 17 | 5 | 0 | 0 | 0 | 265 | 260 | 161 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 11 | 116 | 85 | 24 | 0 | 2 | 43 | 0 | 48 | 0 | 130 | 162 | 34 | 83 | 0 | 136 | 18 | 0 | 5 | 320 | 16 | 11 | 0 | 230 | 0 | 0 | 192 | 0 | 118 | 17 | 100 | 0 | 0 | 360 | 39 | 50 | 0 | 4 | 305 | 39 | 0 | 0 | 38 | 90 | 342 | 104 | 44 | 5 | 0 | 0 | 56 | 29 |  | 717 | 0 | 190 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 124 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 170 | 0 | 408 | 53 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 400 | 70 | 0 | 0 |  | 6234 | 2780 | 9014 | 3186 | 717 | 1616 | 2534 | 673 | 70 | 0 | 116 | 102 | 0 | 90.89
13:00 | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 344 | 0 |  | 0 | 450 | 250 | 48 | 52 | 55 | 0 | 0 | 0 | 100 | 72 | 0 | 63 | 0 | 0 | 6 | 35 | 35 | 55 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 20 | 25 | 45 | 17 | 5 | 0 | 0 | 0 | 265 | 260 | 162 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 11 | 118 | 85 | 24 | 0 | 2 | 43 | 0 | 50 | 0 | 163 | 162 | 34 | 84 | 0 | 136 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 265 | 0 | 0 | 194 | 0 | 120 | 18 | 100 | 17 | 0 | 330 | 75 | 90 | 0 | 4 | 305 | 54 | 0 | 0 | 98 | 90 | 320 | 104 | 39 | 52 | 0 | 0 | 56 | 31 |  | 718 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 122 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 143 | 0 | 382 | 53 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 430 | 55 | 0 | 0 |  | 6611 | 2754 | 9365 | 3067 | 718 | 1579 | 3011 | 702 | 70 | 0 | 118 | 100 | 9365 | 90.89
14:00 | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 345 | 0 |  | 0 | 400 | 280 | 20 | 60 | 55 | 0 | 0 | 0 | 63 | 32 | 0 | 76 | 0 | 0 | 12 | 54 | 35 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 13 | 45 | 17 | 5 | 0 | 0 | 0 | 265 | 260 | 206 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 11 | 122 | 85 | 24 | 0 | 2 | 43 | 0 | 50 | 0 | 110 | 160 | 34 | 84 | 0 | 136 | 18 | 0 | 5 | 290 | 16 | 11 | 0 | 278 | 0 | 0 | 194 | 0 | 125 | 16 | 100 | 83 | 0 | 330 | 35 | 70 | 0 | 4 | 306 | 17 | 0 | 0 | 55 | 90 | 340 | 104 | 38 | 17 | 0 | 0 | 56 | 27 |  | 717 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 19 | 0 | 5 | 116 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 125 | 0 | 383 | 53 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 400 | 70 | 0 | 0 |  | 6390 | 2699 | 9089 | 3097 | 717 | 1493 | 2833 | 666 | 70 | 0 | 122 | 91 | 0 | 90.88
15:00 | 0 | 0 | 0 | 180 | 260 | 12 | 0 | 355 | 0 |  | 0 | 450 | 280 | 16 | 70 | 55 | 0 | 0 | 0 | 60 | 32 | 0 | 85 | 0 | 0 | 13 | 54 | 35 | 20 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 12 | 45 | 17 | 3 | 0 | 0 | 0 | 300 | 260 | 213 | 0 | 50 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 11 | 124 | 103 | 24 | 0 | 1 | 43 | 0 | 50 | 0 | 163 | 164 | 35 | 84 | 0 | 136 | 18 | 0 | 3 | 280 | 16 | 11 | 0 | 263 | 0 | 0 | 200 | 0 | 131 | 13 | 100 | 100 | 0 | 330 | 41 | 70 | 0 | 3 | 306 | 23 | 0 | 0 | 55 | 90 | 320 | 104 | 28 | 17 | 0 | 0 | 56 | 23 |  | 745 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 19 | 0 | 5 | 115 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 126 | 0 | 356 | 53 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 420 | 64 | 0 | 0 |  | 6719 | 2677 | 9396 | 3272 | 745 | 1549 | 2879 | 685 | 70 | 0 | 124 | 72 | 0 | 90.88
16:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 356 | 0 |  | 0 | 450 | 260 | 16 | 48 | 55 | 0 | 0 | 0 | 45 | 16 | 0 | 84 | 0 | 0 | 18 | 35 | 35 | 35 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 20 | 12 | 33 | 17 | 3 | 0 | 0 | 0 | 300 | 260 | 214 | 0 | 53 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 16 | 15 | 120 | 102 | 24 | 0 | 1 | 43 | 0 | 47 | 0 | 163 | 161 | 34 | 84 | 0 | 136 | 18 | 0 | 5 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 149 | 8 | 70 | 100 | 0 | 330 | 45 | 34 | 0 | 2 | 306 | 35 | 0 | 0 | 35 | 90 | 328 | 80 | 16 | 17 | 0 | 0 | 56 | 14 |  | 783 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 19 | 0 | 5 | 113 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 131 | 0 | 349 | 35 | 0 | 94 | 0 | 70 | 0 | 2 | 70 | 430 | 69 | 0 | 0 |  | 6507 | 2589 | 9096 | 3352 | 783 | 1563 | 2472 | 693 | 70 | 0 | 120 | 43 | 0 | 90.87
17:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 341 | 0 |  | 0 | 450 | 225 | 16 | 48 | 55 | 0 | 0 | 0 | 40 | 16 | 0 | 85 | 0 | 0 | 18 | 35 | 35 | 35 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 20 | 12 | 45 | 17 | 10 | 0 | 0 | 0 | 300 | 260 | 203 | 0 | 95 | 3 | 5 | 0 | 0 | 0 | 0 | 1 | 20 | 8 | 16 | 15 | 118 | 103 | 24 | 0 | 0 | 43 | 0 | 24 | 0 | 163 | 164 | 35 | 40 | 0 | 136 | 18 | 0 | 6 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 122 | 3 | 50 | 100 | 0 | 331 | 45 | 34 | 0 | 1 | 253 | 35 | 0 | 0 | 35 | 76 | 320 | 71 | 5 | 17 | 7 | 0 | 56 | 5 |  | 812 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 0 | 5 | 115 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 138 | 0 | 349 | 35 | 0 | 94 | 0 | 49 | 0 | 1 | 50 | 400 | 57 | 0 | 0 |  | 6291 | 2561 | 8852 | 3384 | 812 | 1496 | 2288 | 665 | 70 | 4 | 118 | 15 | 0 | 90.86
18:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 317 | 0 |  | 0 | 340 | 230 | 29 | 48 | 55 | 0 | 0 | 0 | 48 | 50 | 48 | 85 | 0 | 0 | 20 | 54 | 35 | 45 | 22 | 25 | 20 | 25 | 33 | 8 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 25 | 0 | 72 | 60 | 22 | 46 | 17 | 10 | 0 | 0 | 0 | 300 | 260 | 201 | 0 | 97 | 3 | 5 | 0 | 0 | 0 | 0 | 10 | 20 | 8 | 16 | 15 | 128 | 104 | 24 | 0 | 0 | 43 | 0 | 22 | 0 | 110 | 163 | 20 | 40 | 0 | 155 | 18 | 0 | 6 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 178 | 0 | 113 | 0 | 50 | 104 | 0 | 331 | 52 | 42 | 0 | 0 | 216 | 41 | 0 | 0 | 44 | 60 | 320 | 74 | 0 | 30 | 17 | 0 | 56 | 0 |  | 812 | 0 | 175 | 0 | 41 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 19 | 32 | 0 | 0 | 0 | 14 | 0 | 60 | 12 | 0 | 0 | 25 | 12 | 21 | 0 | 8 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 149 | 0 | 347 | 53 | 0 | 94 | 0 | 105 | 0 | 0 | 90 | 350 | 70 | 0 | 0 |  | 6383 | 2815 | 9198 | 3372 | 812 | 1346 | 2640 | 612 | 70 | 218 | 128 | 0 | 0 | 90.85
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 357 | 0 |  | 0 | 400 | 260 | 64 | 80 | 55 | 0 | 0 | 0 | 100 | 72 | 82 | 87 | 0 | 0 | 25 | 54 | 35 | 55 | 22 | 25 | 24 | 25 | 33 | 8 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 10 | 0 |  | 24 | 0 | 68 | 100 | 44 | 46 | 17 | 21 | 0 | 0 | 0 | 300 | 260 | 199 | 0 | 94 | 3 | 5 | 0 | 0 | 0 | 0 | 25 | 20 | 8 | 16 | 21 | 146 | 105 | 46 | 0 | 0 | 43 | 0 | 48 | 0 | 163 | 162 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 265 | 0 | 0 | 193 | 0 | 122 | 0 | 70 | 114 | 0 | 330 | 76 | 70 | 0 | 0 | 287 | 54 | 0 | 0 | 72 | 100 | 320 | 104 | 0 | 72 | 35 | 0 | 56 | 0 |  | 836 | 0 | 180 | 0 | 66 | 0 | 0 | 0 | 0 | 6 | 40 | 0 | 26 | 48 | 0 | 0 | 0 | 50 | 0 | 100 | 12 | 0 | 0 | 52 | 27 | 21 | 0 | 8 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 354 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 410 | 70 | 0 | 0 |  | 7428 | 3212 | 10640 | 3456 | 836 | 1595 | 3532 | 672 | 70 | 333 | 146 | 0 | 0 | 90.82
19:30 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 339 | 0 |  | 0 | 400 | 230 | 100 | 99 | 55 | 0 | 0 | 0 | 100 | 40 | 48 | 100 | 0 | 0 | 25 | 54 | 35 | 55 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 68 | 40 | 0 | 46 | 17 | 22 | 0 | 0 | 0 | 300 | 260 | 199 | 0 | 97 | 3 | 5 | 0 | 0 | 0 | 0 | 1 | 20 | 8 | 16 | 21 | 144 | 106 | 81 | 0 | 0 | 43 | 0 | 48 | 0 | 163 | 163 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 135 | 0 | 100 | 120 | 0 | 331 | 65 | 34 | 0 | 0 | 288 | 54 | 0 | 0 | 55 | 100 | 320 | 104 | 0 | 72 | 0 | 0 | 56 | 0 |  | 837 | 0 | 175 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 48 | 0 | 0 | 0 | 50 | 0 | 75 | 12 | 0 | 0 | 52 | 27 | 22 | 0 | 8 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 354 | 105 | 0 | 108 | 0 | 111 | 0 | 0 | 113 | 470 | 71 | 0 | 0 |  | 7378 | 3244 | 10622 | 3558 | 837 | 1578 | 3435 | 732 | 70 | 268 | 144 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 339 | 0 |  | 0 | 420 | 260 | 100 | 99 | 55 | 0 | 0 | 0 | 100 | 0 | 48 | 100 | 0 | 0 | 28 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 130 | 0 |  | 25 | 0 | 51 | 40 | 0 | 46 | 17 | 25 | 0 | 0 | 0 | 300 | 260 | 199 | 0 | 94 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 16 | 21 | 144 | 105 | 81 | 0 | 0 | 43 | 0 | 48 | 0 | 163 | 162 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 144 | 0 | 100 | 120 | 0 | 330 | 45 | 34 | 0 | 0 | 288 | 54 | 0 | 0 | 55 | 100 | 320 | 104 | 0 | 35 | 0 | 0 | 56 | 0 |  | 837 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 66 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 111 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 150 | 0 | 355 | 105 | 0 | 108 | 0 | 113 | 0 | 0 | 113 | 470 | 71 | 0 | 0 |  | 7331 | 3119 | 10450 | 3565 | 837 | 1601 | 3337 | 731 | 70 | 165 | 144 | 0 | 0 | 90.83
21:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 340 | 0 |  | 0 | 420 | 245 | 53 | 99 | 55 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 0 | 0 | 130 | 0 |  | 24 | 0 | 51 | 10 | 0 | 46 | 17 | 28 | 0 | 0 | 0 | 300 | 260 | 202 | 0 | 94 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 21 | 142 | 107 | 81 | 0 | 0 | 43 | 0 | 48 | 0 | 163 | 162 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 291 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 120 | 0 | 331 | 45 | 34 | 0 | 0 | 290 | 54 | 0 | 0 | 55 | 100 | 370 | 104 | 0 | 0 | 0 | 0 | 56 | 0 |  | 836 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 150 | 0 | 354 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 71 | 0 | 0 |  | 7149 | 3088 | 10237 | 3623 | 836 | 1603 | 3149 | 738 | 70 | 76 | 142 | 0 | 0 | 90.82
22:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 338 | 0 |  | 0 | 420 | 270 | 0 | 48 | 55 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 25 | 0 | 51 | 0 | 0 | 46 | 17 | 36 | 0 | 0 | 0 | 300 | 260 | 196 | 0 | 95 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 21 | 138 | 107 | 24 | 0 | 0 | 43 | 0 | 50 | 0 | 163 | 162 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 120 | 0 | 340 | 8 | 34 | 0 | 0 | 305 | 17 | 0 | 0 | 0 | 100 | 396 | 104 | 0 | 0 | 0 | 0 | 56 | 0 |  | 836 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 110 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 160 | 0 | 355 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 68 | 0 | 0 |  | 6813 | 2909 | 9722 | 3651 | 836 | 1599 | 2617 | 760 | 70 | 51 | 138 | 0 | 0 | 90.81
23:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 340 | 0 |  | 0 | 420 | 275 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 25 | 0 | 17 | 0 | 0 | 46 | 17 | 38 | 0 | 0 | 0 | 300 | 260 | 194 | 0 | 93 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 21 | 138 | 107 | 24 | 0 | 0 | 44 | 0 | 50 | 0 | 163 | 160 | 36 | 83 | 0 | 161 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 120 | 0 | 352 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 392 | 90 | 0 | 0 | 0 | 0 | 55 | 0 |  | 836 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 108 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 160 | 0 | 355 | 35 | 0 | 113 | 0 | 70 | 0 | 0 | 70 | 500 | 71 | 0 | 0 |  | 6482 | 2791 | 9273 | 3657 | 836 | 1623 | 2174 | 758 | 70 | 17 | 138 | 0 | 0 | 90.8
24:00 | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 340 | 0 |  | 0 | 420 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 38 | 0 | 0 | 0 | 300 | 260 | 196 | 0 | 99 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 21 | 126 | 107 | 24 | 0 | 0 | 43 | 0 | 50 | 0 | 163 | 163 | 36 | 83 | 0 | 162 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 120 | 0 | 355 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 370 | 50 | 0 | 0 | 0 | 0 | 55 | 0 |  | 837 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 107 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 170 | 0 | 350 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 500 | 70 | 0 | 0 |  | 6161 | 2629 | 8790 | 3659 | 837 | 1616 | 1725 | 757 | 70 | 0 | 126 | 0 | 0 | 90.79
KWH | 0 | 0 | 0 | 4378500 | 6263100 | 300045 | 0 | 8409080 | 0 |  | 0 | 9459250 | 6452713 | 397440 | 823056 | 884192 | 0 | 0 | 0 | 1080749 | 312624 | 159360 | 1374358 | 0 | 0 | 169296 | 872640 | 512451 | 493864 | 492192 | 600000 | 685080 | 659000 | 807600 | 10536 | 0 | 0 | 1700000 | 0 | 0 | 102508 | 0 | 0 | 522580 | 0 |  | 400800 | 0 | 275457 | 312240 | 146880 | 832320 | 386880 | 503520 | 0 | 0 | 0 | 7052700 | 6344000 | 4699000 | 0 | 1014310 | 189648 | 138240 | 0 | 0 | 0 | 0 | 50386 | 477000 | 191700 | 473400 | 690875 | 2854080 | 2409320 | 624000 | 187200 | 14550 | 1023000 | 0 | 1140600 | 0 | 3511472 | 2511000 | 841344 | 1913280 | 0 | 3442180 | 428000 | 0 | 131940 | 7427500 | 310544 | 264000 | 0 | 4293053 | 0 | 0 | 4008000 | 0 | 2672784 | 123390 | 1423680 | 2831520 | 0 | 8124000 | 609600 | 690552 | 0 | 28617 | 6927600 | 547385 | 0 | 0 | 705600 | 2157120 | 8309000 | 1607040 | 298530 | 315360 | 77781 | 0 | 132228 | 209039 |  | 18289454 | 0 | 4719168 | 0 | 311040 | 0 | 0 | 0 | 0 | 21472 | 81000 | 0 | 438451 | 338208 | 0 | 0 | 0 | 79392 | 0 | 146088 | 127950 | 0 | 0 | 642720 | 39536 | 500160 | 0 | 160650 | 2559272 | 0 | 3663700 | 0 | 0 | 0 | 0 | 0 | 0 | 1329233 | 0 | 3877373 | 0 | 8863363 | 1028640 | 0 | 2140992 | 0 | 1708800 | 0 | 36302 | 1690080 | 11310300 | 1750091 | 0 | 0 |  | 147227459 | 65853435 | 213080894 | 80943424 | 18289454 | 37407145 | 52921786 | 17533272 | 1700000 | 721305 | 2854080 | 710428 | 0
Fuel Cost | 0 | 0 | 0 | 6436395 | 6952041 | 396059.4 | 0 | 8493170.8 | 0 |  | 0 | 10310582.5 | 7162511.43 | 3016569.6 | 5670855.84 | 7480264.32 | 0 | 0 | 0 | 8138039.97 | 2851130.88 | 1568102.4 | 12671580.76 | 0 | 0 | 1538900.64 | 6370272 | 3961246.23 | 4869499.04 | 369144 | 450000 | 0 | 0 | 0 | 101883.12 | 0 | 0 | 459000 | 0 | 0 | 952299.32 | 0 | 0 | 888386 | 0 |  | 0 | 0 | 2671932.9 | 2981892 | 1277856 | 6591974.4 | 487468.8 | 1495454.4 | 0 | 0 | 0 | 5218998 | 6344000 | 4323080 | 0 | 1166456.5 | 214302.24 | 193536 | 0 | 0 | 0 | 0 | 481186.3 | 605790 | 143775 | 828450 | 518156.25 | 21405600 | 2553879.2 | 5665920 | 237744 | 231927 | 1677720 | 0 | 2030268 | 0 | 4003078.08 | 2611440 | 1657447.68 | 3654364.8 | 0 | 5954971.4 | 937320 | 0 | 269157.6 | 7501775 | 232908 | 200640 | 0 | 32455480.68 | 0 | 0 | 20841600 | 0 | 26300194.56 | 1442429.1 | 11602992 | 30721992 | 0 | 7555320 | 5559552 | 6525716.4 | 0 | 0 | 52372656 | 4767723.35 | 0 | 0 | 6046992 | 14366419.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105347255.04 | 0 | 4955126.4 | 0 | 2444774.4 | 0 | 0 | 0 | 0 | 225026.56 | 844020 | 0 | 679599.05 | 3300910.08 | 0 | 0 | 0 | 781217.28 | 0 | 1292878.8 | 985215 | 0 | 0 | 6227956.8 | 383499.2 | 960307.2 | 0 | 121612.05 | 15432410.16 | 0 | 19857254 | 0 | 0 | 0 | 0 | 0 | 0 | 1993849.5 | 0 | 4536526.41 | 0 | 8774729.37 | 10739001.6 | 0 | 20318014.08 | 0 | 13260288 | 0 | 401137.1 | 12489691.2 | 49652217 | 0 | 0 | 0 |  | 418037471.09 | 286004516.28 | 704041987.37 | 76672268.73 | 105347255.04 | 42262760.9 | 363955071.2 | 84941881.16 | 459000 | 6922657.14 | 21405600 | 2075493.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 180 | 12 | 0 | 367 | 0 |  | 0 | 450 | 270 | 1 | 30 | 55 | 0 | 0 | 0 | 80 | 32 | 0 | 61 | 0 | 0 | 0 | 35 | 0 | 44 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 45 | 17 | 5 | 0 | 0 | 0 | 265 | 260 | 161 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 11 | 116 | 85 | 24 | 0 | 2 | 43 | 0 | 48 | 0 | 130 | 162 | 34 | 83 | 0 | 136 | 18 | 0 | 5 | 320 | 16 | 11 | 0 | 230 | 0 | 0 | 192 | 0 | 118 | 17 | 100 | 0 | 0 | 360 | 39 | 50 | 0 | 4 | 305 | 39 | 0 | 0 | 38 | 90 | 342 | 104 | 44 | 5 | 0 | 0 | 56 | 29 |  | 717 | 0 | 190 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 124 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 170 | 0 | 408 | 53 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 400 | 70 | 0 | 0 |  | 9014 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 357 | 0 | 0 | 0 | 400 | 260 | 64 | 80 | 55 | 0 | 0 | 0 | 100 | 72 | 82 | 87 | 0 | 0 | 25 | 54 | 35 | 55 | 22 | 25 | 24 | 25 | 33 | 8 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 10 | 0 | 0 | 24 | 0 | 68 | 100 | 44 | 46 | 17 | 21 | 0 | 0 | 0 | 300 | 260 | 199 | 0 | 94 | 3 | 5 | 0 | 0 | 0 | 0 | 25 | 20 | 8 | 16 | 21 | 146 | 105 | 46 | 0 | 0 | 43 | 0 | 48 | 0 | 163 | 162 | 36 | 83 | 0 | 163 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 265 | 0 | 0 | 193 | 0 | 122 | 0 | 70 | 114 | 0 | 330 | 76 | 70 | 0 | 0 | 287 | 54 | 0 | 0 | 72 | 100 | 320 | 104 | 0 | 72 | 35 | 0 | 56 | 0 |  | 836 | 0 | 180 | 0 | 66 | 0 | 0 | 0 | 0 | 6 | 40 | 0 | 26 | 48 | 0 | 0 | 0 | 50 | 0 | 100 | 12 | 0 | 0 | 52 | 27 | 21 | 0 | 8 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 354 | 105 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 410 | 70 | 0 | 0 |  | 10640 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 16 | 30 | 0 | 0 | 0 | 300 | 300 | 225 | 0 | 94 | 10 | 5 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 147 | 150 | 82 | 17 | 0 | 43 | 0 | 51 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 350 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 55 |  |  | 827 | 16 | 240 | 0 | 115 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 104 | 12 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 105 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 170 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 70 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 102 | 50 | 16 | 30 | 0 | 0 | 0 | 300 | 300 | 225 | 0 | 92 | 10 | 5 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 135 | 150 | 82 | 17 | 1.6 | 43 | 0 | 51 | 0 | 163 | 162 | 36 | 83 | 0 | 137 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 350 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 370 | 104 | 50 | 144 | 116 | 0 | 55 | 30 |  | 852 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 104 | 12 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 105 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 170 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 70 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 300 | 12 | 0 | 346 | 0 | 0 | 0 | 380 | 250 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 28 | 0 | 0 | 0 | 300 | 260 | 214 | 0 | 92 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 86 | 146 | 38 | 0 | 1 | 43 | 0 | 48 | 0 | 110 | 161 | 20 | 78 | 0 | 135 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 63 | 6 | 10 | 65 | 0 | 356 | 24 | 0 | 0 | 1 | 140 | 0 | 0 | 0 | 0 | 100 | 370 | 17 | 14 | 0 | 0 | 0 | 55 | 6 | 0 | 813 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 104 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 160 | 0 | 353 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 350 | 73 | 0 | 0 | 0
199
| Minimum Generation |  | 6990 | 5:00
| Highest Generation |  | 10640 | 19:00
| Day Peak Generation |  | 9014 | 12:00
| Evening Peak Generation |  | 10640 | 19:00
| HVDC Max Flow |  | 837 | 19:30
| HVDC EvPeak Flow |  | 836 | 19:00
| Load factor L.F |  | 83.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9014 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7363 | MW
Evening Peak Generation : |  | 10640 | MW Hour : | 19:00 | Available Max Generation : |  | 14581 | MW
E.P. Demand (at gen end) : |  | 10640 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 10640 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4981 | MW
Total Gen. (MKWH) : |  | 213.0809 | System Load Factor : | 83.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -215 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-05
Actual : | 70.73 | Ft.(MSL) , | Rule curve : | 92.36 | Ft.( MSL )
Gas Consumed : | Total = | 926.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 118935029.63
: |  | Coal : | 84941881.16 | Oil : | 370877728.34 | Total : | 574754639.13
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3440.8818 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1166.414 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1044.4133 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 943.4829 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 852.7401 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 688.1218 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 389.4946 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 177.2981 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 530.6911 |  |  | 0 | 0%
Total | 0 |  | 9233.5376 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71 &100 MW
3) Ashuganj-3,4,5
4) Kaptai-2
5) Raozan #1,2
6) Haripur 360 MW
7) Sirajganj #1 CCPP
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Baroiarhat 132/33 kV T-1 transformer was under shut down from 08:52 to 16:57 for C/M.
b) Bibiyana-Shahjibazar 230 kV Ckt-1 was under shut down from 09:20 to 15:30 for A/M.
c) Barishal 132/33 kV T-1 transformer was under shut down from 06: to 08:14 for C/M.
d) BSRM 230 kV bus coupler was under shut down from 11:47 to 15:41 for D/W.
e) BSRM 230 kV bus coupler was under shut down since 16:28 for D/W.
f) Chandpur 132/33 kV T1,T2 & T3 transformer tripped at 11:56 showing O/V and were switched on |  |  |  |  | About 27 MW power interruption occurred under Chandpur S/S area
at 12:11. |  |  |  |  | from 11:56 to 12:11.
g) Chandpur Desh-Ramganj 132 kV Ckt-1,2 tripped at 11:56 from Desh energy end showing O/V and
were switched on at 12:11.
h) Chandpur S/S- Chandpur Desh 132 kV Ckt-1,2 tripped at 11:56 from Desh energy end showing
O/V and were switched on at 12:09.
i) Cumilla(N) 132/33 kV T-4 transformer was under shut down from 10:24 to 14:28 for C/M. |  |  |  |  | About 10 MW power interruption occurred under Cumilla(N) S/S area
from 10:24 to 14:28.
j) Daudkandi 132/33 kV T-2 transformer was under shut down from 08:20 to 14:59 for C/M.
k) Tongi 230/132 kV T0-2 transformer was under shut down from 10:53 to 11:20 for C/M.
l) Goalpara-Bagerhat 132 kV Ckt -1 was under shut down from 07:51 to 15:47 for D/W.
m) Haripur-HPL 230 kV Ckt-1 was under shut down from 08:07 to 11:38 for C/M.
n) Hathazari-Raozan 230 kV Ckt-2 was under shut down from 09:41 to 12:32 for C/M.
o) Jamalpur 132/33 kV T-2 transformer was under shut down from 09:20 to 11:50 for C/M.
p) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 10:40 to 15:43 for C/M.
q) Kabirpur-Manikganj 132 kV Ckt-2 was under shut down from 09:42 to 20:40 for C/M.
r) Kamrangirchar 132/33 kV T-1 transformer was under shut down from 08:19 to 14:54 for A/M.
s) Kulshi-Bakulia 132 kV Ckt-2 was under shut down from 08:34 to 14:50 for A/M.
t) Aminbazar-Mirpur 132 kV Ckt-2 was under shut down from 09:36 to 16:33 for C/M.
u) Rajshahi 132/33 kV T-3 transformer was under shut down from 09:10 to 14:19 for A/M.
v) Rajshahi-Amnura 132 kV Ckt-2 was under shut down from 08:34 to 16:30 for C/M.
w) Sreemangal 132/33 kV T-1 transformer was switched 12:15.
x) Sikalbaha GT was synchronized at 18:52.
y) Chandpur GT was synchronized at 14:48.
z) Kaliakoir 400/132 kV T-2 transformer was shut down since 07:55(05-03-2021) for C/M. |  |  |  |  | About 50 MW power interruption occurred under Kaliakoir S/S area
from 07:55 to till now.
aa) Goalpara-Orion Rupsha 132 kV Ckt is under shut down since 07:47(05-03-2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6263100
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 300045 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 357 | 8409080 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9459250 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 64 | 397440 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6452713 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 823056 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 884192
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 87 | 1374358 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 492192
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1080749
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 312624 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 25 | 169296 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 872640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 159360 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 512451 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 493864 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1285080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 659000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 807600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 10536 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 265 | 4293053 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 122 | 2672784 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 690552 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1607040
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 315360 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 209039
| Dhaka area Total |  |  |  | 5972 | 2988 | 55384954
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 102508
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123390
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 832320
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1700000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 10 | 522580 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 275457 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 312240
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 1423680 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 386880
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 503520
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 146880 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28617
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 287 | 6927600
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 547385
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2157120
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 77781 | Low demand
| Chattogram area Total |  |  |  | 2382 | 947 | 16067958
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4699000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7052700 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6344000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 3 | 189648 | Macine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 1014310
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 114 | 2831520 | High Voltage.
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 477000
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 191700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 2854080
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 473400
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 50386 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 690875 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 72 | 705600 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 56 | 132228
| Cumilla Area Total |  |  |  | 2980 | 1339 | 27844687
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2409320 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 187200 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 46 | 624000 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14550
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 4008000 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 76 | 609600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 298530
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 400800
| Mymensingh Area Total |  |  |  | 709 | 444 | 8552000
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1023000
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3511472
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 2511000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1140600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 36 | 841344 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1913280
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 3442180
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 428000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 310544 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7427500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 330 | 8124000 | Gas shortage
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 131940
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 320 | 8309000 | On Test
| Sylhet Area Total |  |  |  | 1988 | 1710 | 39377860
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 836 | 18289454
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 311040 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 6 | 21472 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 4719168 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 81000
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1028640
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1233 | 24450774
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 338208 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 438451
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 1329233
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 410 | 11310300
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 70 | 1750091
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 629 | 15166283
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 79392
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 127950 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 3877373 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 354 | 8863363 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 39536 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 500160
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 160650 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 642720 | Engine problem
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 146088
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2140992 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1690080
| Rajshahi Area Total |  |  |  | 2183 | 981 | 18268304
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 112 | 2559272
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3663700 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1708800
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36302
| Rangpur Area Total |  |  |  | 605 | 369 | 7968074
| Total |  |  |  | 20929 | 10640 | 213080894
| Eastern Grid Total |  |  |  | 14031 | 7428 | 147227459
| Western Grid Total |  |  |  | 6898 | 3212 | 65853435
| National Grid Total |  |  |  | 20929 | 10640 | 213080894
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-04
(a) ENTIRE EASTERN GRID : |  | 6944 | MW | (b) ENTIRE WESTERN GRID : |  | 3280 | MW
i) Dhaka area |  | 3643 | MW | i) Khulna area |  | 1257 | MW
ii) Chittagong area |  | 1139 | MW | ii) Rajshahi area |  | 1065 | MW
iii) Comilla area |  | 914 | MW | iii) Barisal area |  | 278 | MW
iv) Mymensingh area |  | 879 | MW | iv) Rangpur area |  | 680 | MW
v) Sylhet area |  | 369 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10224 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 14:00 | Netrokona | 98 | 18:30 | Jessore | 105 | 19:00
Munsiganj | 90 | 22:00 | Jamalpur | 114 | 7:00 | Benapol | 54 | 19:00
Sonargaon | 67 | 19:30 | Sherpur | 110 | 19:00 | Jhenida | 86 | 20:00
Shyampur | 178 | 1:00 | Srimongal | 35 | 18:30 | Bottail | 102 | 18:30
Bhulta | 188 | 22:00 | Shahjibazar | 98 | 21:00 | G.K Project | 41 | 18:30
Madanganj | 40 | 22:00 | Fenchuganj | 30 | 18:30 | Faridpur | 140 | 19:00
Shitalakhya | 107 | 15:00 | Kulawara | 30 | 19:00 | Madaripur | 73 | 19:00
Rahim steel | 21 | 8:00 | Sylhet | 96 | 19:00 | Sariatpur | 46 | 20:00
Matuail | 78 | 9:00 | Chatak | 22 | 19:00 | Gopalganj | 67 | 19:00
Ghorasal | 70 | 21:00 | Sunamganj | 30 | 20:00 | Bagerhat | 94 | 19:00
Narsingdi | 138 | 19:30 | Biani Bazar | 40 | 18:00 | Mongla | 44 | 18:00
Haripur (SBU) | 95 | 12:00 | Comilla (S) | 146 | 18:30 | Satkhira | 89 | 19:00
Sreenagar |  |  | Comilla(N) | 80 | 20:00 | Gallamari | 23 | 13:00
Ullon | 67 | 19:30 | Chandpur | 54 | 19:00 | Magura | 44 | 19:00
Hasnabad | 76 | 18:30 | Feni | 99 | 19:00 | Norail | 34 | 19:00
Magbazar | 78 | 15:00 | Chowmuhani | 144 | 18:30 | Chuadanga | 74 | 19:00
Maniknagar | 60 | 13:00 | Ashuganj | 21 | 13:00 | Borguna | 12 | 19:00
Bangabhaban | 20 | 11:00 | Daudkandi | 116 | 20:00 | Barisal(N) | 32 | 19:00
Narinda | 73 | 18:30 | B.Baria | 125 | 18:30 | Barisal (S) | 90 | 18:30
Dhanmondi | 148 | 13:00 | Ramganj | 62 | 19:00 | Patuakhali | 82 | 21:00
Lalbag | 91 | 13:00 | Chaddagram | 32 | 19:00 | Bhandaria | 40 | 19:00
Madartek | 61 | 19:30 | PHP | 10 | 17:00 | Borhan Uddin | 31 | 21:00
Dhaka University | 0 | #NUM! | Kochua | 48 | 20:00 | Ishurdi | 44 | 19:00
Aftabnagar | 8 | 18:30 | Madunaghat | 63 | 19:00 | Ruppur Paromanobik | 3 | 18:00
Fatullah | 57 | 23:00 | Hathazari | 71 | 20:00 | Natore | 105 | 18:30
Nawabganj | 34 | 19:00 | Khulshi | 184 | 15:00 | Bogra | 139 | 19:30
Mirpur | 87 | 18:30 | Halishahar | 121 | 15:00 | Noagaon | 95 | 19:00
Kalyanpur | 81 | 19:00 | Baraulia | 156 | 0:00 | Rajshahi | 98 | 19:00
Gulshan | 106 | 13:00 | Sikalbaha | 26 | 19:00 | Rajshahi New | 15 | 19:00
Uttara | 72 | 18:30 | Dohazari | 74 | 18:30 | C.Nawabganj | 63 | 18:30
Uttara New | 23 | 18:30 | Cox'sbazar | 98 | 18:30 | Amnura | 47 | 19:00
Kamrangirchar | 81 | 19:00 | Chandraghona | 26 | 18:30 | Pabna | 74 | 19:00
Savar | 98 | 15:00 | Kaptai | 0 | #N/A | Shahjadpur | 88 | 9:00
Bhasantec | 129 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 80 | 8:00
Agargaon | 60 | 13:00 | Bakulia | 97 | 18:30 | Niyamatpur | 86 | 8:00
Satmosjid | 83 | 13:00 | Julda | 21 | 12:00 | Joypurhat | 57 | 19:00
Tongi | 104 | 18:00 | TK chemical | 23 | 19:00 | Sherpur(Bogura) | 46 | 18:30
Kabirpur | 237 | 15:00 | Modern Steel | 0 | #N/A | Mohastangor | 42 | 19:00
Basundhara | 127 | 18:30 | Shahmirpur | 23 | 23:00 | Bangura | 21 | 19:00
Manikganj | 40 | 13:00 | Khagrachhari | 22 | 9:00 | Rangpur | 119 | 18:30
Joydevpur | 130 | 19:00 | Matarbari | 33 | 20:00 | Lalmonirhat | 36 | 18:30
New Tongi | 92 | 15:00 | Baroiar Hat | 30 | 19:00 | Saidpur | 104 | 9:00
Korda | 201 | 12:00 | Rangamati | 10 | 18:30 | Purbasadipur | 89 | 19:00
Dhamrai | 112 | 18:30 | Abul Khair 230 | 160 | 22:00 | Thakurgaon | 66 | 19:00
Rajendrapur | 86 | 19:30 | BSRM | 151 | 12:00 | Palashbari | 112 | 9:00
Valuka | 94 | 9:00 | GPH Ispat | 9 | 1:00 | Barapukuria | 49 | 8:00
Tangail | 174 | 19:00 | Goalpara | 13 | 13:00 | Panchagar | 47 | 19:00
Mymensing | 206 | 18:30 | Central s/s | 96 | 19:00 | Joldhaka | 44 | 19:00
Kishorganj | 102 | 18:30 | Noapara | 47 | 19:00 | Kurigram | 50 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 21:00 | 404 | 4:00 | Kaliakoir | 398 | 0.20833 | 389 | 0.45833
| Bheramara | 397 | 13:00 | 391 | 19:00 | Bhulta | 392 | 0.79167 | 377 | 0.45833
| Ashuganj(N) | 395 | 20:00 | 384 | 11:00 | Gopalganj | 408 | 0.625 | 392 | 0.875
| Payra | 410 | 18:30 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 234 | 17:00 | Hathazari | 226 | 13:00 | 218 | 12:00
| Ishurdi | 242 | 18:00 | 232 | 8:00 | Megnaghat | 241 | 7:00 | 233 | 24:00
| Ashuganj | 240 | 8:00 | 235 | 1:00 | Fenchuganj | 242 | 20:00 | 239 | 2:00
| Serajganj | 235 | 18:00 | 230 | 6:00 | Siddhirganj | 235 | 7:00 | 227 | 15:00
| Baghabari | 238 | 18:00 | 231 | 7:00 | Maniknagar | 233 | 7:00 | 226 | 11:00
| Barapukuria | 235 | 3:00 | 230 | 8:00 | Agargaon | 233 | 17:00 | 225 | 11:00
| Bogra | 234 | 4:00 | 226 | 8:00 | Barisal | 250 | 13:00 | 244 | 23:00
| Rajshahi | 238 | 18:00 | 229 | 12:00 | Bhola 225 MW | 252 | 18:00 | 246 | 18:30
| Khulna South | 245 | 18:00 | 228 | 12:00 | AKSML | 230 | 13:00 | 213 | 4:00
| Rampura | 231 | 21:00 | 227 | 11:00 | BSRM | 231 | 13:00 | 218 | 4:00
| Haripur | 234 | 8:00 | 227 | 24:00 | Bibiyana | 242 | 8:00 | 236 | 11:00
| Hasnabad | 232 | 1:00 | 228 | 4:00 | Bhulta | 236 | 8:00 | 227 | 11:00
| Shyampur | 233 | 18:30 | 220 | 11:00 | Ashuganj (S) | 237 | 19:30 | 231 | 12:00
| Aminbazar | 234 | 1:00 | 226 | 2:00 | Kaliakoir | 234 | 20:00 | 227 | 11:00
| Tongi | 230 | 5:00 | 220 | 15:00 | GPH | 228 | 24:00 | 214 | 6:00
| Comilla (N) | 232 | 8:00 | 227 | 5:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 20:00 | 132 | 1:00 | Madanhat | 136 | 0.375 | 130 | 0.20833
| Munsiganj | 139 | 19:00 | 131 | 12:00 | Hathazari | 135 | 0.77083 | 130 | 0.29167
| Sonargaon | 137 | 19:00 | 130 | 0:00 | Khulshi | 135 | 0.29167 | 127 | 0.25
| Shyampur | 132 | 19:30 | 127 | 11:00 | Halishahar | 138 | 0.29167 | 127 | 0.25
| Bhulta | 131 | 18:30 | 124 | 11:00 | Baraulia | 135 | 0.375 | 129 | 0.5
| Madanganj | 139 | 19:00 | 132 | 2:00 | Sikalbaha | 137 | 0.375 | 127 | 0.16667
| Shitalakhya | 137 | 13:00 | 128 | 1:00 | Dohazari | 133 | 0.375 | 126 | 0.66667
| Rahim steal | 136 | 19:30 | 131 | 11:00 | Cox'sbazar | 126 | 0.41667 | 118 | 0.25
| Matuail | 137 | 20:00 | 132 | 1:00 | Chandraghona | 136 | 0.29167 | 125 | 0.625
| Ghorasal | 138 | 18:00 | 136 | 1:00 | Kaptai | 0 | #N/A | 0 | #N/A
| Narsinghdi | 132 | 18:00 | 129 | 10:00 | A. Khaer Stl. | 134 | 0.375 | 128 | 0.25
| Haripur (SBU) | 136 | 18:30 | 131 | 11:00 | Bakulia | 136 | 0.77083 | 128 | 0.083333
| Sreenagar |  |  |  |  | Julda | 137 | 0.77083 | 128 | 0.16667
| Ullon | 132 | 8:00 | 126 | 11:00 | TK Chemical | 136 | 0.375 | 127 | 0.25
| Hasnabad | 135 | 18:30 | 128 | 3:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 132 | 2:00 | 125 | 12:00 | Shahmirpur | 137 | 0.375 | 128 | 0.625
| Maniknagar | 135 | 8:00 | 130 | 11:00 | Khagrachhari | 134 | 0.375 | 126 | 0.25
| Bangabhaban | 135 | 8:00 | 130 | 11:00 | Matarbari | 130 | 0.375 | 120 | 0.25
| Narinda | 135 | 8:00 | 130 | 11:00 | Baroiar Hat | 134 | 0.375 | 128 | 0.625
| Dhanmondi | 132 | 8:00 | 126 | 11:00 | Rangamati | 136 | 0.54167 | 126 | 0.25
| Lalbag | 133 | 8:00 | 126 | 1:00 | Goalpara S/S | 138 | 18:00 | 128 | 22:00
| Madartek | 132 | 8:00 | 126 | 11:00 | Khulna Central S/S | 138 | 18:00 | 129 | 12:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Noapara | 137 | 18:00 | 127 | 0.91667
| Aftabnagar | 131 | 7:00 | 126 | 11:00 | Jessore | 134 | 18:00 | 124 | 0.91667
| Fatullah | 133 | 21:00 | 127 | 11:00 | Benapol | 134 | 4:00 | 125 | 0.5
| Nawabganj | 129 | 1:00 | 125 | 11:00 | Jhenida | 132 | 5:00 | 124 | 0.83333
| Mirpur | 134 | 20:00 | 129 | 12:00 | Bottail | 136 | 0.125 | 130 | 0.5
| Kalyanpur | 136 | 18:00 | 130 | 12:00 | G.K Project | 142 | 18:00 | 138 | 0.5
| Gulshan | 131 | 7:00 | 126 | 12:00 | Faridpur | 139 | 0.75 | 135 | 0.29167
| Uttara | 135 | 20:00 | 128 | 11:00 | Madaripur | 141 | 0.41667 | 135 | 0.79167
| Uttara New | 136 | 20:00 | 130 | 12:00 | Shariyatpur S/S | 141 | 0.125 | 136 | 0.79167
| Kamrangirchar | 130 | 20:00 | 124 | 11:00 | Gopalganj | 145 | 0.75 | 139 | 0.83333
| Savar | 135 | 19:30 | 128 | 11:00 | Bagerhat | 135 | 18:00 | 120 | 0.5
| Bhasantec | 133 | 18:00 | 126 | 12:00 | Mongla | 133 | 0.75 | 121 | 0.5
| Agargaon | 132 | 20:00 | 127 | 12:00 | Satkhira | 137 | 18:00 | 126 | 0.91667
| Satmosjid | 132 | 19:30 | 127 | 12:00 | Gallamari | 137 | 5:00 | 130 | 0.5
| Tongi | 138 | 19:00 | 130 | 12:00 | Magura | 135 | 3:00 | 124 | 19:00
| Kabirpur | 136 | 13:00 | 127 | 15:00 | Narail | 131 | 0.16667 | 123 | 0.77083
| Basundhara | 136 | 21:00 | 126 | 11:00 | Chuadanga | 129 | 5:00 | 118 | 0.79167
| Manikganj | 136 | 9:00 | 130 | 168:00 | Borguna | 140 | 0.29167 | 135 | 0.625
| Joydevpur | 138 | 18:30 | 133 | 11:00 | Barisal(N) | 141 | 8:00 | 137 | 0.77083
| New Tongi | 136 | 1:00 | 129 | 11:00 | Barisal (S) | 141 | 18:00 | 136 | 0.66667
| Kodda | 135 | 13:00 | 126 | 12:00 | Patuakhali(S) | 138 | 5:00 | 132 | 21:00
| Dhamrai | 132 | 2:00 | 126 | 11:00 | Bhandaria | 140 | 0.33333 | 130 | 0.79167
| Rajendrapur | 134 | 14:00 | 125 | 12:00 | Ishurdi | 140 | 0.75 | 134 | 0.5
| Valuka | 125 | 1:00 | 116 | 18:30 | Ruppur Paromanobik | 140 | 0.75 | 135 | 0.29167
| Tangail | 133 | 1:00 | 124 | 11:00 | Natore | 139 | 18:00 | 133 | 7:00
| Mymensing | 127 | 21:00 | 118 | 18:30 | Bogra | 138 | 18:00 | 130 | 8:00
| Kishorganj | 131 | 5:00 | 123 | 18:30 | Noagaon | 133 | 18:00 | 123 | 8:00
| Netrokona | 125 | 1:00 | 116 | 7:00 | Rajshahi | 135 | 18:00 | 131 | 7:00
| Jamalpur | 139 | 21:00 | 124 | 3:00 | Rajshahi New | 136 | 18:00 | 130 | 9:00
| Sherpur | 137 | 21:00 | 122 | 7:00 | C.Nawabganj | 134 | 19:00 | 123 | 12:00
| Srimongal | 138 | 7:00 | 135 | 19:30 | Amnura | 138 | 18:00 | 122 | 12:00
| Shahjibazar | 134 | 1:00 | 132 | 19:30 | Pabna | 139 | 18:00 | 133 | 8:00
| Fenchuganj | 139 | 8:00 | 136 | 1:00 | Shahjadpur | 140 | 4:00 | 135 | 9:00
| Khulawara | 137 | 6:00 | 135 | 12:00 | Serajganj | 135 | 4:00 | 130 | 8:00
| Sylhet | 135 | 4:00 | 133 | 19:00 | Niyamatpur | 127 | 3:00 | 118 | 8:00
| Chatak | 134 | 2:00 | 131 | 18:00 | Joypurhat | 130 | 4:00 | 121 | 8:00
| Sunamganj | 135 | 3:00 | 132 | 14:00 | Sherpur(Bogura) | 138 | 18:00 | 132 | 7:00
| Biani Bazar | 135 | 2:00 | 131 | 18:00 | Mohastangor | 136 | 18:00 | 129 | 8:00
| Comilla(s) | 128 | 2:00 | 124 | 12:00 | Bangura | 140 | 18:00 | 134 | 7:00
| Comilla(n) | 140 | 16:00 | 136 | 5:00 | Rangpur | 133 | 4:00 | 124 | 8:00
| Chandpur | 142 | 1:00 | 135 | 3:00 | Lalmonirhat | 131 | 2:00 | 124 | 8:00
| Feni | 134 | 7:00 | 128 | 15:00 | Saidpur | 132 | 3:00 | 122 | 8:00
| Chowmuhani | 135 | 1:00 | 128 | 15:00 | Purbasadipur | 130 | 4:00 | 120 | 10:00
| Ashuganj | 136 | 1:00 | 135 | 12:00 | Thakurgaon | 130 | 5:00 | 121 | 9:00
| Daudkandi | 137 | 9:00 | 131 | 3:00 | Palashbari | 131 | 20:00 | 125 | 8:00
| B.Baria | 132 | 1:00 | 130 | 15:00 | Barapukuria | 135 | 3:00 | 130 | 8:00

## L-Curve
Date | 2021-03-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 67 | 6161 | 2629 | 8790 |  |  |  | QF-LDC-11
0:30 | 65.5 | 5808 | 2524.5 | 8332.5 | Date: | 2021-03-04
1:00 | 64 | 5455 | 2420 | 7875
1:30 | 127.5 | 5211 | 2429.5 | 7640.5
2:00 | 191 | 4967 | 2439 | 7406
2:30 | 214 | 4896.5 | 2408.5 | 7305 | [5 empty] | Gen. at Eve. Peak | 10640 | 10640 MW (19:00 )
3:00 | 237 | 4826 | 2378 | 7204 | [6 empty] | 19:00
3:30 | 225 | 4799 | 2341 | 7140 | [5 empty] | Gen. at Day Peak | 9014 | 9014 MW (12:00 )
4:00 | 213 | 4772 | 2304 | 7076 | [6 empty] | 12:00
4:30 | 206 | 4733.5 | 2299.5 | 7033 | [5 empty] | Highest Generation | 10640
5:00 | 199 | 4695 | 2295 | 6990 | [6 empty] | 19:00
5:30 | 173.5 | 4749 | 2332 | 7081
6:00 | 148 | 4803 | 2369 | 7172
6:30 | 77 | 5040.5 | 2437.5 | 7478
7:00 | 6 | 5278 | 2506 | 7784
7:30 | 12 | 5442 | 2596 | 8038
8:00 | 18 | 5606 | 2686 | 8292
8:30 | 33.5 | 5776.5 | 2695 | 8471.5
9:00 | 49 | 5947 | 2704 | 8651
9:30 | 109.5 | 5950.5 | 2709.5 | 8660
10:00 | 170 | 5954 | 2715 | 8669
10:30 | 169 | 6046.5 | 2712 | 8758.5
11:00 | 168 | 6139 | 2709 | 8848
11:30 | 116 | 6186.5 | 2744.5 | 8931
12:00 | 64 | 6234 | 2780 | 9014
12:30 | 48.5 | 6422.5 | 2767 | 9189.5
13:00 | 33 | 6611 | 2754 | 9365
13:30 | 67.5 | 6500.5 | 2726.5 | 9227
14:00 | 102 | 6390 | 2699 | 9089
14:30 | 125.5 | 6554.5 | 2688 | 9242.5
15:00 | 149 | 6719 | 2677 | 9396
15:30 | 163 | 6613 | 2633 | 9246
16:00 | 177 | 6507 | 2589 | 9096
16:30 | 158.5 | 6399 | 2575 | 8974
17:00 | 140 | 6291 | 2561 | 8852
17:30 | 171 | 6337 | 2688 | 9025
18:00 | 202 | 6383 | 2815 | 9198
18:30 | 197 | 6905.5 | 3013.5 | 9919
19:00 | 192 | 7428 | 3212 | 10640
19:30 | 182 | 7378 | 3244 | 10622
20:00 | 215 | 7331 | 3119 | 10450 |  |  |  | Executive Engineer
20:30 | 177.5 | 7240 | 3103.5 | 10343.5 |  |  |  | Network Operation Division
21:00 | 140 | 7149 | 3088 | 10237
21:30 | 100 | 6981 | 2998.5 | 9979.5
22:00 | 60 | 6813 | 2909 | 9722 |  |  |  |  | Page 6 of 7
22:30 | 53 | 6647.5 | 2850 | 9497.5
23:00 | 46 | 6482 | 2791 | 9273
23:30 | 56.5 | 6321.5 | 2710 | 9031.5
24:00 | 67 | 6161 | 2629 | 8790
10640 MW (19:00 )
9014 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-04 |  | Energy | 213080894
[11 empty] | 2021-03-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3659 | 837 | 1616 | 2174 | 757 | 70 | 0 | 0 | 126 | 0
0:30 | 3444.5 | 778 | 1643 | 1770.5 | 725 | 70 | 0 | 0 | 126 | 0 | Date: | 2021-03-04
1:00 | 3230 | 719 | 1670 | 1367 | 693 | 70 | 0 | 0 | 126 | 0
1:30 | 3142.5 | 718.5 | 1639 | 1259 | 696.5 | 70 | 0 | 0 | 115 | 0 | [7 empty] | Total Energy | 213.0809 | Total Energy Gen 213.081 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.081 MKWHr
2:00 | 3055 | 718 | 1608 | 1151 | 700 | 70 | 0 | 0 | 104 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3050 | 718 | 1604 | 1068 | 691 | 70 | 0 | 0 | 104 | 0 | [7 empty] | Energy Requirement | 213.0809
3:00 | 3045 | 718 | 1600 | 985 | 682 | 70 | 0 | 0 | 104 | 0
3:30 | 3044 | 718 | 1581.5 | 939.5 | 682 | 70 | 0 | 0 | 105 | 0 | [6 empty] | Shortage
4:00 | 3043 | 718 | 1563 | 894 | 682 | 70 | 0 | 0 | 106 | 0
4:30 | 3032.5 | 718 | 1534 | 892 | 681.5 | 70 | 0 | 0 | 105 | 0
5:00 | 3022 | 718 | 1505 | 890 | 681 | 70 | 0 | 0 | 104 | 0
5:30 | 3063 | 718 | 1523.5 | 925 | 681.5 | 70 | 0 | 0 | 100 | 0
6:00 | 3104 | 718 | 1542 | 960 | 682 | 70 | 0 | 0 | 96 | 0
6:30 | 3251 | 718.5 | 1539.5 | 1121.5 | 681 | 70 | 0 | 0 | 92 | 4.5 |  |  |  |  | Coal
7:00 | 3398 | 719 | 1537 | 1283 | 680 | 70 | 0 | 0 | 88 | 9
7:30 | 3348 | 718 | 1489.5 | 1615.5 | 680 | 70 | 0 | 0 | 94 | 23 |  |  |  | Oil |  |  |  | ,
8:00 | 3298 | 717 | 1442 | 1948 | 680 | 70 | 0 | 0 | 100 | 37
8:30 | 3298 | 717 | 1396.5 | 2159 | 680 | 70 | 0 | 0 | 100 | 51
9:00 | 3298 | 717 | 1351 | 2370 | 680 | 70 | 0 | 0 | 100 | 65
9:30 | 3249 | 717.5 | 1371.5 | 2406.5 | 668.5 | 70 | 0 | 0 | 101 | 76
10:00 | 3200 | 718 | 1392 | 2443 | 657 | 70 | 0 | 0 | 102 | 87
10:30 | 3217.5 | 717.5 | 1421 | 2476 | 657.5 | 70 | 0 | 0 | 105 | 94
11:00 | 3235 | 717 | 1450 | 2509 | 658 | 70 | 0 | 0 | 108 | 101
11:30 | 3210.5 | 717 | 1533 | 2521.5 | 665.5 | 70 | 0 | 0 | 112 | 101.5
12:00 | 3186 | 717 | 1616 | 2534 | 673 | 70 | 0 | 0 | 116 | 102
12:30 | 3126.5 | 717.5 | 1597.5 | 2772.5 | 687.5 | 70 | 0 | 0 | 117 | 101
13:00 | 3067 | 718 | 1579 | 3011 | 702 | 70 | 0 | 0 | 118 | 100
13:30 | 3067 | 718 | 1579 | 3011 | 702 | 70 | 0 | 0 | 118 | 100
14:00 | 3067 | 718 | 1579 | 3011 | 702 | 70 | 0 | 0 | 118 | 100
14:30 | 3169.5 | 731.5 | 1564 | 2945 | 693.5 | 70 | 0 | 0 | 121 | 86
15:00 | 3272 | 745 | 1549 | 2879 | 685 | 70 | 0 | 0 | 124 | 72
15:30 | 3312 | 764 | 1556 | 2675.5 | 689 | 70 | 0 | 0 | 122 | 57.5
16:00 | 3352 | 783 | 1563 | 2472 | 693 | 70 | 0 | 0 | 120 | 43
16:30 | 3368 | 797.5 | 1529.5 | 2380 | 679 | 70 | 2 | 0 | 119 | 29
17:00 | 3384 | 812 | 1496 | 2288 | 665 | 70 | 4 | 0 | 118 | 15
17:30 | 3378 | 812 | 1421 | 2464 | 638.5 | 70 | 111 | 0 | 123 | 7.5
18:00 | 3372 | 812 | 1346 | 2640 | 612 | 70 | 218 | 0 | 128 | 0
18:30 | 3414 | 824 | 1470.5 | 3086 | 642 | 70 | 275.5 | 0 | 137 | 0
19:00 | 3456 | 836 | 1595 | 3532 | 672 | 70 | 333 | 0 | 146 | 0
19:30 | 3558 | 837 | 1578 | 3435 | 732 | 70 | 268 | 0 | 144 | 0
20:00 | 3565 | 837 | 1601 | 3337 | 731 | 70 | 165 | 0 | 144 | 0
20:30 | 3594 | 836.5 | 1602 | 3243 | 734.5 | 70 | 120.5 | 0 | 143 | 0
21:00 | 3623 | 836 | 1603 | 3149 | 738 | 70 | 76 | 0 | 142 | 0
21:30 | 3637 | 836 | 1601 | 2883 | 749 | 70 | 63.5 | 0 | 140 | 0
22:00 | 3651 | 836 | 1599 | 2617 | 760 | 70 | 51 | 0 | 138 | 0
22:30 | 3654 | 836 | 1611 | 2395.5 | 759 | 70 | 34 | 0 | 138 | 0
23:00 | 3657 | 836 | 1623 | 2174 | 758 | 70 | 17 | 0 | 138 | 0
23:30 | 3658 | 836.5 | 1619.5 | 2174 | 757.5 | 70 | 8.5 | 0 | 132 | 0 | Max Temp. in Dhaka |  | 32.4° C
24:00 | 3659 | 837 | 1616 | 2174 | 757 | 70 | 0 | 0 | 126 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 213.081 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.081 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1700000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [14 empty] | 0 | 8 | 8 | 14 |  | 25 | 25 | 25 | 8 |  |  |  | 102508
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7 | 12 | 15 | 18 | 17 | 18 | 16 | 13 | 8 | 3 | [9 empty] | 123390
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | [19 empty] | 10 | 120 | 130 | 130 | 120 | 120 | 120 | 522580
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 72 |  | 68 | 68 | 51 | 51 | 51 | 17 |  | 275457
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 100 | 45 | 15 |  |  |  | 17 | 98 | 180 | 193 | 195 | 230 | 265 | 278 | 263 | 195 | 195 | 195 |  | 265 | 300 | 300 | 291 | 298 | 245 | 145 | 4293053
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | [6 empty] | 270 | 270 | 270 | 180 | 180 | 180 | 180 | 180 | 260 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6263100
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 189648
33 | Ashuganj 225 MW CCPP | 206 | 200 | 201 | 205 | 212 | 200 | 193 | 181 | 172 | 164 | 166 | 161 | 162 | 206 | 213 | 214 | 203 | 201 |  | 199 | 199 | 199 | 202 | 196 | 194 | 196 | 4699000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6344000
| Ashuganj 450 MW CCPP(North) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7052700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | 139 | [13 empty] | 50 | 53 | 95 | 97 |  | 94 | 97 | 94 | 94 | 95 | 93 | 99 | 1014310
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 362 | 346 | 345 | 343 | 337 | 348 | 357 | 338 | 337 | 338 | 354 | 367 | 344 | 345 | 355 | 356 | 341 | 317 |  | 357 | 339 | 339 | 340 | 338 | 340 | 340 | 8409080
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 390 | 390 | 390 | 360 | 360 | 360 | 360 | 330 | 330 | 360 | 450 | 450 | 400 | 450 | 450 | 450 | 340 |  | 400 | 400 | 420 | 420 | 420 | 420 | 420 | 9459250
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 107 | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 106 | 104 | 103 | 85 | 85 | 85 | 103 | 102 | 103 | 104 |  | 105 | 106 | 105 | 107 | 107 | 107 | 107 | 2409320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 17 | 28 | 37 | 43 | 44 | 39 | 38 | 28 | 16 | 5 | [9 empty] | 298530
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 162 | 162 | 163 | 160 | 160 | 155 | 155 | 161 | 162 | 161 | 164 | 162 | 162 | 160 | 164 | 161 | 164 | 163 |  | 162 | 163 | 162 | 162 | 162 | 160 | 163 | 2511000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 35 | 35 | 34 | 34 | 34 | 34 | 35 | 34 | 35 | 20 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 841344
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 83 | 80 | 80 | 80 | 80 | 83 | 80 | 80 | 83 | 83 | 84 | 84 | 84 | 84 | 40 | 40 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1913280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 137 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 155 |  | 163 | 163 | 163 | 163 | 163 | 161 | 162 | 3442180
51 | Sylhet 20 MW GTPP | 19 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 5 | 6 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 131940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 48 | 48 | 50 | 50 | 50 | 47 | 24 | 22 |  | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 1140600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 310544
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 300 | 305 | 310 | 295 | 305 | 310 | 290 | 280 | 290 | 310 | 320 | 290 | 290 | 280 | 300 | 300 | 300 |  | 310 | 290 | 290 | 290 | 280 | 300 | 300 | 7427500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 327 | 350 | 350 | 320 | 320 | 320 | 350 | 342 | 320 | 340 | 320 | 328 | 320 | 320 |  | 320 | 320 | 320 | 370 | 396 | 392 | 370 | 8309000
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 7 | 10 | 17 | 44 | 55 | 17 | 20 | 35 | 35 | 45 |  | 55 | 55 | 55 | 55 |  |  |  | 493864
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 20 | 24 | 24 | 22 | 23 | 21 | 22 | 24 | 25 | 24 | 25 |  | 24 | 24 | 25 | 24 | 25 | 25 |  | 400800
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 386880
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492192
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [15 empty] | 187200
63 | Impoprt (Tripura) | 126 | 104 | 104 | 106 | 104 | 96 | 88 | 100 | 100 | 102 | 108 | 116 | 118 | 122 | 124 | 120 | 118 | 128 |  | 146 | 144 | 144 | 142 | 138 | 138 | 126 | 2854080
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 41 | 42 | 42 | 42 | 34 | 10 | 5 | 4 | 4 | 5 | 5 | 5 | 3 | 3 | 10 | 10 |  | 21 | 22 | 25 | 28 | 36 | 38 | 38 | 503520
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 477000
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | [5 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 473400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 18 | 15 | 15 | 15 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 15 | 15 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 690875
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 28 | 28 | 28 | 31 | 22 | 31 | 32 | 32 | 28 | 28 | 28 | 28 | 30 | 31 | 20 |  | 24 | 30 | 31 | 31 | 31 | 31 | 31 | 685080
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 28 | 25 | 25 | 25 | 28 | 28 | 659000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807600
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 300045
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [11 empty] | 38 | 98 | 55 | 55 | 35 | 35 | 44 |  | 72 | 55 | 55 | 55 |  |  |  | 705600
| Manikgonj 162MW PP(MPGL) | [11 empty] | 5 | 52 | 17 | 17 | 17 | 17 | 30 |  | 72 | 72 | 35 |  |  |  |  | 315360
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 20 | 50 | 50 | 54 | 80 | 100 | 63 | 60 | 45 | 40 | 48 |  | 100 | 100 | 100 | 100 | 100 |  |  | 1080749
78 | Gazipur 52 MW PP | [17 empty] | 8 |  | 8 | [6 empty] | 10536
79 | Kodda 150MW PP | [17 empty] | 48 |  | 82 | 48 | 48 |  |  |  |  | 159360
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 16 | 48 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 46 | 81 | 81 | 81 | 24 | 24 | 24 | 624000
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 10 |  | 25 | 1 | [5 empty] | 50386
| Gazipur 100 MW PP | [9 empty] | 5 | 25 | 50 | 90 | 70 | 70 | 34 | 34 | 42 |  | 70 | 34 | 34 | 34 | 34 |  |  | 690552
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 28617
| Jodiac Power | [7 empty] | 16 | 17 | 17 | 17 | 39 | 54 | 17 | 23 | 35 | 35 | 41 |  | 54 | 54 | 54 | 54 | 17 |  |  | 547385
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [8 empty] | 12 | 15 | 15 | 30 | 52 | 60 | 70 | 48 | 48 | 48 |  | 80 | 99 | 99 | 99 | 48 | 14 |  | 823056
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 8 | 70 | 60 | 61 | 61 | 61 | 63 | 76 | 85 | 84 | 85 | 85 |  | 87 | 100 | 100 | 100 | 100 | 70 | 40 | 1374358
86 | Meghnaghat CCPP(Summit) | 270 | 260 | 260 | 280 | 275 | 290 | 275 | 265 | 260 | 260 | 290 | 270 | 250 | 280 | 280 | 260 | 225 | 230 |  | 260 | 230 | 260 | 245 | 270 | 275 | 265 | 6452713
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 1 | 48 | 20 | 16 | 16 | 16 | 29 |  | 64 | 100 | 100 | 53 |  |  |  | 397440
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 46 | 84 | 104 | 104 | 104 | 104 | 104 | 104 | 80 | 71 | 74 |  | 104 | 104 | 104 | 104 | 104 | 90 | 50 | 1607040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 10 | 20 | 10 | 40 | 20 | 20 | 60 |  | 100 | 40 | 40 | 10 |  |  |  | 312240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 32 | 72 | 32 | 32 | 16 | 16 | 50 |  | 72 | 40 | [5 empty] | 312624
95 | Patenga 50MW PP (Baraka) | 50 | [5 empty] | 5 | 26 | 41 | 45 | 45 | 45 | 45 | 45 | 45 | 33 | 45 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 832320
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 25 | 13 | 12 | 12 | 12 | 22 |  | 44 | [6 empty] | 146880
97 | katpotti 52 MW | [12 empty] | 6 | 12 | 13 | 18 | 18 | 20 |  | 25 | 25 | 28 |  |  |  |  | 169296
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | [5 empty] | 22 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 15 |  | 884192
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 512451
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 130 | 163 | 110 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3511472
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14550
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 |  |  |  | 17 | 17 | 54 | 46 | 35 | 35 | 35 | 35 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 872640
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 140 | 100 | 60 | 50 | 50 | 81 | 132 | 192 | 200 | 200 | 192 | 192 | 194 | 194 | 200 | 170 | 170 | 178 |  | 193 | 200 | 200 | 200 | 200 | 200 | 200 | 4008000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 82 | 68 | 64 | 52 | 50 | 57 | 103 | 105 | 130 | 144 | 144 | 118 | 120 | 125 | 131 | 149 | 122 | 113 |  | 122 | 135 | 144 | 131 | 131 | 131 | 100 | 2672784
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 20 | 50 | 70 | 70 | 88 | 100 | 100 | 100 | 100 | 70 | 50 | 50 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 1423680
116 | Chandpur 200MW (Desh energy) | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 162 | 200 | 200 |  | 17 | 83 | 100 | 100 | 100 | 104 |  | 114 | 120 | 120 | 120 | 120 | 120 | 120 | 2831520
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 344 | 333 | 327 | 329 | 329 | 349 | 352 | 331 | 331 | 329 | 346 | 360 | 330 | 330 | 330 | 330 | 331 | 331 |  | 330 | 331 | 330 | 331 | 340 | 352 | 355 | 8124000
| Jamalpur 115 MW PP (United) | [8 empty] | 12 | 16 | 16 | 39 | 75 | 35 | 41 | 45 | 45 | 52 |  | 76 | 65 | 45 | 45 | 8 |  |  | 609600
| Anwara 300 MW PP (United) | 306 | 306 | 270 | 232 | 235 | 235 | 306 | 305 | 306 | 306 | 304 | 305 | 305 | 306 | 306 | 306 | 253 | 216 |  | 287 | 288 | 288 | 290 | 305 | 306 | 306 | 6927600
| Juldah unit-2 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2157120
| Anlima Energy Ltd. | [16 empty] | 7 | 17 |  | 35 | [6 empty] | 77781
| Bhairob 54.5 MW | 55 | 56 | 56 | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 132228
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 9 | 18 | 25 | 29 | 29 | 31 | 27 | 23 | 14 | 5 | [9 empty] | 209039
120 | Eastern Zone Total | 5455 | 4967 | 4826 | 4772 | 4695 | 4803 | 5278 | 5606 | 5947 | 5954 | 6139 | 6234 | 6611 | 6390 | 6719 | 6507 | 6291 | 6383 |  | 7428 | 7378 | 7331 | 7149 | 6813 | 6482 | 6161 | 147227459
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [11 empty] | 17 | 32 | 32 | 32 | 16 | 16 | 41 |  | 66 | 53 | 32 | 32 |  |  |  | 311040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 53 | 53 | 56 | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 53 |  | 105 | 105 | 105 | 105 | 35 | 35 |  | 1028640
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 73 | 73 | 72 | 72 | 73 | 74 | 74 | 72 | 73 | 73 | 72 | 70 | 55 | 70 | 64 | 69 | 57 | 70 |  | 70 | 71 | 71 | 71 | 68 | 71 | 70 | 1750091
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 48 | 48 | 48 | 48 | 48 | 16 | 0 | 338208
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 76 | 65 | 45 | 45 | 45 | 45 | 44 | 44 | 42 | 44 | 44 | 43 | 44 | 44 | 42 | 44 | 44 |  | 75 | 75 | 74 | 74 | 74 | 75 | 74 | 1329233
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 27 | 22 | 20 | 20 | 16 | 15 | 13 | 14 | 12 | 12 | 13 | 15 | 15 | 16 | 16 | 15 | 15 | 19 |  | 26 | 26 | 26 | 26 | 25 | 23 | 22 | 438451
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 40 | 40 | 16 | 16 |  |  |  | 81000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 4 | 12 |  | 6 | [6 empty] | 21472
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 719 | 718 | 718 | 718 | 718 | 718 | 719 | 717 | 717 | 718 | 717 | 717 | 718 | 717 | 745 | 783 | 812 | 812 |  | 836 | 837 | 837 | 836 | 836 | 836 | 837 | 18289454
147 | Bheramara 410 MW CCPP | 185 | 185 | 180 | 180 | 180 | 225 | 240 | 240 | 230 | 220 | 215 | 190 | 180 | 165 | 155 | 160 | 170 | 175 |  | 180 | 175 | 180 | 180 | 180 | 180 | 180 | 4719168
148 | Payra 1320 MW | 440 | 450 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 400 | 400 | 400 | 430 | 400 | 420 | 430 | 400 | 350 |  | 410 | 470 | 470 | 480 | 500 | 500 | 500 | 11310300
149
150 | Barapukuria TPP Unit-1 | 103 | 100 | 102 | 102 | 101 | 102 | 100 | 100 | 101 | 108 | 109 | 124 | 122 | 116 | 115 | 113 | 115 | 112 |  | 112 | 112 | 111 | 108 | 110 | 108 | 107 | 2559272
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3663700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 14 |  | 50 | 50 | [5 empty] | 79392
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 144 | 144 | 144 | 145 | 150 | 151 | 152 | 160 | 167 | 169 | 168 | 170 | 143 | 125 | 126 | 131 | 138 | 149 |  | 150 | 150 | 150 | 150 | 160 | 160 | 170 | 3877373
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 400 | 400 | 380 | 370 | 397 | 397 | 365 | 324 | 363 | 363 | 408 | 382 | 383 | 356 | 349 | 349 | 347 |  | 354 | 354 | 355 | 354 | 355 | 355 | 350 | 8863363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 20 | 19 | 19 | 19 | 21 | 21 |  | 21 | 22 | 22 | 22 | 21 | 21 | 22 | 500160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 160650
165 | Amnura 50 MW PP(Sinha) | [12 empty] | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  |  | 127950
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 12 |  | 27 | 27 | [5 empty] | 39536
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 25 |  | 52 | 52 | 52 | 52 |  |  |  | 642720
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 60 |  | 100 | 75 | 66 | 25 |  |  |  | 146088
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 70 | 35 | 35 | 35 | 39 | 92 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 108 | 108 | 113 | 113 | 113 | 70 | 2140992
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1690080
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 54 | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 49 | 105 |  | 107 | 111 | 113 | 113 | 113 | 70 | 34 | 1708800
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 6 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 36302
178
178