## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-12 | Friday
|  | Date (day): | 2021-03-12 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14223.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15147 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-11 | 2021-03-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 | 65 |  | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 108 | 104 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dirty fuel(Gas)
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Dirty fuel(Gas)
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 450 |  | Dirty fuel(Gas)
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 65 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 235 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 98 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 73 | 83 | 87 | 87 |  |  | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 87 | 115 | 115 | 95 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 222 | 221 | 220 | 220 |  | 115 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 49 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 45 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 227 | 300 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 151 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 95 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 77 | 90 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 144 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 32 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2302 | 2884 | 3418 | 3638 | 1490 | 745
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 36 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 87 | 102 | 102
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 15 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 20 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 23 | 25 | 40
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 55 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 306 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 809 | 1180 | 1815 | 1855 | 400 | 98
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 183 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 325 | 360 | 360
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 270 | 300 | 300 | 60 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 56 | 55 | 55
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 80 | 90 | 90 |  | 73 | ST under maint.
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 150 | 180 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 166 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 20 | 21
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1451 | 1587 | 1872 | 2140 | 538 | 73
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 140 | 160 | 160 |  |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 66 | 81 | 81 | 81 |  | 14 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 184 | 193 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 75 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 25 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 484 | 530 | 651.6 | 600 | 0 | 14
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 310 | 308 | 310 | 310
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 20 | 35 | 35 |  | 31 | GT-9 Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 79 | 80 | 80 |  | 6 | Engine problem
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 87 | 105 | 150 |  | 81 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 275 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 367 | 366 | 366
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 251 | 340 | 340 | 340
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1609 | 1831 | 1934 | 1979 | 0 | 311
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 726 | 725 | 738 | 738
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 66 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 13 | 60 | 60 |  | 49 | Engine problem
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 410 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 60 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 54 | 94 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1196 | 1408 | 1617 | 1903 | 0 | 94
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 29 | 33 | 33
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 84 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 520 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 73 | 64 | 72 | 72 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 601 | 761 | 1080 | 1080 | 0 | 194
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 15 | 0 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 42 | 44 | 44 |  | 6 | Engine problem
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 151 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 185 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 385 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 95 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1018 | 1171 | 1555 | 1679 | 381 | 6
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 223 | 263 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 9693 | 11615 | 14223.6 | 15147 | 2933 | 1735
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9203.9687 | 11029 | 13505.9909 | 14382.8035
A. |  | 2021-03-11 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 11615 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7685 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11615 | MW
3 | Day peak Generation : |  |  | 9693 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11029 | MW
4 | Evening peak Generation : |  |  | 11615 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 229.7246 | MKWHr | By Solar | 0.6575 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 134.4466 | MKWHr |  | By Oil: | 57.0683 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 15.1352 | MKWHr |  | By Hydro: | 1.696 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2933 | MW | Dhaka | 4074 | 4074 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1735 | MW | Chittagong | 1202 | 1202 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4668 | MW | Khulna | 1388 | 1388 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1103.43 | MMCFD |  |  | Rajshahi | 1107 | 1107 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 144096871.748 | ii) Oil : | Taka | 405022203.45 | Comilla | 1003 | 1003 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 70218787 | Total | Taka | 619337862.198 | Mymensingh | 917 | 917 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0605 | MKWHr. | Sylhet | 391 | 391 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -30 | MW (E to W) at | 19:30 | hrs | Barisal | 290 | 290 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -30 | MW at | 19:30 | hrs | Rangpur | 657 | 657 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 11029 | 11029 |  | 0
B. |  | 2021-03-12 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15147 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 4247 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 215.5831 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7804 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.5338 | MKWHr. | ii) HVDC Flow at Peak Time |  | 725 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1872 | MKWHr. | iii) Maximum HVDC Flow : |  | 726 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.58 |  | (b) Today: | 89.46 |  | (c) Rule Curve: |  | 91.24
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 300 | 62 | 0 | 0 | 0 |  | 0 | 0 | 230 | 0 | 0 | 30 | 222 | 0 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 38 | 0 | 0 | 130 | 240 | 295 | 183 | 0 | 80 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 124 | 144 | 8 | 17 | 0 | 44 | 32 | 53 | 0 | 163 | 308 | 35 | 79 | 0 | 0 | 19 | 0 | 7 | 300 | 16 | 11 | 0 | 300 | 0 | 0 | 150 | 0 | 128 | 0 | 10 | 200 | 0 | 322 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 100 | 250 | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 725 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 180 | 0 | 357 | 0 | 0 | 113 | 0 | 53 | 0 | 0 | 35 | 520 | 70 | 0 | 0 |  | 5984 | 2815 | 8799 | 4012 | 725 | 1306 | 1884 | 670 | 70 | 8 | 124 | 0 | 0 | 89.6
2:00 | 0 | 0 | 0 | 190 | 300 | 63 | 0 | 0 | 0 |  | 0 | 0 | 225 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 38 | 0 | 0 | 130 | 300 | 295 | 189 | 0 | 85 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 120 | 154 | 0 | 17 | 0 | 44 | 32 | 53 | 0 | 163 | 307 | 35 | 79 | 0 | 0 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 225 | 0 | 0 | 120 | 0 | 103 | 0 | 0 | 200 | 0 | 322 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 100 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 167 | 0 | 72 | 0 | 196 | 0 | 397 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 480 | 72 | 0 | 0 |  | 5605 | 2756 | 8361 | 4152 | 726 | 1338 | 1315 | 630 | 70 | 10 | 120 | 0 | 0 | 89.6
3:00 | 0 | 0 | 0 | 190 | 300 | 86 | 0 | 0 | 0 |  | 0 | 0 | 230 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 35 | 0 | 0 | 130 | 375 | 295 | 183 | 0 | 86 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 116 | 148 | 0 | 17 | 0 | 44 | 32 | 53 | 0 | 163 | 309 | 35 | 79 | 0 | 0 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 65 | 0 | 0 | 120 | 0 | 101 | 0 | 0 | 150 | 0 | 323 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 100 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 178 | 0 | 73 | 0 | 200 | 0 | 370 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 480 | 72 | 0 | 0 |  | 5402 | 2722 | 8124 | 4245 | 726 | 1342 | 983 | 630 | 70 | 12 | 116 | 0 | 0 | 89.59
4:00 | 0 | 0 | 0 | 190 | 300 | 96 | 0 | 0 | 0 |  | 0 | 0 | 225 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 38 | 0 | 0 | 130 | 375 | 260 | 183 | 0 | 86 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 28 | 15 | 114 | 156 | 0 | 17 | 0 | 44 | 32 | 53 | 0 | 163 | 307 | 36 | 79 | 0 | 0 | 19 | 0 | 7 | 300 | 16 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 90 | 0 | 0 | 81 | 0 | 323 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 70 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 14 | 0 | 0 | 0 | 178 | 0 | 53 | 0 | 200 | 0 | 398 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 440 | 72 | 0 | 0 |  | 5188 | 2692 | 7880 | 4212 | 726 | 1363 | 791 | 590 | 70 | 14 | 114 | 0 | 0 | 89.59
5:00 | 0 | 0 | 0 | 190 | 300 | 99 | 0 | 0 | 0 |  | 0 | 0 | 230 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 127 | 375 | 260 | 183 | 0 | 86 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 108 | 157 | 0 | 17 | 0 | 44 | 32 | 53 | 0 | 110 | 305 | 36 | 79 | 0 | 0 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 81 | 0 | 322 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 70 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 175 | 0 | 53 | 0 | 200 | 0 | 333 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 72 | 0 | 0 |  | 5135 | 2550 | 7685 | 4205 | 726 | 1251 | 793 | 520 | 70 | 12 | 108 | 0 | 0 | 89.58
6:00 | 0 | 0 | 0 | 190 | 300 | 102 | 0 | 0 | 0 |  | 0 | 0 | 225 | 0 | 1 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 100 | 305 | 260 | 183 | 0 | 80 | 26 | 57 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 104 | 156 | 0 | 17 | 0 | 44 | 32 | 53 | 0 | 110 | 305 | 36 | 79 | 0 | 0 | 18 | 0 | 7 | 315 | 16 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 86 | 0 | 323 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 100 | 250 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 175 | 0 | 53 | 0 | 200 | 0 | 313 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 73 | 0 | 0 |  | 5188 | 2510 | 7698 | 4084 | 726 | 1245 | 937 | 520 | 70 | 12 | 104 | 0 | 0 | 89.58
7:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 230 | 0 | 20 | 27 | 221 | 0 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 17 | 0 | 0 | 0 | 0 | 25 | 19 | 38 | 0 | 0 | 100 | 280 | 260 | 188 | 0 | 85 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 78 | 156 | 2 | 17 | 0 | 44 | 32 | 53 | 0 | 110 | 307 | 35 | 79 | 0 | 0 | 19 | 0 | 7 | 290 | 16 | 11 | 0 | 60 | 0 | 0 | 129 | 0 | 96 | 0 | 10 | 130 | 0 | 322 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 100 | 250 | 53 | 1 | 0 | 0 | 0 | 0 | 2 |  | 726 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 140 | 0 | 53 | 0 | 160 | 0 | 336 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 300 | 73 | 0 | 0 |  | 5415 | 2405 | 7820 | 4013 | 726 | 1244 | 1224 | 450 | 70 | 12 | 78 | 3 | 0 | 89.57
8:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 230 | 0 | 30 | 32 | 222 | 0 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 23 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 0 | 0 | 100 | 290 | 285 | 195 | 0 | 85 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 102 | 156 | 23 | 17 | 0 | 43 | 31 | 53 | 0 | 110 | 306 | 35 | 76 | 0 | 0 | 19 | 0 | 7 | 315 | 16 | 11 | 0 | 62 | 0 | 0 | 193 | 0 | 120 | 0 | 10 | 132 | 0 | 322 | 0 | 5 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 100 | 250 | 53 | 8 | 0 | 0 | 0 | 0 | 7 |  | 726 | 0 | 380 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 154 | 0 | 53 | 0 | 174 | 0 | 337 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 25 | 340 | 73 | 0 | 0 |  | 5634 | 2578 | 8212 | 4088 | 726 | 1237 | 1470 | 490 | 70 | 12 | 102 | 17 | 0 | 89.57
9:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 225 | 0 | 30 | 45 | 221 | 0 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 0 | 54 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 36 | 19 | 4 | 0 | 0 | 100 | 285 | 280 | 194 | 0 | 91 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 33 | 15 | 106 | 155 | 64 | 17 | 0 | 43 | 32 | 53 | 0 | 130 | 307 | 34 | 73 | 0 | 0 | 19 | 0 | 7 | 325 | 16 | 5 | 0 | 131 | 0 | 0 | 194 | 0 | 123 | 9 | 10 | 150 | 0 | 322 | 0 | 35 | 0 | 3 | 210 | 0 | 0 | 0 | 0 | 100 | 250 | 53 | 21 | 0 | 0 | 0 | 0 | 18 |  | 725 | 0 | 380 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 12 | 0 | 0 | 0 | 169 | 0 | 53 | 0 | 184 | 0 | 420 | 17 | 0 | 37 | 0 | 34 | 0 | 0 | 50 | 400 | 73 | 0 | 0 |  | 5925 | 2771 | 8696 | 4098 | 725 | 1340 | 1745 | 549 | 70 | 12 | 106 | 51 | 0 | 89.56
10:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 225 | 0 | 30 | 45 | 223 | 0 | 0 | 40 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 55 | 20 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 25 | 0 | 0 | 0 | 0 | 38 | 19 | 3 | 0 | 0 | 100 | 270 | 265 | 183 | 0 | 90 | 23 | 56 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 33 | 15 | 116 | 152 | 64 | 17 | 0 | 43 | 42 | 53 | 0 | 110 | 310 | 34 | 76 | 0 | 0 | 19 | 0 | 7 | 300 | 16 | 5 | 0 | 195 | 0 | 0 | 200 | 0 | 132 | 13 | 10 | 150 | 0 | 322 | 0 | 45 | 0 | 4 | 250 | 0 | 0 | 0 | 0 | 100 | 250 | 54 | 39 | 22 | 0 | 0 | 0 | 26 |  | 726 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 153 | 0 | 53 | 0 | 178 | 0 | 411 | 17 | 0 | 102 | 0 | 70 | 0 | 0 | 70 | 430 | 72 | 0 | 0 |  | 6114 | 2866 | 8980 | 4019 | 726 | 1288 | 2089 | 580 | 70 | 10 | 116 | 82 | 0 | 89.56
11:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 230 | 41 | 38 | 45 | 223 | 0 | 0 | 80 | 3 | 0 | 74 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 21 | 0 | 0 | 0 | 0 | 43 | 19 | 3 | 0 | 0 | 100 | 315 | 270 | 187 | 0 | 90 | 23 | 56 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 33 | 11 | 126 | 152 | 73 | 17 | 2 | 43 | 42 | 50 | 0 | 110 | 309 | 34 | 81 | 0 | 0 | 19 | 0 | 7 | 300 | 16 | 5 | 0 | 195 | 0 | 0 | 192 | 0 | 125 | 14 | 10 | 150 | 0 | 322 | 0 | 52 | 0 | 4 | 306 | 0 | 0 | 0 | 0 | 90 | 250 | 68 | 42 | 54 | 0 | 0 | 0 | 30 |  | 726 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 53 | 0 | 175 | 0 | 417 | 17 | 0 | 113 | 0 | 70 | 0 | 4 | 70 | 430 | 72 | 0 | 0 |  | 6415 | 2872 | 9287 | 4062 | 726 | 1297 | 2330 | 580 | 70 | 0 | 126 | 96 | 0 | 89.55
12:00 | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 0 |  | 0 | 0 | 230 | 65 | 64 | 45 | 222 | 0 | 0 | 100 | 32 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 25 | 0 | 0 | 0 | 0 | 31 | 19 | 2 | 0 | 0 | 100 | 340 | 295 | 202 | 0 | 91 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 14 | 132 | 149 | 66 | 17 | 2 | 43 | 42 | 53 | 0 | 130 | 310 | 34 | 78 | 0 | 0 | 19 | 0 | 7 | 305 | 16 | 0 | 0 | 227 | 0 | 0 | 184 | 0 | 132 | 17 | 20 | 150 | 0 | 321 | 0 | 52 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 100 | 251 | 77 | 41 | 54 | 0 | 0 | 0 | 32 |  | 726 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 78 | 0 | 195 | 0 | 414 | 54 | 0 | 113 | 0 | 70 | 0 | 3 | 70 | 430 | 73 | 0 | 0 |  | 6655 | 3038 | 9693 | 4234 | 726 | 1342 | 2509 | 580 | 70 | 0 | 132 | 100 | 0 | 89.55
13:00 | 0 | 0 | 0 | 190 | 300 | 107 | 0 | 0 | 0 |  | 0 | 0 | 230 | 93 | 72 | 45 | 222 | 0 | 0 | 100 | 64 | 0 | 72 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 36 | 19 | 7 | 0 | 0 | 100 | 350 | 265 | 184 | 0 | 90 | 26 | 52 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 14 | 136 | 117 | 40 | 17 | 2 | 43 | 42 | 53 | 0 | 130 | 307 | 33 | 79 | 0 | 0 | 19 | 0 | 7 | 310 | 8 | 5 | 0 | 290 | 0 | 0 | 192 | 0 | 132 | 16 | 90 | 150 | 0 | 321 | 0 | 70 | 0 | 4 | 306 | 27 | 0 | 0 | 0 | 100 | 250 | 91 | 48 | 54 | 0 | 0 | 0 | 31 |  | 726 | 0 | 355 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 83 | 0 | 199 | 0 | 399 | 70 | 0 | 105 | 0 | 110 | 0 | 4 | 100 | 450 | 71 | 0 | 0 |  | 6853 | 3117 | 9970 | 4114 | 726 | 1343 | 2876 | 600 | 70 | 0 | 136 | 105 | 9970 | 89.54
14:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 0 |  | 0 | 0 | 230 | 82 | 94 | 48 | 222 | 0 | 0 | 100 | 64 | 0 | 73 | 0 | 0 | 0 | 45 | 55 | 51 | 22 | 25 | 30 | 33 | 16 | 0 | 0 | 0 | 70 | 120 | 0 | 3 | 27 | 0 | 120 | 0 |  | 25 | 0 | 0 | 0 | 0 | 45 | 19 | 4 | 0 | 0 | 100 | 312 | 265 | 184 | 0 | 90 | 26 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 148 | 117 | 33 | 17 | 1 | 43 | 42 | 53 | 0 | 130 | 309 | 30 | 79 | 0 | 0 | 19 | 0 | 7 | 300 | 8 | 5 | 0 | 295 | 0 | 0 | 192 | 0 | 132 | 14 | 60 | 150 | 0 | 367 | 0 | 52 | 0 | 4 | 306 | 54 | 0 | 0 | 0 | 100 | 250 | 91 | 37 | 54 | 0 | 0 | 0 | 28 |  | 726 | 0 | 355 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 83 | 0 | 174 | 0 | 397 | 70 | 0 | 105 | 0 | 113 | 0 | 4 | 113 | 460 | 72 | 0 | 0 |  | 6858 | 3087 | 9945 | 4088 | 726 | 1331 | 2884 | 610 | 70 | 0 | 148 | 88 | 0 | 89.54
15:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 255 | 75 | 85 | 48 | 222 | 0 | 0 | 94 | 64 | 0 | 72 | 0 | 0 | 0 | 54 | 55 | 47 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 27 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 45 | 19 | 2 | 0 | 0 | 100 | 325 | 270 | 184 | 0 | 90 | 26 | 53 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 152 | 116 | 33 | 17 | 1 | 43 | 42 | 53 | 0 | 130 | 307 | 30 | 79 | 0 | 0 | 19 | 0 | 6 | 320 | 8 | 11 | 0 | 300 | 0 | 0 | 154 | 0 | 134 | 11 | 60 | 145 | 0 | 368 | 0 | 57 | 0 | 3 | 306 | 54 | 0 | 0 | 0 | 100 | 365 | 91 | 28 | 54 | 0 | 0 | 0 | 21 |  | 726 | 0 | 355 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 83 | 0 | 176 | 0 | 419 | 70 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 460 | 71 | 0 | 0 |  | 6991 | 3119 | 10110 | 4244 | 726 | 1369 | 2872 | 610 | 70 | 0 | 152 | 67 | 0 | 89.53
16:00 | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 |  | 0 | 0 | 277 | 75 | 80 | 48 | 222 | 0 | 0 | 96 | 48 | 0 | 73 | 0 | 0 | 0 | 54 | 35 | 52 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 30 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 4 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 90 | 26 | 52 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 142 | 120 | 33 | 17 | 1 | 43 | 42 | 53 | 0 | 130 | 308 | 33 | 75 | 0 | 22 | 19 | 0 | 6 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 141 | 6 | 60 | 152 | 0 | 368 | 0 | 70 | 0 | 2 | 306 | 35 | 0 | 0 | 0 | 90 | 340 | 90 | 16 | 54 | 0 | 0 | 0 | 12 |  | 726 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 82 | 0 | 168 | 0 | 344 | 35 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 420 | 70 | 0 | 0 |  | 6946 | 2929 | 9875 | 4210 | 726 | 1267 | 2850 | 570 | 70 | 0 | 142 | 40 | 0 | 89.53
17:00 | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 |  | 0 | 0 | 255 | 75 | 80 | 48 | 222 | 0 | 32 | 100 | 48 | 0 | 74 | 0 | 0 | 0 | 35 | 35 | 53 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 30 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 5 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 88 | 26 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 140 | 136 | 33 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 309 | 34 | 79 | 0 | 21 | 19 | 0 | 6 | 290 | 8 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 138 | 2 | 30 | 147 | 0 | 367 | 0 | 70 | 0 | 1 | 306 | 35 | 0 | 0 | 0 | 70 | 340 | 91 | 6 | 54 | 0 | 0 | 0 | 5 |  | 725 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 83 | 0 | 168 | 0 | 324 | 35 | 0 | 70 | 0 | 70 | 0 | 2 | 70 | 400 | 71 | 0 | 0 |  | 6846 | 2743 | 9589 | 4253 | 725 | 1245 | 2590 | 550 | 70 | 0 | 140 | 16 | 0 | 89.52
18:00 | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 |  | 0 | 0 | 235 | 75 | 97 | 48 | 222 | 0 | 34 | 100 | 48 | 0 | 74 | 0 | 0 | 1 | 35 | 55 | 43 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 36 | 0 | 120 | 0 |  | 24 | 0 | 82 | 0 | 6 | 50 | 19 | 5 | 0 | 0 | 100 | 325 | 270 | 184 | 0 | 90 | 23 | 55 | 0 | 0 | 0 | 6 | 0 | 19 | 11 | 33 | 15 | 154 | 138 | 33 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 309 | 34 | 79 | 0 | 76 | 19 | 0 | 6 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 138 | 0 | 30 | 135 | 0 | 367 | 2 | 70 | 0 | 0 | 306 | 35 | 0 | 0 | 9 | 70 | 363 | 90 | 0 | 60 | 0 | 0 | 0 | 0 |  | 726 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 7 | 0 | 0 | 30 | 0 | 20 | 16 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 84 | 0 | 168 | 0 | 343 | 35 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 370 | 71 | 0 | 0 |  | 7071 | 2805 | 9876 | 4341 | 726 | 1268 | 2670 | 520 | 70 | 127 | 154 | 0 | 0 | 89.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 |  | 0 | 0 | 235 | 88 | 97 | 55 | 221 | 0 | 87 | 100 | 85 | 48 | 80 | 0 | 0 | 38 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 70 | 120 | 0 | 23 | 36 | 0 | 120 | 0 |  | 24 | 0 | 102 | 30 | 50 | 50 | 19 | 16 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 80 | 23 | 56 | 0 | 0 | 0 | 42 | 7 | 19 | 8 | 33 | 15 | 168 | 139 | 52 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 307 | 28 | 79 | 0 | 88 | 19 | 0 | 7 | 300 | 16 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 140 | 0 | 100 | 150 | 0 | 367 | 41 | 85 | 0 | 0 | 306 | 49 | 0 | 0 | 71 | 100 | 340 | 91 | 0 | 131 | 0 | 0 | 0 | 0 |  | 726 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 30 | 60 | 0 | 0 | 0 | 43 | 0 | 98 | 42 | 50 | 31 | 52 | 22 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 84 | 15 | 180 | 0 | 394 | 94 | 0 | 99 | 0 | 113 | 0 | 0 | 95 | 500 | 69 | 0 | 0 |  | 7874 | 3670 | 11544 | 4462 | 726 | 1377 | 3686 | 650 | 70 | 405 | 168 | 0 | 0 | 89.5
19:30 | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 |  | 0 | 0 | 235 | 100 | 98 | 55 | 221 | 0 | 87 | 100 | 102 | 48 | 83 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 0 | 70 | 120 | 0 | 25 | 36 | 0 | 120 | 0 |  | 24 | 0 | 87 | 15 | 55 | 50 | 19 | 23 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 80 | 23 | 56 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 15 | 166 | 140 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 308 | 20 | 79 | 0 | 87 | 19 | 0 | 7 | 275 | 16 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 151 | 0 | 100 | 180 | 0 | 367 | 75 | 95 | 0 | 0 | 306 | 54 | 0 | 0 | 113 | 100 | 340 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 725 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 13 | 40 | 0 | 29 | 64 | 0 | 0 | 0 | 15 | 0 | 100 | 42 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 84 | 60 | 185 | 0 | 385 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 520 | 64 | 0 | 0 |  | 8012 | 3603 | 11615 | 4460 | 725 | 1344 | 3917 | 670 | 70 | 263 | 166 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 235 | 100 | 99 | 55 | 228 | 0 | 87 | 100 | 102 | 48 | 82 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 25 | 36 | 0 | 120 | 0 |  | 24 | 0 | 68 | 0 | 31 | 50 | 19 | 27 | 0 | 0 | 100 | 325 | 265 | 183 | 0 | 81 | 23 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 166 | 139 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 309 | 20 | 79 | 0 | 90 | 19 | 0 | 7 | 260 | 16 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 197 | 0 | 367 | 75 | 100 | 0 | 0 | 306 | 54 | 0 | 0 | 113 | 100 | 340 | 91 | 0 | 54 | 0 | 0 | 0 | 0 |  | 725 | 0 | 400 | 0 | 66 | 0 | 0 | 0 | 0 | 13 | 40 | 0 | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 100 | 42 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 84 | 60 | 186 | 0 | 396 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 69 | 0 | 0 |  | 7839 | 3614 | 11453 | 4457 | 725 | 1350 | 3786 | 670 | 70 | 229 | 166 | 0 | 0 | 89.51
21:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 235 | 55 | 99 | 55 | 231 | 0 | 90 | 100 | 50 | 48 | 84 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 25 | 93 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 50 | 19 | 36 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 81 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 158 | 140 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 309 | 22 | 79 | 0 | 105 | 19 | 0 | 7 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 184 | 0 | 367 | 75 | 105 | 0 | 0 | 306 | 54 | 0 | 0 | 113 | 100 | 341 | 90 | 0 | 54 | 0 | 0 | 0 | 0 |  | 726 | 0 | 380 | 0 | 66 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 100 | 42 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 81 | 60 | 186 | 0 | 378 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 57 | 0 | 0 |  | 7809 | 3553 | 11362 | 4530 | 726 | 1347 | 3658 | 670 | 70 | 203 | 158 | 0 | 0 | 89.5
22:00 | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 |  | 0 | 0 | 240 | 15 | 99 | 55 | 231 | 0 | 90 | 100 | 24 | 16 | 85 | 0 | 0 | 18 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 25 | 199 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 50 | 19 | 38 | 0 | 0 | 100 | 325 | 265 | 183 | 0 | 80 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 152 | 140 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 305 | 30 | 79 | 0 | 105 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 181 | 0 | 367 | 24 | 52 | 0 | 0 | 270 | 0 | 0 | 0 | 113 | 100 | 340 | 90 | 0 | 35 | 0 | 0 | 0 | 0 |  | 726 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 82 | 10 | 186 | 0 | 340 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 64 | 0 | 0 |  | 7538 | 3223 | 10761 | 4606 | 726 | 1319 | 3225 | 630 | 70 | 33 | 152 | 0 | 0 | 89.5
23:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 0 |  | 0 | 0 | 235 | 0 | 30 | 30 | 227 | 0 | 157 | 40 | 0 | 0 | 83 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 38 | 0 | 0 | 100 | 325 | 275 | 192 | 0 | 85 | 23 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 154 | 152 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 291 | 35 | 79 | 0 | 105 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 182 | 0 | 374 | 24 | 35 | 0 | 0 | 217 | 0 | 0 | 0 | 8 | 100 | 370 | 91 | 0 | 17 | 0 | 0 | 0 | 0 |  | 725 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 82 | 0 | 175 | 0 | 342 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 71 | 0 | 0 |  | 7094 | 3139 | 10233 | 4714 | 725 | 1337 | 2593 | 640 | 70 | 0 | 154 | 0 | 0 | 89.49
24:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 0 |  | 0 | 0 | 240 | 0 | 15 | 30 | 230 | 0 | 160 | 8 | 0 | 0 | 40 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 38 | 0 | 0 | 100 | 315 | 300 | 187 | 0 | 85 | 26 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 14 | 144 | 153 | 40 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 295 | 35 | 79 | 0 | 105 | 19 | 0 | 7 | 310 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 182 | 0 | 367 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 8 | 100 | 365 | 53 | 0 | 0 | 0 | 0 | 0 | 0 |  | 722 | 0 | 335 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 63 | 0 | 158 | 0 | 343 | 70 | 0 | 113 | 0 | 49 | 0 | 0 | 113 | 530 | 71 | 0 | 0 |  | 6862 | 2968 | 9830 | 4692 | 722 | 1337 | 2185 | 680 | 70 | 0 | 144 | 0 | 0 | 89.49
KWH | 0 | 0 | 0 | 4599000 | 7232836 | 2315681 | 0 | 0 | 0 |  | 0 | 0 | 5633745 | 862080 | 1298736 | 908956 | 5491984 | 0 | 775000 | 1446720 | 662688 | 178080 | 1443676 | 0 | 0 | 190176 | 1204560 | 782211 | 718854 | 456156 | 600000 | 705600 | 823900 | 795100 | 52140 | 0 | 0 | 1696000 | 2900000 | 0 | 161982 | 743376 | 0 | 2873724 | 0 |  | 440400 | 0 | 300243 | 36120 | 90240 | 972480 | 423168 | 531360 | 0 | 0 | 2554590 | 7913500 | 6718000 | 4555000 | 0 | 2054890 | 558000 | 1323840 | 0 | 0 | 0 | 43032 | 20266 | 436968 | 150840 | 810700 | 443110 | 3187200 | 3384200 | 934080 | 359172 | 9400 | 1022000 | 885480 | 1275600 | 0 | 3526527 | 7048000 | 787296 | 1860480 | 0 | 592320 | 432000 | 0 | 158220 | 7406500 | 334776 | 229000 | 0 | 5203853 | 0 | 0 | 4164000 | 0 | 3043008 | 99360 | 966720 | 3687840 | 0 | 8230000 | 271200 | 1031616 | 0 | 30959 | 5896364 | 448884 | 0 | 0 | 677040 | 2295360 | 6586500 | 1537920 | 283370 | 865440 | 0 | 0 | 0 | 205302 |  | 17533818 | 0 | 8964576 | 0 | 640320 | 0 | 0 | 0 | 0 | 50432 | 183375 | 0 | 590800 | 331296 | 0 | 0 | 0 | 56048 | 0 | 264376 | 201710 | 39468 | 43529 | 163200 | 14167 | 513600 | 0 | 235404 | 0 | 0 | 3665300 | 0 | 0 | 0 | 0 | 4085955 | 0 | 1694055 | 182400 | 4675164 | 0 | 9043182 | 974400 | 0 | 2109600 | 0 | 1659840 | 0 | 29112 | 1683456 | 11469900 | 1739427 | 0 | 0 |  | 156886695 | 72837910 | 229724605 | 102467285 | 17533818 | 31979272 | 56118420 | 15135200 | 1696000 | 949907 | 3187200 | 657503 | 0
Fuel Cost | 0 | 0 | 0 | 6760530 | 8028447.96 | 3056698.92 | 0 | 0 | 0 |  | 0 | 0 | 6253456.95 | 6543187.2 | 8948291.04 | 7689767.76 | 5711663.36 | 0 | 1340750 | 10893801.6 | 6043714.56 | 1752307.2 | 13310692.72 | 0 | 0 | 1728699.84 | 8793288 | 6046491.03 | 7087900.44 | 342117 | 450000 | 0 | 0 | 0 | 504193.8 | 0 | 0 | 457920 | 5249000 | 0 | 1504812.78 | 810279.84 | 0 | 4885330.8 | 0 |  | 0 | 0 | 2912357.1 | 344946 | 785088 | 7702041.6 | 533191.68 | 1578139.2 | 0 | 0 | 3755247.3 | 5855990 | 6718000 | 4190600 | 0 | 2363123.5 | 630540 | 1853376 | 0 | 0 | 0 | 434623.2 | 193540.3 | 554949.36 | 113130 | 1418725 | 332332.5 | 23904000 | 3587252 | 8481446.4 | 456148.44 | 149836 | 1676080 | 1416768 | 2270568 | 0 | 4020240.78 | 7329920 | 1550973.12 | 3553516.8 | 0 | 1024713.6 | 946080 | 0 | 322768.8 | 7480565 | 251082 | 174040 | 0 | 39341128.68 | 0 | 0 | 21652800 | 0 | 29943198.72 | 1161518.4 | 7878768 | 40013064 | 0 | 7653900 | 2473344 | 9748771.2 | 0 | 0 | 44576511.84 | 3909779.64 | 0 | 0 | 5802232.8 | 15287097.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100994791.68 | 0 | 9412804.8 | 0 | 5032915.2 | 0 | 0 | 0 | 0 | 528527.36 | 1910767.5 | 0 | 915740 | 3233448.96 | 0 | 0 | 0 | 551512.32 | 0 | 2339727.6 | 1553167 | 533607.36 | 421796.01 | 1581408 | 137419.9 | 986112 | 0 | 178200.828 | 0 | 0 | 19865926 | 0 | 0 | 0 | 0 | 5393460.6 | 0 | 2541082.5 | 3102624 | 5469941.88 | 0 | 8952750.18 | 10172736 | 0 | 20020104 | 0 | 12880358.4 | 0 | 321687.6 | 12440739.84 | 50352861 | 0 | 0 | 0 |  | 464501397.36 | 281826218.518 | 746327615.878 | 106565313.568 | 100994791.68 | 37531558.18 | 395943932.76 | 70218787 | 457920 | 9078270.69 | 23904000 | 1633042 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 0 |  | 0 | 0 | 230 | 65 | 64 | 45 | 222 | 0 | 0 | 100 | 32 | 0 | 73 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 25 | 0 | 0 | 0 | 0 | 31 | 19 | 2 | 0 | 0 | 100 | 340 | 295 | 202 | 0 | 91 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 14 | 132 | 149 | 66 | 17 | 2 | 43 | 42 | 53 | 0 | 130 | 310 | 34 | 78 | 0 | 0 | 19 | 0 | 7 | 305 | 16 | 0 | 0 | 227 | 0 | 0 | 184 | 0 | 132 | 17 | 20 | 150 | 0 | 321 | 0 | 52 | 0 | 5 | 305 | 0 | 0 | 0 | 0 | 100 | 251 | 77 | 41 | 54 | 0 | 0 | 0 | 32 |  | 726 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 78 | 0 | 195 | 0 | 414 | 54 | 0 | 113 | 0 | 70 | 0 | 3 | 70 | 430 | 73 | 0 | 0 |  | 9693 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 300 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 100 | 98 | 55 | 221 | 0 | 87 | 100 | 102 | 48 | 83 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 0 | 70 | 120 | 0 | 25 | 36 | 0 | 120 | 0 | 0 | 24 | 0 | 87 | 15 | 55 | 50 | 19 | 23 | 0 | 0 | 100 | 325 | 270 | 183 | 0 | 80 | 23 | 56 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 15 | 166 | 140 | 81 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 308 | 20 | 79 | 0 | 87 | 19 | 0 | 7 | 275 | 16 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 151 | 0 | 100 | 180 | 0 | 367 | 75 | 95 | 0 | 0 | 306 | 54 | 0 | 0 | 113 | 100 | 340 | 90 | 0 | 144 | 0 | 0 | 0 | 0 |  | 725 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 13 | 40 | 0 | 29 | 64 | 0 | 0 | 0 | 15 | 0 | 100 | 42 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 84 | 60 | 185 | 0 | 385 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 520 | 64 | 0 | 0 |  | 11615 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 100 | 100 | 55 | 220 | 0 | 115 | 100 | 100 | 149 | 87 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 120 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 21 | 40 | 0 | 0 | 100 | 360 | 300 | 225 | 0 | 90 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 168 | 160 | 81 | 22 | 0 | 44 | 42 | 51 | 0 | 163 | 310 | 35 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 366 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 340 | 104 | 0 | 144 | 116 | 0 | 0 |  |  | 738 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 44 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 72 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 100 | 100 | 55 | 220 | 0 | 115 | 100 | 100 | 149 | 87 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 120 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 21 | 25 | 0 | 0 | 100 | 360 | 300 | 225 | 0 | 90 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 160 | 81 | 22 | 1.6 | 44 | 42 | 51 | 0 | 163 | 310 | 35 | 80 | 0 | 105 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 366 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 340 | 104 | 50 | 144 | 116 | 0 | 0 | 30 |  | 738 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 44 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 72 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 300 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 222 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 33 |  | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 202 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 100 | 270 | 270 | 180 | 0 | 75 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 33 | 10 | 102 | 157 | 5 | 17 | 1 | 44 | 42 | 50 | 0 | 130 | 300 | 35 | 79 | 0 | 105 | 19 | 0 | 7 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 200 | 0 | 79 | 4 | 0 | 65 | 0 | 339 | 0 | 52 | 0 | 2 | 69 | 0 | 0 | 0 | 0 | 20 | 338 | 0 | 12 | 0 | 0 | 0 | 0 | 6 | 0 | 724 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 62 | 0 | 149 | 0 | 255 | 0 | 0 | 5 | 0 | 65 | 0 | 1 | 0 | 400 | 72 | 0 | 0 | 0
199
| Minimum Generation |  | 7685 | 5:00
| Highest Generation |  | 11615 | 19:30
| Day Peak Generation |  | 9693 | 12:00
| Evening Peak Generation |  | 11615 | 19:30
| HVDC Max Flow |  | 726 | 2:00
| HVDC EvPeak Flow |  | 725 | 19:30
| Load factor L.F |  | 82.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9693 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7804 | MW
Evening Peak Generation : |  | 11615 | MW Hour : | 19:30 | Available Max Generation : |  | 15147 | MW
E.P. Demand (at gen end) : |  | 11615 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10900 | MW
Maximum Generation : |  | 11615 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4247 | MW
Total Gen. (MKWH) : |  | 229.7246 | System Load Factor : | 82.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -30 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-12
Actual : | 89.46 | Ft.(MSL) , | Rule curve : | 91.24 | Ft.( MSL )
Gas Consumed : | Total = | 1103.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144096871.748
: |  | Coal : | 70218787 | Oil : | 405022203.45 | Total : | 619337862.198
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3855.4009 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1310.3788 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1173.9364 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1060.7081 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 958.57 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 773.5303 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 433.3835 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 199.1861 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 596.5809 |  |  | 0 | 0%
Total | 0 |  | 10361.6749 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-100, 71 MW
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
6) Sirajganj #1 CCPP
7) Haripur 412 MW
8) Meghnaghat 450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Feni-Baroierhat 132 kV Ckt-1 was shut down at 08:45 for D/W.
b) Ishurdi 230/132 kV T-01 transformer was under shut down from 08:45 to 15:16 for C/M.
c) Bogura132/33 kV T-2 transformer was under shut down from 08:10 to 10:28 for C/M.
d) Kulsi-Abul Khair 132 kV Ckt was under shut down from 08:31 to 15:56 for C/M.
e) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 10:13 to 18:23 for D/W.
f) Kamrangirchar 132/33 kV T-2 transformer was under shut down from 09:27 to 13:47 for A/M.
g) Kamrangirchar 132 kV main Bus was under shut down from 09:42 to 13:47 for A/M.
h) Baroirhat-Hathazari 132 kV Ckt-1 was under shut down from 13:13 to 16:47 for D/W.
i) Benapole 132/33 kV T-1 transformer was under shut down from 11:51 to 12:06 for C/M.
j) Bagerhat-Mongla 132 kV Ckt-1 was under shut down from 13:12 to 14:11 for C/M.
k) Silalbaha 225 MW CCPP GT was synchronized at 13:33.
l) Sylhet 225 MW CCPP GT was synchronized at 15:34.
m) Sylhet 225 MW CCPP ST was synchronized at 17:30.
n) Silalbaha 225 MW CCPP ST was synchronized at 20:04.
o) Kallyanpur-Aminbazar 132 kV Ckt-1 was shut down at 07:10(12/03/2021) for C/M.
p) Sikalbaha-Shahmirpur 132 kV Ckt-2 was shut down at 07:22(12/03/2021) for A/M.
q) Lalbag-Hasnabad 132 kV Ckt-2 was shut down at 07:27(12/03/2021) for A/M.
r) Tongi-Kabirpur 132 kV Ckt-1 & 2 tripped at 05:42(12-03-2021) showing Dist.Z1,Z3 3-phase relays |  |  |  |  | About 300 MW power interruption occurred under Kabirpur,Tongi S/S
at Tongi end and were switched on at 05:55,05:56(12-03-2021) respectively. |  |  |  |  | areas from 05:42 to 05:55(12-03-2021).
s) Rajendrapur 132/33 kV T1 & T2 transformers tripped at 05:42(12-03-2021) showing Dist.Z1 relay |  |  |  |  | About 76 MW power interruption occurred under Rajendrapur S/S
& bus protection trip and was switched on at 07:3012-03-2021). |  |  |  |  | areas from 05:42 to 07:30(12-03-2021).
t) Sylhet 132/33 kV T2 transformer & 33 kV Bus were shut down at 06:57(12-02-2021) due to red hot |  |  |  |  | About 43 MW power interruption occurred under Sylhet S/S
maintenance at LT Bus DS and was switched on at 08:19(12-03-2021). |  |  |  |  | areas from 06:57 to 08:19(12-03-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4599000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7232836 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 2315681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Dirty fuel(Gas)
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Dirty fuel(Gas)
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Dirty fuel(Gas)
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 862080
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 235 | 5633745 | Dirty fuel(Gas)
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 98 | 1298736
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 908956
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 83 | 1443676 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 456156
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 87 | 775000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1446720
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 5491984 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 662688
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 49 | 190176
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1204560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 178080 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 782211
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 718854
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1305600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 823900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 795100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 52140 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5203853
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 151 | 3043008
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 95 | 1031616 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1537920 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 865440 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 205302
| Dhaka area Total |  |  |  | 5972 | 2884 | 51065018
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 161982
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 99360
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 972480
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1696000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 36 | 743376 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2873724
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 87 | 300243 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 15 | 36120 | High Voltage.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 966720
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 423168
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 531360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 55 | 90240 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30959
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 5896364
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 448884
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2295360
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 1180 | 20466340
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2554590
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4555000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7913500
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6718000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 558000 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1323840 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 43032 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2054890 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 3687840
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436968
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 150840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 166 | 3187200
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 810700
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 20266 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 443110
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 677040
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 0 | On Test
| Cumilla Area Total |  |  |  | 2980 | 1587 | 35134816
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 3384200 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 359172 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 81 | 934080 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9400
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 4164000 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 75 | 271200 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 283370
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 440400
| Mymensingh Area Total |  |  |  | 709 | 530 | 9845822
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1022000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 885480 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3526527
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 308 | 7048000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1275600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 229000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 787296 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1860480
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 87 | 592320 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 432000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 334776 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7406500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8230000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 158220 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 6586500 | On Test
| Sylhet Area Total |  |  |  | 2371 | 1831 | 40374699
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 725 | 17533818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 640320 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 13 | 50432 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8964576 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 183375
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 60 | 182400 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 974400 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1408 | 28529321
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 331296 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 590800
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 84 | 1694055 | Machine problem
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 11469900 | High Voltage.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 64 | 1739427 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 761 | 15825478
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 15 | 56048 | Low demand
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 201710 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 39468 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 43529 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 151 | 4085955 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4675164 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 385 | 9043182 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 14167 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 513600
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235404 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 163200
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 264376
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2109600
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1683456 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1171 | 23128859
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3665300 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1659840
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29112
| Rangpur Area Total |  |  |  | 605 | 263 | 5354252
| Total |  |  |  | 21312 | 11615 | 229724605
| Eastern Grid Total |  |  |  | 14414 | 8012 | 156886695
| Western Grid Total |  |  |  | 6898 | 3603 | 72837910
| National Grid Total |  |  |  | 21312 | 11615 | 229724605
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-11
(a) ENTIRE EASTERN GRID : |  | 7587 | MW | (b) ENTIRE WESTERN GRID : |  | 3442 | MW
i) Dhaka area |  | 4074 | MW | i) Khulna area |  | 1388 | MW
ii) Chittagong area |  | 1202 | MW | ii) Rajshahi area |  | 1107 | MW
iii) Comilla area |  | 1003 | MW | iii) Barisal area |  | 290 | MW
iv) Mymensingh area |  | 917 | MW | iv) Rangpur area |  | 657 | MW
v) Sylhet area |  | 391 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11029 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 18:30 | Netrokona | 121 | 20:00 | Jessore | 119 | 19:00
Munsiganj | 116 | 20:00 | Jamalpur | 135 | 19:00 | Benapol | 72 | 19:30
Sonargaon | 71 | 12:00 | Sherpur | 124 | 19:00 | Jhenida | 106 | 19:00
Shyampur | 188 | 0:00 | Srimongal | 41 | 19:30 | Bottail | 112 | 19:30
Bhulta | 200 | 0:00 | Shahjibazar | 105 | 21:00 | G.K Project | 49 | 19:00
Madanganj | 58 | 16:00 | Fenchuganj | 35 | 18:30 | Faridpur | 164 | 19:00
Shitalakhya | 123 | 12:00 | Kulawara | 34 | 18:30 | Madaripur | 85 | 21:00
Rahim steel | 30 | 10:00 | Sylhet | 85 | 19:00 | Sariatpur | 54 | 19:30
Matuail | 84 | 11:00 | Chatak | 24 | 19:00 | Gopalganj | 77 | 19:00
Ghorasal | 78 | 18:30 | Sunamganj | 32 | 21:00 | Bagerhat | 93 | 19:00
Narsingdi | 154 | 19:30 | Biani Bazar | 47 | 19:00 | Mongla | 36 | 10:00
Haripur (SBU) | 115 | 20:00 | Comilla (S) | 176 | 18:30 | Satkhira | 94 | 21:00
Sreenagar |  |  | Comilla(N) | 95 | 19:00 | Gallamari | 30 | 20:00
Ullon | 72 | 14:00 | Chandpur | 56 | 20:00 | Magura | 48 | 19:30
Hasnabad | 98 | 19:30 | Feni | 105 | 19:00 | Norail | 31 | 19:00
Magbazar | 85 | 14:00 | Chowmuhani | 164 | 19:30 | Chuadanga | 82 | 19:30
Maniknagar | 72 | 20:00 | Ashuganj | 55 | 13:00 | Borguna | 12 | 18:30
Bangabhaban | 22 | 12:00 | Daudkandi | 126 | 20:00 | Barisal(N) | 40 | 19:00
Narinda | 72 | 12:00 | B.Baria | 148 | 21:00 | Barisal (S) | 92 | 19:00
Dhanmondi | 172 | 13:00 | Ramganj | 80 | 19:00 | Patuakhali | 90 | 21:00
Lalbag | 97 | 13:00 | Chaddagram | 36 | 19:30 | Bhandaria | 43 | 19:30
Madartek | 64 | 21:00 | PHP | 8 | 5:00 | Borhan Uddin | 33 | 21:00
Dhaka University | 45 | 15:00 | Kochua | 56 | 18:30 | Ishurdi | 52 | 19:00
Aftabnagar | 8 | 11:00 | Madunaghat | 66 | 18:30 | Ruppur Paromanobik | 3 | 10:00
Fatullah | 60 | 10:00 | Hathazari | 76 | 18:30 | Natore | 107 | 19:00
Nawabganj | 41 | 19:30 | Khulshi | 187 | 14:00 | Bogra | 135 | 19:00
Mirpur | 100 | 18:30 | Halishahar | 112 | 11:00 | Noagaon | 85 | 18:30
Kalyanpur | 72 | 18:30 | Baraulia | 156 | 14:00 | Rajshahi | 128 | 20:00
Gulshan | 120 | 13:00 | Sikalbaha | 27 | 18:30 | Rajshahi New | 17 | 19:00
Uttara | 78 | 18:30 | Dohazari | 72 | 20:00 | C.Nawabganj | 72 | 20:00
Uttara New | 25 | 18:30 | Cox'sbazar | 98 | 19:30 | Amnura | 47 | 19:00
Kamrangirchar | 86 | 18:30 | Chandraghona | 28 | 19:00 | Pabna | 86 | 19:00
Savar | 191 | 15:00 | Kaptai |  |  | Shahjadpur | 88 | 19:30
Bhasantec | 141 | 18:30 | A. Khaer Stl. | 8 | 3:00 | Serajganj | 86 | 19:00
Agargaon | 63 | 13:00 | Bakulia | 94 | 19:00 | Niyamatpur | 76 | 19:00
Satmosjid | 94 | 19:00 | Julda | 22 | 9:00 | Joypurhat | 54 | 20:00
Tongi | 117 | 11:00 | TK chemical | 22.9 | 19:30 | Sherpur(Bogura) | 42 | 18:00
Kabirpur | 243 | 18:30 | Modern Steel | 0 | #N/A | Mohastangor | 48 | 19:00
Basundhara | 140 | 18:30 | Shahmirpur | 28.2 | 21:00 | Bangura | 30 | 19:00
Manikganj | 70 | 19:00 | Khagrachhari | 24 | 19:30 | Rangpur | 118 | 19:00
Joydevpur | 157 | 18:30 | Matarbari | 34 | 19:00 | Lalmonirhat | 33 | 19:00
New Tongi | 91 | 10:00 | Baroiar Hat | 30 | 18:30 | Saidpur | 96 | 19:00
Korda | 211 | 15:00 | Rangamati | 10 | 18:00 | Purbasadipur | 86 | 19:00
Dhamrai | 78 | 8:00 | Abul Khair 230 | 4 | 13:00 | Thakurgaon | 68 | 19:00
Rajendrapur | 106 | 19:00 | BSRM | 153 | 0:00 | Palashbari | 106 | 19:00
Valuka | 124 | 9:00 | GPH Ispat | 79 | 0:00 | Barapukuria | 45 | 19:00
Tangail | 192 | 19:00 | Goalpara | 14 | 13:00 | Panchagar | 44 | 18:30
Mymensing | 164 | 21:00 | Central s/s | 102 | 19:00 | Joldhaka | 37 | 20:00
Kishorganj | 122 | 21:00 | Noapara | 33 | 19:00 | Kurigram | 45 | 20:00
[6 empty] | Mitha Pukur | 13 | 0.79167
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 20:00 | 398 | 15:00 | Kaliakoir | 391 | 0.29167 | 374 | 0.45833
| Bheramara | 402 | 19:00 | 396 | 19:00 | Bhulta | 385 | 0.875 | 365 | 0.375
| Ashuganj(N) | 389 | 19:30 | 374 | 10:00 | Gopalganj | 408 | 0.625 | 386 | 0.79167
| Payra | 409 | 6:00 | 396 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 15:00 | Hathazari | 227 | 13:00 | 220 | 15:00
| Ishurdi | 235 | 5:00 | 227 | 12:00 | Megnaghat | 232 | 8:00 | 220 | 9:00
| Ashuganj | 235 | 18:00 | 227 | 9:00 | Fenchuganj | 240 | 19:00 | 235 | 13:00
| Serajganj | 232 | 1:00 | 228 | 12:00 | Siddhirganj | 229 | 21:00 | 218 | 9:00
| Baghabari | 236 | 3:00 | 228 | 11:00 | Maniknagar | 228 | 21:00 | 215 | 10:00
| Barapukuria | 237 | 1:00 | 230 | 18:30 | Agargaon | 227 | 7:00 | 213 | 12:00
| Bogra | 232 | 3:00 | 223 | 9:00 | Barisal | 250 | 13:00 | 240 | 18:30
| Rajshahi | 235 | 5:00 | 222 | 12:00 | Bhola 225 MW | 253 | 18:00 | 243 | 1:00
| Khulna South | 233 | 21:00 | 216 | 12:00 | AKSML | 226 | 13:00 | 218 | 12:00
| Rampura | 229 | 20:00 | 220 | 9:00 | BSRM | 227 | 19:30 | 218 | 4:00
| Haripur | 228 | 21:00 | 217 | 10:00 | Bibiyana | 241 | 19:30 | 236 | 8:00
| Hasnabad | 226 | 19:30 | 214 | 9:00 | Bhulta | 230 | 19:00 | 219 | 9:00
| Shyampur | 229 | 6:00 | 220 | 4:00 | Ashuganj (S) | 234 | 20:00 | 226 | 16:00
| Aminbazar | 228 | 1:00 | 217 | 2:00 | Kaliakoir | 229 | 21:00 | 220 | 2:00
| Tongi | 223 | 21:00 | 210 | 11:00 | GPH | 226 | 1:00 | 219 | 16:00
| Comilla (N) | 228 | 19:30 | 220 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 19:30 | 125 | 9:00 | Madanhat | 136 | 0.16667 | 131 | 0.625
| Munsiganj | 136 | 19:30 | 125 | 9:00 | Hathazari | 135 | 0.041667 | 131 | 0.5
| Sonargaon | 134 | 19:30 | 125 | 9:00 | Khulshi | 133 | 0.79167 | 129 | 0.20833
| Shyampur | 133 | 20:00 | 124 | 10:00 | Halishahar | 136 | 0.8125 | 129 | 0.125
| Bhulta | 126 | 18:30 | 118 | 9:00 | Baraulia | 135 | 0.54167 | 129 | 0.20833
| Madanganj | 135 | 20:00 | 125 | 10:00 | Sikalbaha | 137 | 0.8125 | 130 | 0.125
| Shitalakhya | 136 | 19:30 | 123 | 2:00 | Dohazari | 133 | 0.79167 | 127 | 0.20833
| Rahim steal | 133 | 19:30 | 124 | 10:00 | Cox'sbazar | 127 | 0.29167 | 120 | 0.66667
| Matuail | 133 | 19:30 | 125 | 9:00 | Chandraghona | 134 | 0.54167 | 130 | 0.125
| Ghorasal | 137 | 18:00 | 133 | 15:00 | Kaptai
| Narsinghdi | 131 | 8:00 | 118 | 11:00 | A. Khaer Stl. | 134 | 0.041667 | 129 | 0.66667
| Haripur (SBU) | 133 | 22:00 | 125 | 9:00 | Bakulia | 135 | 0.041667 | 130 | 0.625
| Sreenagar |  |  |  |  | Julda | 136 | 0.77083 | 131 | 0.125
| Ullon | 130 | 6:00 | 121 | 12:00 | TK Chemical | 136 | 0.79167 | 131 | 0.5
| Hasnabad | 133 | 19:00 | 125 | 4:00 | Modern Steel
| Magbazar | 130 | 2:00 | 121 | 12:00 | Shahmirpur | 138 | 0.083333 | 131 | 0.375
| Maniknagar | 132 | 19:30 | 126 | 15:00 | Khagrachhari | 134 | 0.8125 | 129 | 0.16667
| Bangabhaban | 132 | 19:30 | 126 | 15:00 | Matarbari | 129 | 0.54167 | 121 | 0
| Narinda | 132 | 19:30 | 126 | 15:00 | Baroiar Hat | 133 | 0.041667 | 128 | 0.625
| Dhanmondi | 130 | 6:00 | 121 | 12:00 | Rangamati | 134 | 0.8125 | 129 | 0.5
| Lalbag | 131 | 19:30 | 122 | 2:00 | Goalpara S/S | 136 | 21:00 | 125 | 12:00
| Madartek | 129 | 20:00 | 122 | 12:00 | Khulna Central S/S | 136 | 21:00 | 124 | 12:00
| Dhaka University | 129 | 6:00 | 122 | 11:00 | Noapara | 133 | 20:00 | 122 | 0.5
| Aftabnagar | 130 | 19:00 | 122 | 12:00 | Jessore | 129 | 5:00 | 118 | 0.5
| Fatullah | 133 | 19:30 | 125 | 2:00 | Benapol | 129 | 5:00 | 117 | 0.5
| Nawabganj | 131 | 19:30 | 124 | 9:00 | Jhenida | 129 | 6:00 | 115 | 0.77083
| Mirpur | 132 | 19:30 | 123 | 12:00 | Bottail | 134 | 0.20833 | 125 | 0.79167
| Kalyanpur | 132 | 19:00 | 124 | 9:00 | G.K Project | 140 | 5:00 | 134 | 0.5
| Gulshan | 128 | 7:00 | 121 | 12:00 | Faridpur | 138 | 0.29167 | 128 | 0.79167
| Uttara | 135 | 19:30 | 127 | 12:00 | Madaripur | 140 | 0.29167 | 134 | 0.041667
| Uttara New | 131 | 19:00 | 121 | 9:00 | Shariyatpur S/S | 140 | 0.25 | 130 | 0.79167
| Kamrangirchar | 130 | 20:00 | 120 | 12:00 | Gopalganj | 145 | 0.25 | 134 | 0.77083
| Savar | 132 | 19:30 | 123 | 12:00 | Bagerhat | 134 | 6:00 | 122 | 0.45833
| Bhasantec | 131 | 21:00 | 124 | 12:00 | Mongla | 134 | 0.875 | 121 | 0.5
| Agargaon | 132 | 19:30 | 125 | 12:00 | Satkhira | 134 | 5:00 | 124 | 0.5
| Satmosjid | 132 | 19:30 | 125 | 12:00 | Gallamari | 134 | 21:00 | 126 | 0.5
| Tongi | 138 | 96:00 | 130 | 11:00 | Magura | 126 | 1:00 | 113 | 18:30
| Kabirpur | 136 | 1:00 | 126 | 15:00 | Narail | 127 | 0.125 | 113 | 0.79167
| Basundhara | 136 | 19:00 | 127 | 12:00 | Chuadanga | 126 | 5:00 | 106 | 0.79167
| Manikganj | 139 | 21:00 | 130 | 12:00 | Borguna | 139 | 0.25 | 133 | 0.77083
| Joydevpur | 137 | 19:30 | 128 | 12:00 | Barisal(N) | 140 | 5:00 | 134 | 0.77083
| New Tongi | 136 | 20:00 | 127 | 12:00 | Barisal (S) | 139 | 6:00 | 132 | 0.77083
| Kodda | 134 | 19:00 | 124 | 9:00 | Patuakhali(S) | 139 | 5:00 | 129 | 19:00
| Dhamrai | 136 | 1:00 | 130 | 15:00 | Bhandaria | 138 | 3:.00 | 132 | 0.77083
| Rajendrapur | 133 | 19:30 | 121 | 15:00 | Ishurdi | 138 | 0.25 | 132 | 0.375
| Valuka | 125 | 23:00 | 110 | 15:00 | Ruppur Paromanobik | 136 | 0.125 | 132 | 0.5
| Tangail | 133 | 10:00 | 124 | 18:30 | Natore | 136 | 2:00 | 129 | 12:00
| Mymensing | 128 | 2:00 | 116 | 15:00 | Bogra | 139 | 1:00 | 132 | 12:00
| Kishorganj | 129 | 9:00 | 118 | 18:30 | Noagaon | 133 | 4:00 | 126 | 9:00
| Netrokona | 126 | 9:00 | 109 | 18:30 | Rajshahi | 135 | 19:00 | 127 | 9:00
| Jamalpur | 140 | 21:00 | 122 | 15:00 | Rajshahi New | 135 | 19:00 | 127 | 12:00
| Sherpur | 137 | 10:00 | 120 | 15:00 | C.Nawabganj | 133 | 19:00 | 123 | 12:00
| Srimongal | 137 | 6:00 | 132 | 15:00 | Amnura | 134 | 19:00 | 123 | 11:00
| Shahjibazar | 134 | 6:00 | 129 | 15:00 | Pabna | 137 | 5:00 | 130 | 12:00
| Fenchuganj | 137 | 7:00 | 132 | 15:00 | Shahjadpur | 142 | 3:00 | 136 | 6:00
| Khulawara | 136 | 4:00 | 132 | 15:00 | Serajganj | 134 | 2:00 | 129 | 12:00
| Sylhet | 134 | 5:00 | 129 | 16:00 | Niyamatpur | 132 | 8:00 | 122 | 12:00
| Chatak | 133 | 7:00 | 127 | 13:00 | Joypurhat | 134 | 5:00 | 125 | 8:00
| Sunamganj | 133 | 4:00 | 128 | 13:00 | Sherpur(Bogura) | 137 | 1:00 | 131 | 8:00
| Biani Bazar | 134 | 6:00 | 127 | 15:00 | Mohastangor | 137 | 1:00 | 130 | 9:00
| Comilla(s) | 131 | 7:00 | 122 | 18:30 | Bangura | 136 | 1:00 | 132 | 12:00
| Comilla(n) | 138 | 19:00 | 132 | 15:00 | Rangpur | 136 | 1:00 | 127 | 18:30
| Chandpur | 141 | 1:00 | 135 | 12:00 | Lalmonirhat | 136 | 2:00 | 125 | 18:30
| Feni | 132 | 6:00 | 126 | 16:00 | Saidpur | 133 | 3:00 | 123 | 19:00
| Chowmuhani | 133 | 1:00 | 126 | 15:00 | Purbasadipur | 134 | 1:00 | 122 | 18:00
| Ashuganj | 135 | 9:00 | 131 | 18:30 | Thakurgaon | 134 | 2:00 | 120 | 18:30
| Daudkandi | 132 | 18:00 | 126 | 15:00 | Palashbari | 135 | 1:0 | 126 | 9:00
| B.Baria | 131 | 13:00 | 127 | 21:00 | Barapukuria | 137 | 1:00 | 130 | 18:30

## L-Curve
Date | 2021-03-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 70 | 6862 | 2968 | 9830 |  |  |  | QF-LDC-11
0:30 | 210 | 6423 | 2891.5 | 9314.5 | Date: | 2021-03-11
1:00 | 350 | 5984 | 2815 | 8799
1:30 | 415 | 5794.5 | 2785.5 | 8580
2:00 | 480 | 5605 | 2756 | 8361
2:30 | 500 | 5503.5 | 2739 | 8242.5 | [5 empty] | Gen. at Eve. Peak | 11615 | 11615 MW (19:30 )
3:00 | 520 | 5402 | 2722 | 8124 | [6 empty] | 19:30
3:30 | 500 | 5295 | 2707 | 8002 | [5 empty] | Gen. at Day Peak | 9693 | 9693 MW (12:00 )
4:00 | 480 | 5188 | 2692 | 7880 | [6 empty] | 12:00
4:30 | 425 | 5161.5 | 2621 | 7782.5 | [5 empty] | Highest Generation | 11615
5:00 | 370 | 5135 | 2550 | 7685 | [6 empty] | 19:30
5:30 | 310 | 5161.5 | 2530 | 7691.5
6:00 | 250 | 5188 | 2510 | 7698
6:30 | 155 | 5301.5 | 2457.5 | 7759
7:00 | 60 | 5415 | 2405 | 7820
7:30 | 125 | 5524.5 | 2491.5 | 8016
8:00 | 190 | 5634 | 2578 | 8212
8:30 | 255 | 5779.5 | 2674.5 | 8454
9:00 | 320 | 5925 | 2771 | 8696
9:30 | 367.5 | 6019.5 | 2818.5 | 8838
10:00 | 415 | 6114 | 2866 | 8980
10:30 | 362.5 | 6264.5 | 2869 | 9133.5
11:00 | 310 | 6415 | 2872 | 9287
11:30 | 304 | 6535 | 2955 | 9490
12:00 | 298 | 6655 | 3038 | 9693
12:30 | 269 | 6754 | 3077.5 | 9831.5
13:00 | 240 | 6853 | 3117 | 9970
13:30 | 260 | 6855.5 | 3102 | 9957.5
14:00 | 280 | 6858 | 3087 | 9945
14:30 | 320 | 6924.5 | 3103 | 10027.5
15:00 | 360 | 6991 | 3119 | 10110
15:30 | 345 | 6968.5 | 3024 | 9992.5
16:00 | 330 | 6946 | 2929 | 9875
16:30 | 265 | 6896 | 2836 | 9732
17:00 | 200 | 6846 | 2743 | 9589
17:30 | 160 | 6958.5 | 2774 | 9732.5
18:00 | 120 | 7071 | 2805 | 9876
18:30 | 90 | 7472.5 | 3237.5 | 10710
19:00 | 60 | 7874 | 3670 | 11544
19:30 | 30 | 8012 | 3603 | 11615
20:00 | 10 | 7839 | 3614 | 11453 |  |  |  | Executive Engineer
20:30 | 7.5 | 7824 | 3583.5 | 11407.5 |  |  |  | Network Operation Division
21:00 | 5 | 7809 | 3553 | 11362
21:30 | 12.5 | 7673.5 | 3388 | 11061.5
22:00 | 20 | 7538 | 3223 | 10761 |  |  |  |  | Page 6 of 7
22:30 | 55 | 7316 | 3181 | 10497
23:00 | 90 | 7094 | 3139 | 10233
23:30 | 80 | 6978 | 3053.5 | 10031.5
24:00 | 70 | 6862 | 2968 | 9830
11615 MW (19:30 )
9693 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-11 |  | Energy | 229724605
[11 empty] | 2021-03-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4692 | 722 | 1337 | 2593 | 680 | 70 | 0 | 0 | 144 | 0
0:30 | 4352 | 723.5 | 1321.5 | 2238.5 | 675 | 70 | 4 | 0 | 134 | 0 | Date: | 2021-03-11
1:00 | 4012 | 725 | 1306 | 1884 | 670 | 70 | 8 | 0 | 124 | 0
1:30 | 4082 | 725.5 | 1322 | 1599.5 | 650 | 70 | 9 | 0 | 122 | 0 | [7 empty] | Total Energy | 229.7246 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4152 | 726 | 1338 | 1315 | 630 | 70 | 10 | 0 | 120 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4198.5 | 726 | 1340 | 1149 | 630 | 70 | 11 | 0 | 118 | 0 | [7 empty] | Energy Requirement | 229.7246
3:00 | 4245 | 726 | 1342 | 983 | 630 | 70 | 12 | 0 | 116 | 0
3:30 | 4228.5 | 726 | 1352.5 | 887 | 610 | 70 | 13 | 0 | 115 | 0 | [6 empty] | Shortage
4:00 | 4212 | 726 | 1363 | 791 | 590 | 70 | 14 | 0 | 114 | 0
4:30 | 4208.5 | 726 | 1307 | 792 | 555 | 70 | 13 | 0 | 111 | 0
5:00 | 4205 | 726 | 1251 | 793 | 520 | 70 | 12 | 0 | 108 | 0
5:30 | 4144.5 | 726 | 1248 | 865 | 520 | 70 | 12 | 0 | 106 | 0
6:00 | 4084 | 726 | 1245 | 937 | 520 | 70 | 12 | 0 | 104 | 0
6:30 | 4048.5 | 726 | 1244.5 | 1080.5 | 485 | 70 | 12 | 0 | 91 | 1.5 |  |  |  |  | Coal
7:00 | 4013 | 726 | 1244 | 1224 | 450 | 70 | 12 | 0 | 78 | 3
7:30 | 4050.5 | 726 | 1240.5 | 1347 | 470 | 70 | 12 | 0 | 90 | 10 |  |  |  | Oil |  |  |  | ,
8:00 | 4088 | 726 | 1237 | 1470 | 490 | 70 | 12 | 0 | 102 | 17
8:30 | 4093 | 725.5 | 1288.5 | 1607.5 | 519.5 | 70 | 12 | 0 | 104 | 34
9:00 | 4098 | 725 | 1340 | 1745 | 549 | 70 | 12 | 0 | 106 | 51
9:30 | 4058.5 | 725.5 | 1314 | 1917 | 564.5 | 70 | 11 | 0 | 111 | 66.5
10:00 | 4019 | 726 | 1288 | 2089 | 580 | 70 | 10 | 0 | 116 | 82
10:30 | 4040.5 | 726 | 1292.5 | 2209.5 | 580 | 70 | 5 | 0 | 121 | 89
11:00 | 4062 | 726 | 1297 | 2330 | 580 | 70 | 0 | 0 | 126 | 96
11:30 | 4148 | 726 | 1319.5 | 2419.5 | 580 | 70 | 0 | 0 | 129 | 98
12:00 | 4234 | 726 | 1342 | 2509 | 580 | 70 | 0 | 0 | 132 | 100
12:30 | 4174 | 726 | 1342.5 | 2692.5 | 590 | 70 | 0 | 0 | 134 | 102.5
13:00 | 4114 | 726 | 1343 | 2876 | 600 | 70 | 0 | 0 | 136 | 105
13:30 | 4114 | 726 | 1343 | 2876 | 600 | 70 | 0 | 0 | 136 | 105
14:00 | 4114 | 726 | 1343 | 2876 | 600 | 70 | 0 | 0 | 136 | 105
14:30 | 4179 | 726 | 1356 | 2874 | 605 | 70 | 0 | 0 | 144 | 86
15:00 | 4244 | 726 | 1369 | 2872 | 610 | 70 | 0 | 0 | 152 | 67
15:30 | 4227 | 726 | 1318 | 2861 | 590 | 70 | 0 | 0 | 147 | 53.5
16:00 | 4210 | 726 | 1267 | 2850 | 570 | 70 | 0 | 0 | 142 | 40
16:30 | 4231.5 | 725.5 | 1256 | 2720 | 560 | 70 | 0 | 0 | 141 | 28
17:00 | 4253 | 725 | 1245 | 2590 | 550 | 70 | 0 | 0 | 140 | 16
17:30 | 4297 | 725.5 | 1256.5 | 2630 | 535 | 70 | 63.5 | 0 | 147 | 8
18:00 | 4341 | 726 | 1268 | 2670 | 520 | 70 | 127 | 0 | 154 | 0
18:30 | 4401.5 | 726 | 1322.5 | 3178 | 585 | 70 | 266 | 0 | 161 | 0
19:00 | 4462 | 726 | 1377 | 3686 | 650 | 70 | 405 | 0 | 168 | 0
19:30 | 4460 | 725 | 1344 | 3917 | 670 | 70 | 263 | 0 | 166 | 0
20:00 | 4457 | 725 | 1350 | 3786 | 670 | 70 | 229 | 0 | 166 | 0
20:30 | 4493.5 | 725.5 | 1348.5 | 3722 | 670 | 70 | 216 | 0 | 162 | 0
21:00 | 4530 | 726 | 1347 | 3658 | 670 | 70 | 203 | 0 | 158 | 0
21:30 | 4568 | 726 | 1333 | 3441.5 | 650 | 70 | 118 | 0 | 155 | 0
22:00 | 4606 | 726 | 1319 | 3225 | 630 | 70 | 33 | 0 | 152 | 0
22:30 | 4660 | 725.5 | 1328 | 2909 | 635 | 70 | 16.5 | 0 | 153 | 0
23:00 | 4714 | 725 | 1337 | 2593 | 640 | 70 | 0 | 0 | 154 | 0
23:30 | 4703 | 723.5 | 1337 | 2593 | 660 | 70 | 0 | 0 | 149 | 0 | Max Temp. in Dhaka |  | 32.6° C
24:00 | 4692 | 722 | 1337 | 2593 | 680 | 70 | 0 | 0 | 144 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 3 | 8 | 8 | 8 | 8 |  | 23 | 25 | 25 | 25 | 25 | 8 |  | 161982
| Teknaf 20MW PP (Solartech) | [8 empty] | 9 | 13 | 14 | 17 | 16 | 14 | 11 | 6 | 2 | [9 empty] | 99360
6 | Sikalbaha 225MW CCPP (Gas) | [13 empty] | 27 | 27 | 30 | 30 | 36 |  | 36 | 36 | 36 | 93 | 199 | 203 | 203 | 743376
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2873724
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 82 |  | 102 | 87 | 68 | 51 | 17 |  |  | 300243
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 6 |  | 42 | [6 empty] | 43032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [16 empty] | 32 | 34 |  | 87 | 87 | 87 | 90 | 90 | 157 | 160 | 775000
17 | Siddhirganj 335 MW CCPP | 222 | 221 | 222 | 221 | 222 | 221 | 221 | 222 | 221 | 223 | 223 | 222 | 222 | 222 | 222 | 222 | 222 | 222 |  | 221 | 221 | 228 | 231 | 231 | 227 | 230 | 5491984
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 225 | 65 | 30 | 30 | 30 | 60 | 62 | 131 | 195 | 195 | 227 | 290 | 295 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5203853
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4599000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7232836
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 130 | 130 | 130 | 130 | 127 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2554590
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 23 |  | 23 | 23 | 23 | 26 | 26 | 23 | 26 | 558000
33 | Ashuganj 225 MW CCPP | 183 | 189 | 183 | 183 | 183 | 183 | 188 | 195 | 194 | 183 | 187 | 202 | 184 | 184 | 184 | 183 | 183 | 184 |  | 183 | 183 | 183 | 183 | 183 | 192 | 187 | 4555000
34 | Ashuganj 450 MW CCPP(South) | 295 | 295 | 295 | 260 | 260 | 260 | 260 | 285 | 280 | 265 | 270 | 295 | 265 | 265 | 270 | 270 | 270 | 270 |  | 270 | 270 | 265 | 270 | 265 | 275 | 300 | 6718000
| Ashuganj 450 MW CCPP(North) | 240 | 300 | 375 | 375 | 375 | 305 | 280 | 290 | 285 | 270 | 315 | 340 | 350 | 312 | 325 | 325 | 325 | 325 |  | 325 | 325 | 325 | 325 | 325 | 325 | 315 | 7913500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 57 | 56 | 56 | 56 | 56 | 56 | 52 | 52 | 54 | 53 | 52 | 54 | 55 |  | 56 | 56 | 55 | 56 | 56 | 56 | 55 | 1323840
36 | Chandpur 150 MW CCPP | 80 | 85 | 86 | 86 | 86 | 80 | 85 | 85 | 91 | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 88 | 90 |  | 80 | 80 | 81 | 81 | 80 | 85 | 85 | 2054890
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | [26 empty] | 0
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 144 | 154 | 148 | 156 | 157 | 156 | 156 | 156 | 155 | 152 | 152 | 149 | 117 | 117 | 116 | 120 | 136 | 138 |  | 139 | 140 | 139 | 140 | 140 | 152 | 153 | 3384200
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 21 | 39 | 42 | 41 | 48 | 37 | 28 | 16 | 6 | 0 | [8 empty] | 283370
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1022000
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 885480
46 | Shajibazar 330 MW CCPP | 308 | 307 | 309 | 307 | 305 | 305 | 307 | 306 | 307 | 310 | 309 | 310 | 307 | 309 | 307 | 308 | 309 | 309 |  | 307 | 308 | 309 | 309 | 305 | 291 | 295 | 7048000
47 | Shahjibazar GTPP Unit- 8 & 9 | 35 | 35 | 35 | 36 | 36 | 36 | 35 | 35 | 34 | 34 | 34 | 34 | 33 | 30 | 30 | 33 | 34 | 34 |  | 28 | 20 | 20 | 22 | 30 | 35 | 35 | 787296
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 76 | 73 | 76 | 81 | 78 | 79 | 79 | 79 | 75 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1860480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [15 empty] | 22 | 21 | 76 |  | 88 | 87 | 90 | 105 | 105 | 105 | 105 | 592320
51 | Sylhet 20 MW GTPP | 19 | 18 | 18 | 19 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 432000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 158220
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 |  | 5 | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 229000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1275600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 334776
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 300 | 300 | 305 | 315 | 290 | 315 | 325 | 300 | 300 | 305 | 310 | 300 | 320 | 300 | 290 | 290 |  | 300 | 275 | 260 | 280 | 280 | 290 | 310 | 7406500
| Bibiyana South 400 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 365 | 340 | 340 | 363 |  | 340 | 340 | 340 | 341 | 340 | 370 | 365 | 6586500
58 | Nababganj 55 MW PP (Southern power ) | 17 | [8 empty] | 20 | 45 | 45 | 55 | 51 | 47 | 52 | 53 | 43 |  | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 718854
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 17 | 23 | 24 | 25 | 21 | 25 | 24 | 25 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 440400
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 423168
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 456156
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 359172
63 | Impoprt (Tripura) | 124 | 120 | 116 | 114 | 108 | 104 | 78 | 102 | 106 | 116 | 126 | 132 | 136 | 148 | 152 | 142 | 140 | 154 |  | 168 | 166 | 166 | 158 | 152 | 154 | 144 | 3187200
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 35 | 38 | 38 | 38 | 38 | 11 | 4 | 3 | 3 | 2 | 7 | 4 | 2 | 4 | 5 | 5 |  | 16 | 23 | 27 | 36 | 38 | 38 | 38 | 531360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436968
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 150840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810700
68 | Cumilla 25 MW PP (Summit) | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 11 | 14 | 14 | 18 | 18 | 18 | 15 | 15 |  | 15 | 15 | 15 | 15 | 18 | 18 | 14 | 443110
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 30 | 30 | 31 | 31 | 31 |  | 26 | 30 | 30 | 30 | 31 | 31 | 31 | 705600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795100
73 | Ghorashal 108MW PP (Regent) | 62 | 63 | 86 | 96 | 99 | 102 | 105 | 105 | 105 | 105 | 105 | 108 | 107 | 106 | 105 | 104 | 104 | 104 |  | 104 | 104 | 105 | 105 | 105 | 106 | 106 | 2315681
Feni Lanka Power
| Chowmuhani 113 MW | [17 empty] | 9 |  | 71 | 113 | 113 | 113 | 113 | 8 | 8 | 677040
| Manikgonj 162MW PP(MPGL) | [9 empty] | 22 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 60 |  | 131 | 144 | 54 | 54 | 35 | 17 | 0 | 865440
77 | Siddhirganj 100 PP(Dutch Bangla) | 15 | [5 empty] | 30 | 40 | 40 | 40 | 80 | 100 | 100 | 100 | 94 | 96 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 40 | 8 | 1446720
78 | Gazipur 52 MW PP | [19 empty] | 25 | 25 | [5 empty] | 52140
79 | Kodda 150MW PP | [19 empty] | 48 | 48 | 48 | 48 | 16 |  |  | 178080
80 | Jamalpur 95 MW PP(Powerpac) | 8 | [5 empty] | 2 | 23 | 64 | 64 | 73 | 66 | 40 | 33 | 33 | 33 | 33 | 33 |  | 52 | 81 | 81 | 81 | 81 | 81 | 40 | 934080
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 7 | 16 | [5 empty] | 20266
| Gazipur 100 MW PP | [7 empty] | 5 | 35 | 45 | 52 | 52 | 70 | 52 | 57 | 70 | 70 | 70 |  | 85 | 95 | 100 | 105 | 52 | 35 | 0 | 1031616
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30959
| Jodiac Power | [12 empty] | 27 | 54 | 54 | 35 | 35 | 35 |  | 49 | 54 | 54 | 54 |  |  |  | 448884
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [5 empty] | 1 | 20 | 30 | 30 | 30 | 38 | 64 | 72 | 94 | 85 | 80 | 80 | 97 |  | 97 | 98 | 99 | 99 | 99 | 30 | 15 | 1298736
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 |  |  |  |  | 10 | 50 | 50 | 50 | 60 | 74 | 73 | 72 | 73 | 72 | 73 | 74 | 74 |  | 80 | 83 | 82 | 84 | 85 | 83 | 40 | 1443676
86 | Meghnaghat CCPP(Summit) | 230 | 225 | 230 | 225 | 230 | 225 | 230 | 230 | 225 | 225 | 230 | 230 | 230 | 230 | 255 | 277 | 255 | 235 |  | 235 | 235 | 235 | 235 | 240 | 235 | 240 | 5633745
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 41 | 65 | 93 | 82 | 75 | 75 | 75 | 75 |  | 88 | 100 | 100 | 55 | 15 |  |  | 862080
| Meghnaghat 104 MW PP (OPCL) | 35 |  |  |  |  | 15 | 53 | 53 | 53 | 54 | 68 | 77 | 91 | 91 | 91 | 90 | 91 | 90 |  | 91 | 90 | 91 | 90 | 90 | 91 | 53 | 1537920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 30 | 15 | [5 empty] | 36120
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 3 | 32 | 64 | 64 | 64 | 48 | 48 | 48 |  | 85 | 102 | 102 | 50 | 24 |  |  | 662688
95 | Patenga 50MW PP (Baraka) | 50 | 25 | 22 | 18 | 25 | 25 | 25 | 25 | 36 | 38 | 43 | 31 | 36 | 45 | 45 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 972480
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 6 |  | 50 | 55 | 31 |  |  |  |  | 90240
97 | katpotti 52 MW | [17 empty] | 1 |  | 38 | 49 | 49 | 49 | 18 |  |  | 190176
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 30 | [5 empty] | 27 | 32 | 45 | 45 | 45 | 45 | 45 | 48 | 48 | 48 | 48 | 48 |  | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 908956
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 782211
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 130 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3526527
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 9400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 45 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1204560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 120 | 120 | 120 | 120 | 120 | 129 | 193 | 194 | 200 | 192 | 184 | 192 | 192 | 154 | 193 | 170 | 170 |  | 193 | 193 | 193 | 200 | 200 | 200 | 200 | 4164000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 128 | 103 | 101 | 90 | 80 | 80 | 96 | 120 | 123 | 132 | 125 | 132 | 132 | 132 | 134 | 141 | 138 | 138 |  | 140 | 151 | 149 | 149 | 149 | 149 | 149 | 3043008
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 20 | 90 | 60 | 60 | 60 | 30 | 30 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 966720
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 150 | 81 | 81 | 86 | 130 | 132 | 150 | 150 | 150 | 150 | 150 | 150 | 145 | 152 | 147 | 135 |  | 150 | 180 | 197 | 184 | 181 | 182 | 182 | 3687840
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 322 | 322 | 323 | 323 | 322 | 323 | 322 | 322 | 322 | 322 | 322 | 321 | 321 | 367 | 368 | 368 | 367 | 367 |  | 367 | 367 | 367 | 367 | 367 | 374 | 367 | 8230000
| Jamalpur 115 MW PP (United) | [17 empty] | 2 |  | 41 | 75 | 75 | 75 | 24 | 24 |  | 271200
| Anwara 300 MW PP (United) | 306 | 212 | 125 | 87 | 87 | 156 | 156 | 161 | 210 | 250 | 306 | 305 | 306 | 306 | 306 | 306 | 306 | 306 |  | 306 | 306 | 306 | 306 | 270 | 217 | 215 | 5896364
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 90 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2295360
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | [26 empty] | 0
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 7 | 18 | 26 | 30 | 32 | 31 | 28 | 21 | 12 | 5 | [9 empty] | 205302
120 | Eastern Zone Total | 5984 | 5605 | 5402 | 5188 | 5135 | 5188 | 5415 | 5634 | 5925 | 6114 | 6415 | 6655 | 6853 | 6858 | 6991 | 6946 | 6846 | 7071 |  | 7874 | 8012 | 7839 | 7809 | 7538 | 7094 | 6862 | 156886695
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 49 | 49 | 49 | 32 | 16 | 16 |  | 66 | 66 | 66 | 66 | 66 | 66 | 32 | 640320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 17 | 17 | 17 | 17 | 54 | 70 | 70 | 70 | 35 | 35 | 35 |  | 94 | 94 | 94 | 94 | 70 | 70 | 70 | 974400
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 70 | 72 | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 72 | 72 | 73 | 71 | 72 | 71 | 70 | 71 | 71 |  | 69 | 64 | 69 | 57 | 64 | 71 | 71 | 1739427
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 60 | 64 | 64 | 64 | 64 | 48 | 16 | 331296
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 72 | 72 | 73 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 78 | 83 | 83 | 83 | 82 | 83 | 84 |  | 84 | 84 | 84 | 81 | 82 | 82 | 63 | 1694055
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 26 | 26 | 24 | 23 | 22 | 19 | 19 | 20 | 21 | 20 | 23 | 24 | 26 | 25 | 24 | 26 |  | 30 | 29 | 30 | 30 | 30 | 28 | 28 | 590800
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 15 | 60 | 60 | 60 | 10 |  |  | 182400
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 40 | 40 | 40 | 40 | 16 | 0 | 183375
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 12 |  | 19 | 13 | 13 | 4 |  |  |  | 50432
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 725 | 726 | 726 | 726 | 726 | 726 | 726 | 726 | 725 | 726 | 726 | 726 | 726 | 726 | 726 | 726 | 725 | 726 |  | 726 | 725 | 725 | 726 | 726 | 725 | 722 | 17533818
147 | Bheramara 410 MW CCPP | 325 | 360 | 370 | 370 | 370 | 350 | 365 | 380 | 380 | 355 | 355 | 400 | 355 | 355 | 355 | 350 | 350 | 320 |  | 410 | 410 | 400 | 380 | 350 | 345 | 335 | 8964576
148 | Payra 1320 MW | 520 | 480 | 480 | 440 | 370 | 370 | 300 | 340 | 400 | 430 | 430 | 430 | 450 | 460 | 460 | 420 | 400 | 370 |  | 500 | 520 | 520 | 520 | 480 | 490 | 530 | 11469900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3665300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 7 |  | 43 | 15 | [5 empty] | 56048
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 150 | 167 | 178 | 178 | 175 | 175 | 140 | 154 | 169 | 153 | 153 | 196 | 190 | 159 | 159 | 152 | 152 | 152 |  | 155 | 151 | 151 | 151 | 151 | 147 | 143 | 4085955
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 196 | 200 | 200 | 200 | 200 | 160 | 174 | 184 | 178 | 175 | 195 | 199 | 174 | 176 | 168 | 168 | 168 |  | 180 | 185 | 186 | 186 | 186 | 175 | 158 | 4675164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 357 | 397 | 370 | 398 | 333 | 313 | 336 | 337 | 420 | 411 | 417 | 414 | 399 | 397 | 419 | 344 | 324 | 343 |  | 394 | 385 | 396 | 378 | 340 | 342 | 343 | 9043182
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 513600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235404
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 30 |  | 42 | 42 | 42 | 42 | 42 | 12 |  | 201710
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 50 | [6 empty] | 39468
167 | Katakhali 50 MW Peaking PP | [17 empty] | 20 |  | 31 | [6 empty] | 43529
168 | Santahar 50 MW Peaking PP | [19 empty] | 22 | [6 empty] | 14167
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 16 |  | 52 | 52 | 52 | 52 |  |  |  | 163200
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 98 | 100 | 100 | 100 |  |  |  | 264376
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 102 | 113 | 113 | 105 | 105 | 113 | 113 | 70 | 70 |  | 99 | 113 | 113 | 113 | 113 | 113 | 113 | 2109600
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [6 empty] | 25 | 50 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 70 | 70 |  | 95 | 95 | 113 | 113 | 113 | 113 | 113 | 1683456
173 | Rangpur 20 MW GTPP | 8 | 10 | 12 | 14 | 12 | 12 | 12 | 12 | 12 | 10
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 53 | [6 empty] | 34 | 34 | 70 | 70 | 70 | 110 | 113 | 113 | 113 | 70 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 49 | 1659840
177 | Sympa Solar Power 8MW | [9 empty] | 0 | 4 | 3 | 4 | 4 | 3 | 3 | 2 | 0 | [8 empty] | 29112
178
178