## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-15 | Monday
|  | Date (day): | 2021-03-15 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14388.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15439 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-14 | 2021-03-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 300 | 300 | 300 | 65 |  | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 106 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dirty fuel(Gas)
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 344 | 332 | 300 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 450 |  | Dirty fuel(Gas)
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 245 | 240 | 250 | 250
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 48 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 72 | 85 | 86 |  | 14 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 112 | 150 | 150 | 60 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 90 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 217 | 221 | 220 | 300 | 35 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 50 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 10 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 270 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 131 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 32 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 90 | 90 | 90 |  | 104 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 0 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 1910 | 2768 | 3687 | 4048 | 1130 | 748
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 36 | 102 | 102
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 13 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 42 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 180 | 196 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 34 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 905 | 1153 | 1799 | 1834 | 400 | 98
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 120 | 120 | 100 | 120
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 182 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 275 | 360 | 360
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 265 | 300 | 300 | 60 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 25 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 52 | 55 | 55
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 85 | 90 | 90 |  | 73 | ST under maint.
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 147 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 146 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 40 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1294 | 1420 | 1871 | 2159 | 538 | 73
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 108 | 160 | 160 | 42 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 81 | 50 | 50 |  | 45 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 65 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 421 | 498 | 620.6 | 569 | 42 | 45
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 298 | 294 | 300 | 300
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 21 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 35 | 35 | 35 |  | 31 | GT-9 Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 74 | 75 | 80 | 86
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 148 | 150 | 160 |  | 71 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 0 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 390 | 331 | 400 | 400
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 0 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 300 | 283 | 340 | 340
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1844 | 1806 | 2003 | 2019 | 0 | 295
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 721 | 720 | 739 | 739
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 66 | 66 |  | 49 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 12 | 60 | 60 |  | 49 | Engine problem
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 370 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 95 | 90 | 90 |  | 15 | Engine problem
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1166 | 1286 | 1570 | 1856 | 0 | 142
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 24 | 33 | 33
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 14 | 53 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 450 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 93 | 92 | 0 | 0 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 478 | 683 | 1008 | 1008 | 0 | 194
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 151 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 182 | 162 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 330 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 18 | 18 | 18
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 84 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 888 | 1079 | 1549 | 1673 | 381 | 8
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 3 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 111 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 226 | 264 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 9132 | 10957 | 14388.6 | 15439 | 2615 | 1803
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8716.947 | 10459 | 13734.6324 | 14737.2913
A. |  | 2021-03-14 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10957 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7189 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10957 | MW
3 | Day peak Generation : |  |  | 9132 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10459 | MW
4 | Evening peak Generation : |  |  | 10957 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 216.7672 | MKWHr | By Solar | 0.76238 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 144.5979 | MKWHr |  | By Oil: | 35.1369 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.1799 | MKWHr |  | By Hydro: | 1.68 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2615 | MW | Dhaka | 3808 | 3808 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1803 | MW | Chittagong | 1221 | 1221 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4418 | MW | Khulna | 1241 | 1241 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1169.67 | MMCFD |  |  | Rajshahi | 1065 | 1065 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 156004858.8 | ii) Oil : | Taka | 236646569.73 | Comilla | 959 | 959 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 66028934 | Total | Taka | 458680362.53 | Mymensingh | 843 | 843 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.191 | MKWHr. | Sylhet | 353 | 353 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -160 | MW (E to W) at | 19:30 | hrs | Barisal | 276 | 276 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -220 | MW at | 19:00 | hrs | Rangpur | 693 | 693 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 10459 | 10459 |  | 0
B. |  | 2021-03-15 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15439 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 4039 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 225.5313 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7672 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.4073 | MKWHr. | ii) HVDC Flow at Peak Time |  | 720 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0029 | MKWHr. | iii) Maximum HVDC Flow : |  | 721 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.19 |  | (b) Today: | 88.95 |  | (c) Rule Curve: |  | 90.76
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 303 |  | 0 | 0 | 235 | 0 | 0 | 0 | 183 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 26 | 20 | 40 | 0 | 0 | 120 | 70 | 290 | 182 | 0 | 86 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 30 | 15 | 118 | 129 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 130 | 232 | 36 | 20 | 0 | 148 | 19 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 118 | 0 | 20 | 48 | 0 | 328 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 100 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 63 | 0 | 152 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 94 | 0 | 0 |  | 5527 | 2584 | 8111 | 4233 | 721 | 1567 | 786 | 599 | 70 | 17 | 118 | 0 | 0 | 89.24
2:00 | 0 | 0 | 0 | 190 | 300 | 82 | 0 | 0 | 304 |  | 0 | 0 | 230 | 0 | 0 | 0 | 182 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 12 | 20 | 40 | 0 | 0 | 120 | 160 | 290 | 181 | 0 | 86 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 30 | 15 | 116 | 148 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 130 | 234 | 36 | 10 | 0 | 148 | 18 | 0 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 103 | 0 | 0 | 17 | 0 | 331 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 50 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 43 | 0 | 149 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 91 | 0 | 0 |  | 5296 | 2495 | 7791 | 4285 | 719 | 1439 | 546 | 599 | 70 | 17 | 116 | 0 | 0 | 89.23
3:00 | 0 | 0 | 0 | 190 | 300 | 22 | 0 | 0 | 274 |  | 0 | 0 | 230 | 0 | 0 | 0 | 183 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 202 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 120 | 270 | 265 | 182 | 0 | 84 | 26 | 56 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 112 | 148 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 130 | 232 | 35 | 10 | 0 | 148 | 18 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 17 | 0 | 331 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 50 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 33 | 0 | 140 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 0 | 0 |  | 5215 | 2343 | 7558 | 4279 | 719 | 1280 | 512 | 569 | 70 | 17 | 112 | 0 | 0 | 89.22
4:00 | 0 | 0 | 0 | 190 | 300 | 22 | 0 | 0 | 273 |  | 0 | 0 | 230 | 0 | 0 | 0 | 183 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 202 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 120 | 270 | 265 | 181 | 0 | 82 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 112 | 148 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 130 | 232 | 36 | 10 | 0 | 148 | 19 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 16 | 0 | 331 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 0 | 0 |  | 5067 | 2322 | 7389 | 4184 | 719 | 1227 | 491 | 569 | 70 | 17 | 112 | 0 | 0 | 89.21
5:00 | 0 | 0 | 0 | 190 | 270 | 22 | 0 | 0 | 253 |  | 0 | 0 | 230 | 0 | 0 | 0 | 151 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 201 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 120 | 270 | 265 | 182 | 0 | 80 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 108 | 148 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 110 | 233 | 36 | 10 | 0 | 148 | 18 | 0 | 0 | 265 | 0 | 11 | 0 | 0 | 0 | 0 | 25 | 0 | 98 | 0 | 0 | 16 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 94 | 0 | 0 |  | 4917 | 2272 | 7189 | 4165 | 719 | 1132 | 479 | 499 | 70 | 17 | 108 | 0 | 0 | 89.2
6:00 | 0 | 0 | 0 | 190 | 270 | 22 | 0 | 0 | 284 |  | 0 | 0 | 230 | 0 | 0 | 0 | 152 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 202 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 0 | 20 | 36 | 0 | 0 | 120 | 270 | 265 | 182 | 0 | 80 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 106 | 163 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 110 | 235 | 36 | 10 | 0 | 148 | 18 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 25 | 0 | 85 | 0 | 0 | 16 | 0 | 364 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 94 | 0 | 0 |  | 5023 | 2293 | 7316 | 4242 | 721 | 1212 | 448 | 500 | 70 | 17 | 106 | 0 | 0 | 89.19
7:00 | 0 | 0 | 0 | 190 | 270 | 22 | 0 | 0 | 303 |  | 0 | 0 | 230 | 0 | 0 | 0 | 151 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 213 | 0 | 120 | 0 |  | 11 | 0 | 17 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 120 | 310 | 290 | 196 | 0 | 85 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 0 | 106 | 164 | 0 | 20 | 0 | 44 | 41 | 8 | 0 | 110 | 232 | 35 | 10 | 0 | 148 | 19 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 31 | 0 | 105 | 2 | 0 | 16 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 3 |  | 721 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 345 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 350 | 97 | 0 | 0 |  | 5255 | 2370 | 7625 | 4383 | 721 | 1273 | 546 | 499 | 70 | 17 | 106 | 10 | 0 | 89.18
8:00 | 0 | 0 | 0 | 190 | 270 | 81 | 0 | 0 | 353 |  | 0 | 0 | 235 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 202 | 0 | 120 | 0 |  | 15 | 0 | 17 | 0 | 0 | 4 | 20 | 12 | 0 | 0 | 120 | 320 | 265 | 182 | 0 | 86 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 104 | 163 | 8 | 18 | 1 | 44 | 42 | 8 | 0 | 110 | 234 | 36 | 10 | 0 | 148 | 18 | 0 | 0 | 310 | 16 | 11 | 0 | 12 | 0 | 0 | 150 | 0 | 116 | 6 | 0 | 16 | 0 | 366 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 30 | 270 | 0 | 4 | 0 | 0 | 0 | 0 | 13 |  | 721 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 399 | 35 | 0 | 23 | 0 | 70 | 0 | 1 | 35 | 350 | 95 | 0 | 0 |  | 5490 | 2573 | 8063 | 4348 | 721 | 1439 | 837 | 500 | 70 | 17 | 104 | 27 | 0 | 89.17
9:00 | 0 | 0 | 0 | 190 | 270 | 95 | 0 | 0 | 353 |  | 0 | 0 | 240 | 0 | 0 | 0 | 182 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 216 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 25 | 21 | 6 | 0 | 0 | 120 | 335 | 300 | 201 | 0 | 87 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 108 | 140 | 24 | 18 | 1 | 44 | 42 | 8 | 0 | 110 | 140 | 35 | 10 | 0 | 148 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 123 | 0 | 0 | 16 | 0 | 398 | 0 | 6 | 0 | 3 | 34 | 0 | 0 | 0 | 0 | 30 | 300 | 0 | 29 | 0 | 0 | 0 | 0 | 22 |  | 721 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 140 | 0 | 417 | 35 | 0 | 35 | 0 | 70 | 0 | 3 | 35 | 350 | 95 | 0 | 0 |  | 5660 | 2606 | 8266 | 4373 | 721 | 1473 | 946 | 500 | 70 | 17 | 108 | 58 | 0 | 89.16
10:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 350 |  | 0 | 0 | 235 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 25 | 20 | 6 | 0 | 0 | 120 | 360 | 275 | 189 | 0 | 86 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 15 | 108 | 119 | 24 | 20 | 2 | 44 | 42 | 8 | 0 | 130 | 146 | 35 | 67 | 0 | 149 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 132 | 15 | 0 | 16 | 0 | 366 | 0 | 17 | 0 | 4 | 155 | 0 | 0 | 0 | 0 | 77 | 300 | 0 | 39 | 0 | 0 | 0 | 0 | 29 |  | 721 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 14 | 0 | 140 | 0 | 419 | 35 | 0 | 35 | 0 | 70 | 0 | 4 | 35 | 350 | 94 | 0 | 0 |  | 5952 | 2677 | 8629 | 4427 | 721 | 1564 | 1129 | 500 | 70 | 17 | 108 | 93 | 0 | 89.15
11:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 350 |  | 0 | 0 | 245 | 0 | 0 | 10 | 222 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 120 | 0 |  | 22 | 0 | 15 | 0 | 0 | 41 | 20 | 5 | 0 | 0 | 120 | 370 | 265 | 182 | 0 | 86 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 16 | 112 | 118 | 24 | 20 | 2 | 44 | 42 | 8 | 0 | 130 | 257 | 34 | 74 | 0 | 149 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 131 | 17 | 0 | 16 | 0 | 366 | 0 | 18 | 0 | 4 | 177 | 0 | 0 | 0 | 0 | 90 | 270 | 0 | 47 | 0 | 0 | 0 | 0 | 33 |  | 721 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 15 | 0 | 154 | 0 | 404 | 35 | 0 | 35 | 0 | 70 | 0 | 6 | 35 | 350 | 93 | 0 | 0 |  | 6180 | 2702 | 8882 | 4580 | 721 | 1546 | 1229 | 500 | 70 | 15 | 112 | 109 | 0 | 89.14
12:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 344 |  | 0 | 0 | 245 | 0 | 0 | 15 | 217 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 10 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 217 | 0 | 120 | 0 |  | 22 | 0 | 15 | 0 | 0 | 50 | 18 | 3 | 0 | 0 | 120 | 360 | 315 | 203 | 0 | 86 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 12 | 124 | 104 | 24 | 20 | 2 | 43 | 42 | 21 | 0 | 130 | 298 | 34 | 74 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 131 | 18 | 0 | 17 | 0 | 390 | 0 | 32 | 0 | 4 | 180 | 0 | 0 | 0 | 0 | 90 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 14 | 0 | 182 | 0 | 419 | 35 | 0 | 35 | 0 | 70 | 0 | 6 | 35 | 350 | 93 | 0 | 0 |  | 6374 | 2758 | 9132 | 4774 | 721 | 1569 | 1280 | 500 | 70 | 15 | 124 | 79 | 0 | 89.13
13:00 | 0 | 0 | 0 | 190 | 270 | 106 | 0 | 0 | 345 |  | 0 | 0 | 240 | 0 | 0 | 15 | 220 | 0 | 155 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 10 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 7 | 0 | 0 | 120 | 310 | 295 | 185 | 0 | 78 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 14 | 134 | 105 | 27 | 20 | 2 | 43 | 42 | 50 | 0 | 163 | 297 | 34 | 80 | 0 | 150 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 48 | 0 | 0 | 200 | 0 | 128 | 17 | 20 | 32 | 0 | 366 | 0 | 64 | 0 | 4 | 214 | 0 | 0 | 0 | 0 | 90 | 269 | 2 | 47 | 0 | 0 | 0 | 0 | 35 |  | 721 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 33 | 0 | 206 | 0 | 419 | 94 | 0 | 48 | 0 | 70 | 0 | 6 | 70 | 350 | 92 | 0 | 0 |  | 6479 | 2922 | 9401 | 4656 | 721 | 1712 | 1497 | 500 | 70 | 0 | 134 | 111 | 9401 | 89.12
14:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 321 |  | 0 | 0 | 240 | 0 | 0 | 30 | 220 | 0 | 155 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 10 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 2 | 0 | 0 | 120 | 310 | 295 | 183 | 0 | 83 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 124 | 104 | 51 | 20 | 2 | 43 | 42 | 50 | 0 | 110 | 298 | 34 | 74 | 0 | 150 | 18 | 0 | 6 | 300 | 16 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 130 | 15 | 20 | 32 | 0 | 366 | 0 | 103 | 0 | 3 | 180 | 0 | 0 | 0 | 0 | 90 | 270 | 17 | 42 | 0 | 0 | 0 | 0 | 30 |  | 721 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 32 | 0 | 173 | 0 | 327 | 94 | 0 | 70 | 0 | 70 | 0 | 4 | 70 | 350 | 92 | 0 | 0 |  | 6554 | 2798 | 9352 | 4658 | 721 | 1513 | 1670 | 500 | 70 | 0 | 124 | 96 | 0 | 89.11
15:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 321 |  | 0 | 0 | 240 | 0 | 0 | 30 | 220 | 0 | 155 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 31 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 4 | 0 | 0 | 120 | 310 | 295 | 182 | 0 | 87 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 0 | 18 | 126 | 104 | 56 | 20 | 2 | 43 | 42 | 47 | 0 | 163 | 298 | 33 | 71 | 0 | 150 | 18 | 0 | 6 | 300 | 16 | 11 | 0 | 120 | 0 | 0 | 200 | 0 | 126 | 15 | 20 | 36 | 0 | 367 | 6 | 105 | 0 | 2 | 180 | 0 | 0 | 0 | 0 | 90 | 270 | 17 | 33 | 0 | 0 | 0 | 0 | 24 |  | 721 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 38 | 0 | 171 | 0 | 332 | 94 | 0 | 70 | 0 | 70 | 0 | 4 | 70 | 350 | 92 | 0 | 0 |  | 6589 | 2812 | 9401 | 4644 | 721 | 1572 | 1688 | 500 | 70 | 0 | 126 | 80 | 0 | 89.1
16:00 | 0 | 0 | 0 | 190 | 270 | 99 | 0 | 0 | 321 |  | 0 | 0 | 235 | 0 | 0 | 30 | 219 | 0 | 155 | 1 | 0 | 0 | 30 | 0 | 0 | 0 | 54 | 17 | 0 | 22 | 25 | 30 | 25 | 32 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 120 | 0 |  | 20 | 0 | 0 | 0 | 0 | 50 | 21 | 3 | 0 | 0 | 120 | 310 | 290 | 182 | 0 | 84 | 23 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 130 | 124 | 56 | 20 | 1 | 43 | 42 | 47 | 0 | 163 | 300 | 33 | 71 | 0 | 150 | 18 | 0 | 6 | 310 | 16 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 127 | 7 | 20 | 72 | 0 | 367 | 24 | 52 | 0 | 1 | 179 | 0 | 0 | 0 | 11 | 90 | 270 | 17 | 20 | 0 | 0 | 0 | 0 | 15 |  | 721 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 54 | 0 | 171 | 0 | 359 | 53 | 0 | 35 | 0 | 70 | 0 | 3 | 35 | 350 | 92 | 0 | 0 |  | 6632 | 2737 | 9369 | 4688 | 721 | 1620 | 1593 | 500 | 70 | 0 | 130 | 47 | 0 | 89.09
17:00 | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 301 |  | 0 | 0 | 235 | 1 | 8 | 30 | 222 | 0 | 115 | 8 | 3 | 0 | 30 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 30 | 25 | 32 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 3 | 0 | 0 | 120 | 310 | 295 | 183 | 0 | 87 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 126 | 124 | 64 | 20 | 0 | 43 | 42 | 14 | 0 | 163 | 299 | 34 | 30 | 0 | 149 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 119 | 2 | 20 | 81 | 0 | 367 | 24 | 52 | 0 | 0 | 141 | 0 | 0 | 0 | 26 | 100 | 270 | 17 | 8 | 1 | 0 | 0 | 0 | 6 |  | 721 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 52 | 0 | 170 | 0 | 326 | 35 | 0 | 35 | 0 | 70 | 0 | 2 | 35 | 350 | 86 | 0 | 0 |  | 6421 | 2568 | 8989 | 4531 | 721 | 1447 | 1576 | 500 | 70 | 0 | 126 | 18 | 0 | 89.08
18:00 | 0 | 0 | 0 | 190 | 270 | 106 | 0 | 0 | 280 |  | 0 | 0 | 240 | 18 | 16 | 30 | 224 | 0 | 65 | 24 | 16 | 16 | 45 | 0 | 0 | 5 | 35 | 33 | 17 | 22 | 25 | 30 | 25 | 32 | 0 | 0 | 0 | 70 | 120 | 0 | 1 | 204 | 0 | 100 | 0 |  | 24 | 0 | 30 | 10 | 11 | 50 | 21 | 12 | 0 | 0 | 120 | 275 | 270 | 182 | 0 | 77 | 23 | 20 | 0 | 0 | 0 | 0 | 7 | 21 | 11 | 33 | 18 | 128 | 125 | 62 | 20 | 0 | 43 | 42 | 16 | 0 | 110 | 298 | 35 | 30 | 0 | 148 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 126 | 0 | 0 | 200 | 0 | 123 | 0 | 60 | 83 | 0 | 367 | 24 | 52 | 0 | 0 | 143 | 17 | 0 | 0 | 26 | 100 | 270 | 22 | 0 | 28 | 0 | 0 | 0 | 0 |  | 721 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 8 | 8 | 0 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 0 | 140 | 0 | 303 | 35 | 0 | 35 | 0 | 110 | 0 | 0 | 35 | 350 | 84 | 0 | 0 |  | 6514 | 2560 | 9074 | 4342 | 721 | 1314 | 1915 | 500 | 70 | 84 | 128 | 0 | 0 | 89.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 332 |  | 0 | 0 | 235 | 54 | 82 | 55 | 221 | 0 | 110 | 75 | 64 | 64 | 72 | 0 | 0 | 11 | 54 | 55 | 35 | 22 | 25 | 30 | 25 | 32 | 7 | 0 | 0 | 70 | 120 | 0 | 8 | 203 | 0 | 120 | 0 |  | 24 | 0 | 85 | 40 | 22 | 50 | 21 | 18 | 0 | 0 | 120 | 275 | 265 | 182 | 0 | 77 | 23 | 30 | 0 | 0 | 0 | 0 | 16 | 21 | 11 | 33 | 20 | 150 | 125 | 70 | 20 | 0 | 43 | 42 | 53 | 0 | 110 | 296 | 35 | 72 | 0 | 148 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 264 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 120 | 0 | 332 | 57 | 70 | 0 | 0 | 196 | 29 | 0 | 0 | 55 | 100 | 270 | 88 | 0 | 64 | 0 | 0 | 0 | 0 |  | 721 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 13 | 40 | 0 | 25 | 48 | 0 | 0 | 0 | 43 | 0 | 101 | 42 | 16 | 25 | 25 | 30 | 18 | 0 | 11 | 0 | 0 | 150 | 3 | 0 | 0 | 0 | 156 | 0 | 53 | 0 | 162 | 0 | 300 | 95 | 0 | 92 | 0 | 111 | 0 | 0 | 90 | 410 | 86 | 0 | 0 |  | 7673 | 3265 | 10938 | 4481 | 721 | 1480 | 3112 | 560 | 70 | 364 | 150 | 0 | 0 | 89.04
19:30 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 332 |  | 0 | 0 | 240 | 50 | 48 | 55 | 221 | 0 | 112 | 90 | 50 | 10 | 72 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 203 | 0 | 120 | 0 |  | 24 | 0 | 36 | 40 | 42 | 50 | 21 | 13 | 0 | 0 | 120 | 275 | 265 | 182 | 0 | 85 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 146 | 108 | 81 | 20 | 0 | 43 | 42 | 53 | 0 | 163 | 294 | 35 | 75 | 0 | 148 | 18 | 0 | 0 | 310 | 0 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 147 | 0 | 331 | 65 | 105 | 0 | 0 | 196 | 34 | 0 | 0 | 40 | 100 | 283 | 90 | 0 | 17 | 0 | 0 | 0 | 0 |  | 720 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 12 | 40 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 84 | 42 | 0 | 0 | 25 | 30 | 18 | 0 | 11 | 0 | 0 | 150 | 3 | 0 | 0 | 0 | 151 | 0 | 53 | 0 | 162 | 0 | 330 | 95 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 450 | 92 | 0 | 0 |  | 7645 | 3312 | 10957 | 4484 | 720 | 1621 | 3141 | 600 | 70 | 175 | 146 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 353 |  | 0 | 0 | 235 | 0 | 48 | 55 | 221 | 0 | 117 | 60 | 7 | 0 | 73 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 203 | 0 | 120 | 0 |  | 25 | 0 | 20 | 40 | 42 | 50 | 21 | 22 | 0 | 0 | 120 | 305 | 280 | 182 | 0 | 80 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 148 | 105 | 81 | 20 | 0 | 43 | 42 | 53 | 0 | 163 | 296 | 35 | 75 | 0 | 148 | 18 | 0 | 0 | 290 | 0 | 11 | 0 | 282 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 147 | 0 | 331 | 55 | 90 | 0 | 0 | 198 | 34 | 0 | 0 | 8 | 100 | 270 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 720 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 11 | 40 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 45 | 42 | 0 | 0 | 25 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 54 | 0 | 167 | 0 | 365 | 95 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 450 | 94 | 0 | 0 |  | 7419 | 3316 | 10735 | 4522 | 720 | 1675 | 2898 | 600 | 70 | 102 | 148 | 0 | 0 | 89.05
21:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 355 |  | 0 | 0 | 235 | 0 | 15 | 55 | 223 | 0 | 150 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 40 | 42 | 50 | 21 | 32 | 0 | 0 | 120 | 305 | 290 | 182 | 0 | 85 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 144 | 105 | 81 | 20 | 0 | 43 | 42 | 53 | 0 | 163 | 296 | 35 | 75 | 0 | 148 | 18 | 0 | 0 | 300 | 0 | 11 | 0 | 282 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 147 | 0 | 330 | 55 | 70 | 0 | 0 | 198 | 34 | 0 | 0 | 0 | 100 | 284 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 181 | 0 | 54 | 0 | 180 | 0 | 396 | 95 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 480 | 93 | 0 | 0 |  | 7321 | 3207 | 10528 | 4626 | 721 | 1728 | 2608 | 631 | 70 | 0 | 144 | 0 | 0 | 89.04
22:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 356 |  | 0 | 0 | 235 | 0 | 15 | 30 | 222 | 0 | 145 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 10 | 15 | 50 | 21 | 35 | 0 | 0 | 120 | 295 | 295 | 182 | 0 | 78 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 144 | 108 | 81 | 20 | 0 | 43 | 42 | 53 | 0 | 163 | 300 | 35 | 75 | 0 | 148 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 147 | 0 | 331 | 35 | 52 | 0 | 0 | 198 | 34 | 0 | 0 | 0 | 100 | 270 | 82 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 54 | 0 | 182 | 0 | 345 | 95 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 520 | 81 | 0 | 0 |  | 7126 | 3124 | 10250 | 4624 | 721 | 1666 | 2355 | 670 | 70 | 0 | 144 | 0 | 0 | 89.03
23:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 303 |  | 0 | 0 | 235 | 0 | 0 | 15 | 221 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 30 | 0 | 0 | 120 | 290 | 295 | 182 | 0 | 77 | 23 | 56 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 138 | 109 | 81 | 20 | 0 | 44 | 42 | 53 | 0 | 130 | 296 | 36 | 75 | 0 | 148 | 18 | 0 | 7 | 275 | 16 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 131 | 0 | 70 | 147 | 0 | 332 | 0 | 52 | 0 | 0 | 197 | 17 | 0 | 0 | 0 | 100 | 270 | 53 | 0 | 0 | 0 | 0 | 0 | 0 |  | 720 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 54 | 0 | 182 | 0 | 346 | 35 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 550 | 84 | 0 | 0 |  | 6683 | 2903 | 9586 | 4601 | 720 | 1569 | 1788 | 700 | 70 | 0 | 138 | 0 | 0 | 89.02
24:00 | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 303 |  | 0 | 0 | 235 | 0 | 0 | 0 | 221 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 30 | 0 | 0 | 120 | 290 | 300 | 184 | 0 | 85 | 23 | 56 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 132 | 109 | 0 | 20 | 0 | 44 | 42 | 53 | 0 | 130 | 297 | 35 | 75 | 0 | 148 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 131 | 0 | 0 | 147 | 0 | 330 | 0 | 17 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 100 | 300 | 28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 53 | 0 | 184 | 0 | 399 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 520 | 94 | 0 | 0 |  | 6335 | 2786 | 9121 | 4643 | 721 | 1656 | 1229 | 670 | 70 | 0 | 132 | 0 | 0 | 89.01
KWH | 0 | 0 | 0 | 4561200 | 6797300 | 2021909 | 0 | 0 | 7638000 |  | 0 | 0 | 5621033 | 131520 | 225384 | 441524 | 4940402 | 0 | 2951000 | 220800 | 145008 | 65280 | 518022 | 0 | 0 | 25584 | 1139040 | 148273 | 100920 | 491292 | 600000 | 639540 | 627400 | 789400 | 5592 | 0 | 0 | 1680000 | 2800000 | 0 | 20579 | 4872138 | 0 | 2905722 | 0 |  | 474000 | 0 | 374737 | 129360 | 154560 | 801600 | 485520 | 505920 | 0 | 0 | 2895202 | 7158500 | 6917000 | 4524000 | 0 | 1990220 | 523440 | 864000 | 0 | 0 | 0 | 0 | 25992 | 460944 | 217080 | 449600 | 359390 | 3002880 | 2955120 | 852480 | 449568 | 15450 | 1029000 | 983520 | 665400 | 0 | 3334581 | 5812000 | 833184 | 1166400 | 0 | 3571510 | 422000 | 0 | 96480 | 7339500 | 227536 | 264000 | 0 | 2248144 | 0 | 0 | 3564000 | 0 | 2908800 | 115695 | 640320 | 1525920 | 0 | 8504000 | 327600 | 932652 | 0 | 28000 | 3131345 | 180408 | 0 | 0 | 183960 | 1819200 | 6761300 | 535680 | 337380 | 120960 | 0 | 0 | 0 | 226579 |  | 17407272 | 0 | 9024192 | 0 | 158400 | 0 | 0 | 0 | 0 | 25600 | 74625 | 0 | 509600 | 205824 | 0 | 0 | 0 | 34170 | 0 | 145672 | 107910 | 12268 | 16372 | 78720 | 47003 | 328560 | 0 | 220140 | 0 | 0 | 3669100 | 4000 | 0 | 0 | 0 | 4151773 | 0 | 826126 | 0 | 4193264 | 0 | 8740000 | 987840 | 0 | 1176960 | 0 | 1329600 | 0 | 39274 | 991680 | 10510800 | 2202982 | 0 | 0 |  | 149547479 | 67219727 | 216767206 | 108358397 | 17407272 | 36239458 | 34424087 | 14179900 | 1680000 | 712834 | 3002880 | 762378 | 0
Fuel Cost | 0 | 0 | 0 | 6704964 | 7545003 | 2668919.88 | 0 | 0 | 7867140 |  | 0 | 0 | 6239346.63 | 998236.8 | 1552895.76 | 3735293.04 | 5138018.08 | 0 | 5105230 | 1662624 | 1322472.96 | 642355.2 | 4776162.84 | 0 | 0 | 232558.56 | 8314992 | 1146150.29 | 995071.2 | 368469 | 450000 | 0 | 0 | 0 | 54074.64 | 0 | 0 | 453600 | 5068000 | 0 | 191178.91 | 5310630.42 | 0 | 4939727.4 | 0 |  | 0 | 0 | 3634948.9 | 1235388 | 1344672 | 6348672 | 611755.2 | 1502582.4 | 0 | 0 | 4255946.94 | 5297290 | 6917000 | 4162080 | 0 | 2288753 | 591487.2 | 1209600 | 0 | 0 | 0 | 0 | 248223.6 | 585398.88 | 162810 | 786800 | 269542.5 | 22521600 | 3132427.2 | 7740518.4 | 570951.36 | 246273 | 1687560 | 1573632 | 1184412 | 0 | 3801422.34 | 6044480 | 1641372.48 | 2227824 | 0 | 6178712.3 | 924180 | 0 | 196819.2 | 7412895 | 170652 | 200640 | 0 | 16995968.64 | 0 | 0 | 18532800 | 0 | 28622592 | 1352474.55 | 5218608 | 16556232 | 0 | 7908720 | 2987712 | 8813561.4 | 0 | 0 | 23672968.2 | 1571353.68 | 0 | 0 | 1576537.2 | 12115872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100265886.72 | 0 | 9475401.6 | 0 | 1245024 | 0 | 0 | 0 | 0 | 268288 | 777592.5 | 0 | 789880 | 2008842.24 | 0 | 0 | 0 | 336232.8 | 0 | 1289197.2 | 830907 | 165863.36 | 158644.68 | 762796.8 | 455929.1 | 630835.2 | 0 | 166645.98 | 0 | 0 | 19886522 | 138600 | 0 | 0 | 0 | 5480340.36 | 0 | 1239189 | 0 | 4906118.88 | 0 | 8652600 | 10313049.6 | 0 | 11169350.4 | 0 | 10317696 | 0 | 433977.7 | 7328515.2 | 46142412 | 0 | 0 | 0 |  | 338317836.18 | 245636338.32 | 583954174.5 | 116620739.78 | 100265886.72 | 39384119.02 | 229722373.85 | 66028934 | 453600 | 6924195.88 | 22521600 | 2032725.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 270 | 102 | 0 | 0 | 344 |  | 0 | 0 | 245 | 0 | 0 | 15 | 217 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 10 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 217 | 0 | 120 | 0 |  | 22 | 0 | 15 | 0 | 0 | 50 | 18 | 3 | 0 | 0 | 120 | 360 | 315 | 203 | 0 | 86 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 12 | 124 | 104 | 24 | 20 | 2 | 43 | 42 | 21 | 0 | 130 | 298 | 34 | 74 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 131 | 18 | 0 | 17 | 0 | 390 | 0 | 32 | 0 | 4 | 180 | 0 | 0 | 0 | 0 | 90 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 14 | 0 | 182 | 0 | 419 | 35 | 0 | 35 | 0 | 70 | 0 | 6 | 35 | 350 | 93 | 0 | 0 |  | 9132 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 300 | 106 | 0 | 0 | 332 | 0 | 0 | 0 | 240 | 50 | 48 | 55 | 221 | 0 | 112 | 90 | 50 | 10 | 72 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 70 | 120 | 0 | 8 | 203 | 0 | 120 | 0 | 0 | 24 | 0 | 36 | 40 | 42 | 50 | 21 | 13 | 0 | 0 | 120 | 275 | 265 | 182 | 0 | 85 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 146 | 108 | 81 | 20 | 0 | 43 | 42 | 53 | 0 | 163 | 294 | 35 | 75 | 0 | 148 | 18 | 0 | 0 | 310 | 0 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 147 | 0 | 331 | 65 | 105 | 0 | 0 | 196 | 34 | 0 | 0 | 40 | 100 | 283 | 90 | 0 | 17 | 0 | 0 | 0 | 0 |  | 720 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 12 | 40 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 84 | 42 | 0 | 0 | 25 | 30 | 18 | 0 | 11 | 0 | 0 | 150 | 3 | 0 | 0 | 0 | 151 | 0 | 53 | 0 | 162 | 0 | 330 | 95 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 450 | 92 | 0 | 0 |  | 10957 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 360 | 0 | 0 | 0 | 250 | 100 | 100 | 55 | 300 | 0 | 150 | 100 | 100 | 149 | 86 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 120 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 20 | 20 | 0 | 0 | 120 | 360 | 300 | 225 | 0 | 90 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 160 | 50 | 22 | 0 | 44 | 42 | 51 | 0 | 163 | 300 | 35 | 86 | 0 | 160 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 340 | 90 | 0 | 144 | 116 | 0 | 0 |  |  | 739 | 16 | 400 | 0 | 66 | 220 | 0 | 0 | 25 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 34 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 300 | 108 | 0 | 0 | 300 | 0 | 0 | 0 | 250 | 100 | 100 | 55 | 220 | 0 | 150 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 120 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 20 | 10 | 0 | 0 | 100 | 360 | 300 | 225 | 0 | 90 | 25 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 160 | 50 | 22 | 1.6 | 44 | 42 | 51 | 0 | 163 | 300 | 35 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 340 | 90 | 50 | 144 | 116 | 0 | 0 | 30 |  | 739 | 0 | 400 | 0 | 66 | 0 | 0 | 0 | 25 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 42 | 50 | 50 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 620 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 300 | 51 | 0 | 0 | 322 | 0 | 0 | 0 | 235 | 0 | 15 | 15 | 221 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 25 |  | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 203 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 8 | 0 | 0 | 120 | 295 | 260 | 185 | 0 | 85 | 23 | 10 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 108 | 141 | 40 | 20 | 1 | 43 | 42 | 47 | 0 | 110 | 297 | 35 | 40 | 0 | 148 | 19 | 0 | 5 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 200 | 0 | 130 | 9 | 10 | 48 | 0 | 332 | 0 | 0 | 0 | 2 | 70 | 0 | 0 | 0 | 0 | 100 | 300 | 17 | 16 | 0 | 0 | 0 | 0 | 12 | 0 | 726 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 53 | 0 | 150 | 0 | 345 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 35 | 420 | 95 | 0 | 0 | 0
199
| Minimum Generation |  | 7189 | 5:00
| Highest Generation |  | 10957 | 19:30
| Day Peak Generation |  | 9132 | 12:00
| Evening Peak Generation |  | 10957 | 19:30
| HVDC Max Flow |  | 721 | 1:00
| HVDC EvPeak Flow |  | 720 | 19:30
| Load factor L.F |  | 82.43%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-15
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9132 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7672 | MW
Evening Peak Generation : |  | 10957 | MW Hour : | 19:30 | Available Max Generation : |  | 15439 | MW
E.P. Demand (at gen end) : |  | 10957 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11400 | MW
Maximum Generation : |  | 10957 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4039 | MW
Total Gen. (MKWH) : |  | 216.7672 | System Load Factor : | 82.43% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -220 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-15
Actual : | 88.95 | Ft.(MSL) , | Rule curve : | 90.76 | Ft.( MSL )
Gas Consumed : | Total = | 1169.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156004858.8
: |  | Coal : | 66028934 | Oil : | 236646569.73 | Total : | 458680362.53
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4050.322 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1378.0759 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1234.8426 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1115.8314 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1008.3348 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 813.6924 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 454.0216 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 209.4786 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 627.5645 |  |  | 0 | 0%
Total | 0 |  | 10892.1638 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
6) Sirajganj #1 CCPP
7) Haripur 412 MW
8) Meghnaghat 450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 09:12 to 15:05 for C/M.
b) Khulshi-Hathazari 132 kV Ckt was under shut down from 07:13 to 16:21 for C/M.
c) Rajendrapur 132/33 kV T-3 transformer was switched on at 11:35.
d) Ramganj-Desh Energy 132 kV Ckt-1 was under shut down from 09:54 to 17:19 for DLC.
e) Sreemongal-Shajibazar 132 kV Ckt-1 was under shut down from 09:43 to 14:52 for C/M.
f) Sikalbaha-T.K. Chemical 132 kV Ckt was under shut down from 09:52 to 12:46 due to R/H at Breaker terminal.
g) Mahasthangar 33 kV Bus section was under shutdown from 08:47 to 09:43 due to R/H maintenance at |  |  |  |  | About 20 MW power interruption occurred under Mahasthangar S/S area
Amtoli 33 kV feeder loop. |  |  |  |  | from 08:47 to 09:43.
h) Haripur-Fatullah 132 kV Ckt was under shut down from 09:53 to 11:55 for isolator maintenance work.
i) Haripur 132 kV main Bus was under shut down from 10:00 to 11:37 for Fatullah Ckt isolator maintenance work.
j) Hathazari-Baraulia 132 kV Ckt-1 was shut down at 10:10 for D/W.
k) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 12:37 to 13:40 for CB timing test.
l) Barishal(N) 132/33 kV T-5 transformer tripped at 12:29 showing Differential-2 due to 33 kV Banaripura feeder
fault and was switch on at 12:58.
m) Haripur 132 kV reserve Bus was under shut down from 12:40 to 14:29 due to R/H at BC Breaker isolator.
n) Amnura 132/33 kV T-1 transformer was switched on at 15:33.
o) Hathazari-Baroirhat 132 kV Ckt-2 was under shut down from 14:25 to 16:19 for CB timing test.
p) Chowmuhoni 132/33 kV T-1 & T-2 transformers tripped at 14:45 from 33 kV side due to 33 kV
Lashipur-2 feeder fault and were switch on at 14:55.
q) Haripur-Siddhirganj 230 kV Ckt was under shut down from 16:07 to 18:08 due to R/H maintenance at
Haripur end.
r) Sylhet 132/33 kV T-1 transformer was under shut down from 19:10 to 20:40 due to CT problem. |  |  |  |  | About 33 MW power interruption occurred under Sylhet S/S area
from 19:10 to 20:40.
s) Uttara 3rd Phase-Metro Rail 132 kV Ckt, Metro Rail 132/33 kV T-1&T-2 was switched on at 14:45, 16:27
& 16:35 respectively.
t) Haripur-Bhulta 230 kV Ckt-2 was under shut down since 07:36(15/03/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4561200
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6797300 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 106 | 2021909
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Dirty fuel(Gas)
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7638000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Dirty fuel(Gas)
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 131520 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 5621033 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 225384 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 441524
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 72 | 518022 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 491292
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 112 | 2951000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 220800 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 4940402 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 145008 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 25584 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1139040
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 10 | 65280 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 148273
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 100920 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1239540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 627400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 789400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 5592 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 2248144 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 2908800 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 932652
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 535680 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 120960 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 226579
| Dhaka area Total |  |  |  | 5972 | 2768 | 47818238
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 20579 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115695
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 801600
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1680000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4872138
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2905722
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 36 | 374737
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 129360 | High Voltage.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 640320
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 485520
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 505920
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 42 | 154560 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28000
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 196 | 3131345 | High Voltage.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 34 | 180408 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1819200
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 1153 | 20645104
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 120 | 2895202
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4524000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7158500 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6917000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 523440 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 864000
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 1990220 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 147 | 1525920
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 460944
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3002880
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 449600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 25992 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 359390
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 40 | 183960 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 0 | On Test
| Cumilla Area Total |  |  |  | 2980 | 1420 | 31098128
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 2955120 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 449568
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 81 | 852480 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15450
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3564000 | High Voltage.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 65 | 327600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 337380
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 474000
| Mymensingh Area Total |  |  |  | 709 | 498 | 8975598
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 983520 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3334581
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 294 | 5812000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 665400
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 833184 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1166400 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 148 | 3571510
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 227536 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7339500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 331 | 8504000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 96480 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 283 | 6761300 | On Test
| Sylhet Area Total |  |  |  | 2371 | 1806 | 41010411
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 720 | 17407272
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 158400 | Low demand
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 12 | 25600 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 9024192 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 74625
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 987840 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1286 | 27677929
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 205824 | High Voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 24 | 509600 | Engine problem
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 53 | 826126 | Machine problem
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 450 | 10510800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 92 | 2202982 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 683 | 14255332
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 34170 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 107910 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 12268 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 16372 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 151 | 4151773 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 4193264 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 330 | 8740000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 47003
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 328560 | Engine problem
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 220140
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 78720 | Low demand
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 84 | 145672
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1176960
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 991680
| Rajshahi Area Total |  |  |  | 2183 | 1079 | 20244492
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3669100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 3 | 4000
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 1329600
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39274
| Rangpur Area Total |  |  |  | 605 | 264 | 5041974
| Total |  |  |  | 21312 | 10957 | 216767206
| Eastern Grid Total |  |  |  | 14414 | 7645 | 149547479
| Western Grid Total |  |  |  | 6898 | 3312 | 67219727
| National Grid Total |  |  |  | 21312 | 10957 | 216767206
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-14
(a) ENTIRE EASTERN GRID : |  | 7184 | MW | (b) ENTIRE WESTERN GRID : |  | 3275 | MW
i) Dhaka area |  | 3808 | MW | i) Khulna area |  | 1241 | MW
ii) Chittagong area |  | 1221 | MW | ii) Rajshahi area |  | 1065 | MW
iii) Comilla area |  | 959 | MW | iii) Barisal area |  | 276 | MW
iv) Mymensingh area |  | 843 | MW | iv) Rangpur area |  | 693 | MW
v) Sylhet area |  | 353 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10459 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 19:00 | Jamalpur | 129 | 18:30 | Jhenida | 98 | 19:00
Munsiganj | 118 | 18:30 | Sherpur | 114 | 18:30 | Bottail | 106 | 19:00
Sonargaon | 73 | 21:00 | Srimongal | 39 | 19:00 | G.K Project | 44 | 19:00
Shyampur | 182 | 11:00 | Shahjibazar | 100 | 21:00 | Faridpur | 147 | 19:00
Bhulta | 189 | 11:00 | Fenchuganj | 31 | 18:30 | Madaripur | 74 | 21:00
Madanganj | 55 | 1:00 | Kulawara | 29 | 19:00 | Sariatpur | 44 | 19:30
Shitalakhya | 117 | 19:00 | Sylhet | 97 | 18:00 | Gopalganj | 67 | 19:00
Rahim steel | 20 | 11:00 | Chatak | 28 | 19:30 | Bagerhat | 89 | 19:00
Matuail | 85 | 12:00 | Sunamganj | 33 | 20:00 | Mongla | 42 | 10:00
Ghorasal | 66 | 18:30 | Biani Bazar | 46 | 20:00 | Satkhira | 88 | 19:00
Narsingdi | 134 | 20:00 | Comilla (S) | 150 | 19:00 | Gallamari | 26 | 10:00
Haripur (SBU) | 102 | 21:00 | Comilla(N) | 95 | 19:30 | Magura | 46 | 19:00
Sreenagar |  |  | Chandpur | 55 | 19:30 | Norail | 33 | 19:30
Ullon | 74 | 19:00 | Feni | 96 | 18:30 | Chuadanga | 76 | 19:30
Hasnabad | 96 | 21:00 | Chowmuhani | 140 | 19:30 | Borguna | 12 | 19:30
Magbazar | 80 | 13:00 | Ashuganj | 44 | 16:00 | Barisal(N) | 31 | 19:30
Maniknagar | 65 | 18:30 | Daudkandi | 118 | 19:00 | Barisal (S) | 90 | 18:30
Bangabhaban | 20 | 13:00 | B.Baria | 127 | 21:00 | Patuakhali | 82 | 21:00
Narinda | 86 | 13:00 | Ramganj | 66 | 19:30 | Bhandaria | 40 | 20:00
Dhanmondi | 161 | 13:00 | Chaddagram | 33 | 19:30 | Borhan Uddin | 30 | 19:00
Lalbag | 72 | 13:00 | PHP | 10 | 21:00 | Ishurdi | 49 | 19:00
Madartek | 60 | 19:00 | Kochua | 49 | 20:00 | Ruppur Paromanobik | 3 | 15:00
Dhaka University | 40 | 12:00 | Madunaghat | 55 | 18:00 | Natore | 101 | 19:30
Aftabnagar | 8 | 16:00 | Hathazari | 86 | 18:30 | Bogra | 133 | 20:00
Fatullah | 56 | 15:00 | Khulshi | 178 | 19:00 | Noagaon | 91 | 19:00
Nawabganj | 37 | 19:30 | Halishahar | 121 | 19:00 | Rajshahi | 123 | 19:00
Mirpur | 95 | 18:30 | Baraulia | 149 | 0:00 | Rajshahi New | 10 | 15:00
Kalyanpur | 69 | 18:30 | Sikalbaha | 19 | 19:30 | C.Nawabganj | 70 | 19:00
Gulshan | 106 | 14:00 | Dohazari | 75 | 18:30 | Amnura | 46 | 18:30
Uttara | 73 | 18:30 | Cox'sbazar | 98 | 19:00 | Pabna | 79 | 19:00
Uttara New | 23 | 18:30 | Chandraghona | 30 | 18:30 | Shahjadpur | 86 | 19:00
Kamrangirchar | 84 | 18:30 | Kaptai | 0 | #N/A | Serajganj | 86 | 20:00
Savar | 142 | 19:30 | A. Khaer Stl. | 9 | 6:00 | Niyamatpur | 62 | 18:30
Bhasantec | 126 | 18:30 | Bakulia | 97 | 18:30 | Joypurhat | 55 | 19:00
Agargaon | 56 | 14:00 | Julda | 21 | 17:00 | Sherpur(Bogura) | 46 | 19:30
Satmosjid | 87 | 18:30 | TK chemical | 25.5 | 19:30 | Mohastangor | 46 | 19:00
Tongi | 108 | 15:00 | Modern Steel |  |  | Bangura | 21 | 19:30
Kabirpur | 224 | 16:00 | Shahmirpur | 30 | 18:00 | Rangpur | 120 | 19:00
Basundhara | 131 | 18:30 | Khagrachhari | 22 | 19:30 | Lalmonirhat | 38 | 19:00
Manikganj | 62 | 20:00 | Matarbari | 34 | 18:30 | Saidpur | 96 | 10:00
Joydevpur | 116 | 19:00 | Baroiar Hat | 42 | 19:00 | Purbasadipur | 88 | 19:30
New Tongi | 86 | 15:00 | Rangamati | 12 | 18:30 | Thakurgaon | 68 | 19:00
Kodda | 230 | 19:00 | Abul Khair 230 | 16 | 8:00 | Palashbari | 104 | 19:00
Dhamrai | 100 | 18:00 | BSRM | 143 | 19:30 | Barapukuria | 52 | 9:00
Rajendrapur | 86 | 19:00 | GPH Ispat | 86 | 2:00 | Panchagar | 41 | 18:30
Valuka | 129 | 19:30 | Goalpara | 21 | 1:00 | Joldhaka | 53 | 19:00
Tangail | 169 | 18:30 | Central s/s | 90 | 19:00 | Kurigram | 49 | 19:30
Mymensing | 162 | 18:30 | Noapara | 47 | 19:00 | Mithapukur | 13 | 18:30
Kishorganj | 108 | 21:00 | Jessore | 112 | 19:00
Netrokona | 123 | 19:00 | Benapol | 56 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 19:00 | 397 | 12:00 | Kaliakoir | 394 | 0.25 | 375 | 0.5
| Bheramara | 400 | 19:30 | 393 | 19:30 | Bhulta | 385 | 0.79167 | 362 | 0.5
| Ashuganj(N) | 389 | 19:00 | 370 | 12:00 | Gopalganj | 411 | 0.625 | 393 | 0.91667
| Payra | 411 | 19:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 232 | 1:00 | Hathazari | 224 | 18:30 | 217 | 3:00
| Ishurdi | 238 | 5:00 | 225 | 12:00 | Megnaghat | 231 | 22:00 | 217 | 11:00
| Ashuganj | 235 | 4:00 | 226 | 13:00 | Fenchuganj | 242 | 19:30 | 237 | 11:00
| Serajganj | 234 | 23:00 | 227 | 7:00 | Siddhirganj | 229 | 19:00 | 215 | 12:00
| Baghabari | 236 | 3:00 | 231 | 19:00 | Maniknagar | 229 | 19:00 | 213 | 12:00
| Barapukuria | 232 | 2:00 | 225 | 11:00 | Agargaon | 227 | 6:00 | 210 | 12:00
| Bogra | 231 | 5:00 | 221 | 7:00 | Barisal | 249 | 22:00 | 242 | 18:30
| Rajshahi | 235 | 5:00 | 222 | 12:00 | Bhola 225 MW | 249 | 8:00 | 244 | 1:00
| Khulna South | 248 | 12:00 | 220 | 13:00 | AKSML | 225 | 22:00 | 217 | 3:00
| Rampura | 228 | 18:00 | 218 | 12:00 | BSRM | 226 | 19:00 | 216 | 12:00
| Haripur | 229 | 19:00 | 214 | 12:00 | Bibiyana | 241 | 19:00 | 235 | 12:00
| Hasnabad | 226 | 23:00 | 208 | 12:00 | Bhulta | 232 | 19:00 | 216 | 12:00
| Shyampur | 227 | 19:00 | 220 | 12:00 | Ashuganj (S) | 234 | 19:00 | 224 | 12:00
| Aminbazar | 229 | 1:00 | 214 | 2:00 | Kaliakoir | 229 | 18:30 | 212 | 12:00
| Tongi | 220 | 21:00 | 202 | 12:00 | GPH | 225 | 19:30 | 217 | 1:00
| Comilla (N) | 230 | 19:00 | 217 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 19:00 | 127 | 12:00 | Madanhat | 134 | 0.79167 | 128 | 0.20833
| Munsiganj | 140 | 19:00 | 126 | 12:00 | Hathazari | 133 | 0.8125 | 129 | 0.125
| Sonargaon | 134 | 5:00 | 125 | 12:00 | Khulshi | 131 | 0.77083 | 125 | 0.66667
| Shyampur | 137 | 19:00 | 126 | 11:00 | Halishahar | 133 | 0.77083 | 126 | 0.625
| Bhulta | 130 | 4:00 | 120 | 12:00 | Baraulia | 133 | 0.75 | 127 | 0.375
| Madanganj | 135 | 20:00 | 124 | 12:00 | Sikalbaha | 134 | 0.75 | 128 | 0.16667
| Shitalakhya | 141 | 19:00 | 123 | 12:00 | Dohazari | 130 | 0.77083 | 125 | 0.16667
| Rahim steal | 138 | 18:30 | 127 | 12:00 | Cox'sbazar | 122 | 0.33333 | 115 | 0.041667
| Matuail | 139 | 19:00 | 127 | 12:00 | Chandraghona | 132 | 0.79167 | 127 | 0.083333
| Ghorasal | 136 | 1:00 | 136 | 1:00 | Kaptai
| Narsinghdi | 132 | 1:00 | 128 | 11:00 | A. Khaer Stl. | 130 | 0.70833 | 127 | 0.125
| Haripur (SBU) | 138 | 18:00 | 127 | 12:00 | Bakulia | 133 | 0.8125 | 127 | 0.125
| Sreenagar |  |  |  |  | Julda | 134 | 0.77083 | 127 | 0.29167
| Ullon | 134 | 19:00 | 125 | 12:00 | TK Chemical | 133 | 0.8125 | 128 | 0.45833
| Hasnabad | 136 | 18:30 | 124 | 12:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 134 | 7:00 | 126 | 11:00 | Shahmirpur | 135 | 0.79167 | 127 | 0.125
| Maniknagar | 134 | 18:30 | 126 | 12:00 | Khagrachhari | 131 | 0.8125 | 126 | 0.083333
| Bangabhaban | 134 | 18:30 | 126 | 12:00 | Matarbari | 123 | 0.45833 | 118 | 0.083333
| Narinda | 134 | 18:30 | 126 | 12:00 | Baroiar Hat | 132 | 0.77083 | 124 | 0.54167
| Dhanmondi | 134 | 19:00 | 125 | 12:00 | Rangamati | 131 | 0.75 | 126 | 0.5
| Lalbag | 136 | 19:00 | 121 | 12:00 | Goalpara S/S | 138 | 4:00 | 126 | 12:00
| Madartek | 134 | 19:00 | 125 | 12:00 | Khulna Central S/S | 137 | 6:00 | 125 | 12:00
| Dhaka University | 134 | 18:30 | 125 | 12:00 | Noapara | 135 | 5:00 | 124 | 0.5
| Aftabnagar | 134 | 18:30 | 126 | 12:00 | Jessore | 133 | 2:00 | 120 | 0.5
| Fatullah | 137 | 18:30 | 126 | 12:00 | Benapol | 136 | 4:00 | 121 | 0.5
| Nawabganj | 131 | 18:30 | 121 | 12:00 | Jhenida | 133 | 6:00 | 118 | 0.79167
| Mirpur | 138 | 19:00 | 125 | 13:00 | Bottail | 136 | 0.25 | 127 | 0.79167
| Kalyanpur | 139 | 19:00 | 127 | 12:00 | G.K Project | 141 | 4:00 | 135 | 0.5
| Gulshan | 134 | 19:00 | 125 | 12:00 | Faridpur | 139 | 0.16667 | 132 | 0.95833
| Uttara | 136 | 20:00 | 123 | 12:00 | Madaripur | 143 | 0.25 | 134 | 0.875
| Uttara New | 136 | 19:00 | 126 | 12:00 | Shariyatpur S/S | 143 | 0.25 | 135 | 0.91667
| Kamrangirchar | 134 | 19:00 | 120 | 12:00 | Gopalganj | 145 | 0.25 | 137 | 0.91667
| Savar | 138 | 19:00 | 126 | 12:00 | Bagerhat | 135 | 23:00 | 120 | 0.5
| Bhasantec | 132 | 19:00 | 122 | 12:00 | Mongla | 130 | 0.083333 | 122 | 0.5
| Agargaon | 133 | 19:00 | 123 | 12:00 | Satkhira | 137 | 5:00 | 124 | 0.5
| Satmosjid | 133 | 19:00 | 123 | 12:00 | Gallamari | 138 | 4:00 | 127 | 0.5
| Tongi | 137 | 19:00 | 128 | 12:00 | Magura | 135 | 4:00 | 120 | 12:00
| Kabirpur | 134 | 22:00 | 126 | 12:00 | Narail | 132 | 0.16667 | 117 | 0.79167
| Basundhara | 136 | 22:00 | 124 | 12:00 | Chuadanga | 130 | 5:00 | 111 | 0.79167
| Manikganj | 138 | 19:00 | 128 | 12:00 | Borguna | 140 | 0.25 | 136 | 0.041667
| Joydevpur | 138 | 19:00 | 129 | 12:00 | Barisal(N) | 142 | 6:00 | 137 | 0.5
| New Tongi | 136 | 19:00 | 126 | 12:00 | Barisal (S) | 140 | 5:00 | 135 | 0.91667
| Kodda | 135 | 22:00 | 121 | 12:00 | Patuakhali(S) | 140 | 6:00 | 133 | 22:00
| Dhamrai | 134 | 5:00 | 122 | 12:00 | Bhandaria | 140 | 0.25 | 134 | 0.875
| Rajendrapur | 132 | 19:00 | 119 | 12:00 | Ishurdi | 139 | 0.20833 | 131 | 0.5
| Valuka | 128 | 1:00 | 115 | 18:30 | Ruppur Paromanobik | 138 | 0.16667 | 132 | 0.5
| Tangail | 136 | 2:00 | 125 | 12:00 | Natore | 137 | 4:00 | 128 | 12:00
| Mymensing | 132 | 1:00 | 120 | 10:00 | Bogra | 137 | 5:00 | 130 | 11:00
| Kishorganj | 131 | 2:00 | 123 | 18:30 | Noagaon | 132 | 3:00 | 123 | 12:00
| Netrokona | 129 | 1:00 | 115 | 18:30 | Rajshahi | 134 | 1:00 | 127 | 12:00
| Jamalpur | 138 | 21:00 | 121 | 7:00 | Rajshahi New | 134 | 5:00 | 126 | 12:00
| Sherpur | 136 | 21:00 | 122 | 10:00 | C.Nawabganj | 133 | 18:30 | 123 | 12:00
| Srimongal | 137 | 1:00 | 135 | 6:00 | Amnura | 136 | 18:30 | 123 | 12:00
| Shahjibazar | 134 | 23:00 | 131 | 7:00 | Pabna | 138 | 4:00 | 130 | 12:00
| Fenchuganj | 136 | 4:00 | 135 | 1:00 | Shahjadpur | 139 | 4:00 | 134 | 12:00
| Khulawara | 136 | 1:00 | 134 | 11:00 | Serajganj | 135 | 3:00 | 128 | 12:00
| Sylhet | 134 | 7:00 | 132 | 16:00 | Niyamatpur | 131 | 2:00 | 121 | 12:00
| Chatak | 133 | 1:00 | 132 | 9:00 | Joypurhat | 134 | 4:00 | 121 | 11:00
| Sunamganj | 133 | 5:00 | 131 | 14:00 | Sherpur(Bogura) | 137 | 4:00 | 130 | 8:00
| Biani Bazar | 133 | 4:00 | 131 | 12:00 | Mohastangor | 136 | 4:00 | 127 | 12:00
| Comilla(s) | 124 | 5:00 | 114 | 19:00 | Bangura | 137 | 18:00 | 133 | 8:00
| Comilla(n) | 138 | 18:30 | 130 | 12:00 | Rangpur | 131 | 4:00 | 121 | 12:00
| Chandpur | 135 | 18:30 | 130 | 10:00 | Lalmonirhat | 130 | 4:00 | 120 | 13:00
| Feni | 132 | 18:00 | 124 | 15:00 | Saidpur | 127 | 4:00 | 119 | 19:00
| Chowmuhani | 132 | 20:00 | 124 | 15:00 | Purbasadipur | 128 | 1:00 | 117 | 9:00
| Ashuganj | 135 | 1:00 | 132 | 16:00 | Thakurgaon | 129 | 3:00 | 114 | 13:00
| Daudkandi | 135 | 18:30 | 124 | 12:00 | Palashbari | 132 | 3:00 | 123 | 12:00
| B.Baria | 132 | 6:00 | 128 | 12:00 | Barapukuria | 132 | 4:00 | 125 | 11:00

## L-Curve
Date | 2021-03-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 202 | 6335 | 2786 | 9121 |  |  |  | QF-LDC-11
0:30 | 226 | 5931 | 2685 | 8616 | Date: | 2021-03-14
1:00 | 250 | 5527 | 2584 | 8111
1:30 | 255 | 5411.5 | 2539.5 | 7951
2:00 | 260 | 5296 | 2495 | 7791
2:30 | 250 | 5255.5 | 2419 | 7674.5 | [5 empty] | Gen. at Eve. Peak | 10957 | 10957 MW (19:30 )
3:00 | 240 | 5215 | 2343 | 7558 | [6 empty] | 19:30
3:30 | 270 | 5141 | 2332.5 | 7473.5 | [5 empty] | Gen. at Day Peak | 9132 | 9132 MW (12:00 )
4:00 | 300 | 5067 | 2322 | 7389 | [6 empty] | 12:00
4:30 | 300 | 4992 | 2297 | 7289 | [5 empty] | Highest Generation | 10957
5:00 | 300 | 4917 | 2272 | 7189 | [6 empty] | 19:30
5:30 | 281 | 4970 | 2282.5 | 7252.5
6:00 | 262 | 5023 | 2293 | 7316
6:30 | 141 | 5139 | 2331.5 | 7470.5
7:00 | 20 | 5255 | 2370 | 7625
7:30 | 40 | 5372.5 | 2471.5 | 7844
8:00 | 60 | 5490 | 2573 | 8063
8:30 | 130 | 5575 | 2589.5 | 8164.5
9:00 | 200 | 5660 | 2606 | 8266
9:30 | 247 | 5806 | 2641.5 | 8447.5
10:00 | 294 | 5952 | 2677 | 8629
10:30 | 227 | 6066 | 2689.5 | 8755.5
11:00 | 160 | 6180 | 2702 | 8882
11:30 | 175 | 6277 | 2730 | 9007
12:00 | 190 | 6374 | 2758 | 9132
12:30 | 150 | 6426.5 | 2840 | 9266.5
13:00 | 110 | 6479 | 2922 | 9401
13:30 | 125 | 6516.5 | 2860 | 9376.5
14:00 | 140 | 6554 | 2798 | 9352
14:30 | 180 | 6571.5 | 2805 | 9376.5
15:00 | 220 | 6589 | 2812 | 9401
15:30 | 200 | 6610.5 | 2774.5 | 9385
16:00 | 180 | 6632 | 2737 | 9369
16:30 | 137.5 | 6526.5 | 2652.5 | 9179
17:00 | 95 | 6421 | 2568 | 8989
17:30 | 50.5 | 6467.5 | 2564 | 9031.5
18:00 | 6 | 6514 | 2560 | 9074
18:30 | 113 | 7093.5 | 2912.5 | 10006
19:00 | 220 | 7673 | 3265 | 10938
19:30 | 160 | 7645 | 3312 | 10957
20:00 | 120 | 7419 | 3316 | 10735 |  |  |  | Executive Engineer
20:30 | 101 | 7370 | 3261.5 | 10631.5 |  |  |  | Network Operation Division
21:00 | 82 | 7321 | 3207 | 10528
21:30 | 51 | 7223.5 | 3165.5 | 10389
22:00 | 20 | 7126 | 3124 | 10250 |  |  |  |  | Page 6 of 7
22:30 | 77.5 | 6904.5 | 3013.5 | 9918
23:00 | 135 | 6683 | 2903 | 9586
23:30 | 168.5 | 6509 | 2844.5 | 9353.5
24:00 | 202 | 6335 | 2786 | 9121
10957 MW (19:30 )
9132 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-14 |  | Energy | 216767206
[11 empty] | 2021-03-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4643 | 721 | 1656 | 1788 | 670 | 70 | 0 | 0 | 132 | 0
0:30 | 4438 | 721 | 1611.5 | 1287 | 634.5 | 70 | 8.5 | 0 | 125 | 0 | Date: | 2021-03-14
1:00 | 4233 | 721 | 1567 | 786 | 599 | 70 | 17 | 0 | 118 | 0
1:30 | 4259 | 720 | 1503 | 666 | 599 | 70 | 17 | 0 | 117 | 0 | [7 empty] | Total Energy | 216.7672 | Total Energy Gen 216.767 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.767 MKWHr
2:00 | 4285 | 719 | 1439 | 546 | 599 | 70 | 17 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4282 | 719 | 1359.5 | 529 | 584 | 70 | 17 | 0 | 114 | 0 | [7 empty] | Energy Requirement | 216.7672
3:00 | 4279 | 719 | 1280 | 512 | 569 | 70 | 17 | 0 | 112 | 0
3:30 | 4231.5 | 719 | 1253.5 | 501.5 | 569 | 70 | 17 | 0 | 112 | 0 | [6 empty] | Shortage
4:00 | 4184 | 719 | 1227 | 491 | 569 | 70 | 17 | 0 | 112 | 0
4:30 | 4174.5 | 719 | 1179.5 | 485 | 534 | 70 | 17 | 0 | 110 | 0
5:00 | 4165 | 719 | 1132 | 479 | 499 | 70 | 17 | 0 | 108 | 0
5:30 | 4203.5 | 720 | 1172 | 463.5 | 499.5 | 70 | 17 | 0 | 107 | 0
6:00 | 4242 | 721 | 1212 | 448 | 500 | 70 | 17 | 0 | 106 | 0
6:30 | 4312.5 | 721 | 1242.5 | 497 | 499.5 | 70 | 17 | 0 | 106 | 5 |  |  |  |  | Coal
7:00 | 4383 | 721 | 1273 | 546 | 499 | 70 | 17 | 0 | 106 | 10
7:30 | 4365.5 | 721 | 1356 | 691.5 | 499.5 | 70 | 17 | 0 | 105 | 18.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4348 | 721 | 1439 | 837 | 500 | 70 | 17 | 0 | 104 | 27
8:30 | 4360.5 | 721 | 1456 | 891.5 | 500 | 70 | 17 | 0 | 106 | 42.5
9:00 | 4373 | 721 | 1473 | 946 | 500 | 70 | 17 | 0 | 108 | 58
9:30 | 4400 | 721 | 1518.5 | 1037.5 | 500 | 70 | 17 | 0 | 108 | 75.5
10:00 | 4427 | 721 | 1564 | 1129 | 500 | 70 | 17 | 0 | 108 | 93
10:30 | 4503.5 | 721 | 1555 | 1179 | 500 | 70 | 16 | 0 | 110 | 101
11:00 | 4580 | 721 | 1546 | 1229 | 500 | 70 | 15 | 0 | 112 | 109
11:30 | 4677 | 721 | 1557.5 | 1254.5 | 500 | 70 | 15 | 0 | 118 | 94
12:00 | 4774 | 721 | 1569 | 1280 | 500 | 70 | 15 | 0 | 124 | 79
12:30 | 4715 | 721 | 1640.5 | 1388.5 | 500 | 70 | 7.5 | 0 | 129 | 95
13:00 | 4656 | 721 | 1712 | 1497 | 500 | 70 | 0 | 0 | 134 | 111
13:30 | 4656 | 721 | 1712 | 1497 | 500 | 70 | 0 | 0 | 134 | 111
14:00 | 4656 | 721 | 1712 | 1497 | 500 | 70 | 0 | 0 | 134 | 111
14:30 | 4650 | 721 | 1642 | 1592.5 | 500 | 70 | 0 | 0 | 130 | 95.5
15:00 | 4644 | 721 | 1572 | 1688 | 500 | 70 | 0 | 0 | 126 | 80
15:30 | 4666 | 721 | 1596 | 1640.5 | 500 | 70 | 0 | 0 | 128 | 63.5
16:00 | 4688 | 721 | 1620 | 1593 | 500 | 70 | 0 | 0 | 130 | 47
16:30 | 4609.5 | 721 | 1533.5 | 1584.5 | 500 | 70 | 0 | 0 | 128 | 32.5
17:00 | 4531 | 721 | 1447 | 1576 | 500 | 70 | 0 | 0 | 126 | 18
17:30 | 4436.5 | 721 | 1380.5 | 1745.5 | 500 | 70 | 42 | 0 | 127 | 9
18:00 | 4342 | 721 | 1314 | 1915 | 500 | 70 | 84 | 0 | 128 | 0
18:30 | 4411.5 | 721 | 1397 | 2513.5 | 530 | 70 | 224 | 0 | 139 | 0
19:00 | 4481 | 721 | 1480 | 3112 | 560 | 70 | 364 | 0 | 150 | 0
19:30 | 4484 | 720 | 1621 | 3141 | 600 | 70 | 175 | 0 | 146 | 0
20:00 | 4522 | 720 | 1675 | 2898 | 600 | 70 | 102 | 0 | 148 | 0
20:30 | 4574 | 720.5 | 1701.5 | 2753 | 615.5 | 70 | 51 | 0 | 146 | 0
21:00 | 4626 | 721 | 1728 | 2608 | 631 | 70 | 0 | 0 | 144 | 0
21:30 | 4625 | 721 | 1697 | 2481.5 | 650.5 | 70 | 0 | 0 | 144 | 0
22:00 | 4624 | 721 | 1666 | 2355 | 670 | 70 | 0 | 0 | 144 | 0
22:30 | 4612.5 | 720.5 | 1617.5 | 2071.5 | 685 | 70 | 0 | 0 | 141 | 0
23:00 | 4601 | 720 | 1569 | 1788 | 700 | 70 | 0 | 0 | 138 | 0
23:30 | 4622 | 720.5 | 1612.5 | 1788 | 685 | 70 | 0 | 0 | 135 | 0 | Max Temp. in Dhaka |  | 31.2° C
24:00 | 4643 | 721 | 1656 | 1788 | 670 | 70 | 0 | 0 | 132 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 216.767 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.767 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1680000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 8 | 8 | 8 |  |  |  |  | 20579
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 6 |  | 15 | 17 | 18 | 17 | 15 | 15 | 7 | 2 | [9 empty] | 115695
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 202 | 202 | 201 | 202 | 213 | 202 | 216 | 203 | 204 | 217 | 204 | 204 | 204 | 204 | 204 | 204 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4872138
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2905722
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | [5 empty] | 30 |  | 85 | 36 | 20 |  |  |  |  | 374737
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 98 | 72 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 120 | 120 | 150 | 155 | 155 | 155 | 155 | 115 | 65 |  | 110 | 112 | 117 | 150 | 145 | 145 | 145 | 2951000
17 | Siddhirganj 335 MW CCPP | 183 | 182 | 183 | 183 | 151 | 152 | 151 | 180 | 182 | 180 | 222 | 217 | 220 | 220 | 220 | 219 | 222 | 224 |  | 221 | 221 | 221 | 223 | 222 | 221 | 221 | 4940402
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 12 | 45 | 45 | 45 | 45 | 48 | 115 | 120 | 115 | 115 | 126 |  | 264 | 270 | 282 | 282 | 245 | 145 |  | 2248144
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4561200
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6797300
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2895202
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 523440
33 | Ashuganj 225 MW CCPP | 182 | 181 | 182 | 181 | 182 | 182 | 196 | 182 | 201 | 189 | 182 | 203 | 185 | 183 | 182 | 182 | 183 | 182 |  | 182 | 182 | 182 | 182 | 182 | 182 | 184 | 4524000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 265 | 265 | 265 | 265 | 290 | 265 | 300 | 275 | 265 | 315 | 295 | 295 | 295 | 290 | 295 | 270 |  | 265 | 265 | 280 | 290 | 295 | 295 | 300 | 6917000
| Ashuganj 450 MW CCPP(North) | 70 | 160 | 270 | 270 | 270 | 270 | 310 | 320 | 335 | 360 | 370 | 360 | 310 | 310 | 310 | 310 | 310 | 275 |  | 275 | 275 | 305 | 305 | 295 | 290 | 290 | 7158500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 48 | 53 | 53 | 51 | 20 | 20 |  | 30 | 52 | 52 | 52 | 53 | 56 | 56 | 864000
36 | Chandpur 150 MW CCPP | 86 | 86 | 84 | 82 | 80 | 80 | 85 | 86 | 87 | 86 | 86 | 86 | 78 | 83 | 87 | 84 | 87 | 77 |  | 77 | 85 | 80 | 85 | 78 | 77 | 85 | 1990220
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [26 empty] | 0
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 303 | 304 | 274 | 273 | 253 | 284 | 303 | 353 | 353 | 350 | 350 | 344 | 345 | 321 | 321 | 321 | 301 | 280 |  | 332 | 332 | 353 | 355 | 356 | 303 | 303 | 7638000
42 | RPCL 210MW CCPP | 129 | 148 | 148 | 148 | 148 | 163 | 164 | 163 | 140 | 119 | 118 | 104 | 105 | 104 | 104 | 124 | 124 | 125 |  | 125 | 108 | 105 | 105 | 108 | 109 | 109 | 2955120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 4 | 29 | 39 | 47 | 49 | 47 | 42 | 33 | 20 | 8 | [9 empty] | 337380
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 1029000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 983520
46 | Shajibazar 330 MW CCPP | 232 | 234 | 232 | 232 | 233 | 235 | 232 | 234 | 140 | 146 | 257 | 298 | 297 | 298 | 298 | 300 | 299 | 298 |  | 296 | 294 | 296 | 296 | 300 | 296 | 297 | 5812000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 35 | 36 | 36 | 36 | 35 | 36 | 35 | 35 | 34 | 34 | 34 | 34 | 33 | 33 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 833184
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 67 | 74 | 74 | 80 | 74 | 71 | 71 | 30 | 30 |  | 72 | 75 | 75 | 75 | 75 | 75 | 75 | 1166400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 149 | 148 |  | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 3571510
51 | Sylhet 20 MW GTPP | 19 | 18 | 18 | 19 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | [7 empty] | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 7 | 7 |  | 7 |  |  |  | 7 | 7 | 7 | 96480
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 21 | 50 | 50 | 47 | 47 | 14 | 16 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 665400
56 | Shahjahanulla 25 MW PP | 16 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 |  |  |  | 16 | 16 | 16 | 227536
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 295 | 280 | 290 | 265 | 300 | 300 | 310 | 310 | 320 | 310 | 310 | 320 | 300 | 300 | 310 | 300 | 290 |  | 270 | 310 | 290 | 300 | 290 | 275 | 300 | 7339500
| Bibiyana South 400 MW | 323 | 310 | 310 | 221 | 220 | 244 | 300 | 270 | 300 | 300 | 270 | 300 | 269 | 270 | 270 | 270 | 270 | 270 |  | 270 | 283 | 270 | 284 | 270 | 270 | 300 | 6761300
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 35 | 35 | 17 |  |  |  |  | 100920
59 | Tangail Palli Power Gen 22 MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 15 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 20 | 24 | 24 |  | 24 | 24 | 25 | 24 | 24 | 24 |  | 474000
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 20 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 485520
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491292
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 449568
63 | Impoprt (Tripura) | 118 | 116 | 112 | 112 | 108 | 106 | 106 | 104 | 108 | 108 | 112 | 124 | 134 | 124 | 126 | 130 | 126 | 128 |  | 150 | 146 | 148 | 144 | 144 | 138 | 132 | 3002880
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 36 | 38 | 12 | 6 | 6 | 5 | 3 | 7 | 2 | 4 | 3 | 3 | 12 |  | 18 | 13 | 22 | 32 | 35 | 30 | 30 | 505920
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 15 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 460944
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 217080
67 | Jangalia 33MW PP (Summit) | 30 | 30 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 33 |  | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 449600
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  | 15 | 16 | 12 | 14 | 18 | 18 | 18 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 359390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 31 | 31 | 28 | 28 | 10 | 10 | 10 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 639540
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 627400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 32 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 789400
73 | Ghorashal 108MW PP (Regent) | 106 | 82 | 22 | 22 | 22 | 22 | 22 | 81 | 95 | 102 | 102 | 102 | 106 | 102 | 102 | 99 | 102 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2021909
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [15 empty] | 11 | 26 | 26 |  | 55 | 40 | 8 |  |  |  |  | 183960
| Manikgonj 162MW PP(MPGL) | [16 empty] | 1 | 28 |  | 64 | 17 | [5 empty] | 120960
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 1 | 8 | 24 |  | 75 | 90 | 60 |  |  |  |  | 220800
78 | Gazipur 52 MW PP | [19 empty] | 7 | [6 empty] | 5592
79 | Kodda 150MW PP | [17 empty] | 16 |  | 64 | 10 | [5 empty] | 65280
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 8 | 24 | 24 | 24 | 24 | 27 | 51 | 56 | 56 | 64 | 62 |  | 70 | 81 | 81 | 81 | 81 | 81 |  | 852480
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 7 |  | 16 | [6 empty] | 25992
| Gazipur 100 MW PP | [8 empty] | 6 | 17 | 18 | 32 | 64 | 103 | 105 | 52 | 52 | 52 |  | 70 | 105 | 90 | 70 | 52 | 52 | 17 | 932652
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 28000
| Jodiac Power | [16 empty] | 0 | 17 |  | 29 | 34 | 34 | 34 | 34 | 17 |  | 180408
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 8 | 16 |  | 82 | 48 | 48 | 15 | 15 |  |  | 225384
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 7 | 30 | 30 | 30 | 30 | 45 |  | 72 | 72 | 73 | 84 | 60 |  |  | 518022
86 | Meghnaghat CCPP(Summit) | 235 | 230 | 230 | 230 | 230 | 230 | 230 | 235 | 240 | 235 | 245 | 245 | 240 | 240 | 240 | 235 | 235 | 240 |  | 235 | 240 | 235 | 235 | 235 | 235 | 235 | 5621033
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 18 |  | 54 | 50 | [5 empty] | 131520
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 2 | 17 | 17 | 17 | 17 | 22 |  | 88 | 90 | 90 | 90 | 82 | 53 | 28 | 535680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 40 | 40 | 40 | 40 | 10 |  |  | 129360
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 3 | 16 |  | 64 | 50 | 7 |  |  |  |  | 145008
95 | Patenga 50MW PP (Baraka) | 26 | 12 | [5 empty] | 4 | 25 | 25 | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 801600
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 11 |  | 22 | 42 | 42 | 42 | 15 |  |  | 154560
97 | katpotti 52 MW | [17 empty] | 5 |  | 11 | [6 empty] | 25584
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 10 | 15 | 15 | 30 | 30 | 30 | 30 | 30 |  | 55 | 55 | 55 | 55 | 30 | 15 |  | 441524
100 | Manikganj 55 MW PP (Northern) | [15 empty] | 17 | 17 | 33 |  | 55 | 55 | 17 |  |  |  | 0 | 148273
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 163 | 110 | 163 | 163 | 163 | 110 |  | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 3334581
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15450
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 17 | 54 | 54 | 54 | 54 | 35 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1139040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 70 | 35 | 35 | 35 | 25 | 25 | 31 | 150 | 150 | 150 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3564000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 118 | 103 | 100 | 100 | 98 | 85 | 105 | 116 | 123 | 132 | 131 | 131 | 128 | 130 | 126 | 127 | 119 | 123 |  | 132 | 131 | 130 | 131 | 131 | 131 | 131 | 2908800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | [11 empty] | 20 | 20 | 20 | 20 | 20 | 60 |  | 100 | 100 | 100 | 100 | 100 | 70 | 0 | 640320
116 | Chandpur 200MW (Desh energy) | 48 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 32 | 32 | 36 | 72 | 81 | 83 |  | 120 | 147 | 147 | 147 | 147 | 147 | 147 | 1525920
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 328 | 331 | 331 | 331 | 330 | 364 | 380 | 366 | 398 | 366 | 366 | 390 | 366 | 366 | 367 | 367 | 367 | 367 |  | 332 | 331 | 331 | 330 | 331 | 332 | 330 | 8504000
| Jamalpur 115 MW PP (United) | [14 empty] | 6 | 24 | 24 | 24 |  | 57 | 65 | 55 | 55 | 35 |  |  | 327600
| Anwara 300 MW PP (United) | 123 | 53 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 155 | 177 | 180 | 214 | 180 | 180 | 179 | 141 | 143 |  | 196 | 196 | 198 | 198 | 198 | 197 | 197 | 3131345
| Juldah unit-2 (Acorn) | 100 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 77 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1819200
| Anlima Energy Ltd. | [26 empty] | 0
Bhairob 54.5 MW
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 13 | 22 | 29 | 33 |  | 35 | 30 | 24 | 15 | 6 | [9 empty] | 226579
120 | Eastern Zone Total | 5527 | 5296 | 5215 | 5067 | 4917 | 5023 | 5255 | 5490 | 5660 | 5952 | 6180 | 6374 | 6479 | 6554 | 6589 | 6632 | 6421 | 6514 |  | 7673 | 7645 | 7419 | 7321 | 7126 | 6683 | 6335 | 149547479
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 49 | 49 | 49 | 16 | 16 |  |  | 158400
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 35 | 35 | 35 | 35 | 35 | 94 | 94 | 94 | 53 | 35 | 35 |  | 95 | 95 | 95 | 95 | 95 | 35 |  | 987840
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 94 | 91 | 95 | 95 | 94 | 94 | 97 | 95 | 95 | 94 | 93 | 93 | 92 | 92 | 92 | 92 | 86 | 84 |  | 86 | 92 | 94 | 93 | 81 | 84 | 94 | 2202982
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 48 | 64 | 64 | 32 | 16 |  |  | 205824
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 63 | 43 | 33 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 33 | 32 | 38 | 54 | 52 | 33 |  | 53 | 53 | 54 | 54 | 54 | 54 | 53 | 826126
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 26 | 20 | 19 | 18 | 18 | 17 | 15 | 14 | 19 | 19 | 20 | 21 | 21 | 23 | 22 | 23 | 22 | 23 |  | 25 | 24 | 26 | 27 | 27 | 28 | 28 | 509600
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 40 | 40 | 16 |  |  |  | 74625
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 10 |  | 13 | 12 | 11 |  |  |  |  | 25600
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 721 | 719 | 719 | 719 | 719 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 |  | 721 | 720 | 720 | 721 | 721 | 720 | 721 | 17407272
147 | Bheramara 410 MW CCPP | 355 | 355 | 300 | 300 | 350 | 350 | 350 | 350 | 350 | 420 | 415 | 410 | 410 | 410 | 410 | 405 | 300 | 300 |  | 350 | 370 | 370 | 370 | 370 | 360 | 355 | 9024192
148 | Payra 1320 MW | 450 | 450 | 420 | 420 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 410 | 450 | 450 | 480 | 520 | 550 | 520 | 10510800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 3669100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | [6 empty] | 34170
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 152 | 151 | 147 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 170 | 188 | 200 | 183 | 186 | 187 | 182 | 140 |  | 156 | 151 | 153 | 181 | 185 | 179 | 179 | 4151773
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 152 | 149 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 154 | 182 | 206 | 173 | 171 | 171 | 170 | 140 |  | 162 | 162 | 167 | 180 | 182 | 182 | 184 | 4193264
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 392 | 360 | 313 | 316 | 287 | 306 | 345 | 399 | 417 | 419 | 404 | 419 | 419 | 327 | 332 | 359 | 326 | 303 |  | 300 | 330 | 365 | 396 | 345 | 346 | 399 | 8740000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | [6 empty] | 22 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 18 | 18 | 22 | 22 | 21 | 22 | 22 | 328560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 8 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220140
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 42 | 42 | 42 |  |  |  |  | 107910
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 16 | [6 empty] | 12268
167 | Katakhali 50 MW Peaking PP | [19 empty] | 25 | [6 empty] | 16372
168 | Santahar 50 MW Peaking PP | [17 empty] | 8 |  | 30 | 30 | 26 |  |  |  |  | 47003
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 25 | 25 | 25 | 25 |  |  |  | 78720
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 20 |  | 101 | 84 | 45 |  |  |  |  | 145672
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 23 | 35 | 35 | 35 | 35 | 48 | 70 | 70 | 35 | 35 | 35 |  | 92 | 113 | 113 | 113 | 113 | 113 | 70 | 1176960
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 70 | 35 | 35 | 35 |  | 90 | 113 | 113 | 113 | 113 | 35 |  | 991680
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 4000
175 | Saidpur 20 MW GTPP | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 35 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 110 |  | 111 | 111 | 111 | 111 | 104 | 34 |  | 1329600
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 6 | 6 | 4 | 4 | 3 | 2 | 0 | [8 empty] | 39274
178
178