## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-23 | Tuesday
|  | Date (day): | 2021-03-23 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14307.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15203 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-22 | 2021-03-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 130 | 300 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 100 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 340 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 146 | 161 | 200 | 200 | 160 |  | Dirty fuel(Gas)
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 90 | 300 | 300 | 150 |  | Dirty fuel(Gas)
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 92 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 270 | 265 | 270 | 55 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 81 | 74 | 85 | 85 |  | 15 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 181 | 175 | 180 | 180
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 29 | 49 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 52 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 255 | 287 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 248 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 97 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 129 | 146 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 90 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 120 | 144 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 29 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 3064 | 3829 | 3838 | 4063 | 473 | 1345
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 22 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 45 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water lavel & Unit-5 Under maint.
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 10 | 15
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 14 | 91 | 102 | 102
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 125 | 196 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 861 | 1127 | 1634 | 1664 | 445 | 248
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 80 | 135 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 140 | 80 | 140 | 140
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 184 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 325 | 350 | 350
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 295 | 350 | 350
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 20 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 47 | 55 | 55
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 55 | 63 | 63 | 132 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 134 | 152 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 174 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 15 | 20 | 20 |  | 5 | Engine problem
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 0 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 73 | 113 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 37 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1710 | 1888 | 2060 | 2327 | 285 | 168
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 100 | 105 | 160 | 160 | 42 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 41 | 81 | 81 |  | 14 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 183 | 194 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 115 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 25 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 505 | 497 | 651.6 | 600 | 42 | 14
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 43 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 180 | 182 | 180 | 180 |  | 150 | Machine problem
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 34 | 0 | 0 |  | 66 | Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 78 | 81 | 81
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 248 | 222 | 250 | 250 |  | 150 | ST Under maint
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 9 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 340 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1559 | 1495 | 1609 | 1609 | 0 | 790
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 718 | 725 | 725
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 93 | 66 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 14 | 60 | 60 |  | 49 | Engine problem
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 275 | 280 | 350 | 350
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 33 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 94 | 90 | 95 |  | 10 | Engine problem
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1189 | 1301 | 1539 | 1830 | 0 | 104
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 31 | 25 | 25
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 66 | 68 | 70 | 70 |  | 124 | Under maintenance
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 100 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 530 | 620 | 620
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 3 | 25 | 90 | 90 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 636 | 818 | 1160 | 1160 | 0 | 124
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 17 | 50 | 0 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 0 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  |  | Engine problem
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 162 | 153 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 173 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 396 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 95 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1069 | 1347 | 1535 | 1677 | 381 | 0
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 269 | 263 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 10862 | 12565 | 14307.6 | 15203 | 1750 | 2993
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10260.3325 | 11869 | 13515.074 | 14360.876
A. |  | 2021-03-22 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 12565 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 9207 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12565 | MW
3 | Day peak Generation : |  |  | 10862 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11869 | MW
4 | Evening peak Generation : |  |  | 12565 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 255.7073 | MKWHr | By Solar | 0.7075 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 143.2656 | MKWHr |  | By Oil: | 73.3578 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.4509 | MKWHr |  | By Hydro: | 0.96 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1750 | MW | Dhaka | 4250 | 4250 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2993 | MW | Chittagong | 1263 | 1263 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4743 | MW | Khulna | 1438 | 1438 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1182.5 | MMCFD |  |  | Rajshahi | 1260 | 1260 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 154273253.982 | ii) Oil : | Taka | 548765784.86 | Comilla | 1113 | 1113 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 75998624 | Total | Taka | 779037662.842 | Mymensingh | 989 | 989 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.9985 | MKWHr. | Sylhet | 455 | 455 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -122 | MW (E to W) at | 19:30 | hrs | Barisal | 323 | 323 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -132 | MW at | 20:00 | hrs | Rangpur | 778 | 778 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.8° C |  |  | Total | 11869 | 11869 |  | 0
B. |  | 2021-03-23 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 38.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15203 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
4 | Reserve(Generation end) |  |  |  | 2403 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 260.4897 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9127 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3818 | MKWHr. | ii) HVDC Flow at Peak Time |  | 718 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5837 | MKWHr. | iii) Maximum HVDC Flow : |  | 719 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.53 |  | (b) Today: | 87.41 |  | (c) Rule Curve: |  | 89.48
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 240 | 99 | 0 | 339 | 235 |  | 0 | 0 | 265 | 7 | 48 | 55 | 94 | 0 | 155 | 70 | 7 | 32 | 85 | 0 | 0 | 6 | 54 | 17 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 8 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 57 | 46 | 20 | 38 | 135 | 140 | 0 | 310 | 300 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 150 | 104 | 72 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 180 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 287 | 0 | 0 | 184 | 0 | 145 | 0 | 100 | 179 | 0 | 331 | 16 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 55 | 100 | 341 | 104 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 285 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 94 | 0 | 173 | 0 | 375 | 95 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 7283 | 3126 | 10409 | 4493 | 719 | 1581 | 2694 | 700 | 40 | 32 | 150 | 0 | 0 | 87.55
2:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 339 | 246 |  | 0 | 0 | 265 | 0 | 15 | 15 | 94 | 0 | 155 | 20 | 0 | 16 | 85 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 46 | 20 | 38 | 135 | 140 | 0 | 310 | 300 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 144 | 104 | 72 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 179 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 287 | 0 | 0 | 200 | 0 | 143 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 340 | 104 | 0 | 0 | 0 | 0 | 0 | 0 |  | 718 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 93 | 0 | 179 | 0 | 401 | 95 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 6986 | 3081 | 10067 | 4509 | 718 | 1618 | 2322 | 700 | 40 | 16 | 144 | 0 | 0 | 87.55
3:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 344 | 250 |  | 0 | 0 | 265 | 0 | 0 | 0 | 94 | 0 | 150 | 0 | 0 | 16 | 10 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 38 | 135 | 140 | 0 | 320 | 305 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 134 | 109 | 34 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 180 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 287 | 0 | 0 | 160 | 0 | 144 | 0 | 10 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 370 | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 93 | 0 | 184 | 0 | 401 | 53 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 0 |  | 6662 | 3030 | 9692 | 4577 | 719 | 1632 | 1884 | 690 | 40 | 16 | 134 | 0 | 0 | 87.54
4:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 344 | 260 |  | 0 | 0 | 265 | 0 | 0 | 0 | 94 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 38 | 135 | 140 | 0 | 325 | 310 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 130 | 156 | 24 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 181 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 195 | 0 | 0 | 160 | 0 | 144 | 0 | 0 | 200 | 0 | 333 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 160 | 0 | 91 | 0 | 185 | 0 | 400 | 35 | 0 | 94 | 0 | 34 | 0 | 0 | 35 | 510 | 0 | 0 | 0 |  | 6555 | 2827 | 9382 | 4647 | 719 | 1638 | 1547 | 661 | 40 | 0 | 130 | 0 | 0 | 87.54
5:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 342 | 281 |  | 0 | 0 | 265 | 0 | 0 | 0 | 93 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 38 | 135 | 140 | 0 | 295 | 310 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 157 | 8 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 180 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 195 | 0 | 0 | 160 | 0 | 144 | 0 | 0 | 200 | 0 | 338 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 91 | 0 | 190 | 0 | 399 | 35 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 480 | 0 | 0 | 0 |  | 6475 | 2775 | 9250 | 4588 | 719 | 1662 | 1485 | 630 | 40 | 0 | 126 | 0 | 0 | 87.53
6:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 354 | 262 |  | 0 | 0 | 265 | 0 | 0 | 0 | 93 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 40 | 135 | 140 | 0 | 270 | 300 | 213 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 160 | 8 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 181 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 320 | 16 | 11 | 0 | 195 | 0 | 0 | 175 | 0 | 144 | 0 | 0 | 200 | 0 | 330 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 91 | 0 | 190 | 0 | 399 | 35 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 480 | 0 | 0 | 0 |  | 6421 | 2786 | 9207 | 4541 | 719 | 1650 | 1501 | 630 | 40 | 0 | 126 | 0 | 0 | 87.53
7:00 | 0 | 0 | 0 | 190 | 240 | 100 | 0 | 359 | 230 |  | 0 | 0 | 265 | 0 | 0 | 0 | 94 | 0 | 118 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 34 | 135 | 140 | 0 | 280 | 305 | 214 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 158 | 10 | 17 | 0 | 44 | 42 | 53 | 0 | 130 | 179 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 144 | 3 | 0 | 200 | 0 | 333 | 7 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 0 | 100 | 370 | 0 | 5 | 0 | 0 | 0 | 0 | 3 |  | 719 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 93 | 0 | 190 | 0 | 400 | 35 | 0 | 75 | 0 | 62 | 0 | 1 | 50 | 460 | 0 | 0 | 0 |  | 6494 | 2819 | 9313 | 4622 | 719 | 1599 | 1584 | 610 | 40 | 0 | 126 | 13 | 0 | 87.52
8:00 | 0 | 0 | 0 | 190 | 240 | 97 | 0 | 347 | 200 |  | 0 | 0 | 265 | 0 | 0 | 3 | 95 | 0 | 118 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 231 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 24 | 20 | 4 | 135 | 140 | 0 | 280 | 300 | 215 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 0 | 128 | 156 | 24 | 17 | 1 | 44 | 42 | 53 | 0 | 163 | 180 | 34 | 81 | 0 | 0 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 144 | 4 | 0 | 200 | 0 | 361 | 65 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 0 | 100 | 370 | 16 | 16 | 0 | 0 | 0 | 0 | 10 |  | 719 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 93 | 0 | 190 | 0 | 400 | 95 | 0 | 94 | 0 | 90 | 0 | 2 | 100 | 430 | 0 | 0 | 0 |  | 6598 | 2939 | 9537 | 4607 | 719 | 1568 | 1861 | 580 | 40 | 0 | 128 | 34 | 0 | 87.52
9:00 | 0 | 0 | 0 | 190 | 240 | 96 | 0 | 366 | 181 |  | 0 | 0 | 270 | 13 | 0 | 30 | 93 | 0 | 190 | 7 | 24 | 25 | 52 | 0 | 0 | 0 | 54 | 17 | 20 | 22 | 25 | 25 | 25 | 33 | 20 | 0 | 0 | 40 | 105 | 0 | 0 | 230 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 32 | 20 | 2 | 135 | 140 | 0 | 270 | 300 | 216 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 0 | 120 | 136 | 24 | 17 | 1 | 44 | 42 | 50 | 0 | 163 | 182 | 34 | 78 | 0 | 0 | 18 | 0 | 9 | 320 | 16 | 11 | 0 | 218 | 0 | 0 | 195 | 0 | 144 | 8 | 30 | 200 | 0 | 75 | 103 | 20 | 0 | 2 | 124 | 0 | 0 | 0 | 21 | 100 | 340 | 63 | 27 | 4 | 0 | 0 | 0 | 18 |  | 719 | 0 | 295 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 93 | 0 | 204 | 0 | 361 | 95 | 0 | 94 | 0 | 105 | 0 | 3 | 113 | 410 | 4 | 0 | 0 |  | 6684 | 2988 | 9672 | 4354 | 719 | 1514 | 2281 | 560 | 40 | 25 | 120 | 59 | 0 | 87.51
10:00 | 0 | 0 | 0 | 190 | 180 | 92 | 0 | 343 | 161 |  | 0 | 0 | 270 | 65 | 30 | 55 | 93 | 0 | 150 | 70 | 48 | 32 | 73 | 0 | 0 | 4 | 54 | 35 | 55 | 22 | 25 | 25 | 25 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 40 | 20 | 2 | 135 | 140 | 0 | 295 | 320 | 195 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 120 | 102 | 24 | 17 | 2 | 43 | 42 | 50 | 0 | 163 | 180 | 34 | 78 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 265 | 0 | 0 | 195 | 0 | 144 | 12 | 45 | 150 | 0 | 242 | 109 | 90 | 0 | 4 | 88 | 0 | 0 | 0 | 26 | 100 | 370 | 104 | 36 | 98 | 0 | 0 | 0 | 23 |  | 719 | 0 | 290 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 92 | 0 | 196 | 0 | 337 | 94 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 410 | 3 | 0 | 0 |  | 7253 | 3009 | 10262 | 4440 | 719 | 1443 | 2827 | 559 | 40 | 32 | 120 | 82 | 0 | 87.51
11:00 | 0 | 0 | 0 | 190 | 122 | 92 | 0 | 366 | 146 |  | 0 | 0 | 265 | 73 | 70 | 55 | 0 | 0 | 190 | 100 | 64 | 64 | 78 | 0 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 1 | 223 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 2 | 43 | 20 | 2 | 135 | 140 | 0 | 350 | 300 | 183 | 63 | 0 | 20 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 140 | 100 | 24 | 17 | 2 | 43 | 42 | 48 | 0 | 163 | 182 | 34 | 77 | 0 | 0 | 18 | 0 | 8 | 320 | 16 | 11 | 0 | 258 | 0 | 0 | 194 | 0 | 144 | 15 | 100 | 125 | 0 | 222 | 98 | 90 | 0 | 4 | 141 | 0 | 0 | 0 | 31 | 100 | 363 | 104 | 39 | 111 | 0 | 0 | 0 | 29 |  | 719 | 0 | 285 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 92 | 0 | 195 | 0 | 404 | 94 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 440 | 3 | 0 | 0 |  | 7458 | 3129 | 10587 | 4324 | 719 | 1514 | 3102 | 589 | 40 | 64 | 140 | 95 | 0 | 87.5
12:00 | 0 | 0 | 0 | 190 | 130 | 92 | 0 | 355 | 146 |  | 0 | 0 | 265 | 92 | 97 | 55 | 0 | 0 | 181 | 100 | 84 | 98 | 81 | 0 | 0 | 29 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 22 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 14 | 44 | 20 | 2 | 135 | 140 | 0 | 340 | 325 | 197 | 63 | 0 | 20 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 146 | 100 | 24 | 17 | 2 | 41 | 42 | 53 | 0 | 163 | 180 | 20 | 79 | 0 | 0 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 255 | 0 | 0 | 183 | 0 | 129 | 16 | 100 | 134 | 0 | 248 | 109 | 90 | 0 | 5 | 125 | 0 | 0 | 0 | 73 | 100 | 370 | 104 | 46 | 120 | 0 | 0 | 0 | 29 |  | 719 | 0 | 275 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 26 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 91 | 0 | 191 | 0 | 414 | 94 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 450 | 3 | 0 | 0 |  | 7699 | 3163 | 10862 | 4331 | 719 | 1522 | 3285 | 600 | 40 | 115 | 146 | 104 | 0 | 87.5
13:00 | 0 | 0 | 0 | 190 | 130 | 94 | 0 | 357 | 141 |  | 0 | 0 | 265 | 92 | 95 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 74 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 33 | 50 | 0 | 0 | 40 | 105 | 0 | 25 | 223 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 44 | 43 | 21 | 6 | 135 | 140 | 0 | 310 | 300 | 182 | 63 | 0 | 20 | 52 | 0 | 0 | 0 | 0 | 22 | 19 | 11 | 33 | 20 | 148 | 100 | 24 | 17 | 2 | 41 | 42 | 53 | 0 | 163 | 182 | 33 | 79 | 0 | 0 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 253 | 0 | 0 | 182 | 0 | 126 | 14 | 100 | 143 | 0 | 221 | 109 | 90 | 0 | 4 | 124 | 0 | 0 | 0 | 107 | 100 | 340 | 104 | 44 | 141 | 0 | 0 | 0 | 28 |  | 719 | 0 | 265 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 56 | 0 | 50 | 0 | 52 | 20 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 92 | 0 | 184 | 0 | 413 | 93 | 0 | 94 | 0 | 106 | 0 | 6 | 113 | 470 | 3 | 0 | 0 |  | 7804 | 3303 | 11107 | 4191 | 719 | 1520 | 3495 | 620 | 40 | 276 | 148 | 98 | 11107 | 87.49
14:00 | 0 | 0 | 0 | 190 | 130 | 95 | 0 | 362 | 141 |  | 0 | 0 | 265 | 95 | 95 | 55 | 0 | 0 | 115 | 100 | 102 | 150 | 84 | 0 | 0 | 50 | 54 | 55 | 55 | 17 | 25 | 23 | 25 | 33 | 50 | 0 | 0 | 40 | 105 | 0 | 25 | 217 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 63 | 43 | 21 | 4 | 135 | 140 | 0 | 260 | 265 | 185 | 63 | 0 | 20 | 52 | 0 | 0 | 0 | 0 | 36 | 19 | 11 | 33 | 20 | 160 | 101 | 24 | 17 | 2 | 41 | 42 | 53 | 0 | 110 | 182 | 33 | 79 | 0 | 0 | 16 | 0 | 8 | 310 | 16 | 11 | 0 | 253 | 0 | 0 | 189 | 0 | 123 | 13 | 100 | 143 | 0 | 249 | 109 | 90 | 0 | 3 | 104 | 0 | 0 | 17 | 111 | 100 | 370 | 104 | 40 | 144 | 0 | 0 | 0 | 26 |  | 719 | 0 | 265 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 25 | 16 | 0 | 0 | 0 | 50 | 0 | 58 | 0 | 50 | 0 | 52 | 20 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 93 | 0 | 176 | 0 | 338 | 94 | 0 | 94 | 0 | 106 | 0 | 5 | 113 | 480 | 4 | 0 | 0 |  | 7730 | 3239 | 10969 | 4091 | 719 | 1392 | 3570 | 630 | 40 | 278 | 160 | 89 | 0 | 87.49
15:00 | 0 | 0 | 0 | 190 | 130 | 93 | 0 | 374 | 151 |  | 0 | 0 | 270 | 100 | 95 | 55 | 0 | 0 | 150 | 100 | 102 | 150 | 80 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 32 | 49 | 0 | 0 | 40 | 105 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 0 | 34 | 67 | 60 | 43 | 20 | 2 | 135 | 140 | 0 | 295 | 285 | 196 | 68 | 0 | 20 | 52 | 0 | 0 | 0 | 0 | 43 | 16 | 11 | 33 | 20 | 160 | 101 | 24 | 17 | 2 | 40 | 42 | 53 | 0 | 110 | 178 | 20 | 78 | 0 | 0 | 16 | 0 | 8 | 320 | 8 | 11 | 0 | 253 | 0 | 0 | 190 | 0 | 126 | 11 | 100 | 143 | 0 | 232 | 109 | 90 | 0 | 3 | 107 | 0 | 0 | 17 | 110 | 100 | 370 | 104 | 30 | 144 | 0 | 0 | 0 | 21 |  | 719 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 25 | 16 | 0 | 0 | 0 | 50 | 0 | 75 | 0 | 43 | 0 | 52 | 20 | 16 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 92 | 0 | 176 | 0 | 339 | 94 | 0 | 94 | 0 | 102 | 0 | 4 | 113 | 480 | 25 | 0 | 0 |  | 7830 | 3253 | 11083 | 4156 | 719 | 1432 | 3546 | 630 | 40 | 329 | 160 | 71 | 0 | 87.48
16:00 | 0 | 0 | 0 | 190 | 240 | 93 | 0 | 375 | 157 |  | 0 | 0 | 265 | 100 | 95 | 55 | 0 | 0 | 174 | 100 | 102 | 150 | 83 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 26 | 25 | 32 | 49 | 0 | 0 | 40 | 105 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 0 | 34 | 65 | 60 | 42 | 20 | 2 | 80 | 100 | 0 | 300 | 305 | 125 | 55 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 43 | 17 | 11 | 33 | 20 | 154 | 98 | 24 | 17 | 1 | 41 | 42 | 53 | 0 | 163 | 180 | 32 | 78 | 0 | 0 | 16 | 0 | 8 | 320 | 8 | 11 | 0 | 245 | 0 | 0 | 191 | 0 | 128 | 6 | 100 | 143 | 0 | 245 | 109 | 90 | 0 | 2 | 159 | 0 | 0 | 17 | 111 | 90 | 370 | 104 | 20 | 144 | 0 | 0 | 0 | 13 |  | 719 | 0 | 260 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 21 | 16 | 0 | 0 | 0 | 50 | 0 | 75 | 0 | 43 | 0 | 52 | 17 | 16 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 93 | 0 | 152 | 0 | 412 | 94 | 0 | 94 | 0 | 102 | 0 | 3 | 113 | 480 | 26 | 0 | 0 |  | 7837 | 3314 | 11151 | 4152 | 719 | 1507 | 3578 | 630 | 40 | 326 | 154 | 45 | 0 | 87.48
17:00 | 0 | 0 | 0 | 190 | 300 | 98 | 0 | 349 | 166 |  | 0 | 0 | 265 | 100 | 95 | 55 | 0 | 0 | 174 | 100 | 102 | 150 | 82 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 32 | 8 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 23 | 0 | 34 | 40 | 60 | 42 | 21 | 2 | 80 | 80 | 0 | 275 | 260 | 163 | 55 | 0 | 5 | 10 | 0 | 0 | 0 | 0 | 36 | 18 | 11 | 33 | 10 | 136 | 102 | 24 | 17 | 0 | 42 | 42 | 53 | 0 | 163 | 182 | 33 | 77 | 0 | 0 | 17 | 0 | 8 | 295 | 8 | 11 | 0 | 240 | 0 | 0 | 191 | 0 | 122 | 0 | 100 | 143 | 0 | 222 | 109 | 90 | 0 | 0 | 162 | 0 | 0 | 17 | 110 | 100 | 340 | 104 | 8 | 108 | 0 | 0 | 0 | 5 |  | 718 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 0 | 6 | 8 | 62 | 24 | 16 | 0 | 0 | 0 | 50 | 0 | 74 | 0 | 43 | 0 | 52 | 17 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 96 | 0 | 158 | 0 | 391 | 94 | 0 | 94 | 0 | 107 | 0 | 2 | 113 | 440 | 25 | 0 | 0 |  | 7590 | 3241 | 10831 | 4060 | 718 | 1481 | 3460 | 590 | 40 | 331 | 136 | 15 | 0 | 87.47
18:00 | 0 | 0 | 0 | 190 | 300 | 95 | 0 | 300 | 182 |  | 0 | 25 | 270 | 100 | 96 | 55 | 0 | 0 | 68 | 100 | 102 | 150 | 76 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 32 | 8 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 61 | 10 | 61 | 43 | 21 | 4 | 80 | 80 | 0 | 280 | 265 | 183 | 55 | 0 | 20 | 10 | 0 | 0 | 0 | 9 | 16 | 19 | 11 | 33 | 20 | 152 | 102 | 24 | 17 | 0 | 43 | 42 | 25 | 0 | 163 | 180 | 20 | 40 | 0 | 0 | 17 | 0 | 8 | 285 | 16 | 11 | 0 | 250 | 0 | 0 | 190 | 0 | 112 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 161 | 0 | 0 | 17 | 111 | 100 | 370 | 104 | 0 | 108 | 0 | 0 | 0 | 0 |  | 719 | 0 | 270 | 0 | 66 | 0 | 0 | 0 | 0 | 12 | 8 | 68 | 27 | 16 | 0 | 0 | 0 | 50 | 5 | 95 | 0 | 43 | 5 | 52 | 20 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 100 | 0 | 164 | 0 | 352 | 94 | 0 | 94 | 0 | 112 | 0 | 0 | 113 | 440 | 26 | 0 | 0 |  | 7485 | 3277 | 10762 | 4006 | 719 | 1417 | 3431 | 590 | 40 | 407 | 152 | 0 | 0 | 87.47
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 300 | 95 | 0 | 328 | 172 |  | 0 | 40 | 270 | 100 | 96 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 74 | 0 | 0 | 49 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 30 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 25 | 0 | 85 | 100 | 87 | 43 | 21 | 12 | 80 | 80 | 0 | 325 | 295 | 185 | 55 | 0 | 20 | 25 | 0 | 0 | 0 | 42 | 32 | 19 | 11 | 33 | 18 | 176 | 104 | 41 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 184 | 34 | 78 | 0 | 0 | 17 | 0 | 8 | 315 | 16 | 11 | 50 | 287 | 283 | 25 | 194 | 95 | 122 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 196 | 0 | 0 | 114 | 113 | 100 | 355 | 104 | 0 | 130 | 0 | 0 | 29 | 0 |  | 718 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 15 | 33 | 68 | 30 | 70 | 0 | 0 | 0 | 50 | 7 | 100 | 0 | 43 | 30 | 52 | 24 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 43 | 168 | 0 | 419 | 94 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 490 | 26 | 0 | 0 |  | 8753 | 3628 | 12381 | 4248 | 718 | 1613 | 4443 | 640 | 40 | 503 | 176 | 0 | 0 | 87.45
19:30 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 340 | 161 |  | 0 | 90 | 270 | 100 | 97 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 74 | 0 | 0 | 49 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 25 | 204 | 0 | 0 | 0 |  | 25 | 0 | 85 | 100 | 91 | 45 | 21 | 15 | 80 | 80 | 0 | 325 | 295 | 184 | 55 | 0 | 20 | 47 | 0 | 0 | 0 | 42 | 43 | 19 | 10 | 33 | 15 | 174 | 105 | 41 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 182 | 34 | 78 | 0 | 0 | 17 | 0 | 9 | 285 | 16 | 11 | 50 | 287 | 248 | 25 | 194 | 97 | 146 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 196 | 0 | 0 | 114 | 113 | 100 | 340 | 104 | 0 | 144 | 0 | 0 | 37 | 0 |  | 718 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 14 | 33 | 68 | 31 | 64 | 0 | 0 | 0 | 50 | 32 | 100 | 0 | 43 | 32 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 100 | 96 | 173 | 0 | 396 | 94 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 25 | 0 | 0 |  | 8836 | 3729 | 12565 | 4250 | 718 | 1630 | 4542 | 680 | 40 | 531 | 174 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 340 | 151 |  | 0 | 140 | 270 | 100 | 97 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 80 | 0 | 0 | 49 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 91 | 44 | 21 | 23 | 80 | 80 | 0 | 325 | 295 | 172 | 55 | 0 | 20 | 47 | 0 | 0 | 0 | 42 | 43 | 19 | 10 | 33 | 18 | 174 | 107 | 41 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 181 | 35 | 80 | 0 | 0 | 17 | 0 | 9 | 290 | 16 | 11 | 50 | 293 | 135 | 25 | 194 | 100 | 146 | 0 | 100 | 152 | 0 | 221 | 115 | 90 | 0 | 0 | 197 | 0 | 0 | 114 | 113 | 100 | 340 | 104 | 0 | 144 | 0 | 0 | 36 | 0 |  | 718 | 0 | 290 | 0 | 66 | 0 | 0 | 0 | 0 | 14 | 33 | 68 | 32 | 48 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 43 | 32 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 97 | 96 | 173 | 0 | 399 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 25 | 0 | 0 |  | 8782 | 3681 | 12463 | 4255 | 718 | 1686 | 4376 | 680 | 40 | 534 | 174 | 0 | 0 | 87.46
21:00 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 340 | 141 |  | 0 | 225 | 270 | 100 | 97 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 83 | 0 | 0 | 49 | 54 | 55 | 50 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 25 | 0 | 85 | 100 | 91 | 44 | 21 | 30 | 80 | 80 | 0 | 275 | 260 | 210 | 8 | 0 | 5 | 53 | 0 | 0 | 0 | 42 | 43 | 19 | 10 | 33 | 20 | 174 | 107 | 41 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 189 | 35 | 81 | 0 | 0 | 17 | 0 | 9 | 285 | 16 | 11 | 20 | 278 | 0 | 0 | 194 | 27 | 149 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 197 | 0 | 0 | 114 | 113 | 100 | 340 | 104 | 0 | 144 | 0 | 0 | 36 | 0 |  | 718 | 0 | 305 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 33 | 66 | 30 | 48 | 0 | 0 | 0 | 50 | 17 | 98 | 0 | 43 | 32 | 52 | 20 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 99 | 70 | 173 | 0 | 386 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 560 | 26 | 0 | 0 |  | 8513 | 3658 | 12171 | 4230 | 718 | 1711 | 4094 | 710 | 40 | 494 | 174 | 0 | 0 | 87.45
22:00 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 340 | 130 |  | 0 | 225 | 270 | 100 | 97 | 55 | 0 | 0 | 145 | 100 | 102 | 150 | 80 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 25 | 204 | 0 | 0 | 0 |  | 25 | 0 | 85 | 100 | 91 | 45 | 21 | 35 | 100 | 100 | 0 | 275 | 260 | 180 | 8 | 0 | 10 | 55 | 0 | 0 | 0 | 0 | 43 | 19 | 10 | 33 | 20 | 172 | 107 | 41 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 180 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 291 | 0 | 0 | 194 | 0 | 145 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 197 | 0 | 0 | 67 | 113 | 100 | 340 | 104 | 0 | 144 | 0 | 0 | 36 | 0 |  | 718 | 0 | 325 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 33 | 66 | 31 | 48 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 96 | 30 | 176 | 0 | 405 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 26 | 0 | 0 |  | 8358 | 3582 | 11940 | 4240 | 718 | 1719 | 3929 | 720 | 40 | 402 | 172 | 0 | 0 | 87.45
23:00 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 339 | 130 |  | 0 | 225 | 270 | 70 | 97 | 55 | 0 | 0 | 145 | 100 | 48 | 150 | 70 | 0 | 0 | 49 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 25 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 60 | 91 | 45 | 21 | 38 | 100 | 100 | 0 | 275 | 265 | 180 | 8 | 0 | 10 | 54 | 0 | 0 | 0 | 0 | 25 | 19 | 10 | 33 | 20 | 168 | 108 | 41 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 177 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 293 | 0 | 0 | 194 | 0 | 148 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 196 | 0 | 0 | 0 | 113 | 100 | 370 | 104 | 0 | 54 | 0 | 0 | 36 | 0 |  | 718 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 33 | 62 | 31 | 48 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 25 | 20 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 97 | 30 | 184 | 0 | 386 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 8038 | 3429 | 11467 | 4265 | 718 | 1682 | 3570 | 720 | 40 | 304 | 168 | 0 | 0 | 87.44
24:00 | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 339 | 150 |  | 0 | 250 | 270 | 22 | 97 | 55 | 0 | 0 | 150 | 100 | 7 | 150 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 40 | 105 | 0 | 25 | 203 | 0 | 0 | 0 |  | 0 | 0 | 85 | 10 | 71 | 45 | 21 | 38 | 100 | 100 | 0 | 275 | 265 | 174 | 8 | 0 | 10 | 55 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 164 | 110 | 41 | 17 | 0 | 44 | 42 | 53 | 0 | 163 | 180 | 35 | 81 | 0 | 0 | 18 | 0 | 9 | 280 | 8 | 11 | 0 | 291 | 0 | 0 | 194 | 0 | 148 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 197 | 0 | 0 | 0 | 113 | 100 | 371 | 104 | 0 | 0 | 0 | 0 | 27 | 0 |  | 718 | 0 | 365 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 24 | 66 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 97 | 0 | 200 | 0 | 389 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 0 |  | 7743 | 3386 | 11129 | 4329 | 718 | 1725 | 3155 | 700 | 40 | 298 | 164 | 0 | 0 | 87.44
KWH | 0 | 0 | 0 | 4536000 | 5507836 | 2192318 | 0 | 8473600 | 4472000 |  | 0 | 872450 | 6355695 | 1350720 | 1510704 | 973543 | 1071800 | 0 | 3863000 | 1620480 | 1337328 | 2008800 | 1491937 | 0 | 0 | 631872 | 1311840 | 841546 | 850753 | 449496 | 600000 | 609840 | 639100 | 802700 | 615840 | 0 | 0 | 960000 | 2500000 | 0 | 352002 | 5046075 | 0 | 0 | 0 |  | 439440 | 0 | 642460 | 928200 | 956160 | 977760 | 495120 | 469920 | 2886712 | 2886712 | 0 | 7488800 | 7186000 | 4714000 | 1354909 | 0 | 387072 | 1183680 | 0 | 0 | 0 | 124032 | 406421 | 431928 | 245340 | 816800 | 435810 | 3583680 | 2702360 | 754560 | 339552 | 15000 | 1013000 | 988800 | 1235400 | 0 | 3609327 | 4011000 | 773472 | 1868160 | 0 | 0 | 414000 | 0 | 196740 | 7485500 | 334992 | 264000 | 127104 | 6134725 | 411069 | 59391 | 4500000 | 231687 | 3326400 | 101250 | 1704000 | 3992160 | 0 | 6323000 | 1938000 | 1412400 | 0 | 28108 | 3733 | 0 | 0 | 492480 | 1680000 | 2425920 | 8624600 | 1993920 | 314730 | 1857600 | 0 | 0 | 204480 | 207521 |  | 17381818 | 0 | 7172352 | 0 | 1237440 | 0 | 0 | 0 | 0 | 37760 | 226125 | 1480300 | 607175 | 442848 | 0 | 0 | 0 | 565003 | 67642 | 888328 | 12660 | 375289 | 93405 | 749760 | 219762 | 457200 | 0 | 194706 | 0 | 0 | 3669100 | 0 | 0 | 0 | 0 | 4094209 | 0 | 2262883 | 330240 | 4601600 | 0 | 9336327 | 2028480 | 85811 | 2230752 | 0 | 2350080 | 0 | 40893 | 2439264 | 12781800 | 255927 | 0 | 0 |  | 176990372 | 78716939 | 255707311 | 105405684 | 17381818 | 37859916 | 68710619 | 16450900 | 960000 | 4647192 | 3583680 | 707502 | 0
Fuel Cost | 0 | 0 | 0 | 6667920 | 6113697.96 | 2893859.76 | 0 | 8558336 | 4606160 |  | 0 | 950970.5 | 7054821.45 | 10251964.8 | 10408750.56 | 8236173.78 | 1114672 | 0 | 6682990 | 12202214.4 | 12196431.36 | 19766592 | 13755659.14 | 0 | 0 | 5743716.48 | 9576432 | 6505150.58 | 8388424.58 | 337122 | 450000 | 0 | 0 | 0 | 5955172.8 | 0 | 0 | 259200 | 4525000 | 0 | 3270098.58 | 5500221.75 | 0 | 0 | 0 |  | 0 | 0 | 6231862 | 8864310 | 8318592 | 7743859.2 | 623851.2 | 1395662.4 | 4272333.76 | 4272333.76 | 0 | 5541712 | 7186000 | 4336880 | 1747832.61 | 0 | 437391.36 | 1657152 | 0 | 0 | 0 | 1252723.2 | 3881320.55 | 548548.56 | 184005 | 1429400 | 326857.5 | 26877600 | 2864501.6 | 6851404.8 | 431231.04 | 239100 | 1661320 | 1582080 | 2199012 | 0 | 4114632.78 | 4171440 | 1523739.84 | 3568185.6 | 0 | 0 | 906660 | 0 | 401349.6 | 7560355 | 251244 | 200640 | 2162039.04 | 46378521 | 6979951.62 | 993017.52 | 23400000 | 3873806.64 | 32731776 | 1183612.5 | 13887600 | 43314936 | 0 | 5880390 | 17674560 | 13347180 | 0 | 0 | 28221.48 | 0 | 0 | 4914950.4 | 14397600 | 16156627.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100119271.68 | 0 | 7530969.6 | 0 | 9726278.4 | 0 | 0 | 0 | 0 | 395724.8 | 2356222.5 | 1672739 | 941121.25 | 4322196.48 | 0 | 0 | 0 | 5559629.52 | 687242.72 | 7861702.8 | 97482 | 5073907.28 | 905094.45 | 7265174.4 | 2131691.4 | 877824 | 0 | 147392.442 | 0 | 0 | 19886522 | 0 | 0 | 0 | 0 | 5404355.88 | 0 | 3394324.5 | 5617382.4 | 5383872 | 0 | 9242963.73 | 21177331.2 | 1459645.11 | 21169836.48 | 0 | 18236620.8 | 0 | 451867.65 | 18026160.96 | 56112102 | 0 | 0 | 0 |  | 564933665.24 | 343234649.432 | 908168314.672 | 108721848.252 | 100119271.68 | 45551405.73 | 503973521.97 | 75998624 | 259200 | 44792262.89 | 26877600 | 1874580.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 130 | 92 | 0 | 355 | 146 |  | 0 | 0 | 265 | 92 | 97 | 55 | 0 | 0 | 181 | 100 | 84 | 98 | 81 | 0 | 0 | 29 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 22 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 14 | 44 | 20 | 2 | 135 | 140 | 0 | 340 | 325 | 197 | 63 | 0 | 20 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 146 | 100 | 24 | 17 | 2 | 41 | 42 | 53 | 0 | 163 | 180 | 20 | 79 | 0 | 0 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 255 | 0 | 0 | 183 | 0 | 129 | 16 | 100 | 134 | 0 | 248 | 109 | 90 | 0 | 5 | 125 | 0 | 0 | 0 | 73 | 100 | 370 | 104 | 46 | 120 | 0 | 0 | 0 | 29 |  | 719 | 0 | 275 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 26 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 91 | 0 | 191 | 0 | 414 | 94 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 450 | 3 | 0 | 0 |  | 10862 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 300 | 100 | 0 | 340 | 161 | 0 | 0 | 90 | 270 | 100 | 97 | 55 | 0 | 0 | 175 | 100 | 102 | 150 | 74 | 0 | 0 | 49 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 0 | 40 | 105 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 25 | 0 | 85 | 100 | 91 | 45 | 21 | 15 | 80 | 80 | 0 | 325 | 295 | 184 | 55 | 0 | 20 | 47 | 0 | 0 | 0 | 42 | 43 | 19 | 10 | 33 | 15 | 174 | 105 | 41 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 182 | 34 | 78 | 0 | 0 | 17 | 0 | 9 | 285 | 16 | 11 | 50 | 287 | 248 | 25 | 194 | 97 | 146 | 0 | 100 | 152 | 0 | 222 | 115 | 90 | 0 | 0 | 196 | 0 | 0 | 114 | 113 | 100 | 340 | 104 | 0 | 144 | 0 | 0 | 37 | 0 |  | 718 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 14 | 33 | 68 | 31 | 64 | 0 | 0 | 0 | 50 | 32 | 100 | 0 | 43 | 32 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 100 | 96 | 173 | 0 | 396 | 94 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 25 | 0 | 0 |  | 12565 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 200 | 0 | 0 | 300 | 270 | 100 | 100 | 55 | 0 | 0 | 180 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 40 | 105 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 20 | 15 | 135 | 140 | 0 | 350 | 350 | 225 | 63 | 0 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 160 | 81 | 22 | 0 | 44 | 42 | 51 | 0 | 163 | 180 | 0 | 81 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 250 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 0 |  |  | 725 | 16 | 350 | 0 | 99 | 220 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 90 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 108 | 0 | 412 | 200 | 0 | 0 | 300 | 265 | 100 | 100 | 55 | 0 | 0 | 180 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 40 | 105 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 102 | 50 | 20 | 10 | 135 | 140 | 0 | 350 | 350 | 225 | 63 | 0 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 160 | 81 | 22 | 1.6 | 44 | 42 | 51 | 0 | 163 | 180 | 0 | 81 | 0 | 0 | 20 | 0 | 10 | 341 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 250 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 0 | 30 |  | 725 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 42 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 95 | 100 | 113 | 0 | 8 | 113 | 620 | 90 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 340 | 111 | 0 | 0 | 300 | 240 | 0 | 15 | 36 | 0 | 0 | 180 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 28 |  | 0 | 0 | 0 | 40 | 105 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 39 | 21 | 8 | 80 | 80 | 0 | 325 | 265 | 191 | 8 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 118 | 160 | 24 | 17 | 1 | 44 | 42 | 53 | 0 | 163 | 180 | 0 | 81 | 0 | 0 | 18 | 0 | 7 | 320 | 8 | 11 | 0 | 233 | 0 | 0 | 194 | 0 | 125 | 6 | 50 | 141 | 0 | 246 | 36 | 52 | 0 | 2 | 179 | 0 | 0 | 0 | 0 | 100 | 380 | 64 | 16 | 0 | 0 | 0 | 0 | 8 | 0 | 718 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 200 | 0 | 402 | 53 | 0 | 94 | 0 | 99 | 0 | 1 | 113 | 430 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9207 | 6:00
| Highest Generation |  | 12565 | 19:30
| Day Peak Generation |  | 10862 | 12:00
| Evening Peak Generation |  | 12565 | 19:30
| HVDC Max Flow |  | 719 | 1:00
| HVDC EvPeak Flow |  | 718 | 19:30
| Load factor L.F |  | 84.79%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10862 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9127 | MW
Evening Peak Generation : |  | 12565 | MW Hour : | 19:30 | Available Max Generation : |  | 15203 | MW
E.P. Demand (at gen end) : |  | 12565 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12565 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2403 | MW
Total Gen. (MKWH) : |  | 255.7073 | System Load Factor : | 84.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -132 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-23
Actual : | 87.41 | Ft.(MSL) , | Rule curve : | 89.48 | Ft.( MSL )
Gas Consumed : | Total = | 1182.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 154273253.982
: |  | Coal : | 75998624 | Oil : | 548765784.86 | Total : | 779037662.842
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4495.4649 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1532.6764 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1373.9346 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1241.7169 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1121.9831 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 905.4107 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 501.1529 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 232.9837 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 698.3221 |  |  | 0 | 0%
Total | 0 |  | 12103.6454 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-5
4) Kaptai-2
5) Raozan #2
6) Sirajganj #1 CCPP
7) Siddhirganj 335 MW
8) Ghorashal unit-7
9) Bibiyana-3 ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Dohazari-Cox'sbazar 132 kV Ckt-2 was under shut down from 10:28 to 17:05 for D/W.
b) HVDC 20DF30 Shunt Reactor was under shutdown from 09:31 to 10:25 for maintenance.
c) Bibiyana 3 ST was force shutdown at 09:01 due to fire at DM water plant.
d) Siddhirganj 335 MW was shutdown at 10:56 due to filter change.
e) Rajshahi-Natore 132 kV Ckt-1 was under shut down from 09:03 to 11:48 for C/M.
f) Rangpur 132/33 kV T-1 transformer was under shut down from 10:22 to 11:45 due to flashing. |  |  |  |  | About 10 MW power interruption occurred under Rangpur S/S area
from 10:22 to 11:45.
g) Hathazari 230/132 kV MT-03 transformer was under shut down from 11:36 to 11:50 for C/M.
h) Bhaluka 132/33 kV T-2 transformer was under shut down from 09:19 to 18:05 for D/W. |  |  |  |  | About 15 MW power interruption occurred under Bhaluka S/S area
from 09:19 to 18:05.
i) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 11:03 to 12:53 for C/M.
j) Bhangura 132/33 kV T-1 transformer was shut down at 11:15 for D/W.
k) Khulna(S) 230/132 kV T-03 transformer was under shut down from 09:28 to 11:42 for C/M.
l) Rajshahi-Natore 132 kV Ckt-2 was under shut down from 11:51 to 13:34 for C/M.
m) Hathazari 230/132 kV MT-02 transformer was under shut down from 12:04 to 13:05 for C/M.
n) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 12:58 to 14:15 for C/M.
o) Savar 132/33 kV T-1 transformer was under shut down from 13:15 to 13:59 for Kite removing.
p) Barishal(N)-Bhola 230 kV Ckt-2 tripped at 12:01 from both ends showing Dist. L3-N-phase, Z1 at
Barishal(N) end & Dist. Relay at Bhola end and was switched on at 12:39.
q) Hathazari 230/132 kV MT-01 transformer was under shut down from 13:10 to 13:58 for C/M.
r) Bheramara HVDC 400 kV 10C02B Breaker was switched on at 15:31
s) Bheramara HVDC 400 kV 10C02C Breaker was switched on at 15:32
t) Bottail 132/33 kV T-1 transformer tripped at 13:55 operating Diff. Relay and was switched on at 14:40.
u) Baroierhat 132/33 kV T-2 transformer tripped at 14:48 operating PRD.
v) Hathazari-Raozan 230 kV Ckt-2 was under shut down from 16:15 to 16:25 for C/M.
w) Rangamati 132 kV Bus coupler was under shut down from 16:03 to 16:59 for C/M.
x) After maintenance Meghnaghat 450 MW CCPP GT-1 & GT-2 was synchronized at 17:27 & 230:10 respectively.
y) Tongi-Kabirpur 132 kV Ckt-1 tripped at 02:10(23/03/2021) from both ends showing Dist. B-phase, Z1, |  |  |  |  | For these tripping ACE Kodda 149 MW & Gazipur 100 MW P.P.
E/F, O/C and was switched on at 02:31(23/03/2021). |  |  |  |  | got tripped.
z) Tongi-Kabirpur 132 kV Ckt-2 tripped at 02:10(23/03/2021) from Tongi end showing O/C and was |  |  |  |  | Full interruption occurred at Manikganj(48 MW) & Rajendrapur(70 MW)
switched on at 02:25(23/03/2021). |  |  |  |  | S/S area and partial interruption occurred under Kabirpur(94 MW) &
aa) Kodda-Gazipur 100 MW 132 kV Ckt tripped at 02:10(23/03/2021) from Kodda end showing no relay |  |  |  |  | Kodda(130 MW) S/S area till 02:37(23/03/2021).
and was switched on at 02:37(23/03/2021).
ab) Mirpur-Aminbazar 132 kV Ckt-1 was shut down at 07:18(23/03/2021) for C/M.
ac) Rampura 230/132 kV T-03 transformer was shut down at 07:11(23/03/2021) for NLDC transformer work.
ad) Khulna(C) 132/33 kV T-3 transformer was shut down at 07:10(23/03/2021) for C/M.
ae) Ghorashal unit-7 ST & GT was shutdown at 06:53(23/03/2021) & 07:00(23/03/2021) respectively for maintenance.
af) Shahjibazar GT-8 was shutdown at 06:10(23/03/2021) for maintenance.
ag) Rangamati-Chandraghona 132 kV Ckt-1 was shut down at 07:48(23/03/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4536000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 5507836 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2192318
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8473600 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 161 | 4472000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 90 | 872450 | Synchronized at 17:27.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1350720
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6355695 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1510704
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 973543
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 74 | 1491937 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 449496
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 175 | 3863000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1620480
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1071800 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1337328
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 49 | 631872
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1311840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2008800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 841546
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 850753 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1209840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 639100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 615840
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 287 | 6134725 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 248 | 411069 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 59391 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 97 | 231687
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 146 | 3326400
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1412400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1993920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1857600 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 207521
| Dhaka area Total |  |  |  | 5972 | 3829 | 70625911
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 352002
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 101250
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 977760
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 5046075
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Reserve.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 642460
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 928200
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1704000
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 495120
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 469920
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 956160 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28108
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 196 | 3733 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2425920
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 1127 | 17590708
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2886712 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2886712 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4714000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7488800 | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7186000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 387072 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 47 | 1183680 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1354909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 124032
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 152 | 3992160 | Machine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 431928
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 245340
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 174 | 3583680
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816800
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 406421 | Engine problem
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 435810 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 127104 | Low demand
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 492480
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1680000
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 37 | 204480 | On Test
| Cumilla Area Total |  |  |  | 2980 | 1888 | 40628120
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2702360 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 339552 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 41 | 754560 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15000
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 194 | 4500000
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1938000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 314730
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 439440
| Mymensingh Area Total |  |  |  | 709 | 497 | 11003642
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1013000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 988800 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3609327
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 182 | 4011000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1235400
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 34 | 773472 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1868160
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 414000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 334992 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7485500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 222 | 6323000 | Machine problem
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 196740
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8624600 | FGMO
| Sylhet Area Total |  |  |  | 2371 | 1495 | 37141991
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 718 | 17381818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 1237440 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 14 | 37760 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 280 | 7172352 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 226125 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 96 | 330240
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 2028480 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1301 | 28414215
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 442848
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 607175
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1480300 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 100 | 2262883
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 12781800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 25 | 255927 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 818 | 17830933
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 565003
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 32 | 67642
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 12660 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 375289 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 93405
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 153 | 4094209 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 173 | 4601600 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 396 | 9336327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 219762
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 457200
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 194706
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 749760
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 888328
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 85811 | Low demand
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2230752 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2439264
| Rajshahi Area Total |  |  |  | 2183 | 1347 | 26411718
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3669100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2350080
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40893
| Rangpur Area Total |  |  |  | 605 | 263 | 6060073
| Total |  |  |  | 21312 | 12565 | 255707311
| Eastern Grid Total |  |  |  | 14414 | 8836 | 176990372
| Western Grid Total |  |  |  | 6898 | 3729 | 78716939
| National Grid Total |  |  |  | 21312 | 12565 | 255707311
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-22
(a) ENTIRE EASTERN GRID : |  | 8070 | MW | (b) ENTIRE WESTERN GRID : |  | 3799 | MW
i) Dhaka area |  | 4250 | MW | i) Khulna area |  | 1438 | MW
ii) Chittagong area |  | 1263 | MW | ii) Rajshahi area |  | 1260 | MW
iii) Comilla area |  | 1113 | MW | iii) Barisal area |  | 323 | MW
iv) Mymensingh area |  | 989 | MW | iv) Rangpur area |  | 778 | MW
v) Sylhet area |  | 455 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11869 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 16:00 | Jamalpur | 140 | 19:30 | Jhenida | 110 | 19:00
Munsiganj | 128 | 21:00 | Sherpur | 120 | 19:00 | Bottail | 116 | 19:00
Sonargaon | 80 | 18:30 | Srimongal | 48 | 18:30 | G.K Project | 52 | 19:30
Shyampur | 202 | 2:00 | Shahjibazar | 117 | 18:30 | Faridpur | 170 | 19:30
Bhulta | 207 | 12:00 | Fenchuganj | 34 | 18:30 | Madaripur | 92 | 21:00
Madanganj | 53 | 20:00 | Kulawara | 34 | 18:30 | Sariatpur | 56 | 20:00
Shitalakhya | 128 | 12:00 | Sylhet | 111 | 20:00 | Gopalganj | 81 | 19:30
Rahim steel | 22 | 14:00 | Chatak | 31 | 18:30 | Bagerhat | 106 | 19:00
Matuail | 60 | 10:00 | Sunamganj | 37 | 20:00 | Mongla | 36 | 6:00
Ghorasal | 78 | 22:00 | Biani Bazar | 52 | 18:30 | Satkhira | 100 | 19:00
Narsingdi | 160 | 19:00 | Comilla (S) | 176 | 19:00 | Gallamari | 31 | 12:00
Haripur (SBU) | 122 | 13:00 | Comilla(N) | 117 | 19:30 | Magura | 50 | 19:00
Sreenagar |  |  | Chandpur | 63 | 20:00 | Norail | 36 | 19:30
Ullon | 86 | 18:30 | Feni | 117 | 22:00 | Chuadanga | 85 | 20:00
Hasnabad | 100 | 22:00 | Chowmuhani | 187 | 19:00 | Borguna | 14 | 19:00
Magbazar | 97 | 12:00 | Ashuganj | 52 | 1:00 | Barisal(N) | 42 | 19:00
Maniknagar | 92 | 12:00 | Daudkandi | 136 | 20:00 | Barisal (S) | 102 | 20:00
Bangabhaban | 22 | 10:00 | B.Baria | 154 | 21:00 | Patuakhali | 103 | 19:30
Narinda | 98 | 10:00 | Ramganj | 86 | 22:00 | Bhandaria | 48 | 19:00
Dhanmondi | 192 | 11:00 | Chaddagram | 40 | 18:30 | Borhan Uddin | 39 | 21:00
Lalbag | 86 | 18:30 | PHP | 9 | 14:00 | Ishurdi | 57 | 19:00
Madartek | 72 | 23:00 | Kochua | 62 | 18:30 | Ruppur Paromanobik | 3 | 20:00
Dhaka University | 49 | 11:00 | Madunaghat | 60 | 18:30 | Natore | 126 | 20:00
Aftabnagar | 28 | 18:30 | Hathazari | 95 | 19:00 | Bogra | 163 | 19:00
Fatullah | 60 | 24:00 | Khulshi | 208 | 18:30 | Noagaon | 109 | 20:00
Nawabganj | 44 | 19:00 | Halishahar | 132 | 14:00 | Rajshahi | 142 | 20:00
Mirpur | 110 | 18:00 | Baraulia | 144 | 19:00 | Rajshahi New | 19 | 20:00
Kalyanpur | 93 | 18:00 | Sikalbaha | 29 | 20:00 | C.Nawabganj | 74 | 19:30
Gulshan | 75 | 14:00 | Dohazari | 84 | 18:30 | Amnura | 56 | 20:00
Uttara | 88 | 14:00 | Cox'sbazar | 110 | 22:00 | Pabna | 103 | 20:00
Uttara New | 37 | 13:00 | Chandraghona | 32 | 19:30 | Shahjadpur | 109 | 20:00
Kamrangirchar | 88 | 13:00 | Kaptai | 0 | #N/A | Serajganj | 103 | 20:00
Savar | 185 | 19:00 | A. Khaer Stl. | 11 | 17:00 | Niyamatpur | 80 | 20:00
Bhasantec | 165 | 13:00 | Bakulia | 107 | 19:00 | Joypurhat | 64 | 19:00
Agargaon | 68 | 14:00 | Julda | 25 | 18:00 | Sherpur(Bogura) | 52 | 19:00
Satmosjid | 93 | 18:00 | TK chemical | 28 | 19:00 | Mohastangor | 56 | 19:30
Tongi | 113 | 18:00 | Modern Steel | 0 | #N/A | Bangura | 15 | 8:00
Kabirpur | 240 | 18:30 | Shahmirpur | 25.6 | 1:00 | Rangpur | 124 | 19:00
Basundhara | 191 | 13:00 | Khagrachhari | 24 | 22:00 | Lalmonirhat | 45 | 19:00
Manikganj | 72 | 19:30 | Matarbari | 38 | 20:00 | Saidpur | 108 | 19:00
Joydevpur | 150 | 18:30 | Baroiar Hat | 34 | 19:00 | Purbasadipur | 94 | 20:00
New Tongi | 105 | 12:00 | Rangamati | 12 | 18:30 | Thakurgaon | 75 | 20:00
Kodda | 243 | 16:00 | Abul Khair 230 | 13 | 9:00 | Palashbari | 110 | 19:30
Dhamrai | 112 | 19:00 | BSRM | 157 | 10:00 | Barapukuria | 51 | 19:00
Rajendrapur | 94 | 19:00 | GPH Ispat | 93 | 18:00 | Panchagar | 47 | 20:00
Valuka | 114 | 8:00 | Goalpara | 29 | 12:00 | Joldhaka | 48 | 19:30
Tangail | 203 | 19:30 | Central s/s | 96 | 20:0 | Kurigram | 55 | 20:00
Mymensing | 227 | 18:30 | Noapara | 44 | 20:0 | Mithapukur | 28 | 19:00
Kishorganj | 126 | 23:00 | Jessore | 128 | 19:30
Netrokona | 121 | 20:00 | Benapol | 62 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 24:00 | 399 | 16:00 | Kaliakoir | 391 | 0.125 | 382 | 0.33333
| Bheramara | 395 | 20:00 | 389 | 12:00 | Bhulta | 383 | 0.83333 | 372 | 0.66667
| Ashuganj(N) | 389 | 23:00 | 380 | 16:00 | Gopalganj | 403 | 0.625 | 385 | 0.79167
| Payra | 407 | 19:30 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 230 | 1:00 | Hathazari | 227 | 21:00 | 219 | 10:00
| Ishurdi | 235 | 17:00 | 225 | 7:00 | Megnaghat | 233 | 24:00 | 226 | 3:00
| Ashuganj | 236 | 19:30 | 232 | 7:00 | Fenchuganj | 241 | 21:00 | 236 | 14:00
| Serajganj | 234 | 1:00 | 226 | 7:00 | Siddhirganj | 229 | 20:00 | 222 | 15:00
| Baghabari | 234 | 16:00 | 226 | 18:30 | Maniknagar | 227 | 20:00 | 220 | 16:00
| Barapukuria | 235 | 23:00 | 222 | 7:00 | Agargaon | 226 | 7:00 | 219 | 16:00
| Bogra | 228 | 3:00 | 217 | 19:30 | Barisal | 249 | 21:00 | 239 | 12:00
| Rajshahi | 232 | 13:00 | 219 | 7:00 | Bhola 225 MW | 253 | 8:00 | 245 | 18:30
| Khulna South | 235 | 17:00 | 215 | 7:00 | AKSML | 230 | 21:00 | 217 | 10:00
| Rampura | 229 | 22:00 | 221 | 16:00 | BSRM | 229 | 23:00 | 217 | 10:00
| Haripur | 227 | 20:00 | 221 | 1:00 | Bibiyana | 239 | 5:00 | 234 | 17:00
| Hasnabad | 230 | 20:00 | 222 | 5:00 | Bhulta | 230 | 19:30 | 223 | 16:00
| Shyampur | 226 | 19:30 | 220 | 16:00 | Ashuganj (S) | 234 | 19:30 | 230 | 16:00
| Aminbazar | 227 | 1:00 | 221 | 2:00 | Kaliakoir | 229 | 21:00 | 222 | 8:00
| Tongi | 225 | 21:00 | 215 | 8:00 | GPH | 228 | 21:00 | 218 | 10:00
| Comilla (N) | 230 | 19:30 | 224 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 18:30 | 134 | 7:00 | Madanhat | 137 | 0.875 | 130 | 0.41667
| Munsiganj | 141 | 22:00 | 134 | 6:00 | Hathazari | 135 | 0.875 | 129 | 0.625
| Sonargaon | 139 | 19:00 | 133 | 3:00 | Khulshi | 134 | 0.875 | 127 | 0.33333
| Shyampur | 136 | 19:30 | 131 | 16:00 | Halishahar | 136 | 0.91667 | 128 | 0.41667
| Bhulta | 130 | 18:30 | 125 | 12:00 | Baraulia | 136 | 0.875 | 129 | 0.375
| Madanganj | 140 | 10:00 | 131 | 4:00 | Sikalbaha | 137 | 0.875 | 130 | 0.41667
| Shitalakhya | 143 | 20:00 | 130 | 3:00 | Dohazari | 133 | 0.70833 | 127 | 0.16667
| Rahim steal | 138 | 18:30 | 134 | 7:00 | Cox'sbazar | 121 | 0.70833 | 108 | 0.625
| Matuail | 138 | 18:30 | 134 | 7:00 | Chandraghona | 135 | 0.95833 | 128 | 0.41667
| Ghorasal | 138 | 13:00 | 135 | 1:00 | Kaptai | 0 | #N/A | 0 | #N/A
| Narsinghdi | 134 | 8:00 | 127 | 18:00 | A. Khaer Stl. | 134 | 0.041667 | 128 | 0.54167
| Haripur (SBU) | 139 | 11:00 | 135 | 5:00 | Bakulia | 135 | 0.875 | 129 | 0.41667
| Sreenagar |  |  |  |  | Julda | 135 | 0.75 | 129 | 0.54167
| Ullon | 134 | 1:00 | 130 | 11:00 | TK Chemical | 136 | 0.83333 | 128 | 0.29167
| Hasnabad | 131 | 22:00 | 125 | 16:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 131 | 22:00 | 125 | 16:00 | Shahmirpur | 137 | 0.875 | 129 | 0.625
| Maniknagar | 131 | 22:00 | 125 | 16:00 | Khagrachhari | 134 | 0.91667 | 127 | 0.41667
| Bangabhaban | 134 | 1:00 | 129 | 15:00 | Matarbari | 129 | 0.70833 | 115 | 0.54167
| Narinda | 138 | 20:00 | 130 | 4:00 | Baroiar Hat | 136 | 0.875 | 127 | 0.41667
| Dhanmondi | 134 | 21:00 | 129 | 11:00 | Rangamati | 134 | 0.95833 | 127 | 0.41667
| Lalbag | 134 | 1:00 | 129 | 15:00 | Goalpara S/S | 137 | 17:00 | 126 | 4:00
| Madartek | 134 | 1:00 | 129 | 15:00 | Khulna Central S/S | 137 | 17:00 | 124 | 7:00
| Dhaka University | 137 | 21:00 | 131 | 16:00 | Noapara | 133 | 17:00 | 120 | 0.29167
| Aftabnagar | 130 | 19:30 | 125 | 15:00 | Jessore | 127 | 17:00 | 114 | 0.79167
| Fatullah |  |  |  |  | Benapol | 128 | 17:00 | 114 | 0.79167
| Nawabganj |  |  |  |  | Jhenida | 125 | 9:00 | 109 | 0.79167
| Mirpur | 135 | 20:00 | 132 | 12:00 | Bottail | 131 | 0.16667 | 122 | 0.79167
| Kalyanpur | 135 | 20:00 | 130 | 12:00 | G.K Project | 139 | 17:00 | 132 | 0.8125
| Gulshan | 133 | 20:00 | 130 | 12:00 | Faridpur | 135 | 0.375 | 127 | 0.79167
| Uttara | 134 | 20:00 | 132 | 12:00 | Madaripur | 139 | 0.16667 | 132 | 0.79167
| Uttara New | 136 | 20:00 | 132 | 12:00 | Shariyatpur S/S | 139 | 0.083333 | 130 | 0.79167
| Kamrangirchar | 138 | 20:00 | 131 | 12:00 | Gopalganj | 143 | 0.33333 | 133 | 0.79167
| Savar | 136 | 20:00 | 130 | 12:00 | Bagerhat | 135 | 9:00 | 120 | 0.29167
| Bhasantec | 130 | 20:00 | 124 | 12:00 | Mongla | 135 | 0.70833 | 120 | 0.79167
| Agargaon | 131 | 20:00 | 128 | 12:00 | Satkhira | 135 | 18:00 | 121 | 0.29167
| Satmosjid | 131 | 20:00 | 126 | 12:00 | Gallamari | 139 | 17:00 | 126 | 0.79167
| Tongi | 138 | #REF! | 131 | 8:00 | Magura | 125 | 9:00 | 110 | 19:00
| Kabirpur | 139 | 1:00 | 133 | 10:00 | Narail | 125 | 0.29167 | 105 | 0.79167
| Basundhara | 137 | 22:00 | 130 | 8:00 | Chuadanga | 120 | 9:00 | 100 | 0.79167
| Manikganj | 140 | 22:00 | 132 | 18:00 | Borguna | 140 | 0.20833 | 132 | 0.5
| Joydevpur | 138 | 23:00 | 131 | 2:00 | Barisal(N) | 140 | 1:00 | 134 | 0.79167
| New Tongi | 139 | 21:00 | 131 | 8:00 | Barisal (S) | 140 | 5:00 | 133 | 0.54167
| Kodda | 136 | 19:00 | 127 | 16:00 | Patuakhali(S) | 139 | 8:00 | 130 | 21:00
| Dhamrai | 140 | 00:00 | 134 | 13:00 | Bhandaria | 137 | 0.25 | 130 | 0.83333
| Rajendrapur | 136 | 23:00 | 125 | 9:00 | Ishurdi | 137 | 0.70833 | 131 | 0.79167
| Valuka | 124 | 9:00 | 109 | 19:00 | Ruppur Paromanobik | 135 | 0.41667 | 130 | 0.79167
| Tangail | 133 | 9:00 | 126 | 7:00 | Natore | 137 | 17:00 | 128 | 7:00
| Mymensing | 128 | 9:00 | 114 | 19:00 | Bogra | 136 | 17:00 | 127 | 19:00
| Kishorganj | 129 | 9:00 | 120 | 19:00 | Noagaon | 129 | 18:00 | 118 | 19:00
| Netrokona | 124 | 9:00 | 110 | 19:00 | Rajshahi | 136 | 15:00 | 128 | 19:00
| Jamalpur | 138 | 11:00 | 124 | 9:00 | Rajshahi New | 136 | 13:00 | 128 | 7:00
| Sherpur | 136 | 11:00 | 124 | 19:00 | C.Nawabganj | 134 | 17:00 | 124 | 7:00
| Srimongal | 138 | 5:00 | 132 | 19:00 | Amnura | 135 | 17:00 | 123 | 7:00
| Shahjibazar | 137 | 8:00 | 131 | 16:00 | Pabna | 134 | 18:00 | 129 | 19:00
| Fenchuganj | 137 | 7:00 | 133 | 16:00 | Shahjadpur | 139 | 13:00 | 134 | 7:00
| Khulawara | 137 | 8:00 | 131 | 18:30 | Serajganj | 132 | 17:00 | 126 | 19:00
| Sylhet | 134 | 7:00 | 129 | 16:00 | Niyamatpur | 127 | 18:00 | 113 | 19:00
| Chatak | 132 | 7:00 | 123 | 18:30 | Joypurhat | 128 | 3:00 | 115 | 19:00
| Sunamganj | 132 | 5:00 | 123 | 19:30 | Sherpur(Bogura) | 135 | 2:00 | 126 | 19:00
| Biani Bazar | 132 | 5:00 | 124 | 18:30 | Mohastangor | 134 | 17:00 | 124 | 19:00
| Comilla(s) | 129 | 3:00 | 123 | 19:00 | Bangura | 136 | 13:00 | 132 | 8:00
| Comilla(n) | 140 | 19:00 | 135 | 3:00 | Rangpur | 132 | 5:00 | 114 | 19:00
| Chandpur | 138 | 7:00 | 132 | 18:30 | Lalmonirhat | 128 | 1:00 | 115 | 19:00
| Feni | 137 | 19:30 | 129 | 10:00 | Saidpur | 129 | 1:00 | 116 | 19:30
| Chowmuhani | 136 | 19:00 | 128 | 5:00 | Purbasadipur | 128 | 1:00 | 101 | 18:30
| Ashuganj | 139 | 9:00 | 134 | 18:00 | Thakurgaon | 127 | 3:00 | 110 | 19:00
| Daudkandi | 139 | 19:30 | 130 | 3:00 | Palashbari | 130 | 1:00 | 116 | 19:00
| B.Baria | 135 | 9:00 | 128 | 16:00 | Barapukuria | 131 | 1:00 | 122 | 7:00

## L-Curve
Date | 2021-03-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 4 | 7743 | 3386 | 11129 |  |  |  | QF-LDC-11
0:30 | 6 | 7513 | 3256 | 10769 | Date: | 2021-03-22
1:00 | 8 | 7283 | 3126 | 10409
1:30 | 69 | 7134.5 | 3103.5 | 10238
2:00 | 130 | 6986 | 3081 | 10067
2:30 | 135 | 6824 | 3055.5 | 9879.5 | [5 empty] | Gen. at Eve. Peak | 12565 | 12565 MW (19:30 )
3:00 | 140 | 6662 | 3030 | 9692 | [6 empty] | 19:30
3:30 | 135 | 6608.5 | 2928.5 | 9537 | [5 empty] | Gen. at Day Peak | 10862 | 10862 MW (12:00 )
4:00 | 130 | 6555 | 2827 | 9382 | [6 empty] | 12:00
4:30 | 122.5 | 6515 | 2801 | 9316 | [5 empty] | Highest Generation | 12565
5:00 | 115 | 6475 | 2775 | 9250 | [6 empty] | 19:30
5:30 | 107.5 | 6448 | 2780.5 | 9228.5
6:00 | 100 | 6421 | 2786 | 9207
6:30 | 84 | 6457.5 | 2802.5 | 9260
7:00 | 68 | 6494 | 2819 | 9313
7:30 | 48 | 6546 | 2879 | 9425
8:00 | 28 | 6598 | 2939 | 9537
8:30 | 63 | 6641 | 2963.5 | 9604.5
9:00 | 98 | 6684 | 2988 | 9672
9:30 | 70 | 6968.5 | 2998.5 | 9967
10:00 | 42 | 7253 | 3009 | 10262
10:30 | 77 | 7355.5 | 3069 | 10424.5
11:00 | 112 | 7458 | 3129 | 10587
11:30 | 61 | 7578.5 | 3146 | 10724.5
12:00 | 10 | 7699 | 3163 | 10862
12:30 | 47 | 7751.5 | 3233 | 10984.5
13:00 | 84 | 7804 | 3303 | 11107
13:30 | 105 | 7767 | 3271 | 11038
14:00 | 126 | 7730 | 3239 | 10969
14:30 | 88 | 7780 | 3246 | 11026
15:00 | 50 | 7830 | 3253 | 11083
15:30 | 125 | 7833.5 | 3283.5 | 11117
16:00 | 200 | 7837 | 3314 | 11151
16:30 | 228 | 7713.5 | 3277.5 | 10991
17:00 | 256 | 7590 | 3241 | 10831
17:30 | 276 | 7537.5 | 3259 | 10796.5
18:00 | 296 | 7485 | 3277 | 10762
18:30 | 188 | 8119 | 3452.5 | 11571.5
19:00 | 80 | 8753 | 3628 | 12381
19:30 | 122 | 8836 | 3729 | 12565
20:00 | 132 | 8782 | 3681 | 12463 |  |  |  | Executive Engineer
20:30 | 106 | 8647.5 | 3669.5 | 12317 |  |  |  | Network Operation Division
21:00 | 80 | 8513 | 3658 | 12171
21:30 | 64 | 8435.5 | 3620 | 12055.5
22:00 | 48 | 8358 | 3582 | 11940 |  |  |  |  | Page 6 of 7
22:30 | 28 | 8198 | 3505.5 | 11703.5
23:00 | 8 | 8038 | 3429 | 11467
23:30 | 6 | 7890.5 | 3407.5 | 11298
24:00 | 4 | 7743 | 3386 | 11129
12565 MW (19:30 )
10862 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-22 |  | Energy | 255707311
[11 empty] | 2021-03-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4329 | 718 | 1725 | 3570 | 700 | 40 | 298 | 0 | 164 | 0
0:30 | 4411 | 718.5 | 1653 | 3132 | 700 | 40 | 165 | 0 | 157 | 0 | Date: | 2021-03-22
1:00 | 4493 | 719 | 1581 | 2694 | 700 | 40 | 32 | 0 | 150 | 0
1:30 | 4501 | 718.5 | 1599.5 | 2508 | 700 | 40 | 24 | 0 | 147 | 0 | [7 empty] | Total Energy | 255.7073 | Total Energy Gen 255.707 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.707 MKWHr
2:00 | 4509 | 718 | 1618 | 2322 | 700 | 40 | 16 | 0 | 144 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4543 | 718.5 | 1625 | 2103 | 695 | 40 | 16 | 0 | 139 | 0 | [7 empty] | Energy Requirement | 255.7073
3:00 | 4577 | 719 | 1632 | 1884 | 690 | 40 | 16 | 0 | 134 | 0
3:30 | 4612 | 719 | 1635 | 1715.5 | 675.5 | 40 | 8 | 0 | 132 | 0 | [6 empty] | Shortage
4:00 | 4647 | 719 | 1638 | 1547 | 661 | 40 | 0 | 0 | 130 | 0
4:30 | 4617.5 | 719 | 1650 | 1516 | 645.5 | 40 | 0 | 0 | 128 | 0
5:00 | 4588 | 719 | 1662 | 1485 | 630 | 40 | 0 | 0 | 126 | 0
5:30 | 4564.5 | 719 | 1656 | 1493 | 630 | 40 | 0 | 0 | 126 | 0
6:00 | 4541 | 719 | 1650 | 1501 | 630 | 40 | 0 | 0 | 126 | 0
6:30 | 4581.5 | 719 | 1624.5 | 1542.5 | 620 | 40 | 0 | 0 | 126 | 6.5 |  |  |  |  | Coal
7:00 | 4622 | 719 | 1599 | 1584 | 610 | 40 | 0 | 0 | 126 | 13
7:30 | 4614.5 | 719 | 1583.5 | 1722.5 | 595 | 40 | 0 | 0 | 127 | 23.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4607 | 719 | 1568 | 1861 | 580 | 40 | 0 | 0 | 128 | 34
8:30 | 4480.5 | 719 | 1541 | 2071 | 570 | 40 | 12.5 | 0 | 124 | 46.5
9:00 | 4354 | 719 | 1514 | 2281 | 560 | 40 | 25 | 0 | 120 | 59
9:30 | 4397 | 719 | 1478.5 | 2554 | 559.5 | 40 | 28.5 | 0 | 120 | 70.5
10:00 | 4440 | 719 | 1443 | 2827 | 559 | 40 | 32 | 0 | 120 | 82
10:30 | 4382 | 719 | 1478.5 | 2964.5 | 574 | 40 | 48 | 0 | 130 | 88.5
11:00 | 4324 | 719 | 1514 | 3102 | 589 | 40 | 64 | 0 | 140 | 95
11:30 | 4327.5 | 719 | 1518 | 3193.5 | 594.5 | 40 | 89.5 | 0 | 143 | 99.5
12:00 | 4331 | 719 | 1522 | 3285 | 600 | 40 | 115 | 0 | 146 | 104
12:30 | 4261 | 719 | 1521 | 3390 | 610 | 40 | 195.5 | 0 | 147 | 101
13:00 | 4191 | 719 | 1520 | 3495 | 620 | 40 | 276 | 0 | 148 | 98
13:30 | 4191 | 719 | 1520 | 3495 | 620 | 40 | 276 | 0 | 148 | 98
14:00 | 4191 | 719 | 1520 | 3495 | 620 | 40 | 276 | 0 | 148 | 98
14:30 | 4173.5 | 719 | 1476 | 3520.5 | 625 | 40 | 302.5 | 0 | 154 | 84.5
15:00 | 4156 | 719 | 1432 | 3546 | 630 | 40 | 329 | 0 | 160 | 71
15:30 | 4154 | 719 | 1469.5 | 3562 | 630 | 40 | 327.5 | 0 | 157 | 58
16:00 | 4152 | 719 | 1507 | 3578 | 630 | 40 | 326 | 0 | 154 | 45
16:30 | 4106 | 718.5 | 1494 | 3519 | 610 | 40 | 328.5 | 0 | 145 | 30
17:00 | 4060 | 718 | 1481 | 3460 | 590 | 40 | 331 | 0 | 136 | 15
17:30 | 4033 | 718.5 | 1449 | 3445.5 | 590 | 40 | 369 | 0 | 144 | 7.5
18:00 | 4006 | 719 | 1417 | 3431 | 590 | 40 | 407 | 0 | 152 | 0
18:30 | 4127 | 718.5 | 1515 | 3937 | 615 | 40 | 455 | 0 | 164 | 0
19:00 | 4248 | 718 | 1613 | 4443 | 640 | 40 | 503 | 0 | 176 | 0
19:30 | 4250 | 718 | 1630 | 4542 | 680 | 40 | 531 | 0 | 174 | 0
20:00 | 4255 | 718 | 1686 | 4376 | 680 | 40 | 534 | 0 | 174 | 0
20:30 | 4242.5 | 718 | 1698.5 | 4235 | 695 | 40 | 514 | 0 | 174 | 0
21:00 | 4230 | 718 | 1711 | 4094 | 710 | 40 | 494 | 0 | 174 | 0
21:30 | 4235 | 718 | 1715 | 4011.5 | 715 | 40 | 448 | 0 | 173 | 0
22:00 | 4240 | 718 | 1719 | 3929 | 720 | 40 | 402 | 0 | 172 | 0
22:30 | 4252.5 | 718 | 1700.5 | 3749.5 | 720 | 40 | 353 | 0 | 170 | 0
23:00 | 4265 | 718 | 1682 | 3570 | 720 | 40 | 304 | 0 | 168 | 0
23:30 | 4297 | 718 | 1703.5 | 3570 | 710 | 40 | 301 | 0 | 166 | 0 | Max Temp. in Dhaka |  | 36.8° C
24:00 | 4329 | 718 | 1725 | 3570 | 700 | 40 | 298 | 0 | 164 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 255.707 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.707 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | [9 empty] | 1 | 22 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 352002
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 4 | 8 | 12 | 15 | 16 | 14 | 13 | 11 | 6 | [10 empty] | 101250
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 203 | 204 | 204 | 203 | 203 | 228 | 231 | 230 | 225 | 223 | 218 | 223 | 217 | 216 | 216 | 203 | 203 |  | 203 | 204 | 203 | 203 | 204 | 203 | 203 | 5046075
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 34 | 34 | 34 | 61 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 642460
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 50 | 50 | 50 | 20 |  |  |  | 127104
14 | Titas 50 MW Peaking PP | [17 empty] | 9 |  | 42 | 42 | 42 | 42 |  |  |  | 124032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 155 | 155 | 150 | 155 | 120 | 118 | 118 | 118 | 190 | 150 | 190 | 181 | 175 | 115 | 150 | 174 | 174 | 68 |  | 175 | 175 | 175 | 175 | 145 | 145 | 150 | 3863000
17 | Siddhirganj 335 MW CCPP | 94 | 94 | 94 | 94 | 93 | 93 | 94 | 95 | 93 | 93 | [16 empty] | 1071800
18 | Kodda 300 MW PP Unit-2 (Summit) | 287 | 287 | 287 | 195 | 195 | 195 | 195 | 195 | 218 | 265 | 258 | 255 | 253 | 253 | 253 | 245 | 240 | 250 |  | 287 | 287 | 293 | 278 | 291 | 293 | 291 | 6134725
19 | Ashuganj 195MW PP (APSCL-United) | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 68 | 55 | 55 | 55 |  | 55 | 55 | 55 | 8 | 8 | 8 | 8 | 1354909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4536000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 180 | 122 | 130 | 130 | 130 | 130 | 240 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5507836
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 2886712
29 | Ashuganj TPP Unit- 4 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 80 | 80 |  | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 2886712
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 20 |  | 20 | 20 | 20 | 5 | 10 | 10 | 10 | 387072
33 | Ashuganj 225 MW CCPP | 214 | 214 | 214 | 214 | 214 | 213 | 214 | 215 | 216 | 195 | 183 | 197 | 182 | 185 | 196 | 125 | 163 | 183 |  | 185 | 184 | 172 | 210 | 180 | 180 | 174 | 4714000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 305 | 310 | 310 | 300 | 305 | 300 | 300 | 320 | 300 | 325 | 300 | 265 | 285 | 305 | 260 | 265 |  | 295 | 295 | 295 | 260 | 260 | 265 | 265 | 7186000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 320 | 325 | 295 | 270 | 280 | 280 | 270 | 295 | 350 | 340 | 310 | 260 | 295 | 300 | 275 | 280 |  | 325 | 325 | 325 | 275 | 275 | 275 | 275 | 7488800
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 52 | 52 | 52 | 10 | 10 | 10 |  | 25 | 47 | 47 | 53 | 55 | 54 | 55 | 1183680
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 344 | 344 | 342 | 354 | 359 | 347 | 366 | 343 | 366 | 355 | 357 | 362 | 374 | 375 | 349 | 300 |  | 328 | 340 | 340 | 340 | 340 | 339 | 339 | 8473600
40 | Meghnaghat 450 MW CCPP(MPL) | [17 empty] | 25 |  | 40 | 90 | 140 | 225 | 225 | 225 | 250 | 872450
41 | Haripur 360MW CCPP(HPL) | 235 | 246 | 250 | 260 | 281 | 262 | 230 | 200 | 181 | 161 | 146 | 146 | 141 | 141 | 151 | 157 | 166 | 182 |  | 172 | 161 | 151 | 141 | 130 | 130 | 150 | 4472000
42 | RPCL 210MW CCPP | 104 | 104 | 109 | 156 | 157 | 160 | 158 | 156 | 136 | 102 | 100 | 100 | 100 | 101 | 101 | 98 | 102 | 102 |  | 104 | 105 | 107 | 107 | 107 | 108 | 110 | 2702360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 16 | 27 | 36 | 39 | 46 | 44 | 40 | 30 | 20 | 8 | 0 |  | 0 | [6 empty] | 314730
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 41 | 41 | 41 | 40 | 41 | 42 | 43 |  | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 1013000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 988800
46 | Shajibazar 330 MW CCPP | 180 | 179 | 180 | 181 | 180 | 181 | 179 | 180 | 182 | 180 | 182 | 180 | 182 | 182 | 178 | 180 | 182 | 180 |  | 184 | 182 | 181 | 189 | 180 | 177 | 180 | 4011000
47 | Shahjibazar GTPP Unit- 8 & 9 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 34 | 34 | 20 | 33 | 33 | 20 | 32 | 33 | 20 |  | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 773472
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 77 | 79 | 79 | 79 | 78 | 78 | 77 | 40 |  | 78 | 78 | 80 | 81 | 81 | 81 | 81 | 1868160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 414000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 196740
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 48 | 53 | 53 | 53 | 53 | 53 | 53 | 25 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1235400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 334992
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 310 | 310 | 315 | 320 | 310 | 310 | 320 | 300 | 320 | 310 | 310 | 310 | 320 | 320 | 295 | 285 |  | 315 | 285 | 290 | 285 | 280 | 285 | 280 | 7485500
| Bibiyana South 400 MW | 341 | 340 | 370 | 370 | 370 | 342 | 370 | 370 | 340 | 370 | 363 | 370 | 340 | 370 | 370 | 370 | 340 | 370 |  | 355 | 340 | 340 | 340 | 340 | 370 | 371 | 8624600
58 | Nababganj 55 MW PP (Southern power ) | 17 | [7 empty] | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 35 | 35 | 35 | 50 | 55 | 55 | 55 | 850753
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | [5 empty] | 11 | 18 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 |  | 25 | 25 | 24 | 25 | 25 | 24 |  | 439440
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 495120
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 17 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 22 | 449496
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 339552
63 | Impoprt (Tripura) | 150 | 144 | 134 | 130 | 126 | 126 | 126 | 128 | 120 | 120 | 140 | 146 | 148 | 160 | 160 | 154 | 136 | 152 |  | 176 | 174 | 174 | 174 | 172 | 168 | 164 | 3583680
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 40 | 34 | 4 | 2 | 2 | 2 | 2 | 6 | 4 | 2 | 2 | 2 | 4 |  | 12 | 15 | 23 | 30 | 35 | 38 | 38 | 469920
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 17 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 431928
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 245340
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 20 |  | 18 | 15 | 18 | 20 | 20 | 20 | 20 | 435810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 25 | 25 | 25 | 22 | 20 | 23 | 25 | 26 | 26 | 26 |  | 27 | 27 | 27 | 27 | 29 | 29 | 29 | 609840
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 639100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 802700
73 | Ghorashal 108MW PP (Regent) | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 96 | 92 | 92 | 92 | 94 | 95 | 93 | 93 | 98 | 95 |  | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 2192318
| Feni Lanka Power | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 114 | 114 | 114 | 114 | 67 |  |  | 492480
| Chowmuhani 113 MW | 55 | [7 empty] | 21 | 26 | 31 | 73 | 107 | 111 | 110 | 111 | 110 | 111 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1680000
| Manikgonj 162MW PP(MPGL) | [8 empty] | 4 | 98 | 111 | 120 | 141 | 144 | 144 | 144 | 108 | 108 |  | 130 | 144 | 144 | 144 | 144 | 54 |  | 1857600
77 | Siddhirganj 100 PP(Dutch Bangla) | 70 | 20 | [6 empty] | 7 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1620480
78 | Gazipur 52 MW PP | [8 empty] | 20 | 51 | 51 | 51 | 50 | 50 | 49 | 49 | 8 | 8 |  | 30 | 51 | 51 | 51 | 51 | 25 |  | 615840
79 | Kodda 150MW PP | 32 | 16 | 16 | [5 empty] | 25 | 32 | 64 | 98 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2008800
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 34 | 24 | 8 | 8 | 10 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 754560
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 22 | 36 | 43 | 43 | 36 | 16 |  | 32 | 43 | 43 | 43 | 43 | 25 |  | 406421
| Gazipur 100 MW PP | [8 empty] | 20 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1412400
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 2 | 4 | 4 | 5 | 4 | 3 | 3 | 2 | 0 | [9 empty] | 28108
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 48 | 15 | [7 empty] | 30 | 70 | 97 | 95 | 95 | 95 | 95 | 95 | 96 |  | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 1510704
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 85 | 85 | 10 |  |  |  | 1 | 20 | 52 | 73 | 78 | 81 | 74 | 84 | 80 | 83 | 82 | 76 |  | 74 | 74 | 80 | 83 | 80 | 70 | 65 | 1491937
86 | Meghnaghat CCPP(Summit) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 270 | 270 | 265 | 265 | 265 | 265 | 270 | 265 | 265 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6355695
87 | Meghnaghat 100 MW(IEL) | 7 | [7 empty] | 13 | 65 | 73 | 92 | 92 | 95 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 70 | 22 | 1350720
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 40 |  |  |  |  | 16 | 63 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1993920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | [9 empty] | 30 | 50 | 80 | 90 | 67 | 65 | 40 | 10 |  | 100 | 100 | 100 | 100 | 100 | 60 | 10 | 928200
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [7 empty] | 24 | 48 | 64 | 84 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 48 | 7 | 1337328
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 46 | 46 | 24 | 25 | 25 | 24 | 32 | 40 | 43 | 44 | 43 | 43 | 43 | 42 | 42 | 43 |  | 43 | 45 | 44 | 44 | 45 | 45 | 45 | 977760
96 | Chattogram 108 MW PP (ECPV) | 57 | [9 empty] | 2 | 14 | 44 | 63 | 60 | 60 | 60 | 61 |  | 87 | 91 | 91 | 91 | 91 | 91 | 71 | 956160
97 | katpotti 52 MW | 6 | [8 empty] | 4 | 6 | 29 | 50 | 50 | 50 | 50 | 50 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 |  | 631872
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 15 | [5 empty] | 3 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 973543
100 | Manikganj 55 MW PP (Northern) | 17 | [7 empty] | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 841546
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3609327
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1311840
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 283 | 248 | 135 |  |  |  |  | 411069
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 25 | 25 | 25 |  |  |  |  | 59391
106 | Mymensingh 200 MW PP (United) | 184 | 200 | 160 | 160 | 160 | 175 | 200 | 200 | 195 | 195 | 194 | 183 | 182 | 189 | 190 | 191 | 191 | 190 |  | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 4500000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 95 | 97 | 100 | 27 |  |  |  | 231687
114 | Kodda 149 MW PP Unit-1 (Summit) | 145 | 143 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 129 | 126 | 123 | 126 | 128 | 122 | 112 |  | 122 | 146 | 146 | 149 | 145 | 148 | 148 | 3326400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 10 | [5 empty] | 30 | 45 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1704000
116 | Chandpur 200MW (Desh energy) | 179 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 125 | 134 | 143 | 143 | 143 | 143 | 143 | 152 |  | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 3992160
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 331 | 331 | 331 | 333 | 338 | 330 | 333 | 361 | 75 | 242 | 222 | 248 | 221 | 249 | 232 | 245 | 222 | 222 |  | 222 | 222 | 221 | 222 | 222 | 222 | 222 | 6323000
| Jamalpur 115 MW PP (United) | 16 | [5 empty] | 7 | 65 | 103 | 109 | 98 | 109 | 109 | 109 | 109 | 109 | 109 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1938000
| Anwara 300 MW PP (United) | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 124 | 88 | 141 | 125 | 124 | 104 | 107 | 159 | 162 | 161 |  | 196 | 196 | 197 | 197 | 197 | 196 | 197 | 3733
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2425920
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | [19 empty] | 29 | 37 | 36 | 36 | 36 | 36 | 27 | 204480
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 10 | 18 | 23 | 29 | 29 | 28 | 26 | 21 | 13 | 5 | [9 empty] | 207521
120 | Eastern Zone Total | 7283 | 6986 | 6662 | 6555 | 6475 | 6421 | 6494 | 6598 | 6684 | 7253 | 7458 | 7699 | 7804 | 7730 | 7830 | 7837 | 7590 | 7485 |  | 8753 | 8836 | 8782 | 8513 | 8358 | 8038 | 7743 | 176990372
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 66 | 16 | [6 empty] | 31 | 49 | 90 | 93 | 91 | 85 | 80 | 99 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1237440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 95 | 95 | 53 | 35 | 35 | 35 | 35 | 95 | 95 | 94 | 94 | 94 | 93 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2028480
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | [8 empty] | 4 | 3 | 3 | 3 | 3 | 4 | 25 | 26 | 25 | 26 |  | 26 | 25 | 25 | 26 | 26 |  |  | 255927
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | [12 empty] | 16 | 16 | 16 | 16 | 16 |  | 70 | 64 | 48 | 48 | 48 | 48 | 48 | 442848
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 94 | 93 | 93 | 91 | 91 | 91 | 93 | 93 | 93 | 92 | 92 | 91 | 92 | 93 | 92 | 93 | 96 | 100 |  | 100 | 100 | 97 | 99 | 96 | 97 | 97 | 2262883
| Bhola 225 MW CCPP | 50 | 54 | 60 | 60 | 60 | 58 | 60 | 60 | 50 | 60 | 56 | 66 | 67 | 66 | 65 | 65 | 62 | 68 |  | 68 | 68 | 68 | 66 | 66 | 62 | 66 | 1480300
140 | Bhola 33 MW PP (Venture) | 27 | 27 | 27 | 26 | 25 | 25 | 19 | 18 | 18 | 20 | 23 | 26 | 26 | 25 | 25 | 21 | 24 | 27 |  | 30 | 31 | 32 | 30 | 31 | 31 | 30 | 607175
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 43 | 96 | 96 | 70 | 30 | 30 |  | 330240
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 226125
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 6 | 12 |  | 15 | 14 | 14 |  |  |  |  | 37760
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 719 | 718 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 719 | 718 | 719 |  | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 17381818
147 | Bheramara 410 MW CCPP | 285 | 290 | 295 | 300 | 300 | 310 | 315 | 305 | 295 | 290 | 285 | 275 | 265 | 265 | 260 | 260 | 265 | 270 |  | 280 | 280 | 290 | 305 | 325 | 340 | 365 | 7172352
148 | Payra 1320 MW | 550 | 550 | 540 | 510 | 480 | 480 | 460 | 430 | 410 | 410 | 440 | 450 | 470 | 480 | 480 | 480 | 440 | 440 |  | 490 | 530 | 530 | 560 | 570 | 570 | 550 | 12781800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3669100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 17 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 |  |  | 565003
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 161 | 161 | 161 | 160 | 160 | 163 | 163 | 163 | 174 | 187 | 175 | 162 | 150 | 147 | 147 | 146 | 144 | 145 |  | 149 | 153 | 157 | 169 | 176 | 176 | 176 | 4094209
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 173 | 179 | 184 | 185 | 190 | 190 | 190 | 190 | 204 | 196 | 195 | 191 | 184 | 176 | 176 | 152 | 158 | 164 |  | 168 | 173 | 173 | 173 | 176 | 184 | 200 | 4601600
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 375 | 401 | 401 | 400 | 399 | 399 | 400 | 400 | 361 | 337 | 404 | 414 | 413 | 338 | 339 | 412 | 391 | 352 |  | 419 | 396 | 399 | 386 | 405 | 386 | 389 | 9336327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 7 | 32 | 35 | 17 |  |  |  | 67642
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 17 | 17 | 16 | 16 | 18 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 457200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 194706
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 12660
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 50 | 50 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 |  |  |  | 375289
167 | Katakhali 50 MW Peaking PP | [17 empty] | 5 |  | 30 | 32 | 32 | 32 |  |  |  | 93405
168 | Santahar 50 MW Peaking PP | [12 empty] | 20 | 20 | 20 | 17 | 17 | 20 |  | 24 | 26 | 26 | 20 | 19 | 20 | 14 | 219762
169 | Natore 52 MW PP (Rajlanka) | 8 | [7 empty] | 40 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 25 |  | 749760
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 56 | 58 | 75 | 75 | 74 | 95 |  | 100 | 100 | 100 | 98 | 98 | 49 | 49 | 888328
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 50 | 50 | [5 empty] | 85811
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 70 | 70 | 75 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2230752
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 35 | 35 | 35 | 50 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2439264
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 113 | 113 | 34 | 34 | 34 | 62 | 90 | 105 | 113 | 113 | 113 | 106 | 106 | 102 | 102 | 107 | 112 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2350080
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 5 | 6 | 6 | 6 | 5 | 4 | 3 | 2 | 0 |  | 0 | [6 empty] | 40893
178
178