## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-27 | Saturday
|  | Date (day): | 2021-03-27 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15162.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15935 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-26 | 2021-03-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170 |  | 20 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 190 | 190 | 190 | 190 |  | 175 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 95 | 99 | 99 |  | 9 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 369 | 351 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 348 | 360 | 360 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 235 | 225 | 235 | 235 | 70 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 30 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 85 | 85 |  | 15 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 184 | 180 | 100 | 180
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 20 | 49 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 82 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 54 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 60 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 122 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 54 | 70 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 32 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2133 | 2770 | 4199 | 4499 | 178 | 1184
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 8 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 102 | 102
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 16 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 38 | 38 | 20 | 35
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  |  | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 72 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 703 | 869 | 1679 | 1719 | 520 | 98
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 90 | 90 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 181 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 295 | 350 | 350
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 290 | 350 | 350
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 30 | 50 | 50 | 5 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | under maint.
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 91 | 90 | 90 |  | 73 | Under maint.
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 71 | 120 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 160 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20 | 20 |  | 5 | Engine problem
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 41 | 75 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1395 | 1531 | 2095 | 2262 | 340 | 78
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 207 | 210 | 210
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 72 | 77 | 77 |  | 18 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 191 | 184 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 22 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 526 | 617 | 697.6 | 646 | 0 | 18
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 44 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 140 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 211 | 210 | 210 | 210 |  | 120 | Machine problem
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 81 | 81
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 40 | 150 | 150 | 150 |  | 81 | ST Under maint
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 241 | 240 | 250 | 250 |  | 150 | Engine problem
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 310 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1514 | 1619 | 1777 | 1777 | 0 | 622
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 727 | 720 | 735 | 735
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 410 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 33 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 60 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 75 | 90 | 95 |  | 10 | Engine problem
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1213 | 1397 | 1599 | 1890 | 0 | 104
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 26 | 25 | 25
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 70 | 70 |  | 124 | GT-2 under maint
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 13 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 600 | 622 | 622
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 175 | 124 | 120 | 120 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 635 | 855 | 1192 | 1192 | 0 | 124
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 201 | 198 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 196 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 388 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 21 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 14 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1041 | 1208 | 1643 | 1677 | 381 | 0
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 97 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 253 | 263 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 9413 | 11129 | 15162.6 | 15935 | 1543 | 2428
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8854.7666 | 10469 | 14263.3893 | 14989.9825
A. |  | 2021-03-26 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11129 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8760 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11129 | MW
3 | Day peak Generation : |  |  | 9413 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10469 | MW
4 | Evening peak Generation : |  |  | 11129 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 234.8799 | MKWHr | By Solar | 0.70404 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 147.2356 | MKWHr |  | By Oil: | 49.441 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 15.1292 | MKWHr |  | By Hydro: | 1.7 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1543 | MW | Dhaka | 3606 | 3606 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2428 | MW | Chittagong | 916 | 916 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3971 | MW | Khulna | 1339 | 1339 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1186.25 | MMCFD |  |  | Rajshahi | 1188 | 1188 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 155135593.506 | ii) Oil : | Taka | 342773211.7 | Comilla | 1085 | 1085 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 70195228 | Total | Taka | 568104033.206 | Mymensingh | 970 | 970 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.275 | MKWHr. | Sylhet | 407 | 407 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 30 | MW (E to W) at | 21:00 | hrs | Barisal | 277 | 277 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -200 | MW at | 19:30 | hrs | Rangpur | 681 | 681 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 37.6° C |  |  | Total | 10469 | 10469 |  | 0
B. |  | 2021-03-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 38.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15935 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10400 | MW
4 | Reserve(Generation end) |  |  |  | 3535 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 261.7046 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8585 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.432 | MKWHr. | ii) HVDC Flow at Peak Time |  | 720 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2381 | MKWHr. | iii) Maximum HVDC Flow : |  | 727 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.78 |  | (b) Today: | 86.54 |  | (c) Rule Curve: |  | 89
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 333 | 0 |  | 0 | 450 | 235 | 100 | 85 | 55 | 0 | 0 | 145 | 100 | 32 | 64 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 92 | 20 | 44 | 16 | 38 | 90 | 0 | 80 | 260 | 270 | 170 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 138 | 127 | 56 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 209 | 0 | 80 | 0 | 105 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 193 | 0 | 116 | 0 | 100 | 71 | 0 | 240 | 85 | 70 | 0 | 0 | 106 | 12 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 144 | 5 | 0 | 32 | 0 |  | 721 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 180 | 0 | 388 | 93 | 0 | 94 | 0 | 107 | 0 | 0 | 95 | 540 | 96 | 0 | 0 |  | 7421 | 3184 | 10605 | 4086 | 721 | 1743 | 3093 | 690 | 70 | 64 | 138 | 0 | 0 | 86.83
2:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 342 | 0 |  | 0 | 450 | 235 | 60 | 96 | 55 | 0 | 0 | 150 | 100 | 32 | 48 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 203 | 0 | 120 | 0 |  | 22 | 0 | 0 | 92 | 0 | 26 | 16 | 40 | 90 | 0 | 80 | 260 | 270 | 172 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 138 | 147 | 30 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 210 | 0 | 80 | 0 | 105 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 193 | 0 | 116 | 0 | 100 | 71 | 0 | 240 | 85 | 17 | 0 | 0 | 16 | 50 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 90 | 19 | 0 | 0 | 0 |  | 721 | 0 | 255 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 180 | 0 | 408 | 93 | 0 | 94 | 0 | 100 | 0 | 0 | 95 | 480 | 100 | 0 | 0 |  | 7038 | 3148 | 10186 | 4130 | 721 | 1759 | 2690 | 630 | 70 | 48 | 138 | 0 | 0 | 86.82
3:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 345 | 0 |  | 0 | 450 | 235 | 45 | 97 | 55 | 0 | 0 | 145 | 100 | 0 | 48 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 15 | 205 | 0 | 120 | 0 |  | 21 | 0 | 0 | 92 | 0 | 6 | 16 | 32 | 90 | 0 | 80 | 260 | 270 | 182 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 132 | 149 | 16 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 211 | 0 | 80 | 0 | 104 | 0 | 0 | 7 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 116 | 0 | 100 | 71 | 0 | 239 | 65 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 90 | 48 | 0 | 0 | 0 |  | 721 | 0 | 270 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 180 | 0 | 400 | 70 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 450 | 100 | 0 | 0 |  | 6811 | 3099 | 9910 | 4151 | 721 | 1746 | 2442 | 600 | 70 | 48 | 132 | 0 | 0 | 86.81
4:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 345 | 0 |  | 0 | 450 | 235 | 0 | 82 | 55 | 0 | 0 | 0 | 70 | 0 | 48 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 40 | 0 | 0 | 16 | 38 | 90 | 0 | 80 | 260 | 270 | 191 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 148 | 16 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 210 | 0 | 80 | 0 | 104 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 114 | 0 | 100 | 71 | 0 | 239 | 45 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 54 | 0 | 0 | 0 | 0 |  | 721 | 0 | 295 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 180 | 0 | 390 | 35 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 450 | 136 | 0 | 0 |  | 6432 | 3104 | 9536 | 4036 | 721 | 1772 | 2165 | 600 | 70 | 48 | 124 | 0 | 0 | 86.8
5:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 345 | 0 |  | 0 | 450 | 235 | 0 | 48 | 55 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 10 | 0 | 0 | 13 | 41 | 90 | 0 | 80 | 260 | 270 | 194 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 147 | 16 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 209 | 0 | 80 | 0 | 105 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 112 | 0 | 100 | 71 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 310 | 104 | 0 | 17 | 0 | 0 | 0 | 0 |  | 721 | 0 | 325 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 180 | 0 | 428 | 0 | 0 | 94 | 0 | 70 | 0 | 0 | 95 | 450 | 134 | 0 | 0 |  | 6165 | 3061 | 9226 | 4065 | 721 | 1810 | 1828 | 600 | 70 | 16 | 116 | 0 | 0 | 86.79
6:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 345 | 0 |  | 0 | 450 | 235 | 0 | 15 | 55 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 10 | 0 | 0 | 13 | 41 | 90 | 0 | 80 | 260 | 270 | 195 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 148 | 16 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 210 | 0 | 80 | 0 | 104 | 0 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 99 | 0 | 100 | 71 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 104 | 0 | 17 | 0 | 0 | 0 | 0 |  | 721 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 180 | 0 | 398 | 0 | 0 | 94 | 0 | 70 | 0 | 0 | 95 | 420 | 138 | 0 | 0 |  | 5991 | 3011 | 9002 | 4092 | 721 | 1792 | 1649 | 570 | 70 | 0 | 108 | 0 | 0 | 86.78
7:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 361 | 0 |  | 0 | 400 | 235 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 0 | 35 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 213 | 0 | 120 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 13 | 42 | 90 | 0 | 80 | 280 | 290 | 184 | 8 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 160 | 16 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 211 | 0 | 78 | 0 | 104 | 0 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 99 | 0 | 60 | 71 | 0 | 239 | 0 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 68 | 4 | 0 | 0 | 0 | 0 | 3 |  | 721 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 17 | 0 | 180 | 0 | 428 | 0 | 0 | 94 | 0 | 70 | 0 | 1 | 95 | 420 | 138 | 0 | 0 |  | 5748 | 3012 | 8760 | 4183 | 721 | 1752 | 1351 | 570 | 70 | 0 | 104 | 9 | 0 | 86.77
8:00 | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 369 | 0 |  | 0 | 380 | 235 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 10 | 35 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 202 | 0 | 120 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 13 | 42 | 90 | 0 | 80 | 260 | 265 | 197 | 8 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 16 | 100 | 160 | 16 | 17 | 1 | 44 | 30 | 53 | 0 | 130 | 211 | 0 | 77 | 0 | 104 | 0 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 100 | 0 | 60 | 71 | 0 | 240 | 6 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 16 | 100 | 310 | 54 | 17 | 0 | 0 | 0 | 0 | 10 |  | 727 | 0 | 385 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 180 | 0 | 406 | 53 | 0 | 94 | 0 | 87 | 0 | 2 | 95 | 420 | 136 | 0 | 0 |  | 5709 | 3116 | 8825 | 4154 | 727 | 1698 | 1474 | 570 | 70 | 0 | 100 | 32 | 0 | 86.76
9:00 | 0 | 0 | 0 | 170 | 190 | 91 | 0 | 340 | 0 |  | 0 | 400 | 235 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 0 | 35 | 22 | 25 | 20 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 203 | 0 | 120 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 13 | 36 | 90 | 0 | 80 | 265 | 265 | 204 | 8 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 100 | 159 | 16 | 17 | 2 | 44 | 30 | 53 | 0 | 130 | 212 | 0 | 77 | 0 | 105 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 99 | 6 | 60 | 71 | 0 | 240 | 55 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 36 | 100 | 310 | 54 | 29 | 0 | 0 | 0 | 0 | 11 |  | 727 | 0 | 400 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 180 | 0 | 388 | 53 | 0 | 94 | 0 | 98 | 0 | 3 | 95 | 380 | 115 | 0 | 0 |  | 5741 | 3062 | 8803 | 4143 | 727 | 1639 | 1540 | 530 | 70 | 0 | 100 | 54 | 0 | 86.75
10:00 | 0 | 0 | 0 | 170 | 190 | 89 | 0 | 343 | 0 |  | 0 | 420 | 235 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 17 | 35 | 19 | 25 | 20 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 204 | 0 | 120 | 0 |  | 17 | 0 | 0 | 0 | 0 | 0 | 13 | 40 | 90 | 0 | 80 | 260 | 270 | 211 | 8 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 120 | 155 | 16 | 17 | 2 | 43 | 30 | 50 | 0 | 130 | 210 | 0 | 74 | 0 | 0 | 0 | 0 | 8 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 97 | 13 | 60 | 71 | 0 | 240 | 55 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 36 | 100 | 310 | 53 | 39 | 0 | 0 | 0 | 0 | 27 |  | 727 | 0 | 405 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 13 | 0 | 180 | 0 | 422 | 0 | 0 | 94 | 0 | 94 | 0 | 4 | 95 | 370 | 115 | 0 | 0 |  | 5727 | 3066 | 8793 | 4059 | 727 | 1704 | 1504 | 520 | 70 | 0 | 120 | 89 | 0 | 86.74
11:00 | 0 | 0 | 0 | 170 | 190 | 88 | 0 | 349 | 0 |  | 0 | 420 | 235 | 0 | 0 | 30 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 17 | 35 | 19 | 25 | 20 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 205 | 0 | 120 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 13 | 40 | 90 | 0 | 80 | 275 | 280 | 195 | 8 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 122 | 152 | 24 | 17 | 2 | 43 | 30 | 50 | 0 | 163 | 210 | 0 | 77 | 0 | 0 | 0 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 102 | 16 | 60 | 70 | 0 | 241 | 75 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 36 | 90 | 310 | 53 | 44 | 0 | 0 | 0 | 0 | 30 |  | 727 | 0 | 400 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 13 | 0 | 198 | 0 | 416 | 0 | 0 | 94 | 0 | 95 | 0 | 5 | 95 | 370 | 156 | 0 | 0 |  | 5925 | 3114 | 9039 | 4199 | 727 | 1775 | 1525 | 520 | 70 | 0 | 122 | 101 | 0 | 86.73
12:00 | 0 | 0 | 0 | 170 | 190 | 87 | 0 | 369 | 0 |  | 0 | 420 | 235 | 0 | 0 | 30 | 0 | 0 | 184 | 0 | 0 | 16 | 0 | 0 | 0 | 20 | 54 | 17 | 35 | 19 | 25 | 15 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 218 | 0 | 120 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 13 | 38 | 90 | 0 | 80 | 295 | 295 | 199 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 33 | 19 | 128 | 152 | 24 | 17 | 2 | 42 | 30 | 50 | 0 | 163 | 211 | 0 | 78 | 0 | 40 | 0 | 0 | 7 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 100 | 17 | 100 | 71 | 0 | 241 | 75 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 41 | 90 | 310 | 54 | 46 | 0 | 0 | 0 | 0 | 32 |  | 727 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 13 | 0 | 200 | 0 | 409 | 0 | 0 | 94 | 0 | 97 | 0 | 6 | 95 | 370 | 175 | 0 | 0 |  | 6271 | 3142 | 9413 | 4463 | 727 | 1802 | 1580 | 520 | 70 | 16 | 128 | 107 | 0 | 86.72
13:00 | 0 | 0 | 0 | 170 | 190 | 87 | 0 | 348 | 34 |  | 0 | 420 | 235 | 0 | 20 | 55 | 0 | 0 | 120 | 16 | 0 | 16 | 0 | 0 | 0 | 20 | 54 | 55 | 35 | 19 | 25 | 10 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 120 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 13 | 36 | 90 | 0 | 80 | 260 | 265 | 180 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 33 | 19 | 140 | 151 | 24 | 17 | 2 | 42 | 30 | 52 | 0 | 130 | 212 | 0 | 78 | 0 | 40 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 172 | 0 | 115 | 16 | 100 | 70 | 0 | 241 | 115 | 0 | 0 | 5 | 0 | 40 | 0 | 0 | 36 | 100 | 310 | 96 | 43 | 0 | 0 | 0 | 0 | 29 |  | 727 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 59 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 13 | 0 | 191 | 0 | 414 | 0 | 0 | 102 | 0 | 98 | 0 | 6 | 95 | 370 | 195 | 0 | 0 |  | 6281 | 3157 | 9438 | 4255 | 727 | 1805 | 1804 | 520 | 70 | 16 | 140 | 101 | 9438 | 86.71
14:00 | 0 | 0 | 0 | 170 | 190 | 85 | 0 | 343 | 34 |  | 0 | 360 | 235 | 0 | 30 | 40 | 0 | 0 | 65 | 10 | 0 | 16 | 0 | 0 | 0 | 20 | 54 | 55 | 35 | 19 | 25 | 10 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 205 | 0 | 120 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 13 | 33 | 90 | 0 | 80 | 270 | 270 | 189 | 8 | 81 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 33 | 19 | 138 | 150 | 24 | 17 | 2 | 42 | 30 | 52 | 0 | 110 | 213 | 0 | 77 | 0 | 105 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 172 | 0 | 92 | 14 | 50 | 71 | 0 | 240 | 115 | 0 | 0 | 3 | 0 | 54 | 0 | 0 | 8 | 100 | 310 | 65 | 38 | 0 | 0 | 0 | 0 | 26 |  | 727 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 13 | 0 | 174 | 0 | 409 | 0 | 0 | 113 | 0 | 103 | 0 | 6 | 95 | 370 | 201 | 0 | 0 |  | 6079 | 3080 | 9159 | 4201 | 727 | 1719 | 1680 | 519 | 70 | 16 | 138 | 89 | 0 | 86.7
15:00 | 0 | 0 | 0 | 170 | 190 | 86 | 0 | 375 | 34 |  | 0 | 420 | 230 | 0 | 30 | 40 | 0 | 0 | 110 | 7 | 0 | 16 | 0 | 0 | 0 | 21 | 54 | 55 | 35 | 19 | 25 | 10 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 216 | 0 | 120 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 90 | 0 | 80 | 285 | 295 | 201 | 8 | 81 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 33 | 19 | 140 | 149 | 24 | 17 | 2 | 40 | 30 | 52 | 0 | 130 | 210 | 0 | 77 | 0 | 105 | 0 | 0 | 6 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 80 | 9 | 50 | 70 | 0 | 240 | 115 | 0 | 0 | 2 | 0 | 54 | 0 | 0 | 8 | 100 | 310 | 20 | 31 | 0 | 0 | 0 | 0 | 19 |  | 727 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 183 | 0 | 406 | 0 | 0 | 97 | 0 | 109 | 0 | 4 | 95 | 370 | 201 | 0 | 0 |  | 6225 | 3137 | 9362 | 4404 | 727 | 1815 | 1603 | 520 | 70 | 16 | 140 | 67 | 0 | 86.69
16:00 | 0 | 0 | 0 | 170 | 190 | 89 | 0 | 350 | 214 |  | 0 | 420 | 230 | 0 | 30 | 40 | 0 | 0 | 150 | 7 | 0 | 16 | 0 | 0 | 0 | 20 | 54 | 55 | 17 | 19 | 25 | 10 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 203 | 0 | 120 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 13 | 31 | 90 | 0 | 80 | 260 | 265 | 180 | 8 | 76 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 140 | 169 | 24 | 17 | 1 | 41 | 30 | 52 | 0 | 163 | 213 | 0 | 77 | 0 | 105 | 0 | 0 | 6 | 240 | 16 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 80 | 6 | 50 | 73 | 0 | 241 | 115 | 0 | 0 | 1 | 0 | 54 | 0 | 0 | 8 | 90 | 310 | 28 | 19 | 0 | 0 | 0 | 0 | 11 |  | 727 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 14 | 0 | 191 | 0 | 390 | 0 | 0 | 70 | 0 | 89 | 0 | 2 | 70 | 370 | 213 | 0 | 0 |  | 6260 | 3064 | 9324 | 4357 | 727 | 1958 | 1496 | 520 | 70 | 16 | 140 | 40 | 0 | 86.68
17:00 | 0 | 0 | 0 | 170 | 190 | 45 | 0 | 350 | 303 |  | 0 | 350 | 225 | 0 | 30 | 40 | 0 | 0 | 90 | 7 | 3 | 16 | 0 | 0 | 0 | 20 | 54 | 17 | 17 | 22 | 25 | 10 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 205 | 0 | 120 | 0 |  | 16 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 90 | 0 | 80 | 260 | 265 | 183 | 8 | 85 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 12 | 132 | 199 | 24 | 17 | 0 | 41 | 30 | 14 | 0 | 130 | 212 | 0 | 20 | 0 | 105 | 0 | 0 | 6 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 180 | 0 | 81 | 1 | 20 | 95 | 0 | 241 | 85 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 35 | 7 | 0 | 0 | 0 | 0 | 4 |  | 727 | 0 | 395 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 14 | 0 | 170 | 0 | 350 | 0 | 0 | 35 | 0 | 39 | 0 | 1 | 35 | 350 | 215 | 0 | 0 |  | 6035 | 2825 | 8860 | 4310 | 727 | 1836 | 1256 | 500 | 70 | 16 | 132 | 13 | 0 | 86.67
18:00 | 0 | 0 | 0 | 170 | 190 | 45 | 0 | 341 | 303 |  | 0 | 320 | 225 | 7 | 30 | 40 | 0 | 0 | 90 | 7 | 12 | 32 | 2 | 0 | 0 | 21 | 54 | 17 | 17 | 22 | 25 | 10 | 28 | 33 | 2 | 0 | 0 | 70 | 0 | 0 | 8 | 205 | 0 | 100 | 0 |  | 21 | 0 | 38 | 7 | 0 | 8 | 13 | 35 | 90 | 0 | 80 | 260 | 265 | 180 | 8 | 82 | 26 | 5 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 19 | 136 | 204 | 24 | 17 | 0 | 43 | 30 | 14 | 0 | 110 | 212 | 0 | 20 | 0 | 105 | 0 | 0 | 6 | 280 | 16 | 11 | 0 | 20 | 0 | 0 | 181 | 0 | 81 | 0 | 20 | 103 | 0 | 241 | 85 | 12 | 0 | 0 | 16 | 17 | 0 | 0 | 8 | 100 | 310 | 35 | 0 | 15 | 7 | 0 | 0 | 0 |  | 721 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 14 | 0 | 140 | 0 | 310 | 17 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 350 | 217 | 0 | 0 |  | 6116 | 2689 | 8805 | 4149 | 721 | 1724 | 1435 | 500 | 70 | 70 | 136 | 0 | 0 | 86.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 352 | 350 |  | 0 | 380 | 225 | 35 | 55 | 50 | 0 | 0 | 150 | 35 | 48 | 98 | 0 | 0 | 0 | 25 | 54 | 55 | 55 | 22 | 25 | 15 | 28 | 33 | 16 | 0 | 0 | 70 | 0 | 0 | 24 | 204 | 0 | 120 | 0 |  | 22 | 0 | 84 | 10 | 13 | 29 | 14 | 38 | 90 | 0 | 80 | 270 | 280 | 180 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 24 | 22 | 11 | 33 | 19 | 164 | 207 | 72 | 17 | 0 | 44 | 30 | 51 | 0 | 130 | 210 | 0 | 80 | 0 | 150 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 125 | 0 | 0 | 181 | 0 | 101 | 0 | 100 | 110 | 0 | 242 | 98 | 30 | 0 | 0 | 32 | 39 | 0 | 0 | 65 | 100 | 310 | 73 | 0 | 54 | 41 | 0 | 15 | 0 |  | 722 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 25 | 16 | 0 | 0 | 0 | 25 | 0 | 94 | 0 | 0 | 0 | 34 | 22 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 14 | 28 | 167 | 0 | 338 | 70 | 0 | 72 | 0 | 113 | 0 | 0 | 95 | 400 | 113 | 0 | 0 |  | 7512 | 3311 | 10823 | 4478 | 722 | 1945 | 2571 | 550 | 70 | 323 | 164 | 0 | 0 | 86.63
19:30 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 340 | 348 |  | 0 | 380 | 225 | 1 | 64 | 55 | 0 | 0 | 150 | 70 | 0 | 98 | 0 | 0 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 205 | 0 | 120 | 0 |  | 22 | 0 | 84 | 0 | 0 | 18 | 14 | 38 | 90 | 0 | 80 | 275 | 290 | 182 | 8 | 85 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 160 | 209 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 210 | 0 | 80 | 0 | 150 | 0 | 0 | 7 | 295 | 16 | 11 | 0 | 60 | 0 | 0 | 181 | 0 | 114 | 0 | 100 | 120 | 0 | 242 | 115 | 6 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 17 | 84 | 0 | 0 | 0 |  | 721 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 51 | 25 | 32 | 0 | 0 | 0 | 25 | 0 | 99 | 0 | 0 | 0 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 10 | 60 | 187 | 0 | 362 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 550 | 114 | 0 | 0 |  | 7485 | 3628 | 11113 | 4524 | 721 | 1996 | 2603 | 700 | 70 | 339 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 341 | 348 |  | 0 | 400 | 225 | 0 | 48 | 30 | 0 | 0 | 160 | 50 | 0 | 82 | 0 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 208 | 0 | 120 | 0 |  | 22 | 0 | 85 | 0 | 0 | 18 | 14 | 38 | 90 | 0 | 80 | 300 | 305 | 193 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 162 | 207 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 130 | 210 | 0 | 80 | 0 | 150 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 60 | 0 | 0 | 183 | 0 | 111 | 0 | 100 | 120 | 0 | 240 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 75 | 100 | 310 | 104 | 0 | 17 | 90 | 0 | 0 | 0 |  | 721 | 0 | 405 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 26 | 32 | 0 | 0 | 0 | 25 | 0 | 99 | 0 | 0 | 0 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 60 | 188 | 0 | 388 | 75 | 0 | 110 | 0 | 113 | 0 | 0 | 95 | 560 | 108 | 0 | 0 |  | 7426 | 3667 | 11093 | 4597 | 721 | 2024 | 2483 | 710 | 70 | 326 | 162 | 0 | 0 | 86.64
21:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 351 | 348 |  | 0 | 400 | 225 | 0 | 30 | 30 | 0 | 0 | 180 | 50 | 0 | 82 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 204 | 0 | 120 | 0 |  | 22 | 0 | 68 | 0 | 0 | 19 | 16 | 38 | 90 | 0 | 80 | 295 | 290 | 181 | 8 | 91 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 160 | 207 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 140 | 210 | 0 | 80 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 60 | 0 | 0 | 184 | 0 | 122 | 0 | 100 | 120 | 0 | 240 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 75 | 100 | 310 | 70 | 0 | 17 | 72 | 0 | 0 | 0 |  | 720 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 13 | 60 | 196 | 0 | 388 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 600 | 124 | 0 | 0 |  | 7406 | 3723 | 11129 | 4634 | 720 | 2081 | 2430 | 750 | 70 | 284 | 160 | 0 | 0 | 86.63
22:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 341 | 350 |  | 0 | 400 | 225 | 0 | 30 | 30 | 0 | 0 | 180 | 40 | 0 | 48 | 0 | 0 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 203 | 0 | 120 | 0 |  | 22 | 0 | 68 | 0 | 0 | 19 | 16 | 38 | 90 | 0 | 80 | 295 | 290 | 181 | 8 | 91 | 26 | 47 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 154 | 212 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 140 | 210 | 0 | 80 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 30 | 0 | 0 | 184 | 0 | 126 | 0 | 100 | 120 | 0 | 239 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 310 | 70 | 0 | 17 | 35 | 0 | 0 | 0 |  | 721 | 0 | 405 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 58 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 60 | 188 | 0 | 388 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 560 | 123 | 0 | 0 |  | 7267 | 3653 | 10920 | 4603 | 721 | 2098 | 2319 | 710 | 70 | 245 | 154 | 0 | 0 | 86.62
23:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 340 | 353 |  | 0 | 400 | 225 | 0 | 40 | 30 | 0 | 0 | 180 | 30 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 203 | 0 | 120 | 0 |  | 22 | 0 | 68 | 0 | 0 | 19 | 14 | 38 | 90 | 0 | 80 | 295 | 290 | 181 | 8 | 90 | 26 | 49 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 154 | 211 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 140 | 212 | 0 | 80 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 30 | 0 | 0 | 183 | 0 | 126 | 0 | 100 | 120 | 0 | 239 | 75 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 310 | 70 | 0 | 17 | 35 | 0 | 0 | 0 |  | 721 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 13 | 0 | 187 | 0 | 386 | 74 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 540 | 124 | 0 | 0 |  | 7162 | 3377 | 10539 | 4602 | 721 | 2093 | 2094 | 690 | 70 | 115 | 154 | 0 | 0 | 86.61
24:00 | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 343 | 352 |  | 0 | 400 | 225 | 0 | 30 | 30 | 0 | 0 | 180 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 189 | 0 | 120 | 0 |  | 22 | 0 | 34 | 0 | 0 | 19 | 13 | 41 | 90 | 0 | 80 | 295 | 290 | 181 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 156 | 213 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 140 | 210 | 0 | 80 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 124 | 0 | 100 | 120 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 310 | 70 | 0 | 17 | 35 | 0 | 0 | 0 |  | 721 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 195 | 0 | 13 | 0 | 190 | 0 | 363 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 500 | 103 | 0 | 0 |  | 6992 | 3236 | 10228 | 4598 | 721 | 2052 | 1931 | 650 | 70 | 50 | 156 | 0 | 0 | 86.6
KWH | 0 | 0 | 0 | 4095000 | 4578700 | 2103454 | 0 | 8546328 | 2856000 |  | 0 | 9141750 | 5394880 | 284160 | 923544 | 998171 | 0 | 0 | 2493000 | 810240 | 175392 | 753600 | 21281 | 0 | 0 | 720768 | 1311840 | 999208 | 1064870 | 450180 | 600000 | 530280 | 765700 | 792200 | 18240 | 0 | 0 | 1700000 | 0 | 0 | 419410 | 4804056 | 0 | 2867598 | 0 |  | 492480 | 0 | 446065 | 375240 | 40320 | 226080 | 321888 | 934080 | 2234236 | 0 | 1923456 | 6843500 | 6775000 | 4534000 | 200727 | 1007720 | 587592 | 442080 | 0 | 0 | 0 | 0 | 161470 | 488592 | 239580 | 798500 | 465530 | 3238080 | 3932000 | 837120 | 377676 | 15250 | 1022000 | 710400 | 1191000 | 0 | 3392918 | 4788000 | 0 | 1781760 | 0 | 2345840 | 55000 | 0 | 160380 | 7245500 | 173712 | 264096 | 0 | 870654 | 0 | 0 | 4485600 | 0 | 2541600 | 95310 | 1903680 | 2058720 | 0 | 5769000 | 1794000 | 171600 | 0 | 28207 | 278509 | 924591 | 0 | 0 | 1436400 | 2390400 | 7102500 | 1770240 | 319010 | 637920 | 426545 | 0 | 61560 | 208110 |  | 17432000 | 0 | 9003168 | 0 | 1883520 | 0 | 0 | 0 | 480 | 0 | 231375 | 1500000 | 484400 | 135456 | 0 | 0 | 0 | 48711 | 0 | 395783 | 0 | 0 | 0 | 636000 | 118015 | 453840 | 0 | 245448 | 0 | 0 | 3668000 | 0 | 0 | 0 | 0 | 4557082 | 0 | 496942 | 240000 | 4658891 | 0 | 9511545 | 844800 | 0 | 2292864 | 0 | 2245440 | 0 | 38149 | 2142144 | 11461200 | 3591764 | 0 | 0 |  | 156562874 | 78317017 | 234879891 | 103247449 | 17432000 | 43988140 | 47678332 | 15129200 | 1700000 | 1762654 | 3238080 | 704036 | 0
Fuel Cost | 0 | 0 | 0 | 6019650 | 5082357 | 2776559.28 | 0 | 8631791.28 | 2941680 |  | 0 | 9964507.5 | 5988316.8 | 2156774.4 | 6363218.16 | 8444526.66 | 0 | 0 | 4312890 | 6101107.2 | 1599575.04 | 7415424 | 196210.82 | 0 | 0 | 6551781.12 | 9576432 | 7723877.84 | 10499618.2 | 337635 | 450000 | 0 | 0 | 0 | 176380.8 | 0 | 0 | 459000 | 0 | 0 | 3896318.9 | 5236421.04 | 0 | 4874916.6 | 0 |  | 0 | 0 | 4326830.5 | 3583542 | 350784 | 1790553.6 | 405578.88 | 2774217.6 | 3306669.28 | 0 | 2827480.32 | 5064190 | 6775000 | 4171280 | 258937.83 | 1158878 | 663978.96 | 618912 | 0 | 0 | 0 | 0 | 1542038.5 | 620511.84 | 179685 | 1397375 | 349147.5 | 24285600 | 4167920 | 7601049.6 | 479648.52 | 243085 | 1676080 | 1136640 | 2119980 | 0 | 3867926.52 | 4979520 | 0 | 3403161.6 | 0 | 4058303.2 | 120450 | 0 | 327175.2 | 7317955 | 130284 | 200712.96 | 0 | 6582144.24 | 0 | 0 | 23325120 | 0 | 25009344 | 1114173.9 | 15514992 | 22337112 | 0 | 5365170 | 16361280 | 1621620 | 0 | 0 | 2105528.04 | 8053187.61 | 0 | 0 | 12309948 | 15920064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100408320 | 0 | 9453326.4 | 0 | 14804467.2 | 0 | 0 | 0 | 5035.2 | 0 | 2410927.5 | 1695000 | 750820 | 1322050.56 | 0 | 0 | 0 | 479316.24 | 0 | 3502679.55 | 0 | 0 | 0 | 6162840 | 1144745.5 | 871372.8 | 0 | 185804.136 | 0 | 0 | 19880560 | 0 | 0 | 0 | 0 | 6015348.24 | 0 | 745413 | 4082400 | 5450902.47 | 0 | 9416429.55 | 8819712 | 0 | 21759279.36 | 0 | 17424614.4 | 0 | 421546.45 | 15830444.16 | 50314668 | 0 | 0 | 0 |  | 391677735.84 | 303358022.716 | 695035758.556 | 106980545.626 | 100408320 | 48155047.88 | 325899180.71 | 70195228 | 459000 | 16874030.99 | 24285600 | 1778805.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 190 | 87 | 0 | 369 | 0 |  | 0 | 420 | 235 | 0 | 0 | 30 | 0 | 0 | 184 | 0 | 0 | 16 | 0 | 0 | 0 | 20 | 54 | 17 | 35 | 19 | 25 | 15 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 218 | 0 | 120 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 13 | 38 | 90 | 0 | 80 | 295 | 295 | 199 | 8 | 80 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 33 | 19 | 128 | 152 | 24 | 17 | 2 | 42 | 30 | 50 | 0 | 163 | 211 | 0 | 78 | 0 | 40 | 0 | 0 | 7 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 100 | 17 | 100 | 71 | 0 | 241 | 75 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 41 | 90 | 310 | 54 | 46 | 0 | 0 | 0 | 0 | 32 |  | 727 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 13 | 0 | 200 | 0 | 409 | 0 | 0 | 94 | 0 | 97 | 0 | 6 | 95 | 370 | 175 | 0 | 0 |  | 9413 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 190 | 95 | 0 | 351 | 348 | 0 | 0 | 400 | 225 | 0 | 30 | 30 | 0 | 0 | 180 | 50 | 0 | 82 | 0 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 204 | 0 | 120 | 0 | 0 | 22 | 0 | 68 | 0 | 0 | 19 | 16 | 38 | 90 | 0 | 80 | 295 | 290 | 181 | 8 | 91 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 160 | 207 | 72 | 17 | 0 | 44 | 30 | 53 | 0 | 140 | 210 | 0 | 80 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 60 | 0 | 0 | 184 | 0 | 122 | 0 | 100 | 120 | 0 | 240 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 75 | 100 | 310 | 70 | 0 | 17 | 72 | 0 | 0 | 0 |  | 720 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 13 | 60 | 196 | 0 | 388 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 600 | 124 | 0 | 0 |  | 11129 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 190 | 99 | 0 | 412 | 360 | 0 | 0 | 450 | 235 | 100 | 100 | 55 | 0 | 0 | 180 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 22 | 35 | 100 | 0 | 80 | 350 | 350 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 210 | 77 | 22 | 0 | 44 | 30 | 51 | 0 | 163 | 210 | 0 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 250 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 0 |  |  | 735 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 120 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 190 | 99 | 0 | 412 | 360 | 0 | 0 | 450 | 235 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 22 | 20 | 100 | 0 | 80 | 350 | 350 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 210 | 77 | 22 | 1.6 | 44 | 30 | 51 | 0 | 163 | 210 | 0 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 250 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 0 | 30 |  | 735 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 120 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 190 | 94 | 0 | 353 | 300 | 0 | 0 | 300 | 225 | 0 | 15 | 5 | 0 | 0 | 100 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 22 | 25 | 31 | 33 |  | 0 | 0 | 0 | 70 | 0 | 0 | 3 | 188 | 0 | 120 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 90 | 0 | 80 | 290 | 295 | 136 | 8 | 92 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 116 | 213 | 24 | 17 | 1 | 44 | 30 | 53 | 0 | 163 | 141 | 0 | 78 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 121 | 6 | 76 | 65 | 0 | 239 | 24 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 310 | 16 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 722 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 24 | 0 | 184 | 0 | 414 | 17 | 0 | 56 | 0 | 80 | 0 | 1 | 50 | 400 | 109 | 0 | 0 | 0
199
| Minimum Generation |  | 8760 | 7:00
| Highest Generation |  | 11129 | 21:00
| Day Peak Generation |  | 9413 | 12:00
| Evening Peak Generation |  | 11129 | 21:00
| HVDC Max Flow |  | 727 | 8:00
| HVDC EvPeak Flow |  | 720 | 21:00
| Load factor L.F |  | 87.94%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9413 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8585 | MW
Evening Peak Generation : |  | 11129 | MW Hour : | 21:00 | Available Max Generation : |  | 15935 | MW
E.P. Demand (at gen end) : |  | 11129 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12400 | MW
Maximum Generation : |  | 11129 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3535 | MW
Total Gen. (MKWH) : |  | 234.8799 | System Load Factor : | 87.94% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -200 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-27
Actual : | 86.54 | Ft.(MSL) , | Rule curve : | 89 | Ft.( MSL )
Gas Consumed : | Total = | 1186.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155135593.506
: |  | Coal : | 70195228 | Oil : | 342773211.7 | Total : | 568104033.206
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4339.18 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1478.3978 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1325.1009 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1197.5199 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1082.0824 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 873.2094 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 484.6056 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 224.7313 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 673.4799 |  |  | 0 | 0%
Total | 0 |  | 11678.3071 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Sirajganj #1 CCPP
7) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet 225 MW CCPP tripped at 09:31 due to flame failure and was synchronized at 11:42.
b) AES Haripur 360 MW Gt was synchronized at 12:21.
c) Siddhirganj 210 MW GT-2 was synchronized at 10:01.
d) Siddhirganj 210 MW GT-1 was synchronized at 10:38.
e) Chandpur 150 MW GT was synchronized at 11:53.
f) Rampura-Bashundhara 132 kV Ckt-1 was switched on at 08:26.
g) Tangail-Kaliakoir 132 kV Ckt-2 was under shut down from 09:56 to 12:16 for C/M.
h) Sylhet 225 MW CCPP ST was synchronized at 13:17.
i) Aminbazar 230/132 kV T-3 transformer was under shut down from 17:24 to 17:48 due maintenance work.
j) Gopalganj(N)-Faridpur 132 kV Ckt-1 tripped at 22:59 from both end showing Dist. Z1, auto reclose
and was switched on at 23:22.
k) Shahjibazar 330 MW Gt-2 was shut down at 00:30(27-03-2021) due to filter clearing (DP high).
l) Ashuganj 225 MW STG was shut down at 03:40(27-03-2021) due to work on BFP.
m) Ghorasal 132 kV Bus-2 was under shut down from 06:39(27-03-2021) to 09:54(27-03-2021) red hot
maintenance at bus isolator.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4095000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 190 | 4578700
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2103454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8546328 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 2856000 | Synchronized at 12:21.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9141750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 284160 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 225 | 5394880 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 30 | 923544 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 998171 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 21281 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 450180
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 2493000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 810240 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 175392 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 49 | 720768
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1311840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 753600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 999208
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1064870
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1130280 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 765700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 18240 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 60 | 870654 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 122 | 2541600 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 171600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1770240 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 637920 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 208110
| Dhaka area Total |  |  |  | 5972 | 2770 | 56628910
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 419410 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 95310
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 226080 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1700000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4804056 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2867598
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer O/L
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 446065 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 375240 | Reserve.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1903680
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 321888 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 934080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 40320 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28207
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 278509 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 924591
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2390400
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 426545 | Low demand
| Chattogram area Total |  |  |  | 2382 | 869 | 18181979
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 90 | 2234236 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4534000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 6843500 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6775000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 587592 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 442080 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 1007720 | Synchronized at 11:53.
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 2058720 | Machine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 488592
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3238080
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 798500
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 161470 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 465530
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 1436400 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 61560
| Cumilla Area Total |  |  |  | 2980 | 1531 | 33496743
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 207 | 3932000 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 377676
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 837120 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15250
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 184 | 4485600
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1794000 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 319010
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 492480
| Mymensingh Area Total |  |  |  | 709 | 617 | 12253136
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1022000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 710400 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3392918
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 210 | 4788000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1191000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264096
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1781760
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 2345840
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 55000 | Machine problem
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 173712 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7245500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 240 | 5769000 | Gas shortage
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 160380
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 310 | 7102500 | FGMO
| Sylhet Area Total |  |  |  | 2371 | 1619 | 36002106
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 720 | 17432000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1883520 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 480 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line over load
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9003168
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 231375 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 60 | 240000 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 844800 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1397 | 29635343
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 135456 | Line O/L.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 484400
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1500000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 13 | 496942 | Line O/L.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 11461200 | Line O/L.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 124 | 3591764 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 855 | 17669762
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 48711 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4557082 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 196 | 4658891 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 388 | 9511545 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 118015 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 453840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245448
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 636000
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 395783
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2292864 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 2142144 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1208 | 25060323
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3668000 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2245440
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38149
| Rangpur Area Total |  |  |  | 605 | 263 | 5951589
| Total |  |  |  | 21312 | 11129 | 234879891
| Eastern Grid Total |  |  |  | 14414 | 7406 | 156562874
| Western Grid Total |  |  |  | 6898 | 3723 | 78317017
| National Grid Total |  |  |  | 21312 | 11129 | 234879891
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-26
(a) ENTIRE EASTERN GRID : |  | 6984 | MW | (b) ENTIRE WESTERN GRID : |  | 3485 | MW
i) Dhaka area |  | 3606 | MW | i) Khulna area |  | 1339 | MW
ii) Chittagong area |  | 916 | MW | ii) Rajshahi area |  | 1188 | MW
iii) Comilla area |  | 1085 | MW | iii) Barisal area |  | 277 | MW
iv) Mymensingh area |  | 970 | MW | iv) Rangpur area |  | 681 | MW
v) Sylhet area |  | 407 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10469 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 1:00 | Jamalpur | 143 | 19:00 | Jhenida | 108 | 19:00
Munsiganj | 120 | 19:00 | Sherpur | 128 | 19:00 | Bottail | 96 | 19:00
Sonargaon | 80 | 0:00 | Srimongal | 47 | 19:00 | G.K Project | 43 | 19:30
Shyampur | 196 | 1:00 | Shahjibazar | 102 | 21:00 | Faridpur | 156 | 19:00
Bhulta | 185 | 1:00 | Fenchuganj | 36 | 18:30 | Madaripur | 86 | 19:30
Madanganj | 58 | 0:00 | Kulawara | 32 | 18:30 | Sariatpur | 54 | 20:00
Shitalakhya | 100 | 1:00 | Sylhet | 100 | 18:30 | Gopalganj | 74 | 19:30
Rahim steel | 20 | 1:00 | Chatak | 27 | 19:30 | Bagerhat | 93 | 19:30
Matuail | 48 | 3:00 | Sunamganj | 36 | 20:00 | Mongla | 34 | 1:00
Ghorasal | 69 | 3:00 | Biani Bazar | 46 | 21:00 | Satkhira | 100 | 22:00
Narsingdi | 155 | 1:00 | Comilla (S) | 164 | 19:00 | Gallamari | 30 | 1:00
Haripur (SBU) | 126 | 1:00 | Comilla(N) | 109 | 19:00 | Magura | 50 | 19:00
Sreenagar |  |  | Chandpur | 66 | 19:30 | Norail | 36 | 19:00
Ullon | 80 | 22:00 | Feni | 111 | 19:00 | Chuadanga | 83 | 21:00
Hasnabad | 100 | 19:30 | Chowmuhani | 171 | 19:00 | Borguna | 14 | 22:00
Magbazar | 71 | 19:00 | Ashuganj | 56 | 20:00 | Barisal(N) | 35 | 19:00
Maniknagar | 70 | 21:00 | Daudkandi | 134 | 20:00 | Barisal (S) | 90 | 22:00
Bangabhaban | 6 | 1:00 | B.Baria | 120 | 21:00 | Patuakhali | 86 | 2200
Narinda | 72 | 21:00 | Ramganj | 74 | 18:30 | Bhandaria | 40 | 19:30
Dhanmondi | 108 | 19:30 | Chaddagram | 35 | 19:30 | Borhan Uddin | 32 | 18:30
Lalbag | 70 | 1:00 | PHP | 10 | 10:00 | Ishurdi | 51 | 19:00
Madartek | 71 | 23:00 | Kochua | 57 | 18:30 | Ruppur Paromanobik | 2 | 18:00
Dhaka University | 20 | 21:00 | Madunaghat | 55 | 1:00 | Natore | 123 | 19:30
Aftabnagar | 33 | 23:00 | Hathazari | 84 | 19:30 | Bogra | 144 | 19:30
Fatullah | 59 | 1:00 | Khulshi | 159 | 0:00 | Noagaon | 107 | 19:30
Nawabganj | 44 | 21:00 | Halishahar | 117 | 19:30 | Rajshahi | 131 | 20:00
Mirpur | 98 | 19:00 | Baraulia | 129 | 2:00 | Rajshahi New | 18 | 21:00
Kalyanpur | 87 | 19:00 | Sikalbaha | 27 | 18:30 | C.Nawabganj | 75 | 21:00
Gulshan | 52 | 18:30 | Dohazari | 82 | 18:30 | Amnura | 56 | 21:00
Uttara | 79 | 18:30 | Cox'sbazar | 100 | 23:00 | Pabna | 81 | 20:00
Uttara New | 22 | 22:00 | Chandraghona | 30 | 18:30 | Shahjadpur | 98 | 19:00
Kamrangirchar | 80 | 1:00 | Kaptai |  |  | Serajganj | 82 | 19:00
Savar | 150 | 1:00 | A. Khaer Stl. | 9 | 1:00 | Niyamatpur | 92 | 19:00
Bhasantec | 140 | 20:00 | Bakulia | 89 | 1:00 | Joypurhat | 56 | 20:00
Agargaon | 58 | 19:00 | Julda | 22 | 1:00 | Sherpur(Bogura) | 48 | 19:00
Satmosjid | 89 | 19:00 | TK chemical | 24.5 | 20:00 | Mohastangor | 54 | 19:00
Tongi | 93 | 1:00 | Modern Steel |  |  | Bangura | 19 | 19:00
Kabirpur | 176 | 1:00 | Shahmirpur | 20 | 1:00 | Rangpur | 117 | 19:00
Basundhara | 157 | 18:30 | Khagrachhari | 22 | 1:00 | Lalmonirhat | 41 | 19:00
Manikganj | 68 | 19:30 | Matarbari | 34 | 18:30 | Saidpur | 87 | 19:00
Joydevpur | 126 | 1:00 | Baroiar Hat | 34 | 19:00 | Purbasadipur | 98 | 21:00
New Tongi | 79 | 1:00 | Rangamati | 12 | 18:30 | Thakurgaon | 76 | 19:00
Kodda | 206 | 1:00 | Abul Khair 230 | 12 | 8:00 | Palashbari | 105 | 19:00
Dhamrai | 84 | 1:00 | BSRM | 113 | 1:00 | Barapukuria | 48 | 19:30
Rajendrapur | 78 | 1:00 | GPH Ispat | 81 | 15:00 | Panchagar | 46 | 19:00
Valuka | 98 | 19:00 | Goalpara | 27 | 22:00 | Joldhaka | 57 | 19:30
Tangail | 213 | 19:00 | Central s/s | 81 | 20:00 | Kurigram | 54 | 19:00
Mymensing | 217 | 19:00 | Noapara | 38 | 0.79167 | Mithapukur | 28 | 19:00
Kishorganj | 128 | 23:00 | Jessore | 120 | 19:30
Netrokona | 123 | 18:30 | Benapol | 58 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 1:00 | 402 | 4:00 | Kaliakoir | 394 | 0.125 | 385 | 0.29167
| Bheramara | 408 | 19:00 | 396 | 19:00 | Bhulta | 381 | 0.041667 | 373 | 0.5
| Ashuganj(N) | 387 | 1:00 | 381 | 11:00 | Gopalganj | 406 | 0.625 | 384 | 0.8125
| Payra | 408 | 1:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 10:00 | Hathazari | 227 | 7:00 | 219 | 16:00
| Ishurdi | 233 | 22:00 | 225 | 7:00 | Megnaghat | 232 | 1:00 | 228 | 10:00
| Ashuganj | 235 | 1:00 | 231 | 12:00 | Fenchuganj | 242 | 18:00 | 239 | 11:00
| Serajganj | 233 | 1:00 | 225 | 7:00 | Siddhirganj | 228 | 1:00 | 224 | 9:00
| Baghabari | 232 | 3:00 | 227 | 19:00 | Maniknagar | 228 | 1:00 | 222 | 12:00
| Barapukuria | 235 | 24:00 | 226 | 18:30 | Agargaon | 227 | 3:00 | 218 | 15:00
| Bogra | 227 | 1:00 | 218 | 19:00 | Barisal | 246 | 19:00 | 237 | 19:00
| Rajshahi | 228 | 3:00 | 220 | 19:00 | Bhola 225 MW | 248 | 7:00 | 240 | 23:00
| Khulna South | 236 | 18:30 | 217 | 7:00 | AKSML | 229 | 19:00 | 219 | 15:00
| Rampura | 228 | 1:00 | 223 | 11:00 | BSRM | 230 | 19:00 | 221 | 15:00
| Haripur | 226 | 1:00 | 222 | 12:00 | Bibiyana | 242 | 1:00 | 236 | 12:00
| Hasnabad | 228 | 1:00 | 222 | 12:00 | Bhulta | 229 | 2:00 | 224 | 10:00
| Shyampur | 226 | 1:00 | 220 | 12:00 | Ashuganj (S) | 233 | 2:00 | 230 | 7:00
| Aminbazar | 227 | 1:00 | 221 | 2:00 | Kaliakoir | 228 | 1:00 | 219 | 16:00
| Tongi | 225 | 18:00 | 214 | 4:00 | GPH | 229 | 19:30 | 220 | 17:00
| Comilla (N) | 229 | 1:00 | 224 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 1:00 | 133 | 5:00 | Madanhat | 136 | 0.041667 | 131 | 0.625
| Munsiganj | 138 | 3:00 | 131 | 23:00 | Hathazari | 135 | 0.25 | 130 | 0.66667
| Sonargaon | 134 | 1:00 | 131 | 19:30 | Khulshi | 134 | 0.041667 | 129 | 0.625
| Shyampur | 136 | 18:00 | 132 | 7:00 | Halishahar | 135 | 0.041667 | 130 | 0.58333
| Bhulta | 131 | 18:30 | 126 | 23:00 | Baraulia | 135 | 0.79167 | 130 | 0.66667
| Madanganj | 135 | 1:00 | 129 | 11:00 | Sikalbaha | 139 | 0.91667 | 130 | 0.66667
| Shitalakhya | 140 | 18:30 | 132 | 12:00 | Dohazari | 132 | 0.20833 | 125 | 0.66667
| Rahim steal | 135 | 1:00 | 132 | 12:00 | Cox'sbazar | 126 | 0.25 | 117 | 0.5
| Matuail | 136 | 1:00 | 133 | 5:00 | Chandraghona | 134 | 0.083333 | 129 | 0.625
| Ghorasal | 138 | 19:00 | 136 | 9:00 | Kaptai
| Narsinghdi | 132 | 13:00 | 127 | 19:30 | A. Khaer Stl. | 133 | 0.041667 | 128 | 0.625
| Haripur (SBU) | 136 | 18:00 | 132 | 12:00 | Bakulia | 135 | 0.79167 | 129 | 0.70833
| Sreenagar |  |  |  |  | Julda | 137 | 0.041667 | 131 | 0.625
| Ullon | 136 | 4:00 | 132 | 11:00 | TK Chemical | 136 | 0.083333 | 130 | 0.70833
| Hasnabad | 136 | 18:30 | 132 | 9:00 | Modern Steel
| Magbazar | 135 | 19:00 | 131 | 12:00 | Shahmirpur | 136 | 0.79167 | 130 | 0.66667
| Maniknagar | 131 | 1:00 | 129 | 10:00 | Khagrachhari | 133 | 0.041667 | 128 | 0.625
| Bangabhaban | 131 | 1:00 | 129 | 10:00 | Matarbari | 128 | 0.125 | 119 | 0.625
| Narinda | 131 | 1:00 | 129 | 10:00 | Baroiar Hat | 133 | 0.041667 | 126 | 0.625
| Dhanmondi | 136 | 4:00 | 132 | 11:00 | Rangamati | 133 | 0.083333 | 129 | 0.625
| Lalbag | 136 | 18:00 | 131 | 11:00 | Goalpara S/S | 136 | 4:00 | 127 | 13:00
| Madartek | 135 | 1:00 | 131 | 23:00 | Khulna Central S/S | 137 | 18:30 | 125 | 7:00
| Dhaka University | 135 | 1:00 | 132 | 10:00 | Noapara | 134 | 18:30 | 124 | 0.54167
| Aftabnagar | 135 | 4:00 | 132 | 11:00 | Jessore | 128 | 18:00 | 119 | 0.29167
| Fatullah | 136 | 19:00 | 132 | 7:00 | Benapol | 129 | 18:30 | 119 | 0.29167
| Nawabganj | 130 | 1:00 | 127 | 12:00 | Jhenida | 127 | 18:30 | 116 | 0.79167
| Mirpur | 136 | 1:00 | 131 | 12:00 | Bottail | 131 | 0.75 | 125 | 0.79167
| Kalyanpur | 136 | 1:00 | 132 | 11:00 | G.K Project | 137 | 6:00 | 134 | 0.29167
| Gulshan | 135 | 6:00 | 131 | 12:00 | Faridpur | 135 | 0.375 | 129 | 0.8125
| Uttara | 137 | 1:00 | 131 | 12:00 | Madaripur | 141 | 0.375 | 132 | 0.8125
| Uttara New | 137 | 1:00 | 130 | 11:00 | Shariyatpur S/S | 139 | 0.125 | 131 | 0.8125
| Kamrangirchar | 133 | 1:00 | 130 | 11:00 | Gopalganj | 142 | 0.25 | 133 | 0.8125
| Savar | 139 | 1:00 | 129 | 12:00 | Bagerhat | 134 | 9:00 | 122 | 0.29167
| Bhasantec | 132 | 1:00 | 127 | 15:00 | Mongla | 134 | 0.375 | 122 | 0.29167
| Agargaon | 133 | 5:00 | 128 | 15:00 | Satkhira | 136 | 18:30 | 124 | 0.29167
| Satmosjid | 132 | 1:00 | 128 | 12:00 | Gallamari | 137 | 9:00 | 129 | 0.54167
| Tongi | 138 | 18:00 | 134 | 4:00 | Magura | 125 | 3:00 | 115 | 19:00
| Kabirpur | 136 | 18:00 | 128 | 7:00 | Narail | 124 | 0.33333 | 113 | 0.79167
| Basundhara | 135 | 18:30 | 130 | 5:00 | Chuadanga | 121 | 9:00 | 107 | 0.79167
| Manikganj | 139 | 18:00 | 132 | 5:00 | Borguna | 138 | 0.33333 | 131 | 0.875
| Joydevpur | 138 | 1:00 | 130 | 15:00 | Barisal(N) | 140 | 6:00 | 133 | 0.79167
| New Tongi | 138 | 19:00 | 130 | 8:00 | Barisal (S) | 138 | 8:00 | 131 | 0.8125
| Kodda | 139 | 18:30 | 129 | 5:00 | Patuakhali(S) | 139 | 5:00 | 127 | 19:30
| Dhamrai | 135 | 1:00 | 130 | 7:00 | Bhandaria | 136 | 0.29167 | 128 | 0.8125
| Rajendrapur | 134 | 19:00 | 126 | 6:00 | Ishurdi | 135 | 0.083333 | 131 | 0.29167
| Valuka | 123 | 3:00 | 114 | 8:00 | Ruppur Paromanobik | 135 | 0.083333 | 133 | 0.41667
| Tangail | 132 | 1:00 | 121 | 10:00 | Natore | 134 | 4:00 | 129 | 7:00
| Mymensing | 127 | 1:00 | 116 | 10:00 | Bogra | 137 | 4:00 | 129 | 8:00
| Kishorganj | 128 | 3:00 | 121 | 12:00 | Noagaon | 128 | 3:00 | 119 | 19:00
| Netrokona | 124 | 1:00 | 112 | 11:00 | Rajshahi | 133 | 18:00 | 128 | 7:00
| Jamalpur | 138 | 22:00 | 121 | 7:00 | Rajshahi New | 134 | 3:00 | 128 | 7:00
| Sherpur | 136 | 22:00 | 121 | 10:00 | C.Nawabganj | 131 | 18:30 | 123 | 7:00
| Srimongal | 139 | 6:00 | 135 | 17:00 | Amnura | 130 | 18:00 | 126 | 7:00
| Shahjibazar | 136 | 6:00 | 133 | 12:00 | Pabna | 134 | 3:00 | 131 | 8:00
| Fenchuganj | 138 | 8:00 | 135 | 19:00 | Shahjadpur | 140 | 5:00 | 135 | 8:00
| Khulawara | 137 | 5:00 | 135 | 11:00 | Serajganj | 133 | 4:00 | 128 | 19:00
| Sylhet | 135 | 7:00 | 131 | 11:00 | Niyamatpur | 127 | 1:00 | 114 | 8:00
| Chatak | 134 | 6:00 | 129 | 11:00 | Joypurhat | 128 | 14:00 | 117 | 19:00
| Sunamganj | 133 | 4:00 | 129 | 11:00 | Sherpur(Bogura) | 136 | 3:00 | 128 | 19:00
| Biani Bazar | 135 | 8:00 | 132 | 1:00 | Mohastangor | 134 | 4:00 | 129 | 19:00
| Comilla(s) | 128 | 3:00 | 123 | 18:30 | Bangura | 136 | 4:00 | 131 | 7:00
| Comilla(n) | 138 | 1:00 | 132 | 15:00 | Rangpur | 131 | 3:00 | 121 | 8:00
| Chandpur | 135 | 7:00 | 127 | 15:00 | Lalmonirhat | 131 | 4:00 | 120 | 8:00
| Feni | 133 | 5:00 | 124 | 15:00 | Saidpur | 130 | 3:00 | 117 | 19:00
| Chowmuhani | 136 | 2:00 | 122 | 15:00 | Purbasadipur | 130 | 3:00 | 115 | 19:00
| Ashuganj | 137 | 1:00 | 135 | 11:00 | Thakurgaon | 129 | 3:00 | 113 | 19:00
| Daudkandi | 133 | 1:00 | 128 | 22:00 | Palashbari | 132 | 3:00 | 121 | 7:00
| B.Baria | 134 | 6:00 | 130 | 12:00 | Barapukuria | 134 | 4:00 | 126 | 18:30

## L-Curve
Date | 2021-03-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 100 | 6992 | 3236 | 10228 |  |  |  | QF-LDC-11
0:30 | 80 | 7206.5 | 3210 | 10416.5 | Date: | 2021-03-26
1:00 | 60 | 7421 | 3184 | 10605
1:30 | 94 | 7229.5 | 3166 | 10395.5
2:00 | 128 | 7038 | 3148 | 10186
2:30 | 164 | 6924.5 | 3123.5 | 10048 | [5 empty] | Gen. at Eve. Peak | 11129 | 11129 MW (21:00 )
3:00 | 200 | 6811 | 3099 | 9910 | [6 empty] | 21:00
3:30 | 216 | 6621.5 | 3101.5 | 9723 | [5 empty] | Gen. at Day Peak | 9413 | 9413 MW (12:00 )
4:00 | 232 | 6432 | 3104 | 9536 | [6 empty] | 12:00
4:30 | 260 | 6298.5 | 3082.5 | 9381 | [5 empty] | Highest Generation | 11129
5:00 | 288 | 6165 | 3061 | 9226 | [6 empty] | 21:00
5:30 | 269 | 6078 | 3036 | 9114
6:00 | 250 | 5991 | 3011 | 9002
6:30 | 180 | 5869.5 | 3011.5 | 8881
7:00 | 110 | 5748 | 3012 | 8760
7:30 | 117 | 5728.5 | 3064 | 8792.5
8:00 | 124 | 5709 | 3116 | 8825
8:30 | 143 | 5725 | 3089 | 8814
9:00 | 162 | 5741 | 3062 | 8803
9:30 | 194 | 5734 | 3064 | 8798
10:00 | 226 | 5727 | 3066 | 8793
10:30 | 241 | 5826 | 3090 | 8916
11:00 | 256 | 5925 | 3114 | 9039
11:30 | 196 | 6098 | 3128 | 9226
12:00 | 136 | 6271 | 3142 | 9413
12:30 | 116.5 | 6276 | 3149.5 | 9425.5
13:00 | 97 | 6281 | 3157 | 9438
13:30 | 164.5 | 6180 | 3118.5 | 9298.5
14:00 | 232 | 6079 | 3080 | 9159
14:30 | 231 | 6152 | 3108.5 | 9260.5
15:00 | 230 | 6225 | 3137 | 9362
15:30 | 215 | 6242.5 | 3100.5 | 9343
16:00 | 200 | 6260 | 3064 | 9324
16:30 | 148 | 6147.5 | 2944.5 | 9092
17:00 | 96 | 6035 | 2825 | 8860
17:30 | 62 | 6075.5 | 2757 | 8832.5
18:00 | 28 | 6116 | 2689 | 8805
18:30 | 86 | 6814 | 3000 | 9814
19:00 | 144 | 7512 | 3311 | 10823
19:30 | 200 | 7485 | 3628 | 11113
20:00 | 28 | 7426 | 3667 | 11093 |  |  |  | Executive Engineer
20:30 | 29 | 7416 | 3695 | 11111 |  |  |  | Network Operation Division
21:00 | 30 | 7406 | 3723 | 11129
21:30 | 55 | 7336.5 | 3688 | 11024.5
22:00 | 80 | 7267 | 3653 | 10920 |  |  |  |  | Page 6 of 7
22:30 | 76 | 7214.5 | 3515 | 10729.5
23:00 | 72 | 7162 | 3377 | 10539
23:30 | 86 | 7077 | 3306.5 | 10383.5
24:00 | 100 | 6992 | 3236 | 10228
11129 MW (21:00 )
9413 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-26 |  | Energy | 234879891
[11 empty] | 2021-03-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4598 | 721 | 2052 | 2094 | 650 | 70 | 50 | 0 | 156 | 0
0:30 | 4342 | 721 | 1897.5 | 2593.5 | 670 | 70 | 57 | 0 | 147 | 0 | Date: | 2021-03-26
1:00 | 4086 | 721 | 1743 | 3093 | 690 | 70 | 64 | 0 | 138 | 0
1:30 | 4108 | 721 | 1751 | 2891.5 | 660 | 70 | 56 | 0 | 138 | 0 | [7 empty] | Total Energy | 234.8799 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4130 | 721 | 1759 | 2690 | 630 | 70 | 48 | 0 | 138 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4140.5 | 721 | 1752.5 | 2566 | 615 | 70 | 48 | 0 | 135 | 0 | [7 empty] | Energy Requirement | 234.8799
3:00 | 4151 | 721 | 1746 | 2442 | 600 | 70 | 48 | 0 | 132 | 0
3:30 | 4093.5 | 721 | 1759 | 2303.5 | 600 | 70 | 48 | 0 | 128 | 0 | [6 empty] | Shortage
4:00 | 4036 | 721 | 1772 | 2165 | 600 | 70 | 48 | 0 | 124 | 0
4:30 | 4050.5 | 721 | 1791 | 1996.5 | 600 | 70 | 32 | 0 | 120 | 0
5:00 | 4065 | 721 | 1810 | 1828 | 600 | 70 | 16 | 0 | 116 | 0
5:30 | 4078.5 | 721 | 1801 | 1738.5 | 585 | 70 | 8 | 0 | 112 | 0
6:00 | 4092 | 721 | 1792 | 1649 | 570 | 70 | 0 | 0 | 108 | 0
6:30 | 4137.5 | 721 | 1772 | 1500 | 570 | 70 | 0 | 0 | 106 | 4.5 |  |  |  |  | Coal
7:00 | 4183 | 721 | 1752 | 1351 | 570 | 70 | 0 | 0 | 104 | 9
7:30 | 4168.5 | 724 | 1725 | 1412.5 | 570 | 70 | 0 | 0 | 102 | 20.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4154 | 727 | 1698 | 1474 | 570 | 70 | 0 | 0 | 100 | 32
8:30 | 4148.5 | 727 | 1668.5 | 1507 | 550 | 70 | 0 | 0 | 100 | 43
9:00 | 4143 | 727 | 1639 | 1540 | 530 | 70 | 0 | 0 | 100 | 54
9:30 | 4101 | 727 | 1671.5 | 1522 | 525 | 70 | 0 | 0 | 110 | 71.5
10:00 | 4059 | 727 | 1704 | 1504 | 520 | 70 | 0 | 0 | 120 | 89
10:30 | 4129 | 727 | 1739.5 | 1514.5 | 520 | 70 | 0 | 0 | 121 | 95
11:00 | 4199 | 727 | 1775 | 1525 | 520 | 70 | 0 | 0 | 122 | 101
11:30 | 4331 | 727 | 1788.5 | 1552.5 | 520 | 70 | 8 | 0 | 125 | 104
12:00 | 4463 | 727 | 1802 | 1580 | 520 | 70 | 16 | 0 | 128 | 107
12:30 | 4359 | 727 | 1803.5 | 1692 | 520 | 70 | 16 | 0 | 134 | 104
13:00 | 4255 | 727 | 1805 | 1804 | 520 | 70 | 16 | 0 | 140 | 101
13:30 | 4255 | 727 | 1805 | 1804 | 520 | 70 | 16 | 0 | 140 | 101
14:00 | 4255 | 727 | 1805 | 1804 | 520 | 70 | 16 | 0 | 140 | 101
14:30 | 4329.5 | 727 | 1810 | 1703.5 | 520 | 70 | 16 | 0 | 140 | 84
15:00 | 4404 | 727 | 1815 | 1603 | 520 | 70 | 16 | 0 | 140 | 67
15:30 | 4380.5 | 727 | 1886.5 | 1549.5 | 520 | 70 | 16 | 0 | 140 | 53.5
16:00 | 4357 | 727 | 1958 | 1496 | 520 | 70 | 16 | 0 | 140 | 40
16:30 | 4333.5 | 727 | 1897 | 1376 | 510 | 70 | 16 | 0 | 136 | 26.5
17:00 | 4310 | 727 | 1836 | 1256 | 500 | 70 | 16 | 0 | 132 | 13
17:30 | 4229.5 | 724 | 1780 | 1345.5 | 500 | 70 | 43 | 0 | 134 | 6.5
18:00 | 4149 | 721 | 1724 | 1435 | 500 | 70 | 70 | 0 | 136 | 0
18:30 | 4313.5 | 721.5 | 1834.5 | 2003 | 525 | 70 | 196.5 | 0 | 150 | 0
19:00 | 4478 | 722 | 1945 | 2571 | 550 | 70 | 323 | 0 | 164 | 0
19:30 | 4524 | 721 | 1996 | 2603 | 700 | 70 | 339 | 0 | 160 | 0
20:00 | 4597 | 721 | 2024 | 2483 | 710 | 70 | 326 | 0 | 162 | 0
20:30 | 4615.5 | 720.5 | 2052.5 | 2456.5 | 730 | 70 | 305 | 0 | 161 | 0
21:00 | 4634 | 720 | 2081 | 2430 | 750 | 70 | 284 | 0 | 160 | 0
21:30 | 4618.5 | 720.5 | 2089.5 | 2374.5 | 730 | 70 | 264.5 | 0 | 157 | 0
22:00 | 4603 | 721 | 2098 | 2319 | 710 | 70 | 245 | 0 | 154 | 0
22:30 | 4602.5 | 721 | 2095.5 | 2206.5 | 700 | 70 | 180 | 0 | 154 | 0
23:00 | 4602 | 721 | 2093 | 2094 | 690 | 70 | 115 | 0 | 154 | 0
23:30 | 4600 | 721 | 2072.5 | 2094 | 670 | 70 | 82.5 | 0 | 155 | 0 | Max Temp. in Dhaka |  | 37.6° C
24:00 | 4598 | 721 | 2052 | 2094 | 650 | 70 | 50 | 0 | 156 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1700000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 |  | 15 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 8 | 8 | 8 |  | 24 | 25 | 8 | 8 | 8 | 8 | 8 | 419410
| Teknaf 20MW PP (Solartech) | [8 empty] | 6 | 13 | 16 | 17 | 16 | 14 | 9 | 6 | 1 | [9 empty] | 95310
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 205 | 203 | 203 | 203 | 213 | 202 | 203 | 204 | 205 | 218 | 204 | 205 | 216 | 203 | 205 | 205 |  | 204 | 205 | 208 | 204 | 203 | 203 | 189 | 4804056
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2867598
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 38 |  | 84 | 84 | 85 | 68 | 68 | 68 | 34 | 446065
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 150 | 145 | [7 empty] | 110 | 184 | 120 | 65 | 110 | 150 | 90 | 90 |  | 150 | 150 | 160 | 180 | 180 | 180 | 180 | 2493000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 95 | [15 empty] | 20 |  | 125 | 60 | 60 | 60 | 30 | 30 | 0 | 870654
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4095000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4578700
26
28 | Ashuganj TPP Unit- 3 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2234236
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 587592
33 | Ashuganj 225 MW CCPP | 170 | 172 | 182 | 191 | 194 | 195 | 184 | 197 | 204 | 211 | 195 | 199 | 180 | 189 | 201 | 180 | 183 | 180 |  | 180 | 182 | 193 | 181 | 181 | 181 | 181 | 4534000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 265 | 265 | 270 | 280 | 295 | 265 | 270 | 295 | 265 | 265 | 265 |  | 280 | 290 | 305 | 290 | 290 | 290 | 290 | 6775000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 260 | 265 | 260 | 275 | 295 | 260 | 270 | 285 | 260 | 260 | 260 |  | 270 | 275 | 300 | 295 | 295 | 295 | 295 | 6843500
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 30 | 30 | 30 | 47 | 49 | 50 | 442080
36 | Chandpur 150 MW CCPP | [11 empty] | 80 | 80 | 81 | 81 | 76 | 85 | 82 |  | 80 | 85 | 90 | 91 | 91 | 90 | 90 | 1007720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 333 | 342 | 345 | 345 | 345 | 345 | 361 | 369 | 340 | 343 | 349 | 369 | 348 | 343 | 375 | 350 | 350 | 341 |  | 352 | 340 | 341 | 351 | 341 | 340 | 343 | 8546328
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 380 | 400 | 420 | 420 | 420 | 420 | 360 | 420 | 420 | 350 | 320 |  | 380 | 380 | 400 | 400 | 400 | 400 | 400 | 9141750
41 | Haripur 360MW CCPP(HPL) | [12 empty] | 34 | 34 | 34 | 214 | 303 | 303 |  | 350 | 348 | 348 | 348 | 350 | 353 | 352 | 2856000
42 | RPCL 210MW CCPP | 127 | 147 | 149 | 148 | 147 | 148 | 160 | 160 | 159 | 155 | 152 | 152 | 151 | 150 | 149 | 169 | 199 | 204 |  | 207 | 209 | 207 | 207 | 212 | 211 | 213 | 3932000
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 17 | 29 | 39 | 44 | 46 | 43 | 38 | 31 | 19 | 7 | 0 | [8 empty] | 319010
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 42 | 42 | 40 | 41 | 41 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1022000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 710400
46 | Shajibazar 330 MW CCPP | 209 | 210 | 211 | 210 | 209 | 210 | 211 | 211 | 212 | 210 | 210 | 211 | 212 | 213 | 210 | 213 | 212 | 212 |  | 210 | 210 | 210 | 210 | 210 | 212 | 210 | 4788000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 77 | 77 | 74 | 77 | 78 | 78 | 77 | 77 | 77 | 20 | 20 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1781760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 105 | 105 | 104 | 104 | 105 | 104 | 104 | 104 | 105 |  |  | 40 | 40 | 105 | 105 | 105 | 105 | 105 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2345840
51 | Sylhet 20 MW GTPP | [22 empty] | 18 | 18 | 18 | 18 | 55000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 160380
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 14 | 14 |  | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 1191000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 173712
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 285 | 290 | 290 | 300 | 300 | 310 | 280 | 295 | 300 | 315 | 290 | 290 | 315 | 240 | 305 | 280 |  | 290 | 295 | 280 | 310 | 310 | 300 | 300 | 7245500
| Bibiyana South 400 MW | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7102500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1064870
59 | Tangail Palli Power Gen 22 MW | 23 | 22 | 21 | 23 | 23 | 23 | 23 | 23 | 20 | 17 | 16 | 19 | 19 | 15 | 15 | 15 | 16 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492480
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 14 | 14 | 14 | 16 | 16 | 14 | 13 | 321888
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 450180
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 377676
63 | Impoprt (Tripura) | 138 | 138 | 132 | 124 | 116 | 108 | 104 | 100 | 100 | 120 | 122 | 128 | 140 | 138 | 140 | 140 | 132 | 136 |  | 164 | 160 | 162 | 160 | 154 | 154 | 156 | 3238080
64 | Malancha, Ctg. EPZ (United) | 38 | 40 | 32 | 38 | 41 | 41 | 42 | 42 | 36 | 40 | 40 | 38 | 36 | 33 | 25 | 31 | 35 | 35 |  | 38 | 38 | 38 | 38 | 38 | 38 | 41 | 934080
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 17 | 17 | 17 | 17 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488592
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 798500
68 | Cumilla 25 MW PP (Summit) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 14 | 14 | 19 | 19 | 19 | 19 | 19 | 19 | 12 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 465530
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 20 | 20 | 20 | 15 | 10 | 10 | 10 | 10 | 10 | 10 |  | 15 | 29 | 29 | 29 | 29 | 29 | 29 | 530280
71 | Maona 33 MW PP(Summit) | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 765700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792200
73 | Ghorashal 108MW PP (Regent) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 91 | 89 | 88 | 87 | 87 | 85 | 86 | 89 | 45 | 45 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2103454
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 55 | 8 | 8 | 16 | 36 | 36 | 36 | 41 | 36 | 8 | 8 | 8 | 8 | 8 |  | 65 | 113 | 75 | 75 | 46 | 46 | 46 | 1436400
| Manikgonj 162MW PP(MPGL) | 144 | 90 | 90 | 54 | 17 | 17 | [10 empty] | 0 | 15 |  | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 637920
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 70 | 40 | 7 | [6 empty] | 16 | 10 | 7 | 7 | 7 | 7 |  | 35 | 70 | 50 | 50 | 40 | 30 | 16 | 810240
78 | Gazipur 52 MW PP | [17 empty] | 2 |  | 16 | [6 empty] | 18240
79 | Kodda 150MW PP | 64 | 48 | 48 | 48 | 16 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 98 | 98 | 82 | 82 | 48 | 32 | 16 | 753600
80 | Jamalpur 95 MW PP(Powerpac) | 56 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 837120
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | [15 empty] | 8 |  | 24 | [6 empty] | 161470
| Gazipur 100 MW PP | 70 | 17 | [15 empty] | 12 |  | 30 | 6 |  |  |  |  | 0 | 171600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 5 | 3 | 2 | 1 | 0 | [9 empty] | 28207
| Jodiac Power | 12 | 50 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 54 | 54 | 54 | 17 | 17 |  | 39 | 54 | 54 | 54 | 54 | 54 | 54 | 924591
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 85 | 96 | 97 | 82 | 48 | 15 | [6 empty] | 20 | 30 | 30 | 30 | 30 | 30 |  | 55 | 64 | 48 | 30 | 30 | 40 | 30 | 923544
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 2 | [7 empty] | 0 | 21281
86 | Meghnaghat CCPP(Summit) | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 230 | 230 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5394880
87 | Meghnaghat 100 MW(IEL) | 100 | 60 | 45 | [13 empty] | 0 | 7 |  | 35 | 1 | [5 empty] | 284160
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 68 | 54 | 54 | 53 | 53 | 54 | 96 | 65 | 20 | 28 | 35 | 35 |  | 73 | 104 | 104 | 70 | 70 | 70 | 70 | 1770240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 40 | 10 | 10 | [11 empty] | 7 |  | 10 | [5 empty] | 0 | 375240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 32 | 32 | [14 empty] | 3 | 12 |  | 48 | [5 empty] | 0 | 175392
95 | Patenga 50MW PP (Baraka) | 44 | 26 | 6 | [14 empty] | 8 |  | 29 | 18 | 18 | 19 | 19 | 19 | 19 | 226080
96 | Chattogram 108 MW PP (ECPV) | 20 | [18 empty] | 13 | [5 empty] | 0 | 40320
97 | katpotti 52 MW | 49 | 49 | 49 | 49 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 20 | 21 |  | 25 | 47 | 48 | 49 | 40 |  | 0 | 720768
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 40 | 40 | 40 | 40 | 40 |  | 50 | 55 | 30 | 30 | 30 | 30 | 30 | 998171
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 |  | 10 |  | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 999208
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 110 | 130 | 163 | 130 | 110 |  | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 3392918
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1311840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 193 | 193 | 200 | 200 | 200 | 200 | 200 | 193 | 192 | 191 | 172 | 172 | 170 | 170 | 180 | 181 |  | 181 | 181 | 183 | 184 | 184 | 183 | 200 | 4485600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 116 | 116 | 116 | 114 | 112 | 99 | 99 | 100 | 99 | 97 | 102 | 100 | 115 | 92 | 80 | 80 | 81 | 81 |  | 101 | 114 | 111 | 122 | 126 | 126 | 124 | 2541600
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 100 | 100 | 50 | 50 | 50 | 20 | 20 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1903680
116 | Chandpur 200MW (Desh energy) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 71 | 70 | 71 | 70 | 73 | 95 | 103 |  | 110 | 120 | 120 | 120 | 120 | 120 | 120 | 2058720
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 240 | 240 | 239 | 239 | 238 | 239 | 239 | 240 | 240 | 240 | 241 | 241 | 241 | 240 | 240 | 241 | 241 | 241 |  | 242 | 242 | 240 | 240 | 239 | 239 | 240 | 5769000
| Jamalpur 115 MW PP (United) | 85 | 85 | 65 | 45 |  |  |  | 6 | 55 | 55 | 75 | 75 | 115 | 115 | 115 | 115 | 85 | 85 |  | 98 | 115 | 115 | 115 | 115 | 75 | 0 | 1794000
| Anwara 300 MW PP (United) | 106 | 16 | [15 empty] | 16 |  | 32 | [5 empty] | 0 | 278509
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2390400
| Anlima Energy Ltd. | 5 | 19 | 48 | [14 empty] | 7 |  | 41 | 84 | 90 | 72 | 35 | 35 | 35 | 426545
| Bhairob 54.5 MW | 32 | [18 empty] | 15 | 0 |  |  |  |  | 0 | 61560
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 10 | 11 | 27 | 30 | 32 | 29 | 26 | 19 | 11 | 4 | 0 | [8 empty] | 208110
120 | Eastern Zone Total | 7421 | 7038 | 6811 | 6432 | 6165 | 5991 | 5748 | 5709 | 5741 | 5727 | 5925 | 6271 | 6281 | 6079 | 6225 | 6260 | 6035 | 6116 |  | 7512 | 7485 | 7426 | 7406 | 7267 | 7162 | 6992 | 156562874
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 83 | 83 | 83 | 83 | 66 | 66 | 32 | 66 | 66 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 49 | 66 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1883520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 480
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 70 | 35 |  |  |  | 53 | 53 | [8 empty] | 17 |  | 70 | 75 | 75 | 75 | 75 | 74 | 35 | 844800
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 96 | 100 | 100 | 136 | 134 | 138 | 138 | 136 | 115 | 115 | 156 | 175 | 195 | 201 | 201 | 213 | 215 | 217 |  | 113 | 114 | 108 | 124 | 123 | 124 | 103 | 3591764
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 32 | 32 | 32 | 32 |  | 0 | 135456
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 43 | 43 | 43 | 33 | 33 | 33 | 17 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 |  | 14 | 10 | 12 | 13 | 12 | 13 | 13 | 496942
| Bhola 225 MW CCPP | 65 | 70 | 70 | 70 | 71 | 70 | 70 | 68 | 67 | 65 | 65 | 60 | 59 | 60 | 60 | 50 | 60 | 50 |  | 60 | 51 | 60 | 60 | 58 | 54 | 54 | 1500000
140 | Bhola 33 MW PP (Venture) | 24 | 24 | 22 | 21 | 20 | 18 | 15 | 15 | 15 | 15 | 15 | 17 | 19 | 19 | 20 | 20 | 18 | 17 |  | 25 | 25 | 26 | 26 | 26 | 26 | 25 | 484400
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 28 | 60 | 60 | 60 | 60 |  | 0 | 240000
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 |  |  | 231375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 721 |  | 722 | 721 | 721 | 720 | 721 | 721 | 721 | 17432000
147 | Bheramara 410 MW CCPP | 250 | 255 | 270 | 295 | 325 | 350 | 370 | 385 | 400 | 405 | 400 | 395 | 395 | 350 | 395 | 395 | 395 | 300 |  | 410 | 410 | 405 | 410 | 405 | 410 | 410 | 9003168
148 | Payra 1320 MW | 540 | 480 | 450 | 450 | 450 | 420 | 420 | 420 | 380 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 350 | 350 |  | 400 | 550 | 560 | 600 | 560 | 540 | 500 | 11461200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3668000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 25 | 25 | 25 |  |  |  | 0 | 48711
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 187 | 188 | 201 | 188 | 165 | 180 | 187 | 172 | 164 |  | 179 | 187 | 189 | 198 | 189 | 191 | 195 | 4557082
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 198 | 200 | 191 | 174 | 183 | 191 | 170 | 140 |  | 167 | 187 | 188 | 196 | 188 | 187 | 190 | 4658891
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 388 | 408 | 400 | 390 | 428 | 398 | 428 | 406 | 388 | 422 | 416 | 409 | 414 | 409 | 406 | 390 | 350 | 310 |  | 338 | 362 | 388 | 388 | 388 | 386 | 363 | 9511545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 17 | 17 | 17 | 16 | 16 | 16 | 18 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 453840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245448
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 22 | 33 | 35 | 34 | 33 |  |  | 118015
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 16 | 8 | 8 | 8 | 8 | 8 |  | 34 | 52 | 52 | 52 | 52 | 34 | 24 | 636000
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 94 | 99 | 99 | 100 | 96 | 15 | 0 | 395783
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 102 | 113 | 97 | 70 | 35 | 35 |  | 72 | 113 | 110 | 113 | 113 | 113 | 113 | 2292864
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 70 | 35 | 35 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2142144
173 | Rangpur 20 MW GTPP | 0 | [16 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 100 | 99 | 99 | 70 | 70 | 70 | 87 | 98 | 94 | 95 | 97 | 98 | 103 | 109 | 89 | 39 | 40 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2245440
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 6 | 6 | 4 | 2 | 1 | 0 | [8 empty] | 38149
178
178