## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-03-29 | Monday
|  | Date (day): | 2021-03-29 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15331.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16054 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-28 | 2021-03-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170 |  | 20 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 240 | 300 | 300 | 300 |  | 65 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 98 | 99 | 99 |  | 9 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 321 | 325 | 340 | 350 |  |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 160 | 166 | 200 | 200 | 160 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 38 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 230 | 235 | 235 | 70 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 72 | 85 | 85 |  | 15 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 145 | 120 | 150 |  |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 65 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 216 | 220 | 220 | 220 |  | 115 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 149 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 2 | 34 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 278 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 105 | 121 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 58 | 90 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 37 | 144 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 29 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2971 | 3784 | 4317 | 4577 | 338 | 854
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 45 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 193 | 182 | 190 | 190 |  |  | Gas shortage
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  |  | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 85 | 85 |  |  | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 12 | 10 | 15
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 87 | 90 | 90 |  |  | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 10 | 33 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 42 | 116 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 838 | 1109 | 1617 | 1647 | 520 | 98
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 80 | 80 |  |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 212 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 260 | 300 | 300 |  |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 270 | 300 | 300 |  |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 47 | 50 | 50 | 5 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | under maint.
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 95 | 90 | 90 |  | 73 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 65 | 100 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 160 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 20 | 20 | 20 |  | 5 | Engine problem
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 94 | 113 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 4 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1452 | 1626 | 1995 | 2162 | 340 | 78
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 123 | 145 | 150 | 150
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 74 | 77 | 77 |  | 18 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 173 | 196 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 84 | 115 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 25 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 478 | 575 | 637.6 | 586 | 0 | 18
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Engine problem
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 137 | 137 | 150 | 150 |  | 180 | Machine problem
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 77 | 81 | 81
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150 |  | 81 | ST Under maint
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 329 | 400 | 400
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 8 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 72 | 190 | 310 | 310
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1473 | 1526 | 1777 | 1777 | 0 | 532
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 721 | 839 | 858 | 858
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 2 | 0 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 3 | 60 | 60 |  | 49
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 320 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 94 | 90 | 95 |  | 10 | Engine problem
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1276 | 1488 | 1722 | 2013 | 0 | 104
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 25 | 25
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 50 | 70 | 70 |  | 124 | GT-2 under maint
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 75 | 76 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 570 | 622 | 622
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 38 | 71 | 120 | 120 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 622 | 876 | 1192 | 1192 | 0 | 124
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 16 | 40 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 143 | 144 | 150 | 150 | 60 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 193 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 190 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 379 | 330 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 101 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1164 | 1381 | 1793 | 1827 | 231 | 0
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 6 | 0 | 0 |  | 20 | Engine problem
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 268 | 269 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 10542 | 12634 | 15331.6 | 16054 | 1553 | 2008
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9952.0685 | 11927 | 14473.642 | 15155.6164
A. |  | 2021-03-28 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12634 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 9015 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12634 | MW
3 | Day peak Generation : |  |  | 10542 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11927 | MW
4 | Evening peak Generation : |  |  | 12634 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 257.5758 | MKWHr | By Solar | 0.61685 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 156.963 | MKWHr |  | By Oil: | 60.0696 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.3976 | MKWHr |  | By Hydro: | 1.688 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1553 | MW | Dhaka | 4327 | 4327 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2008 | MW | Chittagong | 1181 | 1181 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3561 | MW | Khulna | 1443 | 1443 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1278.4 | MMCFD |  |  | Rajshahi | 1327 | 1327 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 171904834.23 | ii) Oil : | Taka | 416322885.61 | Comilla | 1104 | 1104 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 75769169 | Total | Taka | 663996888.84 | Mymensingh | 1039 | 1039 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.251 | MKWHr. | Sylhet | 433 | 433 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -12 | MW (E to W) at | 19:30 | hrs | Barisal | 294 | 294 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -40 | MW at | 7:00 | hrs | Rangpur | 779 | 779 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.8° C |  |  | Total | 11927 | 11927 |  | 0
B. |  | 2021-03-29 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16054 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
4 | Reserve(Generation end) |  |  |  | 3254 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 260.9602 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9206 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.3724 | MKWHr. | ii) HVDC Flow at Peak Time |  | 839 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4685 | MKWHr. | iii) Maximum HVDC Flow : |  | 840 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.24 |  | (b) Today: | 85.96 |  | (c) Rule Curve: |  | 88.51
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 123 | 93 | 0 | 343 | 197 |  | 0 | 420 | 230 | 0 | 97 | 55 | 222 | 0 | 75 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 188 | 0 | 120 | 0 |  | 22 | 0 | 51 | 60 | 0 | 0 | 20 | 39 | 100 | 0 | 80 | 275 | 265 | 216 | 8 | 85 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 156 | 162 | 57 | 20 | 0 | 44 | 30 | 50 | 0 | 130 | 135 | 0 | 80 | 0 | 148 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 195 | 0 | 121 | 0 | 100 | 100 | 0 | 240 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 17 | 0 | 0 | 34 | 0 |  | 721 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 220 | 0 | 78 | 0 | 186 | 0 | 379 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 37 | 0 | 0 |  | 7028 | 3407 | 10435 | 4637 | 721 | 1910 | 2200 | 690 | 70 | 51 | 156 | 0 | 0 | 86.34
2:00 | 0 | 0 | 0 | 170 | 134 | 93 | 0 | 350 | 233 |  | 0 | 420 | 230 | 0 | 30 | 55 | 222 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 188 | 0 | 120 | 0 |  | 22 | 0 | 51 | 10 | 0 | 0 | 20 | 40 | 100 | 0 | 80 | 275 | 265 | 212 | 8 | 91 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 150 | 163 | 57 | 20 | 0 | 44 | 30 | 50 | 0 | 130 | 136 | 0 | 80 | 0 | 148 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 117 | 0 | 100 | 100 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 310 | 104 | 0 | 0 | 0 | 0 | 16 | 0 |  | 721 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 149 | 0 | 220 | 0 | 78 | 0 | 185 | 0 | 382 | 0 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 540 | 37 | 0 | 0 |  | 6668 | 3322 | 9990 | 4664 | 721 | 1936 | 1708 | 690 | 70 | 51 | 150 | 0 | 0 | 86.32
3:00 | 0 | 0 | 0 | 170 | 140 | 93 | 0 | 349 | 250 |  | 0 | 420 | 220 | 0 | 15 | 0 | 222 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 188 | 0 | 120 | 0 |  | 24 | 0 | 51 | 10 | 0 | 0 | 17 | 40 | 100 | 0 | 80 | 275 | 265 | 211 | 8 | 87 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 142 | 164 | 8 | 20 | 0 | 44 | 30 | 50 | 0 | 130 | 137 | 0 | 80 | 0 | 148 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 125 | 0 | 94 | 0 | 100 | 114 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 220 | 0 | 77 | 0 | 186 | 0 | 390 | 0 | 0 | 94 | 0 | 8 | 0 | 0 | 113 | 520 | 38 | 0 | 0 |  | 6387 | 3210 | 9597 | 4639 | 721 | 1971 | 1333 | 670 | 70 | 51 | 142 | 0 | 0 | 86.3
4:00 | 0 | 0 | 0 | 170 | 157 | 93 | 0 | 349 | 246 |  | 0 | 420 | 220 | 0 | 15 | 0 | 222 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 188 | 0 | 120 | 0 |  | 24 | 0 | 51 | 10 | 0 | 0 | 17 | 40 | 100 | 0 | 80 | 275 | 265 | 216 | 8 | 91 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 136 | 165 | 8 | 20 | 0 | 44 | 30 | 50 | 0 | 130 | 137 | 0 | 80 | 0 | 148 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 125 | 0 | 100 | 0 | 100 | 114 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 27 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 51 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 184 | 0 | 77 | 0 | 172 | 0 | 345 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 113 | 500 | 38 | 0 | 0 |  | 6344 | 3055 | 9399 | 4618 | 721 | 1921 | 1232 | 650 | 70 | 51 | 136 | 0 | 0 | 86.28
5:00 | 0 | 0 | 0 | 170 | 160 | 93 | 0 | 349 | 233 |  | 0 | 420 | 220 | 0 | 15 | 0 | 222 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 31 | 33 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 188 | 0 | 120 | 0 |  | 24 | 0 | 51 | 10 | 0 | 0 | 16 | 40 | 100 | 0 | 80 | 275 | 265 | 216 | 8 | 91 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 126 | 166 | 8 | 20 | 0 | 44 | 30 | 50 | 0 | 130 | 137 | 0 | 80 | 0 | 121 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 20 | 114 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 60 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 720 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 149 | 0 | 161 | 0 | 77 | 0 | 160 | 0 | 360 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 470 | 38 | 0 | 0 |  | 6132 | 2889 | 9021 | 4567 | 720 | 1912 | 955 | 620 | 70 | 51 | 126 | 0 | 0 | 86.26
6:00 | 0 | 0 | 0 | 170 | 180 | 93 | 0 | 355 | 233 |  | 0 | 420 | 225 | 0 | 15 | 0 | 223 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 188 | 0 | 120 | 0 |  | 24 | 0 | 51 | 10 | 0 | 0 | 17 | 40 | 100 | 0 | 80 | 275 | 265 | 218 | 8 | 91 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 118 | 166 | 8 | 20 | 0 | 44 | 30 | 50 | 0 | 100 | 139 | 0 | 81 | 0 | 120 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 20 | 114 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 60 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 721 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 151 | 0 | 162 | 0 | 78 | 0 | 161 | 0 | 360 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 440 | 38 | 0 | 0 |  | 6163 | 2852 | 9015 | 4619 | 721 | 1902 | 945 | 589 | 70 | 51 | 118 | 0 | 0 | 86.24
7:00 | 0 | 0 | 0 | 170 | 240 | 93 | 0 | 358 | 203 |  | 0 | 420 | 230 | 0 | 15 | 0 | 223 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 2 | 188 | 0 | 120 | 0 |  | 24 | 0 | 51 | 10 | 0 | 0 | 17 | 30 | 100 | 0 | 80 | 275 | 280 | 214 | 8 | 85 | 26 | 49 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 33 | 15 | 112 | 166 | 8 | 20 | 0 | 44 | 30 | 50 | 0 | 100 | 137 | 0 | 81 | 0 | 120 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 144 | 0 | 102 | 2 | 60 | 116 | 0 | 239 | 12 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 100 | 310 | 20 | 6 | 1 | 0 | 0 | 0 | 4 |  | 721 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 151 | 0 | 163 | 0 | 78 | 0 | 162 | 0 | 311 | 0 | 0 | 35 | 0 | 20 | 0 | 1 | 35 | 440 | 37 | 0 | 0 |  | 6352 | 2818 | 9170 | 4670 | 721 | 1802 | 1141 | 590 | 70 | 51 | 112 | 13 | 0 | 86.22
8:00 | 0 | 0 | 0 | 170 | 240 | 93 | 0 | 346 | 172 |  | 0 | 420 | 230 | 0 | 15 | 15 | 223 | 0 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 202 | 0 | 120 | 0 |  | 20 | 0 | 0 | 10 | 0 | 0 | 17 | 9 | 100 | 0 | 80 | 315 | 320 | 206 | 8 | 91 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 112 | 163 | 16 | 20 | 1 | 44 | 30 | 50 | 0 | 163 | 137 | 0 | 81 | 0 | 135 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 118 | 3 | 60 | 116 | 0 | 237 | 24 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 8 | 100 | 0 | 53 | 14 | 17 | 0 | 0 | 0 | 11 |  | 721 | 0 | 405 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 151 | 0 | 169 | 0 | 78 | 0 | 163 | 0 | 359 | 17 | 0 | 35 | 0 | 70 | 0 | 2 | 35 | 430 | 38 | 0 | 0 |  | 6339 | 3023 | 9362 | 4592 | 721 | 1840 | 1415 | 580 | 70 | 0 | 112 | 32 | 0 | 86.2
9:00 | 0 | 0 | 0 | 170 | 240 | 90 | 0 | 344 | 150 |  | 0 | 420 | 230 | 2 | 15 | 15 | 222 | 0 | 190 | 8 | 0 | 10 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 188 | 0 | 120 | 0 |  | 19 | 0 | 0 | 23 | 0 | 4 | 17 | 2 | 100 | 0 | 80 | 280 | 280 | 201 | 8 | 91 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 112 | 145 | 16 | 20 | 1 | 44 | 30 | 50 | 0 | 163 | 136 | 0 | 78 | 0 | 150 | 18 | 0 | 7 | 325 | 16 | 11 | 0 | 1 | 0 | 0 | 200 | 0 | 116 | 7 | 100 | 115 | 0 | 318 | 48 | 6 | 0 | 1 | 0 | 29 | 0 | 0 | 20 | 100 | 0 | 63 | 27 | 17 | 5 | 0 | 0 | 17 |  | 721 | 0 | 365 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 149 | 0 | 200 | 0 | 78 | 0 | 198 | 0 | 420 | 17 | 0 | 87 | 0 | 103 | 0 | 3 | 90 | 430 | 38 | 0 | 0 |  | 6553 | 3246 | 9799 | 4633 | 721 | 1898 | 1719 | 580 | 70 | 10 | 112 | 56 | 0 | 86.18
10:00 | 0 | 0 | 0 | 170 | 240 | 88 | 0 | 331 | 116 |  | 0 | 420 | 230 | 7 | 37 | 50 | 222 | 0 | 150 | 50 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 188 | 0 | 120 | 0 |  | 19 | 0 | 0 | 50 | 0 | 18 | 18 | 2 | 100 | 0 | 80 | 280 | 285 | 210 | 8 | 94 | 24 | 30 | 0 | 0 | 0 | 0 | 6 | 19 | 8 | 25 | 13 | 132 | 140 | 16 | 20 | 2 | 43 | 30 | 47 | 0 | 163 | 139 | 0 | 77 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 38 | 0 | 0 | 200 | 0 | 111 | 9 | 100 | 88 | 0 | 401 | 75 | 44 | 0 | 1 | 0 | 54 | 0 | 0 | 46 | 100 | 24 | 104 | 32 | 17 | 17 | 0 | 0 | 24 |  | 721 | 0 | 385 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 193 | 0 | 75 | 0 | 186 | 0 | 416 | 17 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 430 | 38 | 0 | 0 |  | 6917 | 3279 | 10196 | 4689 | 721 | 1825 | 2091 | 580 | 70 | 16 | 132 | 72 | 0 | 86.16
11:00 | 0 | 0 | 0 | 170 | 240 | 86 | 0 | 332 | 148 |  | 0 | 420 | 230 | 7 | 46 | 42 | 217 | 0 | 150 | 50 | 15 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 27 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 16 | 197 | 0 | 120 | 0 |  | 22 | 0 | 0 | 50 | 0 | 18 | 17 | 3 | 100 | 0 | 80 | 340 | 280 | 200 | 8 | 95 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 25 | 13 | 140 | 120 | 16 | 20 | 2 | 43 | 30 | 50 | 0 | 163 | 137 | 0 | 74 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 105 | 15 | 100 | 68 | 0 | 402 | 75 | 52 | 0 | 4 | 0 | 54 | 0 | 0 | 46 | 100 | 72 | 104 | 41 | 17 | 17 | 0 | 0 | 22 |  | 721 | 0 | 400 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 187 | 0 | 76 | 0 | 190 | 0 | 414 | 17 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 430 | 38 | 0 | 0 |  | 7048 | 3290 | 10338 | 4772 | 721 | 1856 | 2094 | 580 | 70 | 16 | 140 | 89 | 0 | 86.15
12:00 | 0 | 0 | 0 | 170 | 240 | 90 | 0 | 321 | 160 |  | 0 | 420 | 230 | 38 | 48 | 45 | 216 | 0 | 180 | 65 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 33 | 33 | 2 | 0 | 0 | 70 | 0 | 0 | 17 | 193 | 0 | 120 | 0 |  | 19 | 0 | 0 | 80 | 0 | 20 | 19 | 3 | 80 | 0 | 80 | 280 | 280 | 202 | 8 | 86 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 25 | 13 | 144 | 123 | 16 | 17 | 2 | 43 | 30 | 50 | 0 | 163 | 137 | 0 | 72 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 173 | 0 | 105 | 8 | 100 | 65 | 0 | 404 | 84 | 58 | 0 | 2 | 10 | 54 | 0 | 0 | 94 | 100 | 72 | 104 | 44 | 37 | 42 | 0 | 4 | 29 |  | 721 | 0 | 400 | 0 | 83 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 186 | 0 | 75 | 0 | 196 | 0 | 379 | 70 | 0 | 94 | 0 | 112 | 0 | 6 | 113 | 440 | 38 | 0 | 0 |  | 7212 | 3330 | 10542 | 4694 | 721 | 1834 | 2348 | 590 | 70 | 50 | 144 | 91 | 0 | 86.14
13:00 | 0 | 0 | 0 | 170 | 240 | 94 | 0 | 318 | 150 |  | 0 | 420 | 230 | 100 | 92 | 52 | 208 | 0 | 70 | 88 | 102 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 23 | 33 | 33 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 190 | 0 | 120 | 0 |  | 19 | 0 | 0 | 80 | 11 | 36 | 20 | 5 | 80 | 0 | 80 | 280 | 280 | 212 | 8 | 93 | 26 | 30 | 0 | 0 | 0 | 0 | 50 | 19 | 8 | 25 | 18 | 144 | 121 | 16 | 17 | 2 | 42 | 30 | 50 | 0 | 110 | 138 | 0 | 71 | 0 | 150 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 135 | 0 | 0 | 185 | 0 | 104 | 10 | 100 | 65 | 0 | 378 | 108 | 90 | 0 | 1 | 16 | 54 | 0 | 0 | 113 | 100 | 132 | 104 | 40 | 134 | 111 | 0 | 35 | 28 |  | 721 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 142 | 0 | 169 | 0 | 77 | 0 | 187 | 0 | 337 | 70 | 0 | 94 | 0 | 110 | 0 | 6 | 113 | 460 | 36 | 0 | 0 |  | 7763 | 3274 | 11037 | 4591 | 721 | 1724 | 3040 | 609 | 70 | 51 | 144 | 87 | 11037 | 86.13
14:00 | 0 | 0 | 0 | 170 | 240 | 94 | 0 | 312 | 151 |  | 0 | 350 | 230 | 100 | 92 | 55 | 210 | 0 | 32 | 92 | 102 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 186 | 0 | 80 | 0 |  | 19 | 0 | 0 | 80 | 12 | 44 | 20 | 6 | 80 | 0 | 80 | 260 | 265 | 210 | 8 | 91 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 19 | 11 | 33 | 18 | 154 | 121 | 16 | 20 | 2 | 43 | 30 | 53 | 0 | 110 | 138 | 0 | 74 | 0 | 150 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 154 | 0 | 0 | 192 | 0 | 104 | 7 | 100 | 65 | 0 | 378 | 115 | 90 | 0 | 2 | 16 | 54 | 0 | 0 | 113 | 100 | 190 | 104 | 34 | 144 | 116 | 0 | 37 | 24 |  | 721 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 143 | 0 | 157 | 0 | 77 | 0 | 175 | 0 | 327 | 75 | 0 | 94 | 0 | 109 | 0 | 6 | 113 | 460 | 38 | 0 | 0 |  | 7708 | 3227 | 10935 | 4484 | 721 | 1643 | 3128 | 609 | 70 | 51 | 154 | 75 | 0 | 86.12
15:00 | 0 | 0 | 0 | 170 | 240 | 90 | 0 | 317 | 162 |  | 0 | 380 | 230 | 78 | 92 | 55 | 209 | 0 | 80 | 50 | 48 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 26 | 33 | 33 | 8 | 0 | 0 | 70 | 0 | 0 | 25 | 184 | 0 | 120 | 0 |  | 25 | 0 | 0 | 80 | 12 | 44 | 20 | 5 | 80 | 0 | 100 | 280 | 290 | 206 | 8 | 95 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 18 | 11 | 33 | 18 | 158 | 122 | 16 | 20 | 1 | 41 | 30 | 51 | 0 | 163 | 139 | 0 | 73 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 180 | 0 | 102 | 3 | 100 | 65 | 0 | 379 | 115 | 52 | 0 | 1 | 16 | 54 | 0 | 0 | 113 | 100 | 190 | 104 | 27 | 144 | 116 | 0 | 37 | 18 |  | 740 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 60 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 168 | 0 | 77 | 0 | 187 | 0 | 386 | 75 | 0 | 94 | 0 | 108 | 0 | 4 | 113 | 460 | 38 | 0 | 0 |  | 7723 | 3359 | 11082 | 4694 | 740 | 1809 | 2896 | 610 | 70 | 51 | 158 | 54 | 0 | 86.11
16:00 | 0 | 0 | 0 | 170 | 300 | 86 | 0 | 326 | 162 |  | 0 | 380 | 230 | 50 | 64 | 55 | 219 | 0 | 150 | 50 | 48 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 26 | 33 | 25 | 8 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 25 | 0 | 0 | 50 | 14 | 44 | 20 | 4 | 80 | 0 | 100 | 260 | 270 | 207 | 8 | 95 | 26 | 42 | 0 | 0 | 0 | 0 | 24 | 18 | 11 | 33 | 18 | 154 | 121 | 16 | 20 | 1 | 42 | 30 | 53 | 0 | 163 | 137 | 0 | 74 | 0 | 150 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 172 | 0 | 109 | 2 | 100 | 65 | 0 | 379 | 110 | 52 | 0 | 1 | 16 | 54 | 0 | 0 | 113 | 100 | 190 | 104 | 17 | 90 | 72 | 0 | 37 | 10 |  | 794 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 54 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 182 | 0 | 77 | 0 | 191 | 0 | 405 | 75 | 0 | 94 | 0 | 101 | 0 | 3 | 113 | 480 | 38 | 0 | 0 |  | 7602 | 3454 | 11056 | 4798 | 794 | 1850 | 2673 | 630 | 70 | 53 | 154 | 34 | 0 | 86.1
17:00 | 0 | 0 | 0 | 170 | 300 | 41 | 0 | 332 | 170 |  | 0 | 320 | 230 | 50 | 64 | 55 | 216 | 0 | 120 | 50 | 48 | 48 | 25 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 33 | 25 | 10 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 25 | 0 | 0 | 20 | 18 | 45 | 20 | 4 | 80 | 0 | 80 | 260 | 270 | 207 | 8 | 95 | 26 | 43 | 0 | 0 | 0 | 0 | 24 | 21 | 11 | 33 | 18 | 140 | 138 | 16 | 20 | 0 | 42 | 30 | 50 | 0 | 163 | 136 | 0 | 76 | 0 | 150 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 185 | 0 | 121 | 1 | 50 | 65 | 0 | 379 | 115 | 35 | 0 | 0 | 16 | 54 | 0 | 17 | 55 | 100 | 190 | 75 | 6 | 72 | 53 | 0 | 37 | 3 |  | 824 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 57 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 192 | 0 | 77 | 0 | 190 | 0 | 398 | 53 | 0 | 94 | 0 | 71 | 0 | 2 | 70 | 470 | 38 | 0 | 0 |  | 7239 | 3362 | 10601 | 4768 | 824 | 1747 | 2367 | 620 | 70 | 53 | 140 | 12 | 0 | 86.09
18:00 | 0 | 0 | 0 | 170 | 300 | 80 | 0 | 335 | 165 |  | 0 | 320 | 230 | 50 | 70 | 55 | 217 | 0 | 70 | 50 | 48 | 82 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 25 | 0 | 21 | 20 | 21 | 45 | 20 | 4 | 80 | 0 | 80 | 285 | 295 | 205 | 8 | 95 | 26 | 47 | 0 | 0 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 140 | 139 | 16 | 20 | 0 | 43 | 30 | 53 | 0 | 110 | 137 | 0 | 76 | 0 | 150 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 134 | 0 | 0 | 185 | 0 | 121 | 0 | 50 | 65 | 0 | 329 | 115 | 35 | 0 | 0 | 16 | 54 | 0 | 17 | 55 | 100 | 190 | 70 | 0 | 73 | 53 | 0 | 36 | 0 |  | 833 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 6 | 4 | 0 | 60 | 28 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 25 | 10 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 100 | 0 | 168 | 0 | 77 | 0 | 140 | 0 | 375 | 53 | 0 | 94 | 0 | 71 | 0 | 0 | 70 | 460 | 73 | 0 | 0 |  | 7304 | 3288 | 10592 | 4600 | 833 | 1755 | 2457 | 609 | 70 | 128 | 140 | 0 | 0 | 86.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 330 | 166 |  | 0 | 400 | 230 | 89 | 96 | 55 | 223 | 0 | 145 | 84 | 64 | 149 | 63 | 0 | 0 | 0 | 54 | 48 | 55 | 19 | 25 | 24 | 33 | 33 | 31 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 25 | 0 | 85 | 80 | 66 | 45 | 20 | 9 | 80 | 0 | 80 | 260 | 270 | 211 | 8 | 90 | 26 | 47 | 0 | 0 | 0 | 50 | 48 | 22 | 11 | 33 | 20 | 162 | 142 | 57 | 20 | 0 | 43 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 150 | 18 | 0 | 8 | 300 | 16 | 11 | 40 | 275 | 30 | 25 | 196 | 27 | 121 | 0 | 100 | 65 | 0 | 329 | 115 | 71 | 0 | 0 | 33 | 54 | 0 | 50 | 102 | 100 | 190 | 99 | 0 | 136 | 110 | 0 | 37 | 0 |  | 839 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 11 | 33 | 50 | 29 | 64 | 0 | 0 | 0 | 50 | 20 | 100 | 0 | 43 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 8 | 120 | 0 | 174 | 0 | 77 | 43 | 170 | 0 | 323 | 90 | 40 | 94 | 0 | 113 | 0 | 0 | 113 | 490 | 67 | 0 | 0 |  | 8658 | 3890 | 12548 | 4667 | 839 | 1846 | 3785 | 640 | 70 | 539 | 162 | 0 | 0 | 86.05
19:30 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 325 | 166 |  | 0 | 400 | 230 | 100 | 96 | 55 | 220 | 0 | 145 | 100 | 102 | 149 | 72 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 0 | 70 | 0 | 0 | 25 | 182 | 0 | 120 | 0 |  | 25 | 0 | 65 | 80 | 87 | 45 | 20 | 12 | 80 | 0 | 100 | 260 | 270 | 212 | 8 | 95 | 26 | 47 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 160 | 145 | 74 | 20 | 0 | 44 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 150 | 18 | 0 | 8 | 300 | 16 | 11 | 0 | 278 | 0 | 0 | 196 | 0 | 121 | 0 | 100 | 100 | 0 | 329 | 115 | 90 | 0 | 0 | 33 | 54 | 0 | 17 | 113 | 100 | 190 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 839 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 3 | 33 | 50 | 29 | 80 | 0 | 0 | 0 | 50 | 16 | 101 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 6 | 144 | 0 | 193 | 0 | 76 | 100 | 190 | 0 | 330 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 71 | 0 | 0 |  | 8620 | 4014 | 12634 | 4730 | 839 | 1859 | 3800 | 720 | 70 | 456 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 324 | 160 |  | 0 | 400 | 230 | 97 | 96 | 55 | 221 | 0 | 175 | 100 | 102 | 150 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 182 | 0 | 120 | 0 |  | 25 | 0 | 51 | 80 | 88 | 46 | 20 | 22 | 80 | 0 | 100 | 260 | 270 | 210 | 8 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 158 | 144 | 74 | 20 | 0 | 44 | 30 | 53 | 0 | 163 | 138 | 0 | 77 | 0 | 149 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 280 | 0 | 0 | 196 | 0 | 121 | 0 | 100 | 89 | 0 | 328 | 115 | 90 | 0 | 0 | 33 | 54 | 0 | 17 | 113 | 100 | 190 | 104 | 0 | 144 | 116 | 0 | 15 | 0 |  | 839 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 11 | 0 | 33 | 0 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 32 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 190 | 0 | 77 | 100 | 195 | 0 | 352 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 71 | 0 | 0 |  | 8549 | 3910 | 12459 | 4698 | 839 | 1866 | 3719 | 730 | 70 | 379 | 158 | 0 | 0 | 86.06
21:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 315 | 160 |  | 0 | 400 | 230 | 100 | 97 | 55 | 221 | 0 | 185 | 100 | 102 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 25 | 0 | 34 | 80 | 55 | 45 | 20 | 30 | 80 | 0 | 100 | 260 | 290 | 204 | 8 | 90 | 26 | 46 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 144 | 74 | 20 | 0 | 44 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 148 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 245 | 0 | 0 | 193 | 0 | 121 | 0 | 100 | 100 | 0 | 328 | 115 | 90 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 190 | 104 | 0 | 144 | 116 | 0 | 37 | 0 |  | 839 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 33 | 0 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 190 | 0 | 92 | 100 | 195 | 0 | 383 | 94 | 0 | 110 | 0 | 113 | 0 | 0 | 113 | 600 | 72 | 0 | 0 |  | 8399 | 3882 | 12281 | 4697 | 839 | 1928 | 3614 | 750 | 70 | 229 | 154 | 0 | 0 | 86.05
22:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 315 | 165 |  | 0 | 400 | 225 | 100 | 97 | 55 | 221 | 0 | 185 | 100 | 50 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 180 | 0 | 120 | 0 |  | 24 | 0 | 34 | 80 | 0 | 24 | 20 | 27 | 80 | 0 | 80 | 260 | 290 | 200 | 8 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 152 | 144 | 74 | 20 | 0 | 31 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 138 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 119 | 0 | 100 | 100 | 0 | 327 | 115 | 70 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 250 | 104 | 0 | 144 | 116 | 0 | 37 | 0 |  | 840 | 0 | 240 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 33 | 0 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 137 | 0 | 185 | 0 | 95 | 100 | 186 | 0 | 407 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 74 | 0 | 0 |  | 8112 | 3822 | 11934 | 4619 | 840 | 1980 | 3341 | 720 | 70 | 212 | 152 | 0 | 0 | 86.04
23:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 315 | 167 |  | 0 | 400 | 225 | 71 | 97 | 55 | 221 | 0 | 150 | 100 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 24 | 0 | 34 | 80 | 0 | 14 | 20 | 34 | 80 | 0 | 80 | 290 | 315 | 196 | 8 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 148 | 145 | 74 | 20 | 0 | 31 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 138 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 122 | 0 | 100 | 100 | 0 | 328 | 115 | 35 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 290 | 104 | 0 | 144 | 90 | 0 | 37 | 0 |  | 839 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 33 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 132 | 0 | 185 | 0 | 94 | 70 | 178 | 0 | 415 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 74 | 0 | 0 |  | 7978 | 3605 | 11583 | 4679 | 839 | 1992 | 3070 | 700 | 70 | 85 | 148 | 0 | 0 | 86.03
24:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 294 | 221 |  | 0 | 400 | 225 | 0 | 97 | 55 | 221 | 0 | 170 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 181 | 0 | 120 | 0 |  | 24 | 0 | 34 | 80 | 0 | 12 | 20 | 39 | 70 | 0 | 80 | 275 | 300 | 204 | 8 | 94 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 146 | 161 | 73 | 20 | 0 | 31 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 150 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 15 | 0 | 0 | 194 | 0 | 123 | 0 | 100 | 100 | 0 | 329 | 95 | 17 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 310 | 104 | 0 | 108 | 0 | 0 | 34 | 0 |  | 839 | 0 | 205 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 25 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 171 | 0 | 95 | 30 | 170 | 0 | 411 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 75 | 0 | 0 |  | 7664 | 3466 | 11130 | 4654 | 839 | 2045 | 2623 | 700 | 70 | 53 | 146 | 0 | 0 | 86.02
KWH | 0 | 0 | 0 | 4095000 | 5564091 | 2076272 | 0 | 8087560 | 4388000 |  | 0 | 8616000 | 5306560 | 1018560 | 1519440 | 992253 | 5397057 | 0 | 2982000 | 1335360 | 878112 | 944160 | 238077 | 0 | 0 | 0 | 1279800 | 944617 | 1294688 | 394092 | 600000 | 658260 | 783690 | 727200 | 167520 | 0 | 0 | 1688000 | 0 | 0 | 440791 | 4416335 | 0 | 2781206 | 0 |  | 552240 | 0 | 658175 | 1146720 | 300480 | 523200 | 442704 | 467040 | 2186795 | 0 | 2033654 | 6962500 | 6807000 | 5039000 | 217454 | 2192840 | 585720 | 1006560 | 0 | 0 | 0 | 47208 | 492427 | 491328 | 234180 | 778700 | 467460 | 3468480 | 3401920 | 741120 | 420048 | 13700 | 985000 | 711720 | 1228800 | 0 | 3481363 | 3009000 | 0 | 1851840 | 0 | 3501200 | 418000 | 0 | 168120 | 7370500 | 345477 | 264000 | 35136 | 2049927 | 18742 | 14941 | 4250400 | 14758 | 2711664 | 61290 | 2107200 | 2199360 | 0 | 7629000 | 1719600 | 970800 | 0 | 13320 | 165600 | 1075141 | 0 | 95760 | 1853880 | 2340480 | 4893500 | 2048640 | 291700 | 1766880 | 1307236 | 0 | 473040 | 194053 |  | 18372364 | 0 | 8524224 | 0 | 1879680 | 0 | 0 | 0 | 58560 | 13056 | 353250 | 1118000 | 563240 | 351552 | 0 | 0 | 0 | 54726 | 22063 | 337112 | 0 | 55216 | 67551 | 504960 | 145171 | 476880 | 0 | 218430 | 0 | 0 | 3673500 | 0 | 10000 | 3523800 | 0 | 4648818 | 0 | 1919856 | 475200 | 4585136 | 0 | 9066181 | 1152480 | 35002 | 2179872 | 0 | 1982400 | 0 | 42791 | 2351040 | 12724100 | 1159200 | 0 | 0 |  | 174930422 | 82645411 | 257575833 | 112905645 | 18372364 | 44057306 | 57711802 | 16397600 | 1688000 | 2357782 | 3468480 | 616854 | 0
Fuel Cost | 0 | 0 | 0 | 6019650 | 6176141.01 | 2740679.04 | 0 | 8168435.6 | 4519640 |  | 0 | 9391440 | 5890281.6 | 7730870.4 | 10468941.6 | 8394460.38 | 5612939.28 | 0 | 5158860 | 10055260.8 | 8008381.44 | 9290534.4 | 2195069.94 | 0 | 0 | 0 | 9342540 | 7301889.41 | 12765623.68 | 295569 | 450000 | 0 | 0 | 0 | 1619918.4 | 0 | 0 | 455760 | 0 | 0 | 4094948.39 | 4813805.15 | 0 | 4728050.2 | 0 |  | 0 | 0 | 6384297.5 | 10951176 | 2614176 | 4143744 | 557807.04 | 1387108.8 | 3236456.6 | 0 | 2989471.38 | 5152250 | 6807000 | 4635880 | 280515.66 | 2521766 | 661863.6 | 1409184 | 0 | 0 | 0 | 476800.8 | 4702677.85 | 623986.56 | 175635 | 1362725 | 350595 | 26013600 | 3606035.2 | 6729369.6 | 533460.96 | 218378 | 1615400 | 1138752 | 2187264 | 0 | 3968753.82 | 3129360 | 0 | 3537014.4 | 0 | 6057076 | 915420 | 0 | 342964.8 | 7444205 | 259107.75 | 200640 | 597663.36 | 15497448.12 | 318239.16 | 249813.52 | 22102080 | 246753.76 | 26682773.76 | 716480.1 | 17173680 | 23863056 | 0 | 7094970 | 15682752 | 9174060 | 0 | 0 | 1251936 | 9364478.11 | 0 | 955684.8 | 15887751.6 | 15587596.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105824816.64 | 0 | 8950435.2 | 0 | 14774284.8 | 0 | 0 | 0 | 614294.4 | 136826.88 | 3680865 | 1263340 | 873022 | 3431147.52 | 0 | 0 | 0 | 538503.84 | 224160.08 | 2983441.2 | 0 | 746520.32 | 654569.19 | 4893062.4 | 1408158.7 | 915609.6 | 0 | 165351.51 | 0 | 0 | 19910370 | 0 | 285300 | 4122846 | 0 | 6136439.76 | 0 | 2879784 | 8083152 | 5364609.12 | 0 | 8975519.19 | 12031891.2 | 595384.02 | 20686985.28 | 0 | 15383424 | 0 | 472840.55 | 17374185.6 | 55858799 | 0 | 0 | 0 |  | 467458825.13 | 330239939 | 797698764.13 | 121052129.92 | 105824816.64 | 50852704.31 | 393325998.62 | 75769169 | 455760 | 22996886.99 | 26013600 | 1407698.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 240 | 90 | 0 | 321 | 160 |  | 0 | 420 | 230 | 38 | 48 | 45 | 216 | 0 | 180 | 65 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 33 | 33 | 2 | 0 | 0 | 70 | 0 | 0 | 17 | 193 | 0 | 120 | 0 |  | 19 | 0 | 0 | 80 | 0 | 20 | 19 | 3 | 80 | 0 | 80 | 280 | 280 | 202 | 8 | 86 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 25 | 13 | 144 | 123 | 16 | 17 | 2 | 43 | 30 | 50 | 0 | 163 | 137 | 0 | 72 | 0 | 150 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 173 | 0 | 105 | 8 | 100 | 65 | 0 | 404 | 84 | 58 | 0 | 2 | 10 | 54 | 0 | 0 | 94 | 100 | 72 | 104 | 44 | 37 | 42 | 0 | 4 | 29 |  | 721 | 0 | 400 | 0 | 83 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 186 | 0 | 75 | 0 | 196 | 0 | 379 | 70 | 0 | 94 | 0 | 112 | 0 | 6 | 113 | 440 | 38 | 0 | 0 |  | 10542 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 325 | 166 | 0 | 0 | 400 | 230 | 100 | 96 | 55 | 220 | 0 | 145 | 100 | 102 | 149 | 72 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 0 | 70 | 0 | 0 | 25 | 182 | 0 | 120 | 0 | 0 | 25 | 0 | 65 | 80 | 87 | 45 | 20 | 12 | 80 | 0 | 100 | 260 | 270 | 212 | 8 | 95 | 26 | 47 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 160 | 145 | 74 | 20 | 0 | 44 | 30 | 53 | 0 | 163 | 137 | 0 | 77 | 0 | 150 | 18 | 0 | 8 | 300 | 16 | 11 | 0 | 278 | 0 | 0 | 196 | 0 | 121 | 0 | 100 | 100 | 0 | 329 | 115 | 90 | 0 | 0 | 33 | 54 | 0 | 17 | 113 | 100 | 190 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 839 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 3 | 33 | 50 | 29 | 80 | 0 | 0 | 0 | 50 | 16 | 101 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 6 | 144 | 0 | 193 | 0 | 76 | 100 | 190 | 0 | 330 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 71 | 0 | 0 |  | 12634 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 350 | 200 | 0 | 0 | 450 | 235 | 100 | 100 | 55 | 220 | 0 | 150 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 190 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 90 | 50 | 22 | 15 | 100 | 0 | 80 | 300 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 150 | 77 | 22 | 0 | 44 | 30 | 51 | 0 | 163 | 150 | 0 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 310 | 104 | 0 | 144 | 116 | 0 | 0 |  |  | 858 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 150 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 120 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 340 | 200 | 0 | 0 | 450 | 235 | 100 | 100 | 55 | 220 | 0 | 120 | 100 | 100 | 149 | 85 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 190 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 90 | 50 | 22 | 10 | 100 | 0 | 80 | 300 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 150 | 77 | 22 | 1.6 | 44 | 30 | 51 | 0 | 163 | 150 | 0 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 310 | 104 | 50 | 144 | 116 | 0 | 0 | 30 |  | 858 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 50 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 150 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 120 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 330 | 207 | 0 | 0 | 370 | 220 | 0 | 2 | 0 | 221 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 6 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 175 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 20 | 4 | 70 | 0 | 80 | 260 | 290 | 195 | 8 | 30 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 100 | 142 | 16 | 20 | 1 | 31 | 30 | 50 | 0 | 110 | 138 | 0 | 78 | 0 | 150 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 94 | 4 | 90 | 100 | 0 | 329 | 37 | 17 | 0 | 1 | 0 | 36 | 0 | 0 | 0 | 100 | 310 | 0 | 14 | 0 | 0 | 0 | 0 | 8 | 0 | 844 | 0 | 205 | 0 | 66 | 0 | 0 | 0 | 3 | 0 | 25 | 70 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 175 | 0 | 71 | 0 | 182 | 0 | 371 | 0 | 0 | 94 | 0 | 34 | 0 | 0 | 95 | 390 | 75 | 0 | 0 | 0
199
| Minimum Generation |  | 9015 | 6:00
| Highest Generation |  | 12634 | 19:30
| Day Peak Generation |  | 10542 | 12:00
| Evening Peak Generation |  | 12634 | 19:30
| HVDC Max Flow |  | 840 | 22:00
| HVDC EvPeak Flow |  | 839 | 19:30
| Load factor L.F |  | 84.95%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-03-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10542 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9206 | MW
Evening Peak Generation : |  | 12634 | MW Hour : | 19:30 | Available Max Generation : |  | 16054 | MW
E.P. Demand (at gen end) : |  | 12634 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12634 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3254 | MW
Total Gen. (MKWH) : |  | 257.5758 | System Load Factor : | 84.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -40 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-03-29
Actual : | 85.96 | Ft.(MSL) , | Rule curve : | 88.51 | Ft.( MSL )
Gas Consumed : | Total = | 1278.4 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 171904834.23
: |  | Coal : | 75769169 | Oil : | 416322885.61 | Total : | 663996888.84
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4492.8452 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1531.7666 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1373.116 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1240.9761 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1121.3143 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 904.8709 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 500.8756 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 232.8454 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 697.9057 |  |  | 0 | 0%
Total | 0 |  | 12096.5159 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) B.Baria 132/33 kV T1 transformer was under shut down from 11:14 to 12:34 due to red hot maintenance
at 33 kV end.
b) Madunaghat 132/33 kV T1 transformer was under shut down from 09:50 to 18:00 for C/M.
c) Shajadpur 132/33 kV T3 transformer was under shut down from 10:12 to 12:09 for C/M.
d) Tongi(Old) 132/33 kV T1 transformer tripped at 12:14 due to 33 kV feeder fault and was switched on
16:57.
e) Tongi(Old) 132/33 kV T2 transformer tripped at 13:16 due to winding temperature alarm and was
switched on 13:33.
f) Aminbazar 230 kV main Bus-1 was under shut down from 08:30 to 13:00 for D/W.
g) Aminbazar 400/230 kV T02 (New) transformer was switched on at 13:48.
h) Bibiyana South 400 MW GT was synchronized at 13:48.
i) Bibiyana South 400 MW ST was synchronized at 12:52.
j) Rampura 230 kV Bus-1 was under shut down from 08:15 to 15:31 for D/W.
k) Chandraghona-Kaptai 132 kV Ckt-1 & 2 were under shut down from 10:04 to 17:37 for C/M.
l) Rampura 230 kV Bus-2 was under shut down from 15:46 to 17:01 for D/W.
m) Mirpur 132/33 kV T2 transformer was under shut down from 08:56 to 10:28 for D/W.
n) Mirpur 132/33 kV T3 transformer was under shut down from 10:32 to 16:14 for D/W.
o) Bhola 225 MW CCPP GT-1 was synchronized at 00:59(29-03-2021).
p) Madunaghat 132/33 kV T1 transformer was shut down at 06:10(29-03-2021) for C/M.
q) Agargaon 230/132 kV T01 transformer was shut down at 06:27(29-03-2021) for C/M.
r) Sherpur 132/33 kV T1 transformer was shut down at 07:04(29-03-2021) for D/W.
s) Dohazari-Cox'sbazar 132 kv Ckt-2 was shut down at 06:51(29-03-2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4095000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 5564091
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2076272
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 325 | 8087560 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 166 | 4388000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8616000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1018560
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5306560 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 1519440
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 992253
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 72 | 238077 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 394092 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 145 | 2982000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1335360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 5397057 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 878112
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1279800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 944160
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 944617
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1294688
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1258260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 783690
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 727200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 34 | 167520 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 2049927
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 18742 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 14941 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 14758 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 121 | 2711664 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 970800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2048640
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1766880 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 194053
| Dhaka area Total |  |  |  | 5972 | 3784 | 70078774
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 440791
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 61290
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 523200
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1688000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 182 | 4416335 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2781206
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer O/L
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 658175 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1146720 | Engine problem
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2107200
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 442704
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 467040
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 300480 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13320
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 33 | 165600 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1075141
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2340480
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1307236
| Chattogram area Total |  |  |  | 2382 | 1109 | 19934918
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2186795 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2033654 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 5039000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6962500 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6807000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 585720 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 47 | 1006560 | Engine problem
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 47208 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2192840
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 2199360 | Machine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 491328
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 234180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3468480
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 778700
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 492427
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 467460 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 35136 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 95760 | Low demand
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1853880
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 473040
| Cumilla Area Total |  |  |  | 2980 | 1626 | 37668482
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3401920 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 420048
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 741120 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13700
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 196 | 4250400
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1719600 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 291700
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 552240
| Mymensingh Area Total |  |  |  | 709 | 575 | 11390728
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 985000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 711720 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3481363
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 137 | 3009000 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1228800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1851840 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3501200
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 418000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 345477 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7370500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 329 | 7629000 | Gas shortage
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 168120
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 190 | 4893500 | FGMO
| Sylhet Area Total |  |  |  | 2371 | 1526 | 35857520
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 839 | 18372364
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1879680 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 58560 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 3 | 13056 | Line over load
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8524224 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 353250 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 475200
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 1152480 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1488 | 30828814
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 351552 | Line O/L.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 563240
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 50 | 1118000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1919856 | Line O/L.
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 570 | 12724100 | Line O/L.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 71 | 1159200 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 876 | 17835948
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 54726
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 22063 | Engine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 55216 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 67551 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 144 | 3523800 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4648818 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4585136 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 330 | 9066181 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 145171 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 476880
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 218430
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 504960
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 337112
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 35002 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2179872 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2351040
| Rajshahi Area Total |  |  |  | 2183 | 1381 | 28271958
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3673500 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 6 | 10000 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1982400
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42791
| Rangpur Area Total |  |  |  | 605 | 269 | 5708691
| Total |  |  |  | 21312 | 12634 | 257575833
| Eastern Grid Total |  |  |  | 14414 | 8620 | 174930422
| Western Grid Total |  |  |  | 6898 | 4014 | 82645411
| National Grid Total |  |  |  | 21312 | 12634 | 257575833
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-28
(a) ENTIRE EASTERN GRID : |  | 8084 | MW | (b) ENTIRE WESTERN GRID : |  | 3843 | MW
i) Dhaka area |  | 4327 | MW | i) Khulna area |  | 1443 | MW
ii) Chittagong area |  | 1181 | MW | ii) Rajshahi area |  | 1327 | MW
iii) Comilla area |  | 1104 | MW | iii) Barisal area |  | 294 | MW
iv) Mymensingh area |  | 1039 | MW | iv) Rangpur area |  | 779 | MW
v) Sylhet area |  | 433 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11927 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 119 | 16:00 | Jamalpur | 143 | 19:00 | Jhenida | 113 | 19:00
Munsiganj | 126 | 21:00 | Sherpur | 124 | 19:00 | Bottail | 118 | 19:00
Sonargaon | 89 | 18:30 | Srimongal | 47 | 18:30 | G.K Project | 50 | 19:00
Shyampur | 196 | 13:00 | Shahjibazar | 112 | 21:00 | Faridpur | 181 | 20:00
Bhulta | 191 | 19:30 | Fenchuganj | 37 | 18:30 | Madaripur | 90 | 20:00
Madanganj | 57 | 18:00 | Kulawara | 31 | 18:30 | Sariatpur | 58 | 20:00
Shitalakhya | 126 | 12:00 | Sylhet | 104 | 18:30 | Gopalganj | 86 | 19:00
Rahim steel | 32 | 12:00 | Chatak | 29 | 19:00 | Bagerhat | 93 | 18:30
Matuail | 58 | 12:00 | Sunamganj | 36 | 20:00 | Mongla | 38 | 12:00
Ghorasal | 79 | 18:00 | Biani Bazar | 51 | 19:00 | Satkhira | 106 | 22:00
Narsingdi | 165 | 19:00 | Comilla (S) | 164 | 18:30 | Gallamari | 32 | 22:00
Haripur (SBU) | 133 | 15:00 | Comilla(N) | 123 | 21:00 | Magura | 52 | 19:00
Sreenagar |  |  | Chandpur | 62 | 19:00 | Norail | 40 | 19:00
Ullon | 86 | 19:00 | Feni | 112 | 18:30 | Chuadanga | 87 | 20:00
Hasnabad | 103 | 20:00 | Chowmuhani | 164 | 18:30 | Borguna | 14 | 19:00
Magbazar | 94 | 15:00 | Ashuganj | 48 | 1:00 | Barisal(N) | 36 | 19:30
Maniknagar | 87 | 12:00 | Daudkandi | 142 | 21:00 | Barisal (S) | 102 | 19:00
Bangabhaban | 22 | 10:00 | B.Baria | 145 | 19:00 | Patuakhali | 89 | 19:30
Narinda | 85 | 13:00 | Ramganj | 72 | 18:30 | Bhandaria | 44 | 21:00
Dhanmondi | 177 | 14:00 | Chaddagram | 38 | 20:00 | Borhan Uddin | 32 | 22:00
Lalbag | 87 | 13:00 | PHP | 10 | 20:00 | Ishurdi | 55 | 19:00
Madartek | 71 | 22:00 | Kochua | 65 | 18:30 | Ruppur Paromanobik | 3 | 10:00
Dhaka University | 38 | 12:00 | Madunaghat | 59 | 18:30 | Natore | 129 | 19:30
Aftabnagar | 25 | 9:00 | Hathazari | 77 | 13:00 | Bogra | 166 | 19:00
Fatullah | 62 | 24:00 | Khulshi | 203 | 12:00 | Noagaon | 110 | 19:00
Nawabganj | 45 | 20:00 | Halishahar | 134 | 15:00 | Rajshahi | 141 | 19:30
Mirpur | 109 | 19:00 | Baraulia | 142 | 19:00 | Rajshahi New | 19 | 19:00
Kalyanpur | 93 | 13:00 | Sikalbaha | 28 | 19:00 | C.Nawabganj | 80 | 20:00
Gulshan | 126 | 15:00 | Dohazari | 82 | 18:30 | Amnura | 58 | 20:00
Uttara | 97 | 19:00 | Cox'sbazar | 106 | 21:00 | Pabna | 88 | 19:00
Uttara New | 29 | 19:00 | Chandraghona | 28 | 19:00 | Shahjadpur | 109 | 20:00
Kamrangirchar | 90 | 19:00 | Kaptai | 0 | #N/A | Serajganj | 109 | 19:30
Savar | 187 | 19:00 | A. Khaer Stl. | 9 | 6:00 | Niyamatpur | 93 | 19:00
Bhasantec | 160 | 13:00 | Bakulia | 103 | 18:30 | Joypurhat | 59 | 20:00
Agargaon | 68 | 13:00 | Julda | 22 | 1:00 | Sherpur(Bogura) | 52 | 19:00
Satmosjid | 93 | 19:00 | TK chemical | 22 | 14:00 | Mohastangor | 56 | 19:00
Tongi | 100 | 18:00 | Modern Steel | 0 | #N/A | Bangura | 25 | 20:00
Kabirpur | 231 | 19:00 | Shahmirpur | 25.5 | 18:00 | Rangpur | 131 | 19:00
Basundhara | 154 | 18:30 | Khagrachhari | 22 | 19:30 | Lalmonirhat | 44 | 19:00
Manikganj | 66 | 20:00 | Matarbari | 35 | 18:00 | Saidpur | 107 | 19:00
Joydevpur | 160 | 18:30 | Baroiar Hat | 32 | 18:30 | Purbasadipur | 98 | 12:00
New Tongi | 111 | 16:00 | Rangamati | 12 | 18:30 | Thakurgaon | 81 | 20:00
Kodda | 245 | 18:30 | Abul Khair 230 | 13 | 16:00 | Palashbari | 104 | 20:00
Dhamrai | 112 | 19:00 | BSRM | 143 | 10:00 | Barapukuria | 53 | 19:00
Rajendrapur | 100 | 19:00 | GPH Ispat | 88 | 15:00 | Panchagar | 47 | 19:30
Valuka | 120 | 20:00 | Goalpara | 32 | 13:00 | Joldhaka | 56 | 20:00
Tangail | 218 | 19:00 | Central s/s | 90 | 19:00 | Kurigram | 56 | 19:00
Mymensing | 215 | 19:00 | Noapara | 44 | 0.875 | Mithapukur | 29 | 19:00
Kishorganj | 1244 | 22:00 | Jessore | 131 | 19:00
Netrokona | 120 | 20:00 | Benapol | 62 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 7:00 | 400 | 16:00 | Kaliakoir | 391 | 0.16667 | 380 | 0.66667
| Bheramara | 404 | 14:00 | 398 | 1:00 | Bhulta | 381 | 0.29167 | 370 | 0.66667
| Ashuganj(N) | 387 | 22:00 | 376 | 17:00 | Gopalganj | 405 | 0.625 | 384 | 0.8125
| Payra | 407 | 19:00 | 395 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 232 | 1:00 | Hathazari | 225 | 20:00 | 218 | 6:00
| Ishurdi | 233 | 1:00 | 227 | 19:30 | Megnaghat | 232 | 4:00 | 230 | 21:00
| Ashuganj | 235 | 1:00 | 230 | 16:00 | Fenchuganj | 241 | 19:00 | 238 | 7:00
| Serajganj | 232 | 1:00 | 227 | 8:00 | Siddhirganj | 228 | 21:00 | 222 | 10:00
| Baghabari | 237 | 24:00 | 227 | 7:00 | Maniknagar | 227 | 21:00 | 220 | 11:00
| Barapukuria | 237 | 24:00 | 225 | 8:00 | Agargaon | 225 | 4:00 | 216 | 11:00
| Bogra | 228 | 1:00 | 216 | 8:00 | Barisal | 248 | 20:00 | 240 | 3:00
| Rajshahi | 229 | 1:00 | 221 | 19:30 | Bhola 225 MW | 252 | 7:00 | 246 | 15:00
| Khulna South | 232 | 18:00 | 221 | 7:00 | AKSML | 226 | 20:00 | 217 | 5:00
| Rampura | 227 | 1:00 | 221 | 11:00 | BSRM | 229 | 19:30 | 219 | 5:00
| Haripur | 228 | 21:00 | 221 | 11:00 | Bibiyana | 241 | 12:00 | 236 | 17:00
| Hasnabad | 226 | 21:00 | 220 | 18:00 | Bhulta | 230 | 19:00 | 221 | 17:00
| Shyampur | 225 | 19:00 | 220 | 17:00 | Ashuganj (S) | 233 | 20:00 | 227 | 17:00
| Aminbazar | 226 | 1:00 | 222 | 2:00 | Kaliakoir | 228 | 20:00 | 215 | 16:00
| Tongi | 223 | 19:30 | 210 | 16:00 | GPH | 228 | 19:30 | 216 | 6:00
| Comilla (N) | 229 | 19:00 | 222 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 131 | 11:00 | Madanhat | 136 | 0.77083 | 130 | 0.25
| Munsiganj | 136 | 1:00 | 131 | 11:00 | Hathazari | 134 | 0.54167 | 129 | 0.125
| Sonargaon | 137 | 19:00 | 132 | 10:00 | Khulshi | 134 | 0.79167 | 127 | 0.70833
| Shyampur | 134 | 1:00 | 130 | 11:00 | Halishahar | 136 | 0.79167 | 129 | 0.25
| Bhulta | 130 | 1:00 | 125 | 11:00 | Baraulia | 134 | 0.041667 | 129 | 0.45833
| Madanganj | 137 | 4:00 | 130 | 9:00 | Sikalbaha | 137 | 0.79167 | 130 | 0.20833
| Shitalakhya | 141 | 19:00 | 129 | 11:00 | Dohazari | 132 | 0.79167 | 126 | 0.70833
| Rahim steal | 136 | 21:00 | 131 | 11:00 | Cox'sbazar | 125 | 0.29167 | 116 | 0.75
| Matuail | 135 | 1:00 | 131 | 11:00 | Chandraghona | 135 | 0.8125 | 127 | 0.25
| Ghorasal | 137 | 1:00 | 135 | 15:00 | Kaptai
| Narsinghdi | 133 | 1:00 | 129 | 18:30 | A. Khaer Stl. | 132 | 0.54167 | 127 | 0.20833
| Haripur (SBU) | 136 | 19:00 | 130 | 18:00 | Bakulia | 136 | 0.79167 | 129 | 0.70833
| Sreenagar |  |  |  |  | Julda | 138 | 0.79167 | 130 | 0.66667
| Ullon | 135 | 4:00 | 128 | 17:00 | TK Chemical | 133 | 0.041667 | 131 | 0.45833
| Hasnabad | 136 | 19:00 | 128 | 10:00 | Modern Steel
| Magbazar | 134 | 4:00 | 127 | 17:00 | Shahmirpur | 137 | 0.83333 | 129 | 0.25
| Maniknagar | 131 | 1:00 | 125 | 17:00 | Khagrachhari | 134 | 0.8125 | 128 | 0.20833
| Bangabhaban | 131 | 1:00 | 125 | 17:00 | Matarbari | 128 | 0.54167 | 120 | 0.66667
| Narinda | 131 | 1:00 | 125 | 17:00 | Baroiar Hat | 133 | 0.54167 | 127 | 0.125
| Dhanmondi | 135 | 4:00 | 128 | 17:00 | Rangamati | 133 | 0.54167 | 128 | 0.16667
| Lalbag | 136 | 19:00 | 125 | 11:00 | Goalpara S/S | 135 | 17:00 | 129 | 7:00
| Madartek | 135 | 7:00 | 129 | 15:00 | Khulna Central S/S | 134 | 17:00 | 129 | 11:00
| Dhaka University | 135 | 7:00 | 128 | 16:00 | Noapara | 131 | 5:00 | 127 | 0.29167
| Aftabnagar | 135 | 4:00 | 129 | 15:00 | Jessore | 126 | 4:00 | 118 | 0.79167
| Fatullah | 135 | 7:00 | 130 | 11:00 | Benapol | 128 | 4:00 | 118 | 0.79167
| Nawabganj | 130 | 1:00 | 125 | 11:00 | Jhenida | 125 | 6:00 | 112 | 0.79167
| Mirpur | 135 | 20:00 | 128 | 17:00 | Bottail | 131 | 0.20833 | 123 | 0.79167
| Kalyanpur | 135 | 20:00 | 130 | 17:00 | G.K Project | 138 | 2:00 | 134 | 0.8125
| Gulshan | 135 | 7:00 | 128 | 17:00 | Faridpur | 135 | 0.16667 | 127 | 0.8125
| Uttara | 133 | 20:00 | 128 | 16:00 | Madaripur | 141 | 0.33333 | 133 | 0.8125
| Uttara New | 134 | 20:00 | 128 | 11:00 | Shariyatpur S/S | 142 | 0.16667 | 132 | 0.8125
| Kamrangirchar | 136 | 20:00 | 125 | 11:00 | Gopalganj | 143 | 0.16667 | 132 | 0.8125
| Savar | 136 | 20:00 | 127 | 11:00 | Bagerhat | 133 | 18:00 | 125 | 0.29167
| Bhasantec | 130 | 20:00 | 125 | 11:00 | Mongla | 132 | 0.75 | 124 | 0.29167
| Agargaon | 131 | 20:00 | 126 | 11:00 | Satkhira | 133 | 9:00 | 126 | 0.79167
| Satmosjid | 132 | 7:00 | 125 | 11:00 | Gallamari | 135 | 18:00 | 129 | 0.29167
| Tongi | 137 | 14:00 | 130 | 17:00 | Magura | 125 | 3:00 | 110 | 19:00
| Kabirpur | 138 | 1:00 | 129 | 16:00 | Narail | 123 | 0.16667 | 108 | 0.79167
| Basundhara | 135 | 14:00 | 128 | 17:00 | Chuadanga | 121 | 6:00 | 101 | 0.79167
| Manikganj | 139 | 13:00 | 131 | 17:00 | Borguna | 140 | 0.25 | 133 | 0.77083
| Joydevpur | 138 | 20:00 | 130 | 11:00 | Barisal(N) | 141 | 7:00 | 135 | 0.79167
| New Tongi | 136 | 13:00 | 129 | 17:00 | Barisal (S) | 140 | 9:00 | 135 | 0.041667
| Kodda | 139 | 20:00 | 127 | 9:00 | Patuakhali(S) | 139 | 7:00 | 132 | 15:00
| Dhamrai | 134 | 1:00 | 129 | 11:00 | Bhandaria | 139 | 0.29167 | 130 | 0.8125
| Rajendrapur | 135 | 14:00 | 124 | 17:00 | Ishurdi | 136 | 0.041667 | 132 | 0.45833
| Valuka | 122 | 1:00 | 107 | 18:30 | Ruppur Paromanobik | 136 | 0.25 | 132 | 0.41667
| Tangail | 133 | 1:00 | 122 | 18:30 | Natore | 135 | 1:00 | 130 | 7:00
| Mymensing | 127 | 1:00 | 116 | 18:30 | Bogra | 136 | 1:00 | 126 | 8:00
| Kishorganj | 129 | 7:00 | 122 | 18:30 | Noagaon | 128 | 1:00 | 119 | 7:00
| Netrokona | 122 | 1:00 | 110 | 18:30 | Rajshahi | 134 | 3:00 | 129 | 8:00
| Jamalpur | 138 | 23:00 | 125 | 6:00 | Rajshahi New | 135 | 2:00 | 130 | 7:00
| Sherpur | 137 | 24:00 | 119 | 6:00 | C.Nawabganj | 131 | 18:30 | 126 | 11:00
| Srimongal | 140 | 8:00 | 135 | 23:00 | Amnura | 132 | 18:30 | 126 | 7:00
| Shahjibazar | 136 | 4:00 | 133 | 19:00 | Pabna | 135 | 1:00 | 130 | 19:00
| Fenchuganj | 139 | 4:00 | 135 | 18:30 | Shahjadpur | 140 | 1:00 | 132 | 19:00
| Khulawara | 137 | 5:00 | 135 | 13:00 | Serajganj | 133 | 1:00 | 125 | 19:30
| Sylhet | 135 | 4:00 | 133 | 15:00 | Niyamatpur | 126 | 1:00 | 113 | 8:00
| Chatak | 135 | 7:00 | 131 | 18:30 | Joypurhat | 126 | 1:00 | 115 | 8:00
| Sunamganj | 134 | 4:00 | 130 | 18:00 | Sherpur(Bogura) | 136 | 1:00 | 126 | 8:00
| Biani Bazar | 136 | 7:00 | 131 | 18:30 | Mohastangor | 135 | 1:00 | 124 | 8:00
| Comilla(s) | 127 | 4:00 | 122 | 15:00 | Bangura | 136 | 1:00 | 131 | 20:00
| Comilla(n) | 138 | 19:00 | 133 | 11:00 | Rangpur | 131 | 1:00 | 120 | 8:00
| Chandpur | 137 | 12:00 | 131 | 5:00 | Lalmonirhat | 130 | 1:00 | 117 | 19:00
| Feni | 132 | 12:00 | 128 | 5:00 | Saidpur | 130 | 1:00 | 116 | 19:00
| Chowmuhani | 135 | 19:30 | 126 | 3:00 | Purbasadipur | 128 | 1:00 | 113 | 8:00
| Ashuganj | 139 | 7:00 | 135 | 19:00 | Thakurgaon | 128 | 1:00 | 109 | 19:00
| Daudkandi | 136 | 19:00 | 129 | 15:00 | Palashbari | 131 | 2:00 | 120 | 8:00
| B.Baria | 135 | 4:00 | 130 | 16:00 | Barapukuria | 134 | 1:00 | 125 | 8:00

## L-Curve
Date | 2021-03-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 72 | 7664 | 3466 | 11130 |  |  |  | QF-LDC-11
0:30 | 181 | 7346 | 3436.5 | 10782.5 | Date: | 2021-03-28
1:00 | 290 | 7028 | 3407 | 10435
1:30 | 320 | 6848 | 3364.5 | 10212.5
2:00 | 350 | 6668 | 3322 | 9990
2:30 | 340 | 6527.5 | 3266 | 9793.5 | [5 empty] | Gen. at Eve. Peak | 12634 | 12634 MW (19:30 )
3:00 | 330 | 6387 | 3210 | 9597 | [6 empty] | 19:30
3:30 | 310 | 6365.5 | 3132.5 | 9498 | [5 empty] | Gen. at Day Peak | 10542 | 10542 MW (12:00 )
4:00 | 290 | 6344 | 3055 | 9399 | [6 empty] | 12:00
4:30 | 260 | 6238 | 2972 | 9210 | [5 empty] | Highest Generation | 12634
5:00 | 230 | 6132 | 2889 | 9021 | [6 empty] | 19:30
5:30 | 210 | 6147.5 | 2870.5 | 9018
6:00 | 190 | 6163 | 2852 | 9015
6:30 | 115 | 6257.5 | 2835 | 9092.5
7:00 | 40 | 6352 | 2818 | 9170
7:30 | 82 | 6345.5 | 2920.5 | 9266
8:00 | 124 | 6339 | 3023 | 9362
8:30 | 223 | 6446 | 3134.5 | 9580.5
9:00 | 322 | 6553 | 3246 | 9799
9:30 | 325 | 6735 | 3262.5 | 9997.5
10:00 | 328 | 6917 | 3279 | 10196
10:30 | 316 | 6982.5 | 3284.5 | 10267
11:00 | 304 | 7048 | 3290 | 10338
11:30 | 215 | 7130 | 3310 | 10440
12:00 | 126 | 7212 | 3330 | 10542
12:30 | 67 | 7487.5 | 3302 | 10789.5
13:00 | 8 | 7763 | 3274 | 11037
13:30 | 9 | 7735.5 | 3250.5 | 10986
14:00 | 10 | 7708 | 3227 | 10935
14:30 | 141 | 7715.5 | 3293 | 11008.5
15:00 | 272 | 7723 | 3359 | 11082
15:30 | 293 | 7662.5 | 3406.5 | 11069
16:00 | 314 | 7602 | 3454 | 11056
16:30 | 347 | 7420.5 | 3408 | 10828.5
17:00 | 380 | 7239 | 3362 | 10601
17:30 | 316 | 7271.5 | 3325 | 10596.5
18:00 | 252 | 7304 | 3288 | 10592
18:30 | 132 | 7981 | 3589 | 11570
19:00 | 12 | 8658 | 3890 | 12548
19:30 | 12 | 8620 | 4014 | 12634
20:00 | 40 | 8549 | 3910 | 12459 |  |  |  | Executive Engineer
20:30 | 30 | 8474 | 3896 | 12370 |  |  |  | Network Operation Division
21:00 | 20 | 8399 | 3882 | 12281
21:30 | 17 | 8255.5 | 3852 | 12107.5
22:00 | 14 | 8112 | 3822 | 11934 |  |  |  |  | Page 6 of 7
22:30 | 19 | 8045 | 3713.5 | 11758.5
23:00 | 24 | 7978 | 3605 | 11583
23:30 | 48 | 7821 | 3535.5 | 11356.5
24:00 | 72 | 7664 | 3466 | 11130
12634 MW (19:30 )
10542 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-28 |  | Energy | 257575833
[11 empty] | 2021-03-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4654 | 839 | 2045 | 3070 | 700 | 70 | 53 | 0 | 146 | 0
0:30 | 4645.5 | 780 | 1977.5 | 2635 | 695 | 70 | 52 | 0 | 151 | 0 | Date: | 2021-03-28
1:00 | 4637 | 721 | 1910 | 2200 | 690 | 70 | 51 | 0 | 156 | 0
1:30 | 4650.5 | 721 | 1923 | 1954 | 690 | 70 | 51 | 0 | 153 | 0 | [7 empty] | Total Energy | 257.5758 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4664 | 721 | 1936 | 1708 | 690 | 70 | 51 | 0 | 150 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4651.5 | 721 | 1953.5 | 1520.5 | 680 | 70 | 51 | 0 | 146 | 0 | [7 empty] | Energy Requirement | 257.5758
3:00 | 4639 | 721 | 1971 | 1333 | 670 | 70 | 51 | 0 | 142 | 0
3:30 | 4628.5 | 721 | 1946 | 1282.5 | 660 | 70 | 51 | 0 | 139 | 0 | [6 empty] | Shortage
4:00 | 4618 | 721 | 1921 | 1232 | 650 | 70 | 51 | 0 | 136 | 0
4:30 | 4592.5 | 720.5 | 1916.5 | 1093.5 | 635 | 70 | 51 | 0 | 131 | 0
5:00 | 4567 | 720 | 1912 | 955 | 620 | 70 | 51 | 0 | 126 | 0
5:30 | 4593 | 720.5 | 1907 | 950 | 604.5 | 70 | 51 | 0 | 122 | 0
6:00 | 4619 | 721 | 1902 | 945 | 589 | 70 | 51 | 0 | 118 | 0
6:30 | 4644.5 | 721 | 1852 | 1043 | 589.5 | 70 | 51 | 0 | 115 | 6.5 |  |  |  |  | Coal
7:00 | 4670 | 721 | 1802 | 1141 | 590 | 70 | 51 | 0 | 112 | 13
7:30 | 4631 | 721 | 1821 | 1278 | 585 | 70 | 25.5 | 0 | 112 | 22.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4592 | 721 | 1840 | 1415 | 580 | 70 | 0 | 0 | 112 | 32
8:30 | 4612.5 | 721 | 1869 | 1567 | 580 | 70 | 5 | 0 | 112 | 44
9:00 | 4633 | 721 | 1898 | 1719 | 580 | 70 | 10 | 0 | 112 | 56
9:30 | 4661 | 721 | 1861.5 | 1905 | 580 | 70 | 13 | 0 | 122 | 64
10:00 | 4689 | 721 | 1825 | 2091 | 580 | 70 | 16 | 0 | 132 | 72
10:30 | 4730.5 | 721 | 1840.5 | 2092.5 | 580 | 70 | 16 | 0 | 136 | 80.5
11:00 | 4772 | 721 | 1856 | 2094 | 580 | 70 | 16 | 0 | 140 | 89
11:30 | 4733 | 721 | 1845 | 2221 | 585 | 70 | 33 | 0 | 142 | 90
12:00 | 4694 | 721 | 1834 | 2348 | 590 | 70 | 50 | 0 | 144 | 91
12:30 | 4642.5 | 721 | 1779 | 2694 | 599.5 | 70 | 50.5 | 0 | 144 | 89
13:00 | 4591 | 721 | 1724 | 3040 | 609 | 70 | 51 | 0 | 144 | 87
13:30 | 4591 | 721 | 1724 | 3040 | 609 | 70 | 51 | 0 | 144 | 87
14:00 | 4591 | 721 | 1724 | 3040 | 609 | 70 | 51 | 0 | 144 | 87
14:30 | 4642.5 | 730.5 | 1766.5 | 2968 | 609.5 | 70 | 51 | 0 | 151 | 70.5
15:00 | 4694 | 740 | 1809 | 2896 | 610 | 70 | 51 | 0 | 158 | 54
15:30 | 4746 | 767 | 1829.5 | 2784.5 | 620 | 70 | 52 | 0 | 156 | 44
16:00 | 4798 | 794 | 1850 | 2673 | 630 | 70 | 53 | 0 | 154 | 34
16:30 | 4783 | 809 | 1798.5 | 2520 | 625 | 70 | 53 | 0 | 147 | 23
17:00 | 4768 | 824 | 1747 | 2367 | 620 | 70 | 53 | 0 | 140 | 12
17:30 | 4684 | 828.5 | 1751 | 2412 | 614.5 | 70 | 90.5 | 0 | 140 | 6
18:00 | 4600 | 833 | 1755 | 2457 | 609 | 70 | 128 | 0 | 140 | 0
18:30 | 4633.5 | 836 | 1800.5 | 3121 | 624.5 | 70 | 333.5 | 0 | 151 | 0
19:00 | 4667 | 839 | 1846 | 3785 | 640 | 70 | 539 | 0 | 162 | 0
19:30 | 4730 | 839 | 1859 | 3800 | 720 | 70 | 456 | 0 | 160 | 0
20:00 | 4698 | 839 | 1866 | 3719 | 730 | 70 | 379 | 0 | 158 | 0
20:30 | 4697.5 | 839 | 1897 | 3666.5 | 740 | 70 | 304 | 0 | 156 | 0
21:00 | 4697 | 839 | 1928 | 3614 | 750 | 70 | 229 | 0 | 154 | 0
21:30 | 4658 | 839.5 | 1954 | 3477.5 | 735 | 70 | 220.5 | 0 | 153 | 0
22:00 | 4619 | 840 | 1980 | 3341 | 720 | 70 | 212 | 0 | 152 | 0
22:30 | 4649 | 839.5 | 1986 | 3205.5 | 710 | 70 | 148.5 | 0 | 150 | 0
23:00 | 4679 | 839 | 1992 | 3070 | 700 | 70 | 85 | 0 | 148 | 0
23:30 | 4666.5 | 839 | 2018.5 | 3070 | 700 | 70 | 69 | 0 | 147 | 0 | Max Temp. in Dhaka |  | 36.8° C
24:00 | 4654 | 839 | 2045 | 3070 | 700 | 70 | 53 | 0 | 146 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [5 empty] | 2 | 16 | 16 | 16 | 16 | 17 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 440791
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 3 | 7 | 9 | 15 | 8 | 10 | 7 | 3 | 2 | 1 | [9 empty] | 61290
6 | Sikalbaha 225MW CCPP (Gas) | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 202 | 188 | 188 | 197 | 193 | 190 | 186 | 184 | 181 | 181 | 181 |  | 181 | 182 | 182 | 181 | 180 | 181 | 181 | 4416335
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 80 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2781206
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | [10 empty] | 21 |  | 85 | 65 | 51 | 34 | 34 | 34 | 34 | 658175
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 40 | [6 empty] | 35136
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | [6 empty] | 47208
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 150 | 190 | 150 | 150 | 180 | 70 | 32 | 80 | 150 | 120 | 70 |  | 145 | 145 | 175 | 185 | 185 | 150 | 170 | 2982000
17 | Siddhirganj 335 MW CCPP | 222 | 222 | 222 | 222 | 222 | 223 | 223 | 223 | 222 | 222 | 217 | 216 | 208 | 210 | 209 | 219 | 216 | 217 |  | 223 | 220 | 221 | 221 | 221 | 221 | 221 | 5397057
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 1 | 38 | 45 | 45 | 135 | 154 | 95 | 95 | 95 | 134 |  | 275 | 278 | 280 | 245 | 145 | 95 | 15 | 2049927
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4095000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 123 | 134 | 140 | 157 | 160 | 180 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5564091
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 2186795
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 80 | 80 |  | 80 | 100 | 100 | 100 | 80 | 80 | 80 | 2033654
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 585720
33 | Ashuganj 225 MW CCPP | 216 | 212 | 211 | 216 | 216 | 218 | 214 | 206 | 201 | 210 | 200 | 202 | 212 | 210 | 206 | 207 | 207 | 205 |  | 211 | 212 | 210 | 204 | 200 | 196 | 204 | 5039000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 280 | 320 | 280 | 285 | 280 | 280 | 280 | 265 | 290 | 270 | 270 | 295 |  | 270 | 270 | 270 | 290 | 290 | 315 | 300 | 6807000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 315 | 280 | 280 | 340 | 280 | 280 | 260 | 280 | 260 | 260 | 285 |  | 260 | 260 | 260 | 260 | 260 | 290 | 275 | 6962500
35 | Ashuganj 55 MW PP (Precision) | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 42 | 43 | 47 |  | 47 | 47 | 46 | 46 | 46 | 46 | 48 | 1006560
36 | Chandpur 150 MW CCPP | 85 | 91 | 87 | 91 | 91 | 91 | 85 | 91 | 91 | 94 | 95 | 86 | 93 | 91 | 95 | 95 | 95 | 95 |  | 90 | 95 | 95 | 90 | 95 | 95 | 94 | 2192840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 350 | 349 | 349 | 349 | 355 | 358 | 346 | 344 | 331 | 332 | 321 | 318 | 312 | 317 | 326 | 332 | 335 |  | 330 | 325 | 324 | 315 | 315 | 315 | 294 | 8087560
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 350 | 380 | 380 | 320 | 320 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8616000
41 | Haripur 360MW CCPP(HPL) | 197 | 233 | 250 | 246 | 233 | 233 | 203 | 172 | 150 | 116 | 148 | 160 | 150 | 151 | 162 | 162 | 170 | 165 |  | 166 | 166 | 160 | 160 | 165 | 167 | 221 | 4388000
42 | RPCL 210MW CCPP | 162 | 163 | 164 | 165 | 166 | 166 | 166 | 163 | 145 | 140 | 120 | 123 | 121 | 121 | 122 | 121 | 138 | 139 |  | 142 | 145 | 144 | 144 | 144 | 145 | 161 | 3401920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 14 | 27 | 32 | 41 | 44 | 40 | 34 | 27 | 17 | 6 | 0 | [8 empty] | 291700
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 42 | 43 | 41 | 42 | 42 | 43 |  | 43 | 44 | 44 | 44 | 31 | 31 | 31 | 985000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 711720
46 | Shajibazar 330 MW CCPP | 135 | 136 | 137 | 137 | 137 | 139 | 137 | 137 | 136 | 139 | 137 | 137 | 138 | 138 | 139 | 137 | 136 | 137 |  | 137 | 137 | 138 | 137 | 137 | 137 | 137 | 3009000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 78 | 77 | 74 | 72 | 71 | 74 | 73 | 74 | 76 | 76 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1851840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 148 | 148 | 148 | 148 | 121 | 120 | 120 | 135 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 149 | 148 | 138 | 138 | 150 | 3501200
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 168120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 53 | 51 | 53 | 50 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1228800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 345477
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 290 | 290 | 280 | 300 | 290 | 290 | 325 | 300 | 300 | 300 | 290 | 280 | 300 | 310 | 310 | 310 |  | 300 | 300 | 280 | 290 | 310 | 310 | 305 | 7370500
| Bibiyana South 400 MW | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  |  | 24 | 72 | 72 | 132 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 250 | 290 | 310 | 4893500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1294688
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 20 | 19 | 19 | 22 | 19 | 19 | 19 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 552240
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 18 | 17 | 19 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 442704
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 22 |  | 19 |  |  | 22 | 22 | 22 | 22 | 394092
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 420048
63 | Impoprt (Tripura) | 156 | 150 | 142 | 136 | 126 | 118 | 112 | 112 | 112 | 132 | 140 | 144 | 144 | 154 | 158 | 154 | 140 | 140 |  | 162 | 160 | 158 | 154 | 152 | 148 | 146 | 3468480
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 40 | 30 | 9 | 2 | 2 | 3 | 3 | 5 | 6 | 5 | 4 | 4 | 4 |  | 9 | 12 | 22 | 30 | 27 | 34 | 39 | 467040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491328
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 778700
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 18 | 18 | 18 | 18 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 467460
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 30 | 27 | 25 | 23 | 26 | 26 | 26 | 28 | 20 |  | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 658260
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 783690
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 17 | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 727200
73 | Ghorashal 108MW PP (Regent) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 90 | 88 | 86 | 90 | 94 | 94 | 90 | 86 | 41 | 80 |  | 98 | 98 | 98 | 95 | 98 | 98 | 98 | 2076272
| Feni Lanka Power | [16 empty] | 17 | 17 |  | 50 | 17 | 17 |  |  |  |  | 95760
| Chowmuhani 113 MW | 113 | 55 | 8 | 8 | 8 | 8 | 8 | 8 | 20 | 46 | 46 | 94 | 113 | 113 | 113 | 113 | 55 | 55 |  | 102 | 113 | 113 | 113 | 113 | 113 | 113 | 1853880
| Manikgonj 162MW PP(MPGL) | 17 | [5 empty] | 1 | 17 | 17 | 17 | 17 | 37 | 134 | 144 | 144 | 90 | 72 | 73 |  | 136 | 144 | 144 | 144 | 144 | 144 | 108 | 1766880
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | [6 empty] | 7 | 8 | 50 | 50 | 65 | 88 | 92 | 50 | 50 | 50 | 50 |  | 84 | 100 | 100 | 100 | 100 | 100 | 100 | 1335360
78 | Gazipur 52 MW PP | [11 empty] | 2 | 16 | 16 | 8 | 8 | 10 | 25 |  | 31 | 34 | 16 |  |  |  |  | 167520
79 | Kodda 150MW PP | [8 empty] | 10 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 82 |  | 149 | 149 | 150 | 98 | 82 | 48 | 16 | 944160
80 | Jamalpur 95 MW PP(Powerpac) | 57 | 57 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 57 | 74 | 74 | 74 | 74 | 74 | 73 | 741120
81 | Jangalia 52 MW PP (Lakdanavi) | [9 empty] | 6 | 8 | 8 | 50 | 52 | 52 | 24 | 24 | 25 |  | 48 | 52 | 52 | 52 | 25 |  |  | 492427
| Gazipur 100 MW PP | [8 empty] | 6 | 44 | 52 | 58 | 90 | 90 | 52 | 52 | 35 | 35 |  | 71 | 90 | 90 | 90 | 70 | 35 | 17 | 970800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 1 | 4 | 2 | 1 | 2 | 1 | 1 | 0 | [9 empty] | 13320
| Jodiac Power | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1075141
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 37 | 46 | 48 | 92 | 92 | 92 | 64 | 64 | 70 |  | 96 | 96 | 96 | 97 | 97 | 97 | 97 | 1519440
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 10 | 10 | 10 | 10 | 25 | 40 |  | 63 | 72 | 20 |  |  |  |  | 238077
86 | Meghnaghat CCPP(Summit) | 230 | 230 | 220 | 220 | 220 | 225 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 225 | 225 | 225 | 5306560
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 2 | 7 | 7 | 38 | 100 | 100 | 78 | 50 | 50 | 50 |  | 89 | 100 | 97 | 100 | 100 | 71 |  | 1018560
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 75 | 27 | 17 | 17 | 20 | 53 | 63 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 75 | 70 |  | 99 | 104 | 104 | 104 | 104 | 104 | 104 | 2048640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 60 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 23 | 50 | 50 | 80 | 80 | 80 | 80 | 50 | 20 | 20 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1146720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 7 | 15 | 24 | 102 | 102 | 48 | 48 | 48 | 48 |  | 64 | 102 | 102 | 102 | 50 | 24 | 0 | 878112
95 | Patenga 50MW PP (Baraka) | [8 empty] | 4 | 18 | 18 | 20 | 36 | 44 | 44 | 44 | 45 | 45 |  | 45 | 45 | 46 | 45 | 24 | 14 | 12 | 523200
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 11 | 12 | 12 | 14 | 18 | 21 |  | 66 | 87 | 88 | 55 |  |  |  | 300480
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | [5 empty] | 15 | 15 | 50 | 42 | 45 | 52 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 992253
100 | Manikganj 55 MW PP (Northern) | 55 | 17 | 17 |  |  |  | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 944617
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3481363
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1279800
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 30 | [5 empty] | 0 | 18742
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 25 | [6 empty] | 14941
106 | Mymensingh 200 MW PP (United) | 195 | 140 | 125 | 125 | 100 | 100 | 144 | 200 | 200 | 200 | 200 | 173 | 185 | 192 | 180 | 172 | 185 | 185 |  | 196 | 196 | 196 | 193 | 200 | 200 | 194 | 4250400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 27 | [6 empty] | 14758
114 | Kodda 149 MW PP Unit-1 (Summit) | 121 | 117 | 94 | 100 | 100 | 100 | 102 | 118 | 116 | 111 | 105 | 105 | 104 | 104 | 102 | 109 | 121 | 121 |  | 121 | 121 | 121 | 121 | 119 | 122 | 123 | 2711664
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 20 | 20 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2107200
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 114 | 114 | 114 | 114 | 116 | 116 | 115 | 88 | 68 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 100 | 89 | 100 | 100 | 100 | 100 | 2199360
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 240 | 240 | 240 | 239 | 238 | 238 | 239 | 237 | 318 | 401 | 402 | 404 | 378 | 378 | 379 | 379 | 379 | 329 |  | 329 | 329 | 328 | 328 | 327 | 328 | 329 | 7629000
| Jamalpur 115 MW PP (United) | 16 | [5 empty] | 12 | 24 | 48 | 75 | 75 | 84 | 108 | 115 | 115 | 110 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 95 | 1719600
| Anwara 300 MW PP (United) | [11 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 16 |  | 33 | 33 | 33 |  |  |  |  | 165600
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2340480
| Anlima Energy Ltd. | [8 empty] | 5 | 17 | 17 | 42 | 111 | 116 | 116 | 72 | 53 | 53 |  | 110 | 116 | 116 | 116 | 116 | 90 |  | 1307236
| Bhairob 54.5 MW | 34 | 16 | [9 empty] | 4 | 35 | 37 | 37 | 37 | 37 | 36 |  | 37 |  | 15 | 37 | 37 | 37 | 34 | 473040
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 11 | 17 | 24 | 22 | 29 | 28 | 24 | 18 | 10 | 3 | 0 | [8 empty] | 194053
120 | Eastern Zone Total | 7028 | 6668 | 6387 | 6344 | 6132 | 6163 | 6352 | 6339 | 6553 | 6917 | 7048 | 7212 | 7763 | 7708 | 7723 | 7602 | 7239 | 7304 |  | 8658 | 8620 | 8549 | 8399 | 8112 | 7978 | 7664 | 174930422
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 66 | 32 | 32 | 32 | 32 | 66 | 66 | 66 | 66 | 83 | 83 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1879680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [11 empty] | 2 | 3 | 3 | 3 | 5 | 5 | 6 |  |  |  | 11 | 4 | 4 | 3 | 3 | 58560
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [6 empty] | 17 | 17 | 17 | 17 | 70 | 70 | 75 | 75 | 75 | 53 | 53 |  | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 1152480
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 37 | 37 | 38 | 38 | 38 | 38 | 37 | 38 | 38 | 38 | 38 | 38 | 36 | 38 | 38 | 38 | 38 | 73 |  | 67 | 71 | 71 | 72 | 74 | 74 | 75 | 1159200
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 64 | 80 | 64 | 64 | 64 | 48 | 16 | 351552
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 75 | 76 | 75 | 77 | 77 | 77 | 77 | 77 | 77 |  | 77 | 76 | 77 | 92 | 95 | 94 | 95 | 1919856
| Bhola 225 MW CCPP | 50 | 50 | 50 | 51 | 60 | 60 | 50 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 60 | 54 | 57 | 60 |  | 50 | 50 | [5 empty] | 1118000
140 | Bhola 33 MW PP (Venture) | 27 | 28 | 28 | 27 | 26 | 24 | 23 | 20 | 18 | 18 | 19 | 19 | 20 | 20 | 21 | 21 | 21 | 28 |  | 29 | 29 | 29 | 29 | 29 | 25 | 24 | 563240
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 43 | 100 | 100 | 100 | 100 | 70 | 30 | 475200
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [8 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 353250
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 4 |  | 11 | 3 | [5 empty] | 13056
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 721 | 721 | 721 | 721 | 720 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 721 | 740 | 794 | 824 | 833 |  | 839 | 839 | 839 | 839 | 840 | 839 | 839 | 18372364
147 | Bheramara 410 MW CCPP | 355 | 360 | 355 | 355 | 355 | 360 | 355 | 405 | 365 | 385 | 400 | 400 | 395 | 360 | 385 | 380 | 355 | 340 |  | 330 | 320 | 310 | 280 | 240 | 220 | 205 | 8524224
148 | Payra 1320 MW | 540 | 540 | 520 | 500 | 470 | 440 | 440 | 430 | 430 | 430 | 430 | 440 | 460 | 460 | 460 | 480 | 470 | 460 |  | 490 | 570 | 580 | 600 | 570 | 550 | 550 | 12724100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 149 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3673500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | [5 empty] | 54726
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 148 | 149 | 148 | 150 | 149 | 151 | 151 | 151 | 149 | 148 | 145 | 143 | 142 | 143 | 140 | 140 | 140 | 100 |  | 120 | 144 | 144 | 144 | 137 | 132 | 130 | 3523800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 220 | 220 | 220 | 184 | 161 | 162 | 163 | 169 | 200 | 193 | 187 | 186 | 169 | 157 | 168 | 182 | 192 | 168 |  | 174 | 193 | 190 | 190 | 185 | 185 | 171 | 4648818
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 185 | 186 | 172 | 160 | 161 | 162 | 163 | 198 | 186 | 190 | 196 | 187 | 175 | 187 | 191 | 190 | 140 |  | 170 | 190 | 195 | 195 | 186 | 178 | 170 | 4585136
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 379 | 382 | 390 | 345 | 360 | 360 | 311 | 359 | 420 | 416 | 414 | 379 | 337 | 327 | 386 | 405 | 398 | 375 |  | 323 | 330 | 352 | 383 | 407 | 415 | 411 | 9066181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 20 | 16 | [5 empty] | 22063
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 19 | 18 | 18 | 19 | 20 | 21 |  | 21 | 21 | 22 | 22 | 21 | 21 | 21 | 476880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218430
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 43 | [6 empty] | 55216
167 | Katakhali 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 |  |  |  |  | 67551
168 | Santahar 50 MW Peaking PP | [17 empty] | 10 |  | 34 | 34 | 34 | 34 | 33 |  |  | 145171
169 | Natore 52 MW PP (Rajlanka) | 34 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 52 | 52 | 52 | 52 | 52 | 25 | 8 | 504960
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 100 | 101 | 101 | 59 | 59 |  |  | 337112
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 40 | [6 empty] | 35002
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 50 | 35 | 35 | 35 | 87 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 110 | 113 | 113 | 113 | 2179872
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2351040
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | [18 empty] | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 10000
176 | Rangpur 113 MW PP (Confidence) | 113 | 70 | 8 |  |  |  | 20 | 70 | 103 | 113 | 113 | 112 | 110 | 109 | 108 | 101 | 71 | 71 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1982400
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 6 | 6 | 4 | 3 | 2 | 0 | [8 empty] | 42791
178
178