## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-01 | Thursday
|  | Date (day): | 2021-04-01 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15264.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16287 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-03-31 | 2021-04-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170 |  | 20 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 100 | 100 | 100 |  | 9 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 297 | 283 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 181 | 135 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 8 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 255 | 270 | 270 |  | 170
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 27 | 25 | 0 | 0 |  |  | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 60 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 185 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 22 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 218 | 219 | 222 | 222 |  | 113 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 20 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 147 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 20 | 35 | 35 | 35
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 53 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 280 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 85 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 78 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 53 | 144 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 30 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2425 | 3417 | 4287 | 4732 | 108 | 1007
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 18 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 45 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 103 | 107 | 107 | 123 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 85 | Machine problem
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  |  | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 40 | 42
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 91 | 92 | 92 |  |  | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 115 | 195 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 812 | 1162 | 1496 | 1523 | 483 | 213
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 100 | 100 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 |  |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 175 | 209 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 280 | 340 | 340
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 285 | 330 | 330
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 10 | 10 | 10 | 45 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | under maint.
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 135 | 140 |  | 23 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 197 | 100 | 150 | 200 |  | 100 | Engine problem
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 164 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20 |  | 5 | Engine problem
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 92 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 113 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 0 | 0 | 40 | 40
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1485 | 1792 | 2080 | 2302 | 380 | 128
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 137 | 200 | 200
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 24 | 16 | 56 |  | 39 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 163 | 200 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 379 | 517 | 626.6 | 615 | 0 | 39
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 40 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 130 | 294 | 288 | 300 |  | 30
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 79 | 81 | 81
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 176 | 165 | 176 |  | 55 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 365 | 373 | 400 | 400
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 190 | 35 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1527 | 1573 | 1940 | 1963 | 0 | 386
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 803 | 837 | 852 | 852
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 83 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 25 | 25 |  | 29 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 250 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 94 | 90 | 95 |  | 10 | Engine problem
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1267 | 1401 | 1716 | 2007 | 0 | 104
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 28 | 25 | 25
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 67 | 70 | 70 |  | 124 | GT-2 under maint
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 75 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 590 | 622 | 622
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 38 | 67 | 75 | 75 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 610 | 875 | 1147 | 1147 | 0 | 124
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 40 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 50 | 50
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 126 | 93 | 140 | 140 |  | 70 | ST under maint.
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 169 | 162 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 185 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 415 | 400 | 400 |  |  | FGMO
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 28 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 83 | 94 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1120 | 1403 | 1691 | 1725 | 171 | 70
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 98 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 253 | 263 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 9878 | 12403 | 15264.6 | 16287 | 1266 | 2271
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9459.083 | 11877 | 14617.2421 | 15596.2831
A. |  | 2021-03-31 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 12403 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 9059 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12403 | MW
3 | Day peak Generation : |  |  | 9878 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11877 | MW
4 | Evening peak Generation : |  |  | 12403 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 253.7071 | MKWHr | By Solar | 0.57732 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 146.7357 | MKWHr |  | By Oil: | 65.0385 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.6888 | MKWHr |  | By Hydro: | 2.0176 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1266 | MW | Dhaka | 4450 | 4450 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2271 | MW | Chittagong | 1306 | 1306 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3537 | MW | Khulna | 1523 | 1523 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1211.2 | MMCFD |  |  | Rajshahi | 1277 | 1277 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 160035392.094 | ii) Oil : | Taka | 460986449.53 | Comilla | 1115 | 1115 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 77038576 | Total | Taka | 698060417.624 | Mymensingh | 903 | 903 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.6065 | MKWHr. | Sylhet | 288 | 288 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -20 | MW (E to W) at | 19:30 | hrs | Barisal | 335 | 335 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -48 | MW at | 21:00 | hrs | Rangpur | 680 | 680 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.3° C |  |  | Total | 11877 | 11877 |  | 0
B. |  | 2021-04-01 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 39.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16287 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 3287 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 265.9189 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9266 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.6982 | MKWHr. | ii) HVDC Flow at Peak Time |  | 837 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.951 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 0 |  | (b) Today: | 85.06 |  | (c) Rule Curve: |  | 88
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-03-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 350 | 317 |  | 0 | 0 | 260 | 0 | 64 | 55 | 221 | 0 | 90 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 50 | 35 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 80 | 0 | 120 | 0 |  | 24 | 0 | 68 | 80 | 0 | 19 | 20 | 42 | 80 | 0 | 70 | 290 | 265 | 214 | 8 | 120 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 144 | 195 | 48 | 17 | 0 | 43 | 0 | 25 | 0 | 163 | 130 | 0 | 81 | 0 | 150 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 194 | 0 | 331 | 0 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 55 | 100 | 350 | 104 | 0 | 0 | 116 | 0 | 0 | 0 |  | 840 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 61 | 31 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 178 | 0 | 92 | 0 | 172 | 0 | 364 | 94 | 0 | 70 | 0 | 39 | 0 | 0 | 70 | 580 | 0 | 0 | 17 |  | 6894 | 3409 | 10303 | 4711 | 840 | 1539 | 2201 | 730 | 70 | 68 | 144 | 0 | 0 | 0
2:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 348 | 321 |  | 0 | 0 | 265 | 0 | 48 | 15 | 220 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 25 | 28 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 62 | 0 | 120 | 0 |  | 24 | 0 | 68 | 80 | 0 | 0 | 20 | 42 | 80 | 0 | 70 | 295 | 265 | 214 | 8 | 127 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 136 | 195 | 48 | 17 | 0 | 43 | 0 | 25 | 0 | 163 | 130 | 0 | 81 | 0 | 150 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 57 | 0 | 0 | 116 | 0 | 0 | 0 |  | 843 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 24 | 62 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 178 | 0 | 94 | 0 | 175 | 0 | 361 | 94 | 0 | 70 | 0 | 6 | 0 | 0 | 70 | 580 | 0 | 0 | 17 |  | 6611 | 3374 | 9985 | 4696 | 843 | 1530 | 1912 | 730 | 70 | 68 | 136 | 0 | 0 | 0
3:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 348 | 321 |  | 0 | 0 | 235 | 0 | 15 | 15 | 220 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 65 | 0 | 120 | 0 |  | 24 | 0 | 68 | 80 | 0 | 0 | 20 | 42 | 80 | 0 | 70 | 280 | 265 | 213 | 8 | 121 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 130 | 194 | 24 | 17 | 0 | 43 | 0 | 25 | 0 | 163 | 129 | 0 | 81 | 0 | 150 | 18 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 149 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 0 | 0 | 116 | 0 | 0 | 0 |  | 838 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 178 | 0 | 94 | 0 | 174 | 0 | 355 | 94 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 560 | 0 | 0 | 0 |  | 6460 | 3248 | 9708 | 4714 | 838 | 1529 | 1649 | 710 | 70 | 68 | 130 | 0 | 0 | 0
4:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 349 | 327 |  | 0 | 0 | 240 | 0 | 15 | 15 | 220 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 20 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 61 | 0 | 120 | 0 |  | 24 | 0 | 68 | 80 | 0 | 0 | 20 | 42 | 80 | 0 | 70 | 265 | 265 | 212 | 8 | 127 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 194 | 16 | 17 | 0 | 43 | 0 | 25 | 0 | 163 | 129 | 0 | 81 | 0 | 148 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 0 | 0 | 53 | 0 | 0 | 0 |  | 837 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 186 | 0 | 94 | 0 | 175 | 0 | 334 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 6336 | 3037 | 9373 | 4694 | 837 | 1507 | 1393 | 680 | 70 | 68 | 124 | 0 | 0 | 0
5:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 349 | 328 |  | 0 | 0 | 240 | 0 | 15 | 15 | 220 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 60 | 0 | 120 | 0 |  | 22 | 0 | 68 | 80 | 0 | 0 | 20 | 42 | 80 | 0 | 70 | 260 | 265 | 212 | 8 | 128 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 122 | 194 | 16 | 17 | 0 | 43 | 0 | 25 | 0 | 130 | 130 | 0 | 81 | 0 | 148 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 0 | 0 | 17 | 0 | 0 | 0 |  | 837 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 204 | 0 | 94 | 0 | 175 | 0 | 361 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 6271 | 3028 | 9299 | 4707 | 837 | 1507 | 1308 | 680 | 70 | 68 | 122 | 0 | 0 | 0
6:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 348 | 302 |  | 0 | 0 | 235 | 0 | 15 | 15 | 220 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 60 | 0 | 120 | 0 |  | 22 | 0 | 68 | 50 | 0 | 0 | 20 | 42 | 80 | 0 | 70 | 260 | 265 | 181 | 8 | 127 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 213 | 16 | 17 | 0 | 43 | 0 | 25 | 0 | 130 | 130 | 0 | 81 | 0 | 148 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 0 | 0 | 17 | 0 | 0 | 0 |  | 718 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 204 | 0 | 94 | 0 | 174 | 0 | 361 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 6159 | 2900 | 9059 | 4663 | 718 | 1480 | 1264 | 680 | 70 | 68 | 116 | 0 | 0 | 0
7:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 363 | 265 |  | 0 | 0 | 265 | 0 | 15 | 15 | 220 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 61 | 0 | 120 | 0 |  | 24 | 0 | 68 | 50 | 0 | 0 | 20 | 38 | 80 | 0 | 70 | 275 | 280 | 195 | 8 | 127 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 102 | 194 | 16 | 17 | 0 | 43 | 0 | 25 | 0 | 130 | 130 | 0 | 81 | 0 | 148 | 18 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 130 | 0 | 100 | 200 | 0 | 328 | 0 | 0 | 0 | 1 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 1 | 0 | 17 | 0 | 0 | 1 |  | 718 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 95 | 0 | 204 | 0 | 94 | 0 | 176 | 0 | 364 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 |  | 6155 | 2910 | 9065 | 4712 | 718 | 1456 | 1285 | 650 | 70 | 68 | 102 | 4 | 0 | 0
8:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 357 | 231 |  | 0 | 0 | 270 | 0 | 15 | 15 | 220 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 60 | 0 | 120 | 0 |  | 24 | 0 | 68 | 80 | 0 | 0 | 20 | 7 | 100 | 0 | 80 | 275 | 265 | 180 | 8 | 125 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 88 | 173 | 16 | 17 | 0 | 43 | 0 | 25 | 0 | 130 | 130 | 0 | 81 | 0 | 148 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 130 | 6 | 100 | 200 | 0 | 331 | 0 | 0 | 0 | 2 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 34 | 3 | 0 | 17 | 0 | 0 | 4 |  | 717 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 56 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 192 | 0 | 94 | 0 | 173 | 0 | 322 | 53 | 0 | 24 | 0 | 34 | 0 | 1 | 35 | 470 | 0 | 0 | 0 |  | 6214 | 2984 | 9198 | 4695 | 717 | 1337 | 1587 | 620 | 70 | 68 | 88 | 16 | 0 | 0
9:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 342 | 221 |  | 0 | 0 | 255 | 0 | 15 | 15 | 220 | 0 | 73 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 60 | 0 | 120 | 0 |  | 24 | 0 | 34 | 80 | 0 | 11 | 20 | 3 | 100 | 0 | 100 | 275 | 265 | 181 | 8 | 126 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 15 | 72 | 141 | 16 | 17 | 1 | 44 | 0 | 25 | 0 | 130 | 132 | 0 | 81 | 0 | 149 | 18 | 0 | 0 | 290 | 16 | 0 | 0 | 5 | 0 | 0 | 130 | 0 | 140 | 7 | 100 | 200 | 0 | 331 | 0 | 33 | 0 | 3 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 35 | 6 | 0 | 72 | 0 | 0 | 14 |  | 837 | 0 | 380 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 24 | 62 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 157 | 0 | 94 | 0 | 195 | 0 | 330 | 53 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 430 | 38 | 0 | 0 |  | 6285 | 3080 | 9365 | 4664 | 837 | 1359 | 1700 | 580 | 70 | 50 | 72 | 33 | 0 | 0
10:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 314 | 215 |  | 0 | 0 | 250 | 0 | 20 | 55 | 218 | 0 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 24 | 20 | 3 | 100 | 0 | 100 | 275 | 265 | 182 | 8 | 127 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 58 | 105 | 16 | 17 | 2 | 44 | 0 | 47 | 0 | 163 | 130 | 0 | 81 | 0 | 149 | 18 | 0 | 7 | 305 | 16 | 0 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 14 | 100 | 200 | 0 | 367 | 0 | 70 | 0 | 2 | 16 | 54 | 0 | 0 | 55 | 100 | 400 | 37 | 35 | 1 | 92 | 0 | 0 | 25 |  | 735 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 164 | 0 | 92 | 0 | 193 | 0 | 360 | 53 | 0 | 56 | 0 | 70 | 0 | 2 | 70 | 400 | 38 | 0 | 0 |  | 6513 | 3062 | 9575 | 4640 | 735 | 1479 | 1963 | 550 | 70 | 0 | 58 | 80 | 0 | 0
11:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 307 | 208 |  | 0 | 0 | 235 | 0 | 40 | 55 | 216 | 0 | 118 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 40 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 70 | 0 | 24 | 0 | 3 | 100 | 0 | 100 | 290 | 275 | 191 | 8 | 140 | 26 | 35 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 33 | 15 | 80 | 105 | 16 | 17 | 2 | 42 | 0 | 48 | 0 | 130 | 130 | 0 | 81 | 0 | 149 | 18 | 0 | 7 | 290 | 16 | 0 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 17 | 100 | 200 | 0 | 374 | 0 | 70 | 0 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 400 | 69 | 46 | 17 | 116 | 0 | 0 | 27 |  | 765 | 0 | 360 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 159 | 0 | 92 | 0 | 187 | 0 | 366 | 53 | 0 | 70 | 0 | 70 | 0 | 5 | 70 | 400 | 37 | 0 | 0 |  | 6640 | 3086 | 9726 | 4687 | 765 | 1429 | 2044 | 550 | 70 | 0 | 80 | 101 | 0 | 0
12:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 297 | 181 |  | 0 | 0 | 230 | 8 | 27 | 55 | 218 | 0 | 150 | 22 | 20 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 20 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 0 | 0 | 120 | 0 |  | 21 | 0 | 0 | 70 | 0 | 26 | 20 | 2 | 80 | 0 | 80 | 315 | 265 | 175 | 8 | 140 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 92 | 105 | 16 | 17 | 1 | 42 | 0 | 48 | 0 | 163 | 130 | 0 | 78 | 0 | 150 | 18 | 0 | 7 | 320 | 16 | 0 | 0 | 47 | 0 | 0 | 163 | 0 | 149 | 0 | 100 | 197 | 0 | 365 | 8 | 70 | 0 | 2 | 115 | 54 | 0 | 0 | 26 | 100 | 190 | 78 | 48 | 53 | 116 | 0 | 0 | 30 |  | 803 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 126 | 0 | 169 | 0 | 92 | 0 | 190 | 0 | 400 | 53 | 0 | 83 | 0 | 98 | 0 | 5 | 95 | 400 | 38 | 0 | 0 |  | 6628 | 3250 | 9878 | 4471 | 803 | 1486 | 2320 | 550 | 70 | 0 | 92 | 86 | 0 | 0
13:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 291 | 162 |  | 0 | 0 | 275 | 61 | 55 | 55 | 215 | 0 | 145 | 94 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 25 | 33 | 33 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 38 | 20 | 2 | 80 | 0 | 80 | 275 | 265 | 171 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 12 | 94 | 105 | 16 | 17 | 1 | 42 | 0 | 50 | 0 | 163 | 193 | 0 | 77 | 0 | 150 | 18 | 0 | 7 | 290 | 16 | 0 | 0 | 106 | 0 | 0 | 191 | 0 | 149 | 15 | 100 | 150 | 0 | 367 | 65 | 95 | 0 | 4 | 115 | 54 | 0 | 0 | 26 | 100 | 190 | 104 | 38 | 108 | 116 | 0 | 0 | 27 |  | 837 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 113 | 0 | 155 | 0 | 92 | 0 | 170 | 0 | 355 | 94 | 0 | 94 | 0 | 108 | 0 | 5 | 113 | 410 | 51 | 0 | 0 |  | 7050 | 3291 | 10341 | 4409 | 837 | 1412 | 2867 | 560 | 70 | 2 | 94 | 90 | 10341 | 0
14:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 292 | 162 |  | 0 | 0 | 265 | 66 | 48 | 55 | 213 | 0 | 120 | 100 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 25 | 33 | 32 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 43 | 20 | 2 | 80 | 0 | 80 | 270 | 270 | 162 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 12 | 112 | 103 | 16 | 20 | 2 | 42 | 0 | 53 | 0 | 110 | 297 | 0 | 77 | 0 | 150 | 18 | 0 | 7 | 290 | 16 | 0 | 0 | 147 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 150 | 0 | 313 | 45 | 70 | 0 | 3 | 70 | 54 | 0 | 0 | 26 | 100 | 218 | 104 | 39 | 108 | 116 | 0 | 0 | 25 |  | 837 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 3 | 52 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 154 | 0 | 92 | 0 | 168 | 0 | 345 | 93 | 0 | 94 | 0 | 107 | 0 | 4 | 113 | 430 | 51 | 0 | 0 |  | 7019 | 3360 | 10379 | 4442 | 837 | 1351 | 2863 | 580 | 70 | 51 | 112 | 73 | 0 | 85.38
15:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 288 | 156 |  | 0 | 0 | 260 | 66 | 47 | 55 | 214 | 0 | 185 | 100 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 25 | 33 | 32 | 51 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 42 | 20 | 2 | 80 | 0 | 80 | 270 | 280 | 156 | 8 | 141 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 15 | 114 | 125 | 16 | 20 | 1 | 39 | 0 | 50 | 0 | 163 | 295 | 0 | 76 | 0 | 150 | 18 | 0 | 7 | 315 | 16 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 149 | 6 | 100 | 151 | 0 | 387 | 52 | 70 | 0 | 3 | 70 | 54 | 0 | 0 | 38 | 100 | 0 | 104 | 31 | 108 | 116 | 0 | 0 | 18 |  | 837 | 0 | 315 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 66 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 125 | 0 | 164 | 0 | 90 | 0 | 172 | 0 | 384 | 93 | 0 | 94 | 0 | 110 | 0 | 2 | 113 | 450 | 52 | 0 | 0 |  | 7061 | 3451 | 10512 | 4417 | 837 | 1449 | 2883 | 600 | 70 | 81 | 114 | 61 | 0 | 85.36
16:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 282 | 145 |  | 0 | 0 | 265 | 66 | 47 | 55 | 212 | 0 | 185 | 100 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 25 | 33 | 32 | 51 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 0 | 39 | 20 | 2 | 80 | 0 | 80 | 270 | 280 | 198 | 8 | 141 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 116 | 122 | 16 | 20 | 1 | 39 | 0 | 50 | 0 | 163 | 294 | 0 | 77 | 0 | 177 | 18 | 0 | 7 | 310 | 16 | 0 | 0 | 150 | 0 | 0 | 181 | 0 | 149 | 4 | 100 | 180 | 0 | 410 | 77 | 90 | 0 | 1 | 106 | 54 | 0 | 0 | 65 | 100 | 0 | 104 | 18 | 141 | 116 | 0 | 0 | 11 |  | 837 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 66 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 119 | 0 | 170 | 0 | 92 | 0 | 181 | 0 | 393 | 92 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 490 | 51 | 0 | 0 |  | 7293 | 3499 | 10792 | 4494 | 837 | 1444 | 3058 | 640 | 70 | 97 | 116 | 36 | 0 | 85.34
17:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 286 | 145 |  | 0 | 0 | 260 | 97 | 40 | 55 | 220 | 0 | 175 | 100 | 32 | 48 | 20 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 26 | 33 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 90 | 18 | 42 | 0 | 3 | 80 | 0 | 80 | 270 | 280 | 210 | 8 | 134 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 128 | 143 | 16 | 20 | 0 | 41 | 0 | 50 | 0 | 163 | 296 | 0 | 77 | 0 | 176 | 18 | 0 | 7 | 300 | 16 | 0 | 0 | 150 | 0 | 0 | 181 | 0 | 149 | 1 | 100 | 180 | 0 | 366 | 113 | 105 | 0 | 1 | 140 | 54 | 0 | 0 | 65 | 100 | 15 | 104 | 6 | 144 | 116 | 0 | 0 | 4 |  | 837 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 16 | 51 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 101 | 0 | 158 | 0 | 95 | 0 | 176 | 0 | 394 | 92 | 0 | 94 | 0 | 110 | 0 | 1 | 113 | 470 | 64 | 0 | 0 |  | 7427 | 3429 | 10856 | 4400 | 837 | 1449 | 3233 | 620 | 70 | 106 | 128 | 13 | 0 | 85.32
18:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 291 | 145 |  | 0 | 0 | 265 | 100 | 30 | 55 | 219 | 0 | 73 | 70 | 50 | 48 | 24 | 0 | 0 | 0 | 54 | 55 | 30 | 0 | 25 | 26 | 33 | 16 | 51 | 0 | 32 | 70 | 0 | 0 | 7 | 0 | 0 | 120 | 0 |  | 24 | 0 | 44 | 60 | 32 | 45 | 20 | 2 | 80 | 0 | 80 | 270 | 295 | 194 | 8 | 143 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 142 | 142 | 24 | 20 | 0 | 40 | 0 | 50 | 0 | 110 | 297 | 0 | 78 | 0 | 176 | 18 | 0 | 7 | 290 | 16 | 0 | 0 | 167 | 0 | 0 | 181 | 0 | 131 | 0 | 70 | 100 | 0 | 394 | 75 | 105 | 0 | 0 | 108 | 54 | 0 | 0 | 65 | 100 | 71 | 104 | 1 | 108 | 116 | 0 | 0 | 0 |  | 837 | 0 | 270 | 0 | 83 | 0 | 0 | 0 | 4 | 11 | 16 | 66 | 20 | 16 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 25 | 16 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 93 | 0 | 158 | 0 | 96 | 0 | 176 | 0 | 372 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 440 | 66 | 0 | 0 |  | 7220 | 3424 | 10644 | 4401 | 837 | 1371 | 3012 | 590 | 102 | 188 | 142 | 1 | 0 | 85.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 288 | 141 |  | 0 | 0 | 260 | 100 | 30 | 55 | 217 | 0 | 185 | 90 | 102 | 147 | 57 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 33 | 70 | 0 | 0 | 18 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 82 | 45 | 20 | 10 | 80 | 0 | 80 | 300 | 305 | 209 | 8 | 141 | 26 | 10 | 0 | 0 | 0 | 0 | 30 | 22 | 11 | 33 | 18 | 168 | 140 | 24 | 20 | 0 | 40 | 0 | 50 | 0 | 163 | 294 | 0 | 79 | 0 | 176 | 18 | 0 | 9 | 320 | 16 | 0 | 0 | 264 | 0 | 0 | 190 | 0 | 143 | 0 | 100 | 94 | 0 | 400 | 115 | 105 | 0 | 0 | 158 | 54 | 0 | 70 | 113 | 100 | 71 | 104 | 0 | 119 | 116 | 0 | 28 | 0 |  | 837 | 0 | 260 | 0 | 83 | 0 | 0 | 0 | 4 | 11 | 33 | 65 | 26 | 23 | 0 | 0 | 0 | 46 | 30 | 100 | 0 | 0 | 37 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 94 | 0 | 172 | 0 | 97 | 48 | 180 | 0 | 405 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 520 | 67 | 0 | 0 |  | 8288 | 3821 | 12109 | 4593 | 837 | 1505 | 3738 | 670 | 103 | 495 | 168 | 0 | 0 | 85.24
19:30 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 283 | 135 |  | 0 | 0 | 255 | 100 | 25 | 55 | 219 | 0 | 185 | 100 | 102 | 147 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 33 | 70 | 0 | 0 | 18 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 91 | 45 | 20 | 15 | 100 | 0 | 80 | 280 | 285 | 209 | 8 | 140 | 23 | 10 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 164 | 137 | 24 | 17 | 0 | 40 | 0 | 50 | 0 | 163 | 294 | 0 | 79 | 0 | 176 | 18 | 0 | 9 | 320 | 16 | 0 | 0 | 280 | 0 | 0 | 200 | 85 | 149 | 0 | 100 | 100 | 0 | 373 | 115 | 105 | 0 | 0 | 195 | 54 | 0 | 92 | 113 | 100 | 35 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 837 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 33 | 67 | 28 | 48 | 0 | 0 | 0 | 50 | 34 | 100 | 0 | 0 | 39 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 93 | 0 | 162 | 0 | 75 | 100 | 185 | 0 | 415 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 590 | 67 | 0 | 0 |  | 8461 | 3942 | 12403 | 4493 | 837 | 1495 | 4028 | 740 | 103 | 543 | 164 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 281 | 122 |  | 0 | 0 | 260 | 100 | 15 | 55 | 223 | 0 | 175 | 100 | 102 | 147 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 34 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 91 | 45 | 20 | 20 | 100 | 0 | 80 | 260 | 265 | 217 | 8 | 135 | 23 | 10 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 136 | 50 | 17 | 0 | 43 | 0 | 50 | 0 | 163 | 296 | 0 | 80 | 0 | 176 | 18 | 0 | 0 | 305 | 16 | 0 | 0 | 300 | 0 | 0 | 200 | 101 | 149 | 0 | 100 | 122 | 0 | 304 | 115 | 105 | 0 | 0 | 195 | 54 | 0 | 100 | 113 | 100 | 0 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 836 | 0 | 240 | 0 | 70 | 0 | 0 | 0 | 6 | 0 | 33 | 63 | 29 | 80 | 0 | 0 | 0 | 50 | 34 | 100 | 0 | 0 | 39 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 88 | 0 | 155 | 0 | 74 | 100 | 186 | 0 | 397 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 590 | 67 | 0 | 0 |  | 8384 | 3919 | 12303 | 4323 | 836 | 1447 | 4141 | 740 | 104 | 544 | 168 | 0 | 0 | 85.26
21:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 277 | 117 |  | 0 | 60 | 265 | 100 | 15 | 55 | 224 | 0 | 175 | 100 | 102 | 147 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 34 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 83 | 43 | 20 | 29 | 100 | 0 | 80 | 260 | 265 | 214 | 8 | 147 | 23 | 10 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 162 | 127 | 56 | 17 | 0 | 44 | 0 | 50 | 0 | 163 | 295 | 0 | 80 | 0 | 176 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 150 | 0 | 306 | 115 | 105 | 0 | 0 | 195 | 54 | 0 | 100 | 113 | 100 | 58 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 836 | 0 | 230 | 0 | 79 | 0 | 0 | 0 | 18 | 0 | 33 | 54 | 31 | 80 | 0 | 0 | 0 | 50 | 34 | 100 | 0 | 0 | 41 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 144 | 0 | 74 | 100 | 181 | 0 | 380 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 68 | 0 | 0 |  | 8400 | 3890 | 12290 | 4332 | 836 | 1472 | 4076 | 750 | 104 | 558 | 162 | 0 | 0 | 85.24
22:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 301 | 126 |  | 0 | 90 | 250 | 100 | 10 | 55 | 221 | 0 | 175 | 100 | 102 | 98 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 30 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 70 | 50 | 39 | 20 | 35 | 100 | 0 | 80 | 260 | 265 | 209 | 8 | 148 | 26 | 10 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 127 | 57 | 17 | 0 | 44 | 0 | 50 | 0 | 163 | 298 | 0 | 79 | 0 | 176 | 18 | 0 | 9 | 270 | 16 | 0 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 150 | 0 | 350 | 115 | 105 | 0 | 0 | 250 | 54 | 0 | 64 | 113 | 100 | 69 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 837 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 18 | 0 | 33 | 42 | 33 | 80 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 144 | 0 | 73 | 100 | 175 | 0 | 366 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 52 | 0 | 0 |  | 8357 | 3772 | 12129 | 4392 | 837 | 1482 | 4023 | 750 | 100 | 383 | 162 | 0 | 0 | 85.22
23:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 321 | 131 |  | 0 | 225 | 265 | 78 | 0 | 55 | 221 | 0 | 175 | 100 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 38 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 85 | 70 | 0 | 41 | 20 | 37 | 100 | 0 | 80 | 260 | 265 | 216 | 8 | 135 | 26 | 10 | 0 | 0 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 158 | 127 | 57 | 17 | 0 | 44 | 0 | 50 | 0 | 163 | 295 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 150 | 0 | 366 | 45 | 52 | 0 | 0 | 302 | 54 | 0 | 0 | 113 | 100 | 139 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 837 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 33 | 63 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 145 | 0 | 73 | 100 | 176 | 0 | 395 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 67 | 0 | 0 |  | 7957 | 3652 | 11609 | 4507 | 837 | 1679 | 3424 | 750 | 108 | 146 | 158 | 0 | 0 | 85.2
24:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 324 | 140 |  | 0 | 225 | 265 | 55 | 0 | 0 | 220 | 0 | 180 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 30 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 79 | 70 | 0 | 46 | 20 | 38 | 100 | 0 | 80 | 260 | 265 | 219 | 8 | 140 | 26 | 10 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 154 | 128 | 57 | 16 | 0 | 44 | 0 | 50 | 0 | 163 | 295 | 0 | 81 | 0 | 163 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 150 | 0 | 366 | 8 | 17 | 0 | 0 | 256 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 35 | 116 | 0 | 0 | 0 |  | 836 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 33 | 65 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 147 | 0 | 73 | 100 | 177 | 0 | 385 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 68 | 0 | 0 |  | 7768 | 3602 | 11370 | 4807 | 836 | 1691 | 2969 | 730 | 100 | 83 | 154 | 0 | 0 | 85.18
KWH | 0 | 0 | 0 | 4126500 | 7139791 | 2277000 | 0 | 7719940 | 5058000 |  | 0 | 437000 | 6086720 | 1032000 | 716904 | 1029172 | 5374057 | 0 | 3211000 | 1247117 | 649296 | 921120 | 289452 | 0 | 0 | 0 | 1306440 | 874175 | 746273 | 159948 | 600000 | 600660 | 794700 | 745000 | 483360 | 0 | 325615 | 1692000 | 0 | 0 | 406560 | 636157 | 0 | 2907560 | 0 |  | 576480 | 0 | 1128347 | 1825680 | 360000 | 624480 | 398832 | 483360 | 2145262 | 0 | 1913438 | 6867000 | 6674000 | 4785000 | 200727 | 3211880 | 465408 | 316320 | 0 | 0 | 0 | 144840 | 253608 | 470844 | 154080 | 782300 | 428540 | 2951040 | 3514760 | 668160 | 364968 | 10700 | 993000 | 0 | 963600 | 0 | 3601800 | 4428000 | 0 | 1898880 | 0 | 3727500 | 421000 | 0 | 102240 | 7274500 | 380880 | 16048 | 0 | 2571817 | 0 | 0 | 3139200 | 133550 | 3476880 | 52380 | 2397120 | 4130400 | 0 | 8418000 | 1021200 | 1408080 | 0 | 25080 | 2070000 | 1299475 | 0 | 308940 | 1717800 | 2439360 | 5645300 | 1914240 | 281730 | 1641600 | 2289545 | 0 | 37080 | 180001 |  | 19698181 | 0 | 7868160 | 0 | 1848000 | 0 | 0 | 0 | 48000 | 22656 | 372375 | 1536000 | 552379 | 65376 | 0 | 0 | 0 | 193619 | 99730 | 636272 | 0 | 0 | 107426 | 635040 | 133708 | 484560 | 0 | 205992 | 0 | 0 | 3664800 | 0 | 0 | 2530000 | 0 | 4264045 | 0 | 2141300 | 576960 | 4513745 | 0 | 8940310 | 1748640 | 0 | 1636800 | 0 | 1668480 | 0 | 27430 | 1842336 | 13024000 | 864382 | 0 | 36600 |  | 171719797 | 81987302 | 253707099 | 111139295 | 19698181 | 35596358 | 61602771 | 16688800 | 2017615 | 3435718 | 2951040 | 577321 | 0
Fuel Cost | 0 | 0 | 0 | 6065955 | 7925168.01 | 3005640 | 0 | 7797139.4 | 5209740 |  | 0 | 476330 | 6756259.2 | 7832880 | 4939468.56 | 8706795.12 | 5589019.28 | 0 | 5555030 | 9390791.01 | 5921579.52 | 9063820.8 | 2668747.44 | 0 | 0 | 0 | 9537012 | 6757372.75 | 7358251.78 | 119961 | 450000 | 0 | 0 | 0 | 4674091.2 | 0 | 87916.05 | 456840 | 0 | 0 | 3776942.4 | 693411.13 | 0 | 4942852 | 0 |  | 0 | 0 | 10944965.9 | 17435244 | 3132000 | 4945881.6 | 502528.32 | 1435579.2 | 3174987.76 | 0 | 2812753.86 | 5081580 | 6674000 | 4402200 | 258937.83 | 3693662 | 525911.04 | 442848 | 0 | 0 | 0 | 1462884 | 2421956.4 | 597971.88 | 115560 | 1369025 | 321405 | 22132800 | 3725645.6 | 6066892.8 | 463509.36 | 170558 | 1628520 | 0 | 1715208 | 0 | 4106052 | 4605120 | 0 | 3626860.8 | 0 | 6448575 | 921990 | 0 | 208569.6 | 7347245 | 285660 | 12196.48 | 0 | 19442936.52 | 0 | 0 | 16323840 | 2232956 | 34212499.2 | 612322.2 | 19536528 | 44814840 | 0 | 7828740 | 9313344 | 13306356 | 0 | 0 | 15649200 | 11318427.25 | 0 | 3083221.2 | 14721546 | 16246137.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 113461522.56 | 0 | 8261568 | 0 | 14525280 | 0 | 0 | 0 | 503520 | 237434.88 | 3880147.5 | 1735680 | 856187.45 | 638069.76 | 0 | 0 | 0 | 1905210.96 | 1013256.8 | 5631007.2 | 0 | 0 | 1040957.94 | 6153537.6 | 1296967.6 | 930355.2 | 0 | 155935.944 | 0 | 0 | 19863216 | 0 | 0 | 2960100 | 0 | 5628539.4 | 0 | 3211950 | 9814089.6 | 5281081.65 | 0 | 8850906.9 | 18255801.6 | 0 | 15533232 | 0 | 12947404.8 | 0 | 303101.5 | 13614863.04 | 57175360 | 0 | 0 | 0 |  | 499619192.05 | 335666285.884 | 835285477.934 | 118352982.114 | 113461522.56 | 41682409.98 | 427886423.45 | 77038576 | 544756.05 | 33100026.08 | 22132800 | 1085981.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 297 | 181 |  | 0 | 0 | 230 | 8 | 27 | 55 | 218 | 0 | 150 | 22 | 20 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 20 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 70 | 0 | 0 | 17 | 0 | 0 | 120 | 0 |  | 21 | 0 | 0 | 70 | 0 | 26 | 20 | 2 | 80 | 0 | 80 | 315 | 265 | 175 | 8 | 140 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 92 | 105 | 16 | 17 | 1 | 42 | 0 | 48 | 0 | 163 | 130 | 0 | 78 | 0 | 150 | 18 | 0 | 7 | 320 | 16 | 0 | 0 | 47 | 0 | 0 | 163 | 0 | 149 | 0 | 100 | 197 | 0 | 365 | 8 | 70 | 0 | 2 | 115 | 54 | 0 | 0 | 26 | 100 | 190 | 78 | 48 | 53 | 116 | 0 | 0 | 30 |  | 803 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 126 | 0 | 169 | 0 | 92 | 0 | 190 | 0 | 400 | 53 | 0 | 83 | 0 | 98 | 0 | 5 | 95 | 400 | 38 | 0 | 0 |  | 9878 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 283 | 135 | 0 | 0 | 0 | 255 | 100 | 25 | 55 | 219 | 0 | 185 | 100 | 102 | 147 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 33 | 70 | 0 | 0 | 18 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 85 | 100 | 91 | 45 | 20 | 15 | 100 | 0 | 80 | 280 | 285 | 209 | 8 | 140 | 23 | 10 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 164 | 137 | 24 | 17 | 0 | 40 | 0 | 50 | 0 | 163 | 294 | 0 | 79 | 0 | 176 | 18 | 0 | 9 | 320 | 16 | 0 | 0 | 280 | 0 | 0 | 200 | 85 | 149 | 0 | 100 | 100 | 0 | 373 | 115 | 105 | 0 | 0 | 195 | 54 | 0 | 92 | 113 | 100 | 35 | 104 | 0 | 144 | 116 | 0 | 0 | 0 |  | 837 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 33 | 67 | 28 | 48 | 0 | 0 | 0 | 50 | 34 | 100 | 0 | 0 | 39 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 93 | 0 | 162 | 0 | 75 | 100 | 185 | 0 | 415 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 590 | 67 | 0 | 0 |  | 12403 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 270 | 100 | 0 | 55 | 222 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 92 | 50 | 22 | 42 | 100 | 0 | 100 | 340 | 330 | 225 | 8 | 140 | 26 | 10 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 200 | 56 | 22 | 0 | 44 | 0 | 51 | 0 | 163 | 300 | 0 | 81 | 0 | 176 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 350 | 104 | 0 | 144 | 116 | 0 | 40 |  |  | 852 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 140 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 95 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 75 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 225 | 270 | 100 | 0 | 55 | 222 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 92 | 50 | 22 | 40 | 100 | 0 | 100 | 340 | 330 | 225 | 8 | 135 | 26 | 10 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 200 | 16 | 22 | 1.6 | 44 | 0 | 51 | 0 | 163 | 288 | 0 | 81 | 0 | 165 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 150 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 350 | 104 | 50 | 144 | 116 | 0 | 40 | 30 |  | 852 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 25 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 140 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 75 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 311 | 126 | 0 | 0 | 225 | 265 | 0 | 0 | 15 | 222 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 24 | 33 |  | 0 | 0 | 37 | 70 | 0 | 0 | 5 | 0 | 0 | 120 | 0 | 0 | 3 | 0 | 0 | 70 | 0 | 0 | 17 | 2 | 100 | 0 | 80 | 260 | 250 | 192 | 8 | 135 | 26 | 10 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 30 | 20 | 120 | 142 | 16 | 16 | 0 | 44 | 0 | 50 | 0 | 110 | 288 | 0 | 80 | 0 | 163 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 115 | 0 | 100 | 141 | 0 | 365 | 0 | 0 | 0 | 2 | 34 | 54 | 0 | 0 | 0 | 100 | 340 | 12 | 9 | 0 | 116 | 0 | 0 | 12 | 0 | 836 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 145 | 0 | 23 | 0 | 183 | 0 | 324 | 17 | 0 | 70 | 0 | 60 | 0 | 1 | 35 | 500 | 67 | 0 | 0 | 0
199
| Minimum Generation |  | 9059 | 6:00
| Highest Generation |  | 12403 | 19:30
| Day Peak Generation |  | 9878 | 12:00
| Evening Peak Generation |  | 12403 | 19:30
| HVDC Max Flow |  | 843 | 2:00
| HVDC EvPeak Flow |  | 837 | 19:30
| Load factor L.F |  | 85.23%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-03-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9878 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9266 | MW
Evening Peak Generation : |  | 12403 | MW Hour : | 19:30 | Available Max Generation : |  | 16287 | MW
E.P. Demand (at gen end) : |  | 12403 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12403 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3287 | MW
Total Gen. (MKWH) : |  | 253.7071 | System Load Factor : | 85.23% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -48 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-01
Actual : | 85.06 | Ft.(MSL) , | Rule curve : | 88 | Ft.( MSL )
Gas Consumed : | Total = | 1211.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160035392.094
: |  | Coal : | 77038576 | Oil : | 460986449.53 | Total : | 698060417.624
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4625.691 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1577.9046 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1414.6258 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1278.5446 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1155.2308 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 932.2428 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 514.9411 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 239.8601 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 719.0222 |  |  | 0 | 0%
Total | 0 |  | 12458.0631 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shahjibazar CCPP GT-2 was synchronized at 12:17.
b) Sikalbaha 225 MW CCPP GT was shut down at 09:27 due to DP high.
c) Agargaon 132/33 kV T-2 transformer was under shut down at 10:34 for C/M.
d) Hathazari-Baraulia 132 kV Ckt-2 was under shut down from 08:52 to 16:03 for D/W.
e) Mirpur 132 kV reserve bus was under shut down from 12:50 to 18:09 for C/M.
f) Mirpur-Aminbazar 132 kV Ckt-1 was under shut down from 09:12 to 18:10 for C/M.
g) Rampura 230 kV bus-1 was under shut down from 08:24 to 18:18 for D/W.
h) Tongi 132/33 kV T-1 transformer was under shut down from 11:22 to 15:51 for C/M.
i) Kodda 132/33 kV T-3,T-4 & T-5 transformer at 11:28 from 33 kV side due to over temperature showing |  |  |  |  | About 195 MW power interruption occurred under Kodda S/S area
O/C relay and were switched on at 11:40 |  |  |  |  | from 11:28 to 11:40.
j) Daudkandi-Cumilla(N) 132 kV Ckt-1 tripped at 15:06 from both end showing Dist.ABC Z1 and was
switched on at 15:14.
k) Sherpur 132/33 kV T2 transformer was switched on at 16:19.
l) Tongi-Kabirpur 132 kV Ckt-1 tripped at 18:06 from both end showing Dist Z1,B phase at Tongi end &
dist Z2 at Kabirpur end and was switched on at 20:17.
m) Bibiyana south tripped at 14:32 due to gas buster problem and was synchronized at 16:28 again trip
at 19:39.
n) Meghnaghat 450 MW CCPP GT-2 & ST were synchronized at 20:35 & 21:54 respectively.
o) Kaptai #02 was synchronized at 14:25.
p) Bogura-Barapukuria 230 kV Ckt-1 tripped at 06:35 showing auto reclose at Bogura end & dist R phase
Z1, E/F relay at Barapukuria end and was switched on at 08:26.
q) Bogura-Barapukuria 230 kV Ckt-2 tripped at 07:04 showing dist Z1,L2,F/F relay at Bogura end & dist
relay at Barapukuria end and was switched on at 08:26(01-04-2021).
r) Above the tripping Barapukuria unit-3,Rangpur confidence are got trip and was synchronized Rangpur |  |  |  |  | About 521 MW power interruption occurred under Rangpur Zone area
confidence at 07:28. |  |  |  |  | from 07:04 to 07:19.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-03-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4126500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7139791 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2277000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 283 | 7719940 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 135 | 5058000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 437000 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1032000
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 6086720 | GT-2 Under shut down.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 25 | 716904 | Machine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1029172
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 60 | 289452 | Machine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 159948 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3211000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1247117
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 219 | 5374057 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 649296
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1306440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 921120
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 874175
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 746273 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1200660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 794700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 745000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 483360
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 2571817 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 85 | 133550 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3476880
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1408080
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1914240
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1641600 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 180001
| Dhaka area Total |  |  |  | 5972 | 3417 | 64951793
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 18 | 406560 | 33 kV Feeder Fault
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 52380
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 624480 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 103 | 2017615 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 636157 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2907560
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer O/L
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1128347 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1825680
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2397120
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 398832
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 483360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 360000 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25080
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 195 | 2070000 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299475
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2439360
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2289545
| Chattogram area Total |  |  |  | 2382 | 1162 | 21361551
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2145262 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1913438 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4785000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6867000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6674000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 465408 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 316320 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 144840
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3211880 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 4130400 | Machine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 470844
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 154080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 2951040
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 782300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 253608
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 428540 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 92 | 308940 | Machine problem
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1717800
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 0 | 37080 | Tripped at 19:28
| Cumilla Area Total |  |  |  | 2980 | 1792 | 37958507
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 137 | 3514760 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 364968
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 668160 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10700
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3139200
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1021200 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 281730
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 576480
| Mymensingh Area Total |  |  |  | 709 | 517 | 9577198
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 993000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3601800
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 294 | 4428000 | GT-2 Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 963600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 16048
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1898880
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 176 | 3727500 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 380880 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7274500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 373 | 8418000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 102240
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 35 | 5645300 | Machine problem
| Sylhet Area Total |  |  |  | 2371 | 1573 | 37870748
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 837 | 19698181
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 1848000 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 48000 | Machine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 22656 | Line over load
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 7868160 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 372375 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 576960
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 1748640 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1401 | 32182972
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 65376 | Line O/L.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 552379
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1536000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 2141300 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13024000 | Line O/L.
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 67 | 864382 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 36600 | Line O/L.
| Barisal Area Total |  |  |  | 1826 | 875 | 18220037
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 193619
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 99730 | Machine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 107426 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 93 | 2530000 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 162 | 4264045 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4513745 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 8940310 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 133708 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 484560
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 205992
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 635040
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 636272
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1636800
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1842336
| Rajshahi Area Total |  |  |  | 2183 | 1403 | 26223583
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3664800 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1668480
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27430
| Rangpur Area Total |  |  |  | 605 | 263 | 5360710
| Total |  |  |  | 21312 | 12403 | 253707099
| Eastern Grid Total |  |  |  | 14414 | 8461 | 171719797
| Western Grid Total |  |  |  | 6898 | 3942 | 81987302
| National Grid Total |  |  |  | 21312 | 12403 | 253707099
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-03-31
(a) ENTIRE EASTERN GRID : |  | 8062 | MW | (b) ENTIRE WESTERN GRID : |  | 3815 | MW
i) Dhaka area |  | 4450 | MW | i) Khulna area |  | 1523 | MW
ii) Chittagong area |  | 1306 | MW | ii) Rajshahi area |  | 1277 | MW
iii) Comilla area |  | 1115 | MW | iii) Barisal area |  | 335 | MW
iv) Mymensingh area |  | 903 | MW | iv) Rangpur area |  | 680 | MW
v) Sylhet area |  | 288 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11877 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 19:00 | Jamalpur | 144 | 19:00 | Jhenida | 118 | 22:00
Munsiganj | 136 | 22:00 | Sherpur | 130 | 19:00 | Bottail | 124 | 19:00
Sonargaon | 89 | 22:00 | Srimongal | 28 | 18:30 | G.K Project | 52 | 19:00
Shyampur | 200 | 0:00 | Shahjibazar | 86 | 21:00 | Faridpur | 200 | 22:00
Bhulta | 222 | 17:00 | Fenchuganj | 35 | 19:00 | Madaripur | 105 | 22:00
Madanganj | 65 | 18:00 | Kulawara | 29 | 19:00 | Sariatpur | 66 | 21:00
Shitalakhya | 127 | 19:00 | Sylhet | 109 | 19:00 | Gopalganj | 92 | 19:30
Rahim steel | 31 | 11:00 | Chatak | 21 | 18:00 | Bagerhat | 103 | 21;00
Matuail | 60 | 12:00 | Sunamganj | 21 | 23:00 | Mongla | 30 | 12:00
Ghorasal | 78 | 8:00 | Biani Bazar | 40 | 18:30 | Satkhira | 110 | 21:00
Narsingdi | 126 | 1:00 | Comilla (S) | 176 | 18:30 | Gallamari | 35 | 18:30
Haripur (SBU) | 124 | 24:00 | Comilla(N) | 128 | 21:00 | Magura | 54 | 22:00
Sreenagar |  |  | Chandpur | 79 | 19:00 | Norail | 42 | 19:00
Ullon | 93 | 19:30 | Feni | 121 | 19:00 | Chuadanga | 84 | 1:00
Hasnabad | 110 | 22:00 | Chowmuhani | 172 | 21:00 | Borguna | 16 | 1:00
Magbazar | 104 | 15:00 | Ashuganj | 54 | 1:00 | Barisal(N) | 43 | 19:00
Maniknagar | 94 | 13:00 | Daudkandi | 152 | 21:00 | Barisal (S) | 108 | 19:00
Bangabhaban | 26 | 11:00 | B.Baria | 150 | 19:00 | Patuakhali | 104 | 22:00
Narinda | 94 | 15:00 | Ramganj | 86 | 19:00 | Bhandaria | 50 | 21:00
Dhanmondi | 190 | 12:00 | Chaddagram | 40 | 19:30 | Borhan Uddin | 41 | 23:00
Lalbag | 91 | 17:00 | PHP | 10 | 4:00 | Ishurdi | 63 | 19:00
Madartek | 76 | 22:00 | Kochua | 64 | 21:00 | Ruppur Paromanobik | 3 | 13:00
Dhaka University | 44 | 12:00 | Madunaghat | 73 | 19:00 | Natore | 132 | 21:00
Aftabnagar | 10 | 13:00 | Hathazari | 94 | 22:00 | Bogra | 159 | 20:00
Fatullah | 62 | 10:00 | Khulshi | 207 | 16:00 | Noagaon | 105 | 21:00
Nawabganj | 52 | 21:00 | Halishahar | 136 | 14:00 | Rajshahi | 145 | 21:00
Mirpur | 119 | 18:30 | Baraulia | 145 | 12:00 | Rajshahi New | 19 | 21:00
Kalyanpur | 99 | 18:30 | Sikalbaha | 25 | 21:00 | C.Nawabganj | 76 | 19:30
Gulshan | 150 | 13:00 | Dohazari | 102 | 19:30 | Amnura | 56 | 19:00
Uttara | 94 | 13:00 | Cox'sbazar | 88 | 19:30 | Pabna | 85 | 19:00
Uttara New | 32 | 15:00 | Chandraghona | 30 | 19:00 | Shahjadpur | 118 | 20:00
Kamrangirchar | 90 | 12:00 | Kaptai | 4 | 0.79167 | Serajganj | 118 | 19:30
Savar | 196 | 16:00 | A. Khaer Stl. | 9 | 18:30 | Niyamatpur | 84 | 19:30
Bhasantec | 174 | 13:00 | Bakulia | 113 | 19:30 | Joypurhat | 50 | 21:00
Agargaon | 75 | 17:00 | Julda | 21 | 18:30 | Sherpur(Bogura) | 50 | 19:00
Satmosjid | 103 | 13:00 | TK chemical | 27.1 | 20:00 | Mohastangor | 54 | 20:00
Tongi | 112 | 18:00 | Modern Steel | 0 | #N/A | Bangura | 21 | 19:00
Kabirpur | 255 | 21:00 | Shahmirpur | 28.5 | 16:00 | Rangpur | 111 | 20:00
Basundhara | 157 | 18:30 | Khagrachhari | 24 | 13:00 | Lalmonirhat | 37 | 20:00
Manikganj | 76 | 22:00 | Matarbari | 30 | 18:00 | Saidpur | 92 | 9:00
Joydevpur | 160 | 21:00 | Baroiar Hat | 34 | 21:00 | Purbasadipur | 87 | 19:00
New Tongi | 112 | 12:00 | Rangamati | 12 | 19:00 | Thakurgaon | 67 | 19:30
Kodda | 265 | 21:00 | Abul Khair 230 | 13 | 10:00 | Palashbari | 98 | 19:00
Dhamrai | 116 | 20:00 | BSRM | 145 | 18:00 | Barapukuria | 48 | 18:30
Rajendrapur | 84 | 20:00 | GPH Ispat | 90 | 21:00 | Panchagar | 47 | 19:30
Valuka | 120 | 20:00 | Goalpara | 33 | 23:00 | Joldhaka | 48 | 18:30
Tangail | 233 | 21:00 | Central s/s | 96 | 19:00 | Kurigram | 51 | 20:00
Mymensing | 200 | 20:00 | Noapara | 59 | 0.875 | Mithapukur | 21 | 18:00
Kishorganj | 94 | 15:00 | Jessore | 131 | 19:00
Netrokona | 94 | 20:00 | Benapol | 68 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-03-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 1:00 | 398 | 17:00 | Kaliakoir | 391 | 0.16667 | 377 | 0.45833
| Bheramara | 406 | 22:00 | 395 | 20:00 | Bhulta | 381 | 0.91667 | 368 | 0.45833
| Ashuganj(N) | 388 | 21:00 | 375 | 16:00 | Gopalganj | 404 | 0.625 | 384 | 0.95833
| Payra | 406 | 22:00 | 396 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 230 | 12:00 | 220 | 7:00
| Ishurdi | 235 | 3:00 | 225 | 19:30 | Megnaghat | 230 | 20:00 | 224 | 9:00
| Ashuganj | 236 | 19:30 | 230 | 15:00 | Fenchuganj | 242 | 1:00 | 237 | 11:00
| Serajganj | 232 | 1:00 | 228 | 7:00 | Siddhirganj | 228 | 18:00 | 220 | 11:00
| Baghabari | 233 | 17:00 | 227 | 19:30 | Maniknagar | 229 | 18:00 | 218 | 11:00
| Barapukuria | 240 | 1:00 | 231 | 7:00 | Agargaon | 225 | 9:00 | 214 | 11:00
| Bogra | 228 | 1:00 | 220 | 9:00 | Barisal | 252 | 13:00 | 238 | 18:30
| Rajshahi | 233 | 18:00 | 220 | 13:00 | Bhola 225 MW | 255 | 6:00 | 240 | 19:00
| Khulna South | 233 | 8:00 | 209 | 20:00 | AKSML | 229 | 13:00 | 221 | 1:00
| Rampura | 227 | 1:00 | 220 | 13:00 | BSRM | 231 | 22:00 | 221 | 11:00
| Haripur | 226 | 4:00 | 219 | 11:00 | Bibiyana | 243 | 22:00 | 237 | 11:00
| Hasnabad | 226 | 22:00 | 215 | 11:00 | Bhulta | 229 | 1:00 | 220 | 11:00
| Shyampur | 225 | 22:00 | 220 | 11:00 | Ashuganj (S) | 234 | 22:00 | 228 | 16:00
| Aminbazar | 225 | 1:00 | 222 | 2:00 | Kaliakoir | 227 | 19:30 | 216 | 11:00
| Tongi | 223 | 21:00 | 213 | 9:00 | GPH | 231 | 12:00 | 221 | 4:00
| Comilla (N) | 230 | 19:30 | 223 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 130 | 11:00 | Madanhat | 138 | 0.5 | 132 | 0.125
| Munsiganj | 134 | 1:00 | 129 | 11:00 | Hathazari | 136 | 0.5 | 131 | 0.29167
| Sonargaon | 136 | 20:00 | 130 | 9:00 | Khulshi | 138 | 0.5 | 130 | 0.66667
| Shyampur | 135 | 22:00 | 128 | 16:00 | Halishahar | 138 | 0.54167 | 131 | 0.16667
| Bhulta | 131 | 2:00 | 123 | 11:00 | Baraulia | 137 | 0.5 | 132 | 0.375
| Madanganj | 133 | 1:00 | 127 | 12:00 | Sikalbaha | 140 | 0.83333 | 132 | 0.45833
| Shitalakhya | 141 | 20:00 | 128 | 11:00 | Dohazari | 136 | 0.5 | 129 | 0.66667
| Rahim steal | 134 | 18:30 | 130 | 11:00 | Cox'sbazar | 128 | 0.5 | 109 | 0.20833
| Matuail | 135 | 1:00 | 130 | 11:00 | Chandraghona | 137 | 0.5 | 130 | 0.16667
| Ghorasal | 138 | 21:00 | 135 | 1:00 | Kaptai | 138 | 0.29167 | 130 | 0.375
| Narsinghdi | 137 | 20:00 | 130 | 16:00 | A. Khaer Stl. | 134 | 0.54167 | 130 | 0.29167
| Haripur (SBU) | 136 | 4:00 | 130 | 11:00 | Bakulia | 139 | 0.8125 | 132 | 0.45833
| Sreenagar |  |  |  |  | Julda | 139 | 0.5 | 135 | 0.041667
| Ullon | 135 | 5:00 | 126 | 14:00 | TK Chemical | 138 | 0.54167 | 132 | 0.25
| Hasnabad | 137 | 19:30 | 127 | 10:00 | Modern Steel
| Magbazar | 135 | 5:00 | 125 | 15:00 | Shahmirpur | 140 | 0.8125 | 133 | 0.16667
| Maniknagar | 135 | 22:00 | 125 | 11:00 | Khagrachhari | 137 | 0.54167 | 130 | 0.041667
| Bangabhaban | 135 | 22:00 | 125 | 11:00 | Matarbari | 132 | 0.5 | 117 | 0.041667
| Narinda | 135 | 22:00 | 125 | 11:00 | Baroiar Hat | 136 | 0.5 | 129 | 0.041667
| Dhanmondi | 135 | 5:00 | 126 | 14:00 | Rangamati | 137 | 0.8125 | 130 | 0.083333
| Lalbag | 136 | 20:00 | 124 | 11:00 | Goalpara S/S | 139 | 8:00 | 124 | 20:00
| Madartek | 135 | 6:00 | 127 | 11:00 | Khulna Central S/S | 138 | 8:00 | 123 | 20:00
| Dhaka University | 135 | 7:00 | 126 | 15:00 | Noapara | 134 | 8:00 | 120 | 0.83333
| Aftabnagar | 135 | 1:00 | 127 | 11:00 | Jessore | 128 | 8:00 | 112 | 0.83333
| Fatullah | 135 | 22:00 | 129 | 11:00 | Benapol | 129 | 8:00 | 111 | 0.83333
| Nawabganj | 129 | 1:00 | 123 | 11:00 | Jhenida | 124 | 8:00 | 105 | 0.83333
| Mirpur | 135 | 1:00 | 127 | 11:00 | Bottail | 129 | 0.29167 | 120 | 0.83333
| Kalyanpur | 136 | 1:00 | 128 | 11:00 | G.K Project | 138 | 18:00 | 132 | 0.83333
| Gulshan | 134 | 1:00 | 126 | 11:00 | Faridpur | 134 | 0.16667 | 126 | 0.83333
| Uttara | 134 | 20:00 | 126 | 11:00 | Madaripur | 141 | 0.20833 | 130 | 0.79167
| Uttara New | 135 | 22:00 | 126 | 11:00 | Shariyatpur S/S | 138 | 0.125 | 130 | 0.79167
| Kamrangirchar | 136 | 20:00 | 124 | 11:00 | Gopalganj | 141 | 0.375 | 131 | 0.91667
| Savar | 136 | 22:00 | 127 | 10:00 | Bagerhat | 135 | 8:00 | 120 | 0.8125
| Bhasantec | 137 | 22:00 | 128 | 9:00 | Mongla | 136 | 0.33333 | 119 | 0.83333
| Agargaon | 138 | 22:00 | 129 | 9:00 | Satkhira | 137 | 8;00 | 119 | 0.83333
| Satmosjid | 138 | 22:00 | 129 | 3:00 | Gallamari | 138 | 8:00 | 124 | 0.83333
| Tongi | 139 | 21:00 | 131 | 7:00 | Magura | 122 | 8:00 | 104 | 21:00
| Kabirpur | 136 | 1:00 | 129 | 11:00 | Narail | 122 | 0.33333 | 103 | 20:00
| Basundhara | 137 | 20:00 | 127 | 11:00 | Chuadanga | 117 | 8:00 | 94 | 0.83333
| Manikganj | 141 | 22:00 | 131 | 8:00 | Borguna | 140 | 0.375 | 127 | 0.77083
| Joydevpur | 138 | 20:00 | 127 | 11:00 | Barisal(N) | 142 | 9:00 | 132 | 0.77083
| New Tongi | 137 | 21:00 | 130 | 9:00 | Barisal (S) | 139 | 7:00 | 131 | 0.79167
| Kodda | 138 | 19:00 | 127 | 7:00 | Patuakhali(S) | 139 | 8:00 | 127 | 18:30
| Dhamrai | 134 | 1:00 | 128 | 16:00 | Bhandaria | 138 | 0.125 | 126 | 0.95833
| Rajendrapur | 137 | 18:30 | 124 | 9:00 | Ishurdi | 136 | 0.125 | 130 | 0.83333
| Valuka | 129 | 1:00 | 117 | 18:30 | Ruppur Paromanobik | 135 | 0.041667 | 131 | 0.8125
| Tangail | 133 | 1:00 | 126 | 16:00 | Natore | 136 | 17:00 | 130 | 9:00
| Mymensing | 132 | 1:00 | 122 | 18:30 | Bogra | 136 | 18:00 | 128 | 7:00
| Kishorganj | 134 | 8:00 | 126 | 16:00 | Noagaon | 130 | 18:00 | 120 | 9:00
| Netrokona | 131 | 1:00 | 118 | 18:30 | Rajshahi | 135 | 17:00 | 129 | 12:00
| Jamalpur | 139 | 22:00 | 124 | 6:00 | Rajshahi New | 137 | 18:00 | 129 | 12:00
| Sherpur | 137 | 22:00 | 120 | 7:00 | C.Nawabganj | 134 | 18:00 | 125 | 13:00
| Srimongal | 140 | 1:00 | 137 | 15:00 | Amnura | 133 | 17:00 | 126 | 7:00
| Shahjibazar | 139 | 4:00 | 134 | 18:30 | Pabna | 135 | 3:00 | 129 | 21:00
| Fenchuganj | 139 | 1:00 | 136 | 16:00 | Shahjadpur | 141 | 5:00 | 134 | 9:00
| Khulawara | 139 | 1:00 | 136 | 15:00 | Serajganj | 133 | 1:00 | 127 | 9:00
| Sylhet | 137 | 21:00 | 134 | 15:00 | Niyamatpur | 126 | 16:00 | 115 | 9:00
| Chatak | 136 | 1:00 | 133 | 15:00 | Joypurhat | 130 | 18:00 | 120 | 7:00
| Sunamganj | 136 | 1:00 | 132 | 18:00 | Sherpur(Bogura) | 136 | 1:00 | 128 | 9:00
| Biani Bazar | 138 | 1:00 | 132 | 18:30 | Mohastangor | 135 | 1:00 | 127 | 7:00
| Comilla(s) | 130 | 9:00 | 122 | 18:30 | Bangura | 135 | 15:00 | 130 | 19:00
| Comilla(n) | 139 | 19:30 | 134 | 2:00 | Rangpur | 136 | 1:00 | 124 | 9:00
| Chandpur | 142 | 9:00 | 133 | 18:00 | Lalmonirhat | 135 | 1:00 | 123 | 9:00
| Feni | 138 | 20:00 | 129 | 18:00 | Saidpur | 134 | 1:00 | 123 | 9:00
| Chowmuhani | 135 | 19:00 | 128 | 2:00 | Purbasadipur | 133 | 2:00 | 121 | 19:00
| Ashuganj | 141 | 20:00 | 135 | 15:00 | Thakurgaon | 132 | 3:00 | 120 | 19:00
| Daudkandi | 134 | 19:30 | 129 | 2:00 | Palashbari | 134 | 1:00 | 125 | 9:00
| B.Baria | 138 | 20:00 | 130 | 15:00 | Barapukuria | 140 | 1:00 | 131 | 7:00

## L-Curve
Date | 2021-03-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 38 | 7768 | 3602 | 11370 |  |  |  | QF-LDC-11
0:30 | 79 | 7331 | 3505.5 | 10836.5 | Date: | 2021-03-31
1:00 | 120 | 6894 | 3409 | 10303
1:30 | 156 | 6752.5 | 3391.5 | 10144
2:00 | 192 | 6611 | 3374 | 9985
2:30 | 198 | 6535.5 | 3311 | 9846.5 | [5 empty] | Gen. at Eve. Peak | 12403 | 12403 MW (19:30 )
3:00 | 204 | 6460 | 3248 | 9708 | [6 empty] | 19:30
3:30 | 186 | 6398 | 3142.5 | 9540.5 | [5 empty] | Gen. at Day Peak | 9878 | 9878 MW (12:00 )
4:00 | 168 | 6336 | 3037 | 9373 | [6 empty] | 12:00
4:30 | 144 | 6303.5 | 3032.5 | 9336 | [5 empty] | Highest Generation | 12403
5:00 | 120 | 6271 | 3028 | 9299 | [6 empty] | 19:30
5:30 | 124 | 6215 | 2964 | 9179
6:00 | 128 | 6159 | 2900 | 9059
6:30 | 68 | 6157 | 2905 | 9062
7:00 | 8 | 6155 | 2910 | 9065
7:30 | 6 | 6184.5 | 2947 | 9131.5
8:00 | 4 | 6214 | 2984 | 9198
8:30 | 92 | 6249.5 | 3032 | 9281.5
9:00 | 180 | 6285 | 3080 | 9365
9:30 | 186 | 6399 | 3071 | 9470
10:00 | 192 | 6513 | 3062 | 9575
10:30 | 207 | 6576.5 | 3074 | 9650.5
11:00 | 222 | 6640 | 3086 | 9726
11:30 | 175 | 6634 | 3168 | 9802
12:00 | 128 | 6628 | 3250 | 9878
12:30 | 104 | 6839 | 3270.5 | 10109.5
13:00 | 80 | 7050 | 3291 | 10341
13:30 | 115 | 7034.5 | 3325.5 | 10360
14:00 | 150 | 7019 | 3360 | 10379
14:30 | 235 | 7040 | 3405.5 | 10445.5
15:00 | 320 | 7061 | 3451 | 10512
15:30 | 336 | 7177 | 3475 | 10652
16:00 | 352 | 7293 | 3499 | 10792
16:30 | 351 | 7360 | 3464 | 10824
17:00 | 350 | 7427 | 3429 | 10856
17:30 | 373 | 7323.5 | 3426.5 | 10750
18:00 | 396 | 7220 | 3424 | 10644
18:30 | 224 | 7754 | 3622.5 | 11376.5
19:00 | 52 | 8288 | 3821 | 12109
19:30 | 20 | 8461 | 3942 | 12403
20:00 | 18 | 8384 | 3919 | 12303 |  |  |  | Executive Engineer
20:30 | 33 | 8392 | 3904.5 | 12296.5 |  |  |  | Network Operation Division
21:00 | 48 | 8400 | 3890 | 12290
21:30 | 48 | 8378.5 | 3831 | 12209.5
22:00 | 48 | 8357 | 3772 | 12129 |  |  |  |  | Page 6 of 7
22:30 | 44 | 8157 | 3712 | 11869
23:00 | 40 | 7957 | 3652 | 11609
23:30 | 39 | 7862.5 | 3627 | 11489.5
24:00 | 38 | 7768 | 3602 | 11370
12403 MW (19:30 )
9878 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-03-31 |  | Energy | 253707099
[11 empty] | 2021-03-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4807 | 836 | 1691 | 3424 | 730 | 100 | 83 | 0 | 154 | 0
0:30 | 4759 | 838 | 1615 | 2812.5 | 730 | 85 | 75.5 | 0 | 149 | 0 | Date: | 2021-03-31
1:00 | 4711 | 840 | 1539 | 2201 | 730 | 70 | 68 | 0 | 144 | 0
1:30 | 4703.5 | 841.5 | 1534.5 | 2056.5 | 730 | 70 | 68 | 0 | 140 | 0 | [7 empty] | Total Energy | 253.7071 | Total Energy Gen 253.707 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 253.707 MKWHr
2:00 | 4696 | 843 | 1530 | 1912 | 730 | 70 | 68 | 0 | 136 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4705 | 840.5 | 1529.5 | 1780.5 | 720 | 70 | 68 | 0 | 133 | 0 | [7 empty] | Energy Requirement | 253.7071
3:00 | 4714 | 838 | 1529 | 1649 | 710 | 70 | 68 | 0 | 130 | 0
3:30 | 4704 | 837.5 | 1518 | 1521 | 695 | 70 | 68 | 0 | 127 | 0 | [6 empty] | Shortage
4:00 | 4694 | 837 | 1507 | 1393 | 680 | 70 | 68 | 0 | 124 | 0
4:30 | 4700.5 | 837 | 1507 | 1350.5 | 680 | 70 | 68 | 0 | 123 | 0
5:00 | 4707 | 837 | 1507 | 1308 | 680 | 70 | 68 | 0 | 122 | 0
5:30 | 4685 | 777.5 | 1493.5 | 1286 | 680 | 70 | 68 | 0 | 119 | 0
6:00 | 4663 | 718 | 1480 | 1264 | 680 | 70 | 68 | 0 | 116 | 0
6:30 | 4687.5 | 718 | 1468 | 1274.5 | 665 | 70 | 68 | 0 | 109 | 2 |  |  |  |  | Coal
7:00 | 4712 | 718 | 1456 | 1285 | 650 | 70 | 68 | 0 | 102 | 4
7:30 | 4703.5 | 717.5 | 1396.5 | 1436 | 635 | 70 | 68 | 0 | 95 | 10 |  |  |  | Oil |  |  |  | ,
8:00 | 4695 | 717 | 1337 | 1587 | 620 | 70 | 68 | 0 | 88 | 16
8:30 | 4679.5 | 777 | 1348 | 1643.5 | 600 | 70 | 59 | 0 | 80 | 24.5
9:00 | 4664 | 837 | 1359 | 1700 | 580 | 70 | 50 | 0 | 72 | 33
9:30 | 4652 | 786 | 1419 | 1831.5 | 565 | 70 | 25 | 0 | 65 | 56.5
10:00 | 4640 | 735 | 1479 | 1963 | 550 | 70 | 0 | 0 | 58 | 80
10:30 | 4663.5 | 750 | 1454 | 2003.5 | 550 | 70 | 0 | 0 | 69 | 90.5
11:00 | 4687 | 765 | 1429 | 2044 | 550 | 70 | 0 | 0 | 80 | 101
11:30 | 4579 | 784 | 1457.5 | 2182 | 550 | 70 | 0 | 0 | 86 | 93.5
12:00 | 4471 | 803 | 1486 | 2320 | 550 | 70 | 0 | 0 | 92 | 86
12:30 | 4440 | 820 | 1449 | 2593.5 | 555 | 70 | 1 | 0 | 93 | 88
13:00 | 4409 | 837 | 1412 | 2867 | 560 | 70 | 2 | 0 | 94 | 90
13:30 | 4409 | 837 | 1412 | 2867 | 560 | 70 | 2 | 0 | 94 | 90
14:00 | 4409 | 837 | 1412 | 2867 | 560 | 70 | 2 | 0 | 94 | 90
14:30 | 4413 | 837 | 1430.5 | 2875 | 580 | 70 | 41.5 | 0 | 104 | 75.5
15:00 | 4417 | 837 | 1449 | 2883 | 600 | 70 | 81 | 0 | 114 | 61
15:30 | 4455.5 | 837 | 1446.5 | 2970.5 | 620 | 70 | 89 | 0 | 115 | 48.5
16:00 | 4494 | 837 | 1444 | 3058 | 640 | 70 | 97 | 0 | 116 | 36
16:30 | 4447 | 837 | 1446.5 | 3145.5 | 630 | 70 | 101.5 | 0 | 122 | 24.5
17:00 | 4400 | 837 | 1449 | 3233 | 620 | 70 | 106 | 0 | 128 | 13
17:30 | 4400.5 | 837 | 1410 | 3122.5 | 605 | 86 | 147 | 0 | 135 | 7
18:00 | 4401 | 837 | 1371 | 3012 | 590 | 102 | 188 | 0 | 142 | 1
18:30 | 4497 | 837 | 1438 | 3375 | 630 | 102.5 | 341.5 | 0 | 155 | 0.5
19:00 | 4593 | 837 | 1505 | 3738 | 670 | 103 | 495 | 0 | 168 | 0
19:30 | 4493 | 837 | 1495 | 4028 | 740 | 103 | 543 | 0 | 164 | 0
20:00 | 4323 | 836 | 1447 | 4141 | 740 | 104 | 544 | 0 | 168 | 0
20:30 | 4327.5 | 836 | 1459.5 | 4108.5 | 745 | 104 | 551 | 0 | 165 | 0
21:00 | 4332 | 836 | 1472 | 4076 | 750 | 104 | 558 | 0 | 162 | 0
21:30 | 4362 | 836.5 | 1477 | 4049.5 | 750 | 102 | 470.5 | 0 | 162 | 0
22:00 | 4392 | 837 | 1482 | 4023 | 750 | 100 | 383 | 0 | 162 | 0
22:30 | 4449.5 | 837 | 1580.5 | 3723.5 | 750 | 104 | 264.5 | 0 | 160 | 0
23:00 | 4507 | 837 | 1679 | 3424 | 750 | 108 | 146 | 0 | 158 | 0
23:30 | 4657 | 836.5 | 1685 | 3424 | 740 | 104 | 114.5 | 0 | 156 | 0 | Max Temp. in Dhaka |  | 35.3° C
24:00 | 4807 | 836 | 1691 | 3424 | 730 | 100 | 83 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 253.707 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 253.707 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-03-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [17 empty] | 32 |  | 33 | 33 | 34 | 34 | 30 | 38 | 30 | 325615
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 7 |  | 18 | 18 | 25 | 25 | 25 | 25 | 25 | 406560
| Teknaf 20MW PP (Solartech) | [7 empty] | 6 | 7 | 14 | 17 |  | 15 |  | 6 | 4 | 1 | [9 empty] | 52380
6 | Sikalbaha 225MW CCPP (Gas) | 80 | 62 | 65 | 61 | 60 | 60 | 61 | 60 | 60 | [16 empty] | 0 | 636157
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2907560
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 34 | [8 empty] | 44 |  | 85 | 85 | 85 | 85 | 85 | 85 | 79 | 1128347
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [20 empty] | 50 | 50 | 50 |  |  | 0 | 144840
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 90 | 90 | 90 | 100 | 95 | 73 | 73 | 73 | 73 | 120 | 118 | 150 | 145 | 120 | 185 | 185 | 175 | 73 |  | 185 | 185 | 175 | 175 | 175 | 175 | 180 | 3211000
17 | Siddhirganj 335 MW CCPP | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 218 | 216 | 218 | 215 | 213 | 214 | 212 | 220 | 219 |  | 217 | 219 | 223 | 224 | 221 | 221 | 220 | 5374057
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 | [7 empty] | 5 | 45 | 45 | 47 | 106 | 147 | 150 | 150 | 150 | 167 |  | 264 | 280 | 300 | 298 | 298 | 145 | 0 | 2571817
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4126500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7139791
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 2145262
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913438
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 26 | 23 | 23 | 26 | 23 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 23 | 23 | 23 | 26 | 26 | 26 | 465408
33 | Ashuganj 225 MW CCPP | 214 | 214 | 213 | 212 | 212 | 181 | 195 | 180 | 181 | 182 | 191 | 175 | 171 | 162 | 156 | 198 | 210 | 194 |  | 209 | 209 | 217 | 214 | 209 | 216 | 219 | 4785000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 280 | 265 | 265 | 265 | 275 | 265 | 265 | 270 | 280 | 280 | 280 | 295 |  | 305 | 285 | 265 | 265 | 265 | 265 | 265 | 6674000
| Ashuganj 450 MW CCPP(North) | 290 | 295 | 280 | 265 | 260 | 260 | 275 | 275 | 275 | 275 | 290 | 315 | 275 | 270 | 270 | 270 | 270 | 270 |  | 300 | 280 | 260 | 260 | 260 | 260 | 260 | 6867000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 35 | 20 | 20 | 20 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 316320
36 | Chandpur 150 MW CCPP | 120 | 127 | 121 | 127 | 128 | 127 | 127 | 125 | 126 | 127 | 140 | 140 | 140 | 140 | 141 | 141 | 134 | 143 |  | 141 | 140 | 135 | 147 | 148 | 135 | 140 | 3211880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 348 | 348 | 349 | 349 | 348 | 363 | 357 | 342 | 314 | 307 | 297 | 291 | 292 | 288 | 282 | 286 | 291 |  | 288 | 283 | 281 | 277 | 301 | 321 | 324 | 7719940
40 | Meghnaghat 450 MW CCPP(MPL) | [22 empty] | 60 | 90 | 225 | 225 | 437000
41 | Haripur 360MW CCPP(HPL) | 317 | 321 | 321 | 327 | 328 | 302 | 265 | 231 | 221 | 215 | 208 | 181 | 162 | 162 | 156 | 145 | 145 | 145 |  | 141 | 135 | 122 | 117 | 126 | 131 | 140 | 5058000
42 | RPCL 210MW CCPP | 195 | 195 | 194 | 194 | 194 | 213 | 194 | 173 | 141 | 105 | 105 | 105 | 105 | 103 | 125 | 122 | 143 | 142 |  | 140 | 137 | 136 | 127 | 127 | 127 | 128 | 3514760
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 3 | 6 | 35 | 46 | 48 | 38 | 39 | 31 | 18 | 6 | 1 | [8 empty] | 281730
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 42 | 42 | 42 | 42 | 39 | 39 | 41 | 40 |  | 40 | 40 | 43 | 44 | 44 | 44 | 44 | 993000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 130 | 130 | 129 | 129 | 130 | 130 | 130 | 130 | 132 | 130 | 130 | 130 | 193 | 297 | 295 | 294 | 296 | 297 |  | 294 | 294 | 296 | 295 | 298 | 295 | 295 | 4428000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 77 | 77 | 76 | 77 | 77 | 78 |  | 79 | 79 | 80 | 80 | 79 | 80 | 81 | 1898880
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 150 | 150 | 148 | 148 | 148 | 148 | 148 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 177 | 176 | 176 |  | 176 | 176 | 176 | 176 | 176 | 163 | 163 | 3727500
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [9 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 9 | 9 | 0 |  | 9 | 9 | 9 | 102240
54 | Hobiganj 11MW PP Cofidence-E | [24 empty] | 8 | 8 | 16048
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 47 | 48 | 48 | 50 | 53 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 963600
56 | Shahjahanulla 25 MW PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 380880
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 285 | 280 | 290 | 290 | 310 | 300 | 290 | 305 | 290 | 320 | 290 | 290 | 315 | 310 | 300 | 290 |  | 320 | 320 | 305 | 280 | 270 | 280 | 290 | 7274500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 190 | 190 | 218 |  |  | 15 | 71 |  | 71 | 35 |  | 58 | 69 | 139 | 400 | 5645300
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 40 | 20 | 35 | 35 | 35 | 35 | 35 | 30 |  | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 746273
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 22 | 21 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576480
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 0 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 398832
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | [19 empty] | 19 | 159948
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 17 | 17 | 17 | 17 | 17 | 16 | 364968
63 | Impoprt (Tripura) | 144 | 136 | 130 | 124 | 122 | 116 | 102 | 88 | 72 | 58 | 80 | 92 | 94 | 112 | 114 | 116 | 128 | 142 |  | 168 | 164 | 168 | 162 | 162 | 158 | 154 | 2951040
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 7 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 2 |  | 10 | 15 | 20 | 29 | 35 | 37 | 38 | 483360
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 16 | 19 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 470844
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 154080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 782300
68 | Cumilla 25 MW PP (Summit) | 20 | 21 | 21 | 21 | 21 | 21 |  | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 15 | 18 | 18 | 18 |  | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 428540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 25 | 25 | 20 | 25 | 25 | 25 | 25 | 25 | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 |  | 20 | 28 | 28 | 28 | 28 | 28 | 28 | 600660
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794700
72 | Rupganj 33 MW PP(Summit) | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 25 | 16 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 745000
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 95 | 95 | 95 | 93 | 95 | 95 | 96 | 96 | 93 | 93 | 96 |  | 99 | 100 | 100 | 100 | 96 | 96 | 96 | 2277000
| Feni Lanka Power | [19 empty] | 70 | 92 | 100 | 100 | 64 |  | 0 | 308940
| Chowmuhani 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 26 | 26 | 26 | 26 | 38 | 65 | 65 | 65 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1717800
| Manikgonj 162MW PP(MPGL) | [9 empty] | 1 | 17 | 53 | 108 | 108 | 108 | 141 | 144 | 108 |  | 119 | 144 | 144 | 144 | 144 | 144 | 35 | 1641600
77 | Siddhirganj 100 PP(Dutch Bangla) | 30 | [8 empty] | 1 | 7 | 22 | 94 | 100 | 100 | 100 | 100 | 70 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1247117
78 | Gazipur 52 MW PP | [12 empty] | 26 | 50 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 |  | 0 | 483360
79 | Kodda 150MW PP | [8 empty] | 16 | [5 empty] | 32 | 48 | 48 | 48 |  | 147 | 147 | 147 | 147 | 98 | 32 | 0 | 921120
80 | Jamalpur 95 MW PP(Powerpac) | 48 | 48 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 50 | 56 | 57 | 57 | 57 | 668160
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 30 | 52 | 52 | 52 | 52 | 25 | 8 | 253608
| Gazipur 100 MW PP | [8 empty] | 33 | 70 | 70 | 70 | 95 | 70 | 70 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 52 | 17 | 1408080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 4 | 2 | 4 | 3 | 3 | 1 | 1 | [9 empty] | 25080
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299475
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 64 | 48 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 40 | 27 | 55 | 48 | 47 | 47 | 40 | 30 |  | 30 | 25 | 15 | 15 | 10 |  | 0 | 716904
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 20 | 24 |  | 57 | 60 | 60 | 60 | 50 |  | 0 | 289452
86 | Meghnaghat CCPP(Summit) | 260 | 265 | 235 | 240 | 240 | 235 | 265 | 270 | 255 | 250 | 235 | 230 | 275 | 265 | 260 | 265 | 260 | 265 |  | 260 | 255 | 260 | 265 | 250 | 265 | 265 | 6086720
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 8 | 61 | 66 | 66 | 66 | 97 | 100 |  | 100 | 100 | 100 | 100 | 100 | 78 | 55 | 1032000
| Meghnaghat 104 MW PP (OPCL) | 104 | 57 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 37 | 69 | 78 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1914240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 50 | 50 | 80 | 80 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 90 | 60 |  | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 1825680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 20 | 32 | 32 | 32 | 32 | 32 | 50 |  | 102 | 102 | 102 | 102 | 102 | 7 | 7 | 649296
95 | Patenga 50MW PP (Baraka) | 19 | [7 empty] | 11 | 24 | 24 | 26 | 38 | 43 | 42 | 39 | 42 | 45 |  | 45 | 45 | 45 | 43 | 39 | 41 | 46 | 624480
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 18 | 32 |  | 82 | 91 | 91 | 83 | 50 |  | 0 | 360000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 1029172
100 | Manikganj 55 MW PP (Northern) | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 874175
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 110 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3601800
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | [9 empty] | 10700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1306440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 60 | 60 | 24 |  |  |  | 5 | 103 | 130 | 130 | 130 | 163 | 191 | 190 | 190 | 181 | 181 | 181 |  | 190 | 200 | 200 | 200 | 200 | 193 | 200 | 3139200
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 85 | 101 |  |  |  | 0 | 133550
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 130 | 131 | 130 | 130 | 130 | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 131 |  | 143 | 149 | 149 | 149 | 149 | 149 | 149 | 3476880
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2397120
116 | Chandpur 200MW (Desh energy) | 194 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 197 | 150 | 150 | 151 | 180 | 180 | 100 |  | 94 | 100 | 122 | 150 | 150 | 150 | 150 | 4130400
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 331 | 331 | 331 | 331 | 331 | 331 | 328 | 331 | 331 | 367 | 374 | 365 | 367 | 313 | 387 | 410 | 366 | 394 |  | 400 | 373 | 304 | 306 | 350 | 366 | 366 | 8418000
| Jamalpur 115 MW PP (United) | [11 empty] | 8 | 65 | 45 | 52 | 77 | 113 | 75 |  | 115 | 115 | 115 | 115 | 115 | 45 | 8 | 1021200
| Anwara 300 MW PP (United) | 16 | [8 empty] | 16 | 16 | 115 | 115 | 70 | 70 | 106 | 140 | 108 |  | 158 | 195 | 195 | 195 | 250 | 302 | 256 | 2070000
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2439360
| Anlima Energy Ltd. | 116 | 116 | 116 | 53 | 17 | 17 | 17 | 17 | 72 | 92 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2289545
| Bhairob 54.5 MW | [19 empty] | 28 | [5 empty] | 0 | 37080
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 4 | 14 | 25 | 27 | 30 | 27 | 25 | 18 | 11 | 4 | 0 | [8 empty] | 180001
120 | Eastern Zone Total | 6894 | 6611 | 6460 | 6336 | 6271 | 6159 | 6155 | 6214 | 6285 | 6513 | 6640 | 6628 | 7050 | 7019 | 7061 | 7293 | 7427 | 7220 |  | 8288 | 8461 | 8384 | 8400 | 8357 | 7957 | 7768 | 171719797
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 83 |  | 83 | 83 | 70 | 79 | 83 | 83 | 83 | 1848000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 4 | 4 | 6 | 18 | 18 | 4 | 4 | 48000
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 94 | 93 | 93 | 92 | 92 | 92 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1748640
130
131
132 | United Payra Power Ltd. | 17 | 17 | [23 empty] | 0 | 36600
133 | Bhola Nutan Biddut BD LTD (GAS) | [8 empty] | 38 | 38 | 37 | 38 | 51 | 51 | 52 | 51 | 64 | 66 |  | 67 | 67 | 67 | 68 | 52 | 67 | 68 | 864382
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 16 | 16 | [11 empty] | 16 |  | 23 | 48 | 80 | 80 | 80 | 64 | 64 | 65376
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 92 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 92 | 92 | 92 | 92 | 92 | 90 | 92 | 95 | 96 |  | 97 | 75 | 74 | 74 | 73 | 73 | 73 | 2141300
| Bhola 225 MW CCPP | 61 | 62 | 65 | 66 | 65 | 58 | 67 | 56 | 62 | 66 | 66 | 64 | 52 | 65 | 66 | 66 | 51 | 66 |  | 65 | 67 | 63 | 54 | 42 | 63 | 65 | 1536000
140 | Bhola 33 MW PP (Venture) | 31 | 29 | 29 | 27 | 22 | 21 | 18 | 17 | 17 | 17 | 13 | 16 | 19 | 17 | 19 | 22 | 19 | 20 |  | 26 | 28 | 29 | 31 | 33 | 33 | 33 | 552379
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 48 | 100 | 100 | 100 | 100 | 100 | 100 | 576960
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 24 | [5 empty] | 32 | 24 | 8 |  |  |  | 16 | 16 | 16 | 16 | 16 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 372375
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 9 | 11 |  | 11 | [6 empty] | 22656
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 840 | 843 | 838 | 837 | 837 | 718 | 718 | 717 | 837 | 735 | 765 | 803 | 837 | 837 | 837 | 837 | 837 | 837 |  | 837 | 837 | 836 | 836 | 837 | 837 | 836 | 19698181
147 | Bheramara 410 MW CCPP | 340 | 350 | 370 | 350 | 350 | 350 | 390 | 390 | 380 | 370 | 360 | 345 | 330 | 320 | 315 | 300 | 280 | 270 |  | 260 | 250 | 240 | 230 | 230 | 230 | 230 | 7868160
148 | Payra 1320 MW | 580 | 580 | 560 | 530 | 530 | 530 | 500 | 470 | 430 | 400 | 400 | 400 | 410 | 430 | 450 | 490 | 470 | 440 |  | 520 | 590 | 590 | 600 | 600 | 600 | 580 | 13024000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3664800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 46 | 50 | 50 | 50 | 50 |  |  | 193619
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 100 | 100 | 115 | 120 | 126 | 113 | 114 | 125 | 119 | 101 | 93 |  | 94 | 93 | 88 | 75 | 75 | 75 | 75 | 2530000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 178 | 178 | 178 | 186 | 204 | 204 | 204 | 192 | 157 | 164 | 159 | 169 | 155 | 154 | 164 | 170 | 158 | 158 |  | 172 | 162 | 155 | 144 | 144 | 145 | 147 | 4264045
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 172 | 175 | 174 | 175 | 175 | 174 | 176 | 173 | 195 | 193 | 187 | 190 | 170 | 168 | 172 | 181 | 176 | 176 |  | 180 | 185 | 186 | 181 | 175 | 176 | 177 | 4513745
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 364 | 361 | 355 | 334 | 361 | 361 | 364 | 322 | 330 | 360 | 366 | 400 | 355 | 345 | 384 | 393 | 394 | 372 |  | 405 | 415 | 397 | 380 | 366 | 395 | 385 | 8940310
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 30 | 34 | 34 | 34 |  |  |  | 99730
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 484560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 205992
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [12 empty] | 2 | 3 | [5 empty] | 37 | 39 | 39 | 41 |  |  |  | 107426
168 | Santahar 50 MW Peaking PP | [17 empty] | 16 |  | 35 | 34 | 33 | 33 | 32 |  |  | 133708
169 | Natore 52 MW PP (Rajlanka) | 8 | [6 empty] | 8 | 8 | 8 | 8 | 28 | 43 | 52 | 52 | 52 | 52 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 635040
170 | Chapainawabganj 100 MW Peaking PP | [13 empty] | 48 | 49 | 49 | 49 | 60 |  | 100 | 100 | 100 | 100 | 100 | 25 | 0 | 636272
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 35 |  |  |  |  | 24 | 35 | 56 | 70 | 83 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1636800
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 35 |  |  |  |  | 35 | 35 | 70 | 70 | 95 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1842336
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 39 | 6 | [5 empty] | 34 | 34 | 70 | 70 | 98 | 108 | 107 | 110 | 113 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1668480
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 1 | 2 | 2 | 5 | 5 | 5 | 4 | 2 | 1 | 1 | 0 | [8 empty] | 27430
178
178